## Cover
Evergy Services, Inc. (ESI) Evaluation, Measurement, and Verification Report – Commercial & Industrial Databook
Prepared for:
Submitted by:
Guidehouse, Inc.
1375 Walnut Street, Suite 100
Boulder, CO 80302
Tel: +1.303.728.2500
Guidehouse.com
Reference No.: 213765
2022-06-30
This deliverable was prepared by Guidehouse Inc. for the sole use and benefit of, and pursuant to a client relationship exclusively with Evergy Services, Inc. (“Client”). The work presented in this deliverable represents Guidehouse’s professional judgement based on the information available at the time this report was prepared. The information in this deliverable may not be relied upon by anyone other than Client. Accordingly, Guidehouse disclaims any contractual or other responsibility to others based on their access to or use of the deliverable.

## Program to Date - C&I Portfolio
Program to Date Energy Savings at the Customer Meter by Territory
Sector | Gross |  |  | Net
| Reported Savings (kWh) | Verified Savings (kWh) | Realization Rate (%) | MEEIA Cycle 3 3-Year Target (kWh) | Verified 3 -Year Savings (kWh) | Percentage of MEEIA 3-Year Target Achieved
Evergy Metro | 52747009.5031 | 55215486.3261 | 104.7% | 103671719.8545 | 47106255.9502 | 45.44%
Evergy MO West | 48705354.9659 | 49603370.5136 | 101.8% | 77133112.9189 | 42404151.1497 | 54.98%
Evergy TOTAL | 101452364.469 | 104818856.8397 | 103.3% | 180804832.7734 | 89510407.0999 | 49.51%
Program to Date Demand Savings at the Customer Meter by Territory
Sector | Gross |  |  | Net
| Reported Savings (kW) | Verified Savings (kW) | Realization Rate (%) | MEEIA Cycle 3 3-Year Target (kW) | Verified 3 -Year Savings (kW) | Percentage of MEEIA 3-Year Target Achieved
Evergy Metro | 10253.4358 | 10240.0274 | 99.87% | 13538.2057 | 8711.672 | 64.35%
Evergy MO West | 9670.6371 | 8381.4882 | 86.67% | 9328.0181 | 7181.4767 | 76.99%
Evergy TOTAL | 19924.0729 | 18621.5156 | 93.46% | 22866.2238 | 15893.1486 | 69.5%

## PY2 - C&I Portfolio
PY2 Energy Savings at the Customer Meter by Territory
Sector | Gross |  |  | Net
| Reported Savings (kWh) | Verified Savings (kWh) | Realization Rate (%) | MEEIA Cycle 3 3-Year Target (kWh) | Verified 3 -Year Savings (kWh) | Percentage of MEEIA 3-Year Target Achieved
Evergy Metro | 24574932.0528 | 24950785.3716 | 101.5% | 103671719.8545 | 20100168.8632 | 19.39%
Evergy MO West | 29080142.1888 | 28972042.144 | 99.63% | 77133112.9189 | 23413060.3815 | 30.35%
Evergy TOTAL | 53655074.2416 | 53922827.5156 | 100.5% | 180804832.7734 | 43513229.2447 | 24.07%
PY2 Demand Savings at the Customer Meter by Territory
Sector | Gross |  |  | Net
| Reported Savings (kW) | Verified Savings (kW) | Realization Rate (%) | MEEIA Cycle 3 3-Year Target (kW) | Verified 3 -Year Savings (kW) | Percentage of MEEIA 3-Year Target Achieved
Evergy Metro | 4918.2433 | 4576.3366 | 93.05% | 13538.2057 | 3689.0907 | 27.25%
Evergy MO West | 6156.4493 | 4830.0069 | 78.45% | 9328.0181 | 3906.7367 | 41.88%
Evergy TOTAL | 11074.6926 | 9406.3435 | 84.94% | 22866.2238 | 7595.8274 | 33.22%

## PY2 - Evergy Metro
Evergy Services, Inc. (ESI) Evaluation, Measurement, and Verification Report – Commercial & Industrial Databook
Overall Portfolio: Evergy Metro Data Tables
Data is sourced to Guidehouse analysis unless otherwise noted.
Energy Savings at the Customer Meter – PY2
Sector | Program |  | Gross |  |  | Net
|  | Reported Savings (kWh) | Verified Savings (kWh) | Realization Rate (%) | MEEIA 3-Year Target (kWh) | Verified Savings (kWh) | % of MEEIA 3-Year Target Achieved
Commercial & Industrial EE Programs | Business ESP - Standard | 11162365 | 10386880 | 93.05% | 53977377.4297 | 8216022.08 | 15.22%
| Business ESP - Custom | 13412567.0528 | 14563905.3716 | 108.6% | 30239803.0328 | 11884146.7832 | 39.3%
| Process Efficiency | 0 | 0 | N/A | 19454539.392 | 0 | 0%
Educational Programs | Business Online Energy Audit | Online Energy Audit programs are not part of MEEIA Targets for Energy or Demand Savings.
Evergy Metro TOTAL |  | 24574932.0528 | 24950785.3716 | 101.5% | 103671719.8545 | 20100168.8632 | 19.39%
Note: Gross realization rates are the ratio of verified gross savings to reported gross savings and indicates the accuracy of deemed savings tracked by Evergy Metro.
Coincident Demand Savings at the Customer Meter – PY2
Sector | Program |  | Gross |  |  | Net
|  | Reported Savings (kW) | Verified Savings (kW) | Realization Rate (%) | MEEIA 3-Year Target (kW) | Verified Savings (kW) | % of MEEIA 3-Year Target Achieved
Commercial & Industrial EE Programs | Business ESP - Standard | 2467 | 1808 | 73.29% | 8522.6148 | 1430.128 | 16.78%
| Business ESP - Custom | 2451.2433 | 2768.3366 | 112.9% | 4833.6325 | 2258.9627 | 46.73%
| Process Efficiency | 0 | 0 | N/A | 181.9584 | 0 | 0%
Educational Programs | Business Online Energy Audit | Online Energy Audit programs are not part of MEEIA Targets for Energy or Demand Savings.
Evergy Metro TOTAL |  | 4918.2433 | 4576.3366 | 93.05% | 13538.2057 | 3689.0907 | 27.25%
Note: Gross realization rates are the ratio of verified gross savings to reported gross savings and indicates the accuracy of deemed savings tracked by Evergy Metro.
Energy Savings at the Customer Meter – Program to Date
Sector | Program |  | Gross |  |  | Net
|  | Reported Savings (kWh) | Verified Savings (kWh) | Realization Rate (%) | MEEIA 3-Year Target (kWh) | Verified Savings (kWh) | % of MEEIA 3-Year Target Achieved
Commercial & Industrial EE Programs | Business ESP - Standard | 27380255.452 | 27851419.5211 | 101.7% | 53977377.4297 | 24981980.0203 | 46.28%
| Business ESP - Custom | 25366754.0511 | 27364066.805 | 107.9% | 30239803.0328 | 22124275.9299 | 73.16%
| Process Efficiency | 0 | 0 | N/A | 19454539.392 | 0 | 0%
Educational Programs | Business Online Energy Audit | Online Energy Audit programs are not part of MEEIA Targets for Energy or Demand Savings.
Evergy Metro TOTAL |  | 52747009.5031 | 55215486.3261 | 104.7% | 103671719.8545 | 47106255.9502 | 45.44%
Note: Gross realization rates are the ratio of verified gross savings to reported gross savings and indicates the accuracy of deemed savings tracked by Evergy Metro.
Coincident Demand Savings at the Customer Meter – Program to Date
Sector | Program |  | Gross |  |  | Net
|  | Reported Savings (kW) | Verified Savings (kW) | Realization Rate (%) | MEEIA 3-Year Target (kW) | Verified Savings (kW) | % of MEEIA 3-Year Target Achieved
Commercial & Industrial EE Programs | Business ESP - Standard | 5382.6497 | 4880.6791 | 90.67% | 8522.6148 | 4379.9 | 51.39%
| Business ESP - Custom | 4870.7861 | 5359.3482 | 110% | 4833.6325 | 4331.772 | 89.62%
| Process Efficiency | 0 | 0 | N/A | 181.9584 | 0 | 0%
Educational Programs | Business Online Energy Audit | Online Energy Audit programs are not part of MEEIA Targets for Energy or Demand Savings.
Evergy Metro TOTAL |  | 10253.4358 | 10240.0274 | 99.87% | 13538.2057 | 8711.672 | 64.35%
Note: Gross realization rates are the ratio of verified gross savings to reported gross savings and indicates the accuracy of deemed savings tracked by Evergy Metro.
NTG Components by Program
Program Name | Free Ridership | Participant Spillover | Non-Participant Spillover | NTGR
Business EER - Standard | 0.245 | 0.021 | 0.015 | 79.1%
Business EER - Custom | 0.239 | 0.04 | 0.015 | 81.6%
Process Efficiency | N/A - Savings not claimed in PY2
Business Online Energy Audit | N/A - Savings not claimed in PY2
Benefit-Cost Ratios by Program and Cost Test – PY2
Sector | Program | Total Resource Cost Test | Societal Cost Test | Utility Cost Test | Participant Cost Test | Rate Impact Measure Test
Guidehouse
Commercial EE Programs | Business ESP - Standard | 0.85802 | 1.0143 | 1.4315 | 1.5421 | 0.51675
| Business ESP - Custom | 0.98473 | 1.1907 | 2.121 | 1.6415 | 0.57553
| Process Efficiency | 0 | 0 | 0 | 0 | 0
Total C&I Sector Level |  | 0.91196 | 1.0919 | 1.7273 | 1.5965 | 0.54551
*Ratios are based on net savings
**Guidehouse performed benefit-cost calculations on the Standard, Custom, and Process Efficiency programs. These programs represent the C&I EE portfolio.
Program Administrative Costs - PY2
Sector | Program | Rebate Costs | Program Admin Costs* | Total Costs | Benefits from Energy and Demand Savings | Total Net Benefits
Commercial EE Programs | Business ESP - Standard | 1023704 | 1394472 | 2418176 | 3461534.8594 | 1043358.8594
| Business ESP - Custom | 1296310 | 1141698 | 2438008 | 5170924.87 | 2732916.87
| Process Efficiency | 0 | 141404 | 141404 | 0 | -141404
Portfolio | Portfolio Total** | 2320014 | 2677574 | 4997588 | 8632459.7294 | 3634871.7294
*Evergy allocates indirect program administrative costs to programs as a percentage of total budget. These costs are not tracked separately from direct program administrative costs and are therefore included in that total.
**Only C&I EE programs inluded, no portfolio-level costs.
Discount Rate Matrix - PY2
MEEIA 3 - Discount Rate Matrix
Benefit Cost Test
TRC | SCT | UCT | PCT | RIM
6.731% | 3% | 6.731% | 10% | 6.731%
Note: The EM&V report applied the following discount rates when calculating net present value.
Benefit-Cost Ratios by Program and Cost Test – PTD ($2021)
Sector | Program | Total Resource Cost Test | Societal Cost Test | Utility Cost Test | Participant Cost Test | Rate Impact Measure Test
Guidehouse
Commercial EE Programs | Business ESP - Standard | 0.95945 | 1.1253 | 1.9272 | 1.5624 | 0.5624
| Business ESP - Custom | 0.94211 | 1.1814 | 2.5471 | 1.3757 | 0.61262
| Process Efficiency | 0 | 0 | 0 | 0 | 0
Total C&I Sector Level |  | 0.94019 | 1.1389 | 2.1397 | 1.4647 | 0.58256
*Ratios are based on net savings
**Guidehouse performed benefit-cost calculations on the Standard, Custom, and Process Efficiency programs. These programs represent the C&I EE portfolio.
Program Administrative Costs - PTD ($2021)
Sector | Program | Rebate Costs | Program Admin Costs* | Total Costs | Benefits from Energy and Demand Savings | Total Net Benefits
Commercial EE Programs | Business ESP - Standard | 2537354.2776 | 2660879.8168 | 5198234.0944 | 10018284.0098 | 4820049.9154
| Business ESP - Custom | 2363089.839 | 1782338.8562 | 4145428.6952 | 10558893.5107 | 6413464.8155
| Process Efficiency | 0 | 273010.4076 | 273010.4076 | 0 | -273010.4076
Portfolio | Portfolio Total** | 4900444.1166 | 4716229.0806 | 9616673.1972 | 20577177.5205 | 10960504.3233
*Evergy allocates indirect program administrative costs to programs as a percentage of total budget. These costs are not tracked separately from direct program administrative costs and are therefore included in that total.
**Only C&I EE programs inluded, no portfolio-level costs.

## PY2 - Evergy MO West
Evergy Services, Inc. (ESI) Evaluation, Measurement, and Verification Report – Commercial & Industrial Databook
Overall Portfolio: Evergy MO West Data Tables
Data is sourced to Guidehouse analysis unless otherwise noted.
Energy Savings at the Customer Meter – PY2
Sector | Program |  | Gross |  |  | Net
|  | Reported Savings (kWh) | Verified Savings (kWh) | Realization Rate (%) | MEEIA 3-Year Target (kWh) | Verified Savings (kWh) | % of MEEIA 3-Year Target Achieved
Commercial & Industrial EE Programs | Business ESP - Standard | 11967648 | 12439712 | 103.9% | 46646197.1989 | 9839812.192 | 21.09%
| Business ESP - Custom | 16644699.1888 | 16081967.144 | 96.62% | 10016241.48 | 13122885.1895 | 131%
| Process Efficiency | 467795 | 450363 | 96.27% | 20470674.24 | 450363 | 2.2%
Educational Programs | Business Online Energy Audit | Online Energy Audit programs are not part of MEEIA Targets for Energy or Demand Savings.
Evergy MO West TOTAL |  | 29080142.1888 | 28972042.144 | 99.63% | 77133112.9189 | 23413060.3815 | 30.35%
Note: Gross realization rates are the ratio of verified gross savings to reported gross savings and indicates the accuracy of deemed savings tracked by Evergy Metro.
Coincident Demand Savings at the Customer Meter – PY2
Sector | Program |  | Gross |  |  | Net
|  | Reported Savings (kW) | Verified Savings (kW) | Realization Rate (%) | MEEIA 3-Year Target (kW) | Verified Savings (kW) | % of MEEIA 3-Year Target Achieved
Commercial & Industrial EE Programs | Business ESP - Standard | 2309 | 1870 | 80.99% | 7513.8897 | 1479.17 | 19.69%
| Business ESP - Custom | 3773.9493 | 2893.6969 | 76.68% | 1586.6804 | 2361.2567 | 148.8%
| Process Efficiency | 73.5 | 66.31 | 90.22% | 227.448 | 66.31 | 29.15%
Educational Programs | Business Online Energy Audit | Online Energy Audit programs are not part of MEEIA Targets for Energy or Demand Savings.
Evergy MO West TOTAL |  | 6156.4493 | 4830.0069 | 78.45% | 9328.0181 | 3906.7367 | 41.88%
Note: Gross realization rates are the ratio of verified gross savings to reported gross savings and indicates the accuracy of deemed savings tracked by Evergy Metro.
Energy Savings at the Customer Meter – Program to Date
Sector | Program |  | Gross |  |  | Net
|  | Reported Savings (kWh) | Verified Savings (kWh) | Realization Rate (%) | MEEIA 3-Year Target (kWh) | Verified Savings (kWh) | % of MEEIA 3-Year Target Achieved
Commercial & Industrial EE Programs | Business ESP - Standard | 26333948.992 | 27977387.4529 | 106.2% | 46646197.1989 | 24755980.6268 | 53.07%
| Business ESP - Custom | 21903610.9739 | 21175620.0608 | 96.68% | 10016241.48 | 17197807.5229 | 171.7%
| Process Efficiency | 467795 | 450363 | 96.27% | 20470674.24 | 450363 | 2.2%
Educational Programs | Business Online Energy Audit | Online Energy Audit programs are not part of MEEIA Targets for Energy or Demand Savings.
Evergy MO West TOTAL |  | 48705354.9659 | 49603370.5136 | 101.8% | 77133112.9189 | 42404151.1497 | 54.98%
Note: Gross realization rates are the ratio of verified gross savings to reported gross savings and indicates the accuracy of deemed savings tracked by Evergy Metro.
Coincident Demand Savings at the Customer Meter – Program to Date
Sector | Program |  | Gross |  |  | Net
|  | Reported Savings (kW) | Verified Savings (kW) | Realization Rate (%) | MEEIA 3-Year Target (kW) | Verified Savings (kW) | % of MEEIA 3-Year Target Achieved
Commercial & Industrial EE Programs | Business ESP - Standard | 4874.3207 | 4579.7184 | 93.96% | 7513.8897 | 4080.4996 | 54.31%
| Business ESP - Custom | 4722.8164 | 3735.4598 | 79.09% | 1586.6804 | 3034.667 | 191.3%
| Process Efficiency | 73.5 | 66.31 | 90.22% | 227.448 | 66.31 | 29.15%
Educational Programs | Business Online Energy Audit | Online Energy Audit programs are not part of MEEIA Targets for Energy or Demand Savings.
Evergy MO West TOTAL |  | 9670.6371 | 8381.4882 | 86.67% | 9328.0181 | 7181.4767 | 76.99%
Note: Gross realization rates are the ratio of verified gross savings to reported gross savings and indicates the accuracy of deemed savings tracked by Evergy Metro.
NTG Components by Program
Program Name | Free Ridership | Participant Spillover | Non-Participant Spillover | NTGR
Business EER - Standard | 0.245 | 0.021 | 0.015 | 79.1%
Business EER - Custom | 0.239 | 0.04 | 0.015 | 81.6%
Process Efficiency |  |  |  | 100%
Business Online Energy Audit | N/A - Savings not claimed in PY1
Guidehouse assumed a NTGR of 1 for the two Process Efficiency projects reported in PY2. Guidehouse will conduct NTG research for the Process Efficiency program in PY3
Benefit-Cost Ratios by Program and Cost Test – PY2
Sector | Program | Total Resource Cost Test | Societal Cost Test | Utility Cost Test | Participant Cost Test | Rate Impact Measure Test
Guidehouse
Commercial EE Programs | Business ESP - Standard | 0.94218 | 1.1229 | 1.6231 | 1.7677 | 0.48721
| Business ESP - Custom | 1.0804 | 1.392 | 2.5523 | 1.7018 | 0.57199
| Process Efficiency | 0.23152 | 0.23567 | 0.2333 | 3.5267 | 0.17141
Total C&I Sector Level |  | 1.0107 | 1.2628 | 2.0599 | 1.7322 | 0.53433
*Ratios are based on net savings
**Guidehouse performed benefit-cost calculations on the Standard, Custom, and Process Efficiency programs. These programs represent the C&I EE portfolio.
Program Administrative Costs - PY2
Sector | Program | Rebate Costs | Program Admin Costs* | Total Costs | Benefits from Energy and Demand Savings | Total Net Benefits
Commercial EE Programs | Business ESP - Standard | 1360888 | 1172751 | 2533639 | 4112408.4922 | 1578769.4922 | 1.6231
| Business ESP - Custom | 1784113 | 1033790 | 2817903 | 7191996.6181 | 4374093.6181 | 2.5523
| Process Efficiency | 19981 | 133632 | 153613 | 35837.9213 | -117775.0787
Portfolio | Portfolio Total** | 3164982 | 2340173 | 5505155 | 11340243.0316 | 5835088.0316
*Evergy allocates indirect program administrative costs to programs as a percentage of total budget. These costs are not tracked separately from direct program administrative costs and are therefore included in that total.
**Only C&I EE programs inluded, no portfolio-level costs.
Discount Rate Matrix - PY2
MEEIA 3 - Discount Rate Matrix
Benefit Cost Test
TRC | SCT | UCT | PCT | RIM
6.731% | 3% | 6.731% | 10% | 6.731%
Note: The EM&V report applied the following discount rates when calculating net present value.
Benefit-Cost Ratios by Program and Cost Test – PTD ($2021)
Sector | Program | Total Resource Cost Test | Societal Cost Test | Utility Cost Test | Participant Cost Test | Rate Impact Measure Test
Guidehouse
Commercial EE Programs | Business ESP - Standard | 0.94819 | 1.1213 | 1.9365 | 1.6678 | 0.51237
| Business ESP - Custom | 1.1385 | 1.4626 | 2.5891 | 1.8397 | 0.5705
| Process Efficiency | 0.12689 | 0.13124 | 0.12743 | 3.5267 | 0.10644
Total C&I Sector Level |  | 1.0109 | 1.2414 | 2.1357 | 1.7403 | 0.53436
*Ratios are based on net savings
**Guidehouse performed benefit-cost calculations on the Standard, Custom, and Process Efficiency programs. These programs represent the C&I EE portfolio.
Program Administrative Costs - PTD ($2021)
Sector | Program | Rebate Costs | Program Admin Costs* | Total Costs | Benefits from Energy and Demand Savings | Total Net Benefits
Commercial EE Programs | Business ESP - Standard | 2955664.9672 | 2143006.4119 | 5098671.3791 | 9873448.5163 | 4774777.1372
| Business ESP - Custom | 2026954.4697 | 1379460.851 | 3406415.3207 | 8819587.6315 | 5413172.3108
| Process Efficiency | 18720.1989 | 244780.8208 | 263501.0197 | 33576.5485 | -229924.4712
Portfolio | Portfolio Total** | 5001339.6358 | 3767248.0837 | 8768587.7195 | 18726612.6963 | 9958024.9768
*Evergy allocates indirect program administrative costs to programs as a percentage of total budget. These costs are not tracked separately from direct program administrative costs and are therefore included in that total.
**Only C&I EE programs inluded, no portfolio-level costs.

## PY1 - C&I Portfolio
Program to Date Energy Savings at the Customer Meter by Territory
Sector | Gross |  |  | Net
| Reported Savings (kWh) | Verified Savings (kWh) | Realization Rate (%) | MEEIA Cycle 3 3-Year Target (kWh) | Verified 3 -Year Savings (kWh) | Percentage of MEEIA 3-Year Target Achieved
Evergy Metro | 28172077.4503 | 30264700.9546 | 107.4% | 103671719.8545 | 27006087.087 | 26.05%
Evergy MO West | 19625212.7771 | 20631328.3696 | 105.1% | 77133112.9189 | 18991090.7682 | 24.62%
Evergy TOTAL | 47797290.2274 | 50896029.3242 | 106.5% | 180804832.7734 | 45997177.8552 | 25.44%
Program to Date Demand Savings at the Customer Meter by Territory
Sector | Gross |  |  | Net
| Reported Savings (kW) | Verified Savings (kW) | Realization Rate (%) | MEEIA Cycle 3 3-Year Target (kW) | Verified 3 -Year Savings (kW) | Percentage of MEEIA 3-Year Target Achieved
Evergy Metro | 5335.1925 | 5663.6908 | 106.2% | 13538.2057 | 5022.5813 | 37.1%
Evergy MO West | 3514.1878 | 3551.4813 | 101.1% | 9328.0181 | 3274.74 | 35.11%
Evergy TOTAL | 8849.3803 | 9215.1721 | 104.1% | 22866.2238 | 8297.3213 | 36.29%

## PY1 - Evergy Metro
Evergy Services, Inc. (ESI) Evaluation, Measurement, and Verification Report – Commercial & Industrial Databook
Overall Portfolio: Evergy Metro Data Tables
Data is sourced to Guidehouse analysis unless otherwise noted.
Energy Savings at the Customer Meter – PY1
Sector | Program |  | Gross |  |  | Net
|  | Reported Savings (kWh) | Verified Savings (kWh) | Realization Rate (%) | MEEIA 3-Year Target (kWh) | Verified Savings (kWh) | % of MEEIA 3-Year Target Achieved
Commercial & Industrial EE Programs | Business ESP - Standard | 16217890.452 | 17464539.5211 | 107.7% | 53977377.4297 | 16765957.9403 | 31.06%
| Business ESP - Custom | 11954186.9983 | 12800161.4334 | 107.1% | 30239803.0328 | 10240129.1467 | 33.86%
| Process Efficiency | 0 | 0 | N/A | 19454539.392 | 0 | N/A
Educational Programs | Business Online Energy Audit | Online Energy Audit programs are not part of MEEIA Targets for Energy or Demand Savings.
Evergy Metro TOTAL |  | 28172077.4503 | 30264700.9546 | 107.4% | 103671719.8545 | 27006087.087 | 26.05%
Note: Gross realization rates are the ratio of verified gross savings to reported gross savings and indicates the accuracy of deemed savings tracked by Evergy Metro.
Coincident Demand Savings at the Customer Meter – PY1
Sector | Program |  | Gross |  |  | Net
|  | Reported Savings (kW) | Verified Savings (kW) | Realization Rate (%) | MEEIA 3-Year Target (kW) | Verified Savings (kW) | % of MEEIA 3-Year Target Achieved
Commercial & Industrial EE Programs | Business ESP - Standard | 2915.6497 | 3072.6791 | 105.4% | 8522.6148 | 2949.772 | 34.61%
| Business ESP - Custom | 2419.5428 | 2591.0117 | 107.1% | 4833.6325 | 2072.8093 | 42.88%
| Process Efficiency | 0 | 0 | N/A | 181.9584 | 0 | N/A
Educational Programs | Business Online Energy Audit | Online Energy Audit programs are not part of MEEIA Targets for Energy or Demand Savings.
Evergy Metro TOTAL |  | 5335.1925 | 5663.6908 | 106.2% | 13538.2057 | 5022.5813 | 37.1%
Note: Gross realization rates are the ratio of verified gross savings to reported gross savings and indicates the accuracy of deemed savings tracked by Evergy Metro.
NTG Components by Program
Program Name | Free Ridership | Participant Spillover | Non-Participant Spillover | NTGR
Business EER - Standard | 0.05 | 0.002 | 0.004 | 96%
Business EER - Custom | 0.24 | 0.04 | 0 | 80%
Process Efficiency | N/A - Savings not claimed in PY1
Business Online Energy Audit | N/A - Savings not claimed in PY1
Benefit-Cost Ratios by Program and Cost Test – PY1
Sector | Program | Total Resource Cost Test | Societal Cost Test | Utility Cost Test | Participant Cost Test | Rate Impact Measure Test
Guidehouse
Commercial EE Programs | Business ESP - Standard | 1.01 | 1.19 | 2.31 | 1.57 | 0.59
| Business ESP - Custom | 0.91 | 1.17 | 3.07 | 1.2 | 0.65
| Process Efficiency | N/A | N/A | N/A | N/A | N/A
Total C&I Sector Level |  | 0.96 | 1.17 | 2.53 | 1.38 | 0.61
*Ratios are based on net savings
**Guidehouse performed benefit-cost calculations on the Standard, Custom, and Process Efficiency programs. These programs represent the C&I EE portfolio.
Program Administrative Costs - PY1
Sector | Program | Rebate Costs | Program Admin Costs* | Total Costs | Benefits from Energy and Demand Savings | Total Net Benefits
Commercial EE Programs | Business ESP - Standard | 1578246 | 1354399 | 2932645 | 6775172 | 3842527
| Business ESP - Custom | 1148577 | 712682 | 1861259 | 5714254 | 3852995
| Process Efficiency | 0 | 140529 | 140529 | 0 | -140529
Portfolio | Portfolio Total** | 2726823 | 2207610 | 4934433 | 12489426 | 7554993
*Evergy allocates indirect program administrative costs to programs as a percentage of total budget. These costs are not tracked separately from direct program administrative costs and are therefore included in that total.
**Only C&I EE programs inluded, no portfolio-level costs.
MEEIA 3 - Discount Rate Matrix
Benefit Cost Test
TRC | SCT | UCT | PCT | RIM
6.73% | 3% | 6.73% | 10% | 6.73%
Note: The EM&V report applied the following discount rates when calculating net present value.

## PY1 - Evergy MO West
Evergy Services, Inc. (ESI) Evaluation, Measurement, and Verification Report – Commercial & Industrial Databook
Overall Portfolio: Evergy MO West Data Tables
Data is sourced to Guidehouse analysis unless otherwise noted.
Energy Savings at the Customer Meter – PY1
Sector | Program |  | Gross |  |  | Net
|  | Reported Savings (kWh) | Verified Savings (kWh) | Realization Rate (%) | MEEIA 3-Year Target (kWh) | Verified Savings (kWh) | % of MEEIA 3-Year Target Achieved
Commercial & Industrial EE Programs | Business ESP - Standard | 14366300.992 | 15537675.4529 | 108.2% | 46646197.1989 | 14916168.4348 | 31.98%
| Business ESP - Custom | 5258911.7851 | 5093652.9167 | 96.86% | 10016241.48 | 4074922.3334 | 40.68%
| Process Efficiency | 0 | 0 | N/A | 20470674.24 | 0 | N/A
Educational Programs | Business Online Energy Audit | Online Energy Audit programs are not part of MEEIA Targets for Energy or Demand Savings.
Evergy MO West TOTAL |  | 19625212.7771 | 20631328.3696 | 105.1% | 77133112.9189 | 18991090.7682 | 24.62%
Note: Gross realization rates are the ratio of verified gross savings to reported gross savings and indicates the accuracy of deemed savings tracked by Evergy Metro.
Coincident Demand Savings at the Customer Meter – PY1
Sector | Program |  | Gross |  |  | Net
|  | Reported Savings (kW) | Verified Savings (kW) | Realization Rate (%) | MEEIA 3-Year Target (kW) | Verified Savings (kW) | % of MEEIA 3-Year Target Achieved
Commercial & Industrial EE Programs | Business ESP - Standard | 2565.3207 | 2709.7184 | 105.6% | 7513.8897 | 2601.3296 | 34.62%
| Business ESP - Custom | 948.8671 | 841.7629 | 88.71% | 1586.6804 | 673.4103 | 42.44%
| Process Efficiency | 0 | 0 | N/A | 227.448 | 0 | N/A
Educational Programs | Business Online Energy Audit | Online Energy Audit programs are not part of MEEIA Targets for Energy or Demand Savings.
Evergy MO West TOTAL |  | 3514.1878 | 3551.4813 | 101.1% | 9328.0181 | 3274.74 | 35.11%
Note: Gross realization rates are the ratio of verified gross savings to reported gross savings and indicates the accuracy of deemed savings tracked by Evergy Metro.
NTG Components by Program
Program Name | Free Ridership | Participant Spillover | Non-Participant Spillover | NTGR
Business EER - Standard | 0.05 | 0.002 | 0.004 | 96%
Business EER - Custom | 0.24 | 0.04 | 0 | 80%
Process Efficiency | N/A - Savings not claimed in PY1
Business Online Energy Audit | N/A - Savings not claimed in PY1
Benefit-Cost Ratios by Program and Cost Test – PY1
Sector | Program | Total Resource Cost Test | Societal Cost Test | Utility Cost Test | Participant Cost Test | Rate Impact Measure Test
Guidehouse
Commercial EE Programs | Business ESP - Standard | 0.95 | 1.12 | 2.21 | 1.6 | 0.53
| Business ESP - Custom | 1.38 | 1.76 | 2.72 | 2.47 | 0.57
| Process Efficiency | N/A | N/A | N/A | N/A | N/A
Total C&I Sector Level |  | 1.01 | 1.21 | 2.24 | 1.75 | 0.53
*Ratios are based on net savings
**Guidehouse performed benefit-cost calculations on the Standard, Custom, and Process Efficiency programs. These programs represent the C&I EE portfolio.
Program Administrative Costs - PY1
Sector | Program | Rebate Costs | Program Admin Costs* | Total Costs | Benefits from Energy and Demand Savings | Total Net Benefits
Commercial EE Programs | Business ESP - Standard | 1680649 | 1044256 | 2724905 | 6020533 | 3295628
| Business ESP - Custom | 355419 | 410903 | 766322 | 2081406 | 1315084
| Process Efficiency | 0 | 119581 | 119581 | 0 | -119581
Portfolio | Portfolio Total** | 2036068 | 1574740 | 3610808 | 8101939 | 4491131
*Evergy allocates indirect program administrative costs to programs as a percentage of total budget. These costs are not tracked separately from direct program administrative costs and are therefore included in that total.
**Only C&I EE programs inluded, no portfolio-level costs.
MEEIA 3 - Discount Rate Matrix
Benefit Cost Test
TRC | SCT | UCT | PCT | RIM
6.731% | 3% | 6.731% | 10% | 6.731%
Note: The EM&V report applied the following discount rates when calculating net present value.

## Business ESP - Standard
Evergy Services, Inc. (ESI) Evaluation, Measurement, and Verification Report – Commercial & Industrial Databook
Business Energy Savings Program - Standard: Data Tables
Executive Summary
Data is sourced to Guidehouse analysis unless otherwise noted.
Every Metro Program Savings Summary - PY2
| Gross |  |  | Net
| Reported Savings | Verified Savings | Realization Rate | MEEIA 3-Year Target | Verified Savings | % of MEEIA 3-Year Target Achieved
Energy at Customer Meter (kWh) | 11162365 | 10386880 | 93.05% | 53977377.4297 | 8216022.08 | 15.22%
Coinc Demand at Customer Meter (kW) | 2467 | 1808 | 73.29% | 8522.6148 | 1430.128 | 16.78%
Source: Program Tracking Database and Guidehouse analysis
Every Metro Program Savings Summary - Program to Date
| Gross |  |  | Net
| Reported Savings | Verified Savings | Realization Rate | MEEIA 3-Year Target | Verified Savings | % of MEEIA 3-Year Target Achieved
Energy at Customer Meter (kWh) | 27380255.452 | 27851419.5211 | 101.7% | 53977377.4297 | 24981980.0203 | 46.28%
Coinc Demand at Customer Meter (kW) | 5382.6497 | 4880.6791 | 90.67% | 8522.6148 | 4379.9 | 51.39%
Source: Program Tracking Database and Guidehouse analysis
Evergy MO West Program Savings Summary - PY2
| Gross |  |  | Net
| Reported Savings | Verified Savings | Realization Rate | MEEIA 3-Year Target | Verified Savings | % of MEEIA 3-Year Target Achieved
Energy at Customer Meter (kWh) | 11967648 | 12439712 | 103.9% | 46646197.1989 | 9839812.192 | 21.09%
Coinc Demand at Customer Meter (kW) | 2309 | 1870 | 80.99% | 7513.8897 | 1479.17 | 19.69%
Source: Program Tracking Database and Guidehouse analysis
Evergy MO West Program Savings Summary - Program to Date
| Gross |  |  | Net
| Reported Savings | Verified Savings | Realization Rate | MEEIA 3-Year Target | Verified Savings | % of MEEIA 3-Year Target Achieved
Energy at Customer Meter (kWh) | 26333948.992 | 27977387.4529 | 106.2% | 46646197.1989 | 24755980.6268 | 53.07%
Coinc Demand at Customer Meter (kW) | 4874.3207 | 4579.7184 | 93.96% | 7513.8897 | 4080.4996 | 54.31%
Source: Program Tracking Database and Guidehouse analysis
Net to Gross Component Summary
Free Ridership | Participant Spillover | Non-Participant Spillover | NTGR
0.245 | 0.021 | 0.015 | 79.1%
Note: The NTG ratio is rounded to the nearest 100th.
Evergy Metro Savings by Measure Type
Measure Type | Total Number of Measures | Reported Energy Savings (kWh) | Verified Energy Savings (kWh) | % of Total Verified Energy (%) | Reported Demand Savings (kW) | Verified Demand Savings (kW) | % of Total Verified Demand (%)
Cooking | 1 | 4438 | 4438 | 0.04273% | 0 | 0 | 0%
Cooling | 151 | 767657 | 432719 | 4.166% | 669 | 164 | 9.071%
HVAC | 7 | 23462 | 27264 | 0.2625% | 5 | 1 | 0.05531%
Lighting | 651 | 9365046 | 8856245 | 85.26% | 1645 | 1499 | 82.91%
Lighting Control | 6 | 392448 | 462412 | 4.452% | 75 | 71 | 3.927%
Pools | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Pumps/Fans | 1 | 32900 | 27388 | 0.2637% | 8 | 7 | 0.3872%
Refrigeration | 62 | 576414 | 576414 | 5.549% | 66 | 66 | 3.65%
Total | 879 | 11162365 | 10386880 | 100% | 2468 | 1808 | 100%
Source: Program Tracking Database and Guidehouse analysis
Evergy MO West Savings by Measure Type
Measure Type | Total Number of Measures | Reported Energy Savings (kWh) | Verified Energy Savings (kWh) | % of Total Verified Energy (%) | Reported Demand Savings (kW) | Verified Demand Savings (kW) | % of Total Verified Demand (%)
Cooking | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Cooling | 185 | 689952 | 780582 | 6.275% | 740 | 342 | 18.29%
HVAC | 21 | 27863 | 28059 | 0.2256% | 7 | 6 | 0.3209%
Lighting | 910 | 10900551 | 11241740 | 90.37% | 1511 | 1470 | 78.61%
Lighting Control | 10 | 115207 | 155257 | 1.248% | 24 | 25 | 1.337%
Pools | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Pumps/Fans | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Refrigeration | 33 | 234075 | 234075 | 1.882% | 27 | 27 | 1.444%
Total | 1159 | 11967648 | 12439713 | 100% | 2309 | 1870 | 100%
Source: Program Tracking Database and Guidehouse analysis
Additional Detail
Verified Inputs for Lighting Projects
Building Type | Verified (Guidehouse Analysis and IL TRM) |  |  |  | Total Number of Loggers Installed
| Waste Heat Factor (Energy) | Waste Heat Factor (Demand) | Revised Coincident Factor (CF) | Revised Hours of Use (HOU)
Industrial | 1.0199 | 1.0398 | 0.63952 | 4584.1978 | 33
Office | 1.1075 | 1.3058 | 0.69254 | 3635.5783 | 29
Other | 1.08 | 1.3 | 0.73224 | 4924.6831 | 61
Retail | 1.1223 | 1.2909 | 0.74488 | 4920.8006 | 103
School | 1.095 | 1.435 | 0.62507 | 3642.1243 | 45
Warehouse | 1.02 | 1.17 | 0.54654 | 3611.4342 | 60
Exterior | 1 | 1 | 0 | 5391.9547 | 18
Source: Program Tracking Database and Guidehouse analysis and Illinois TRM
Evergy Metro Data Tables
Measures with 2% or more program level savings
Measure name | Primary Key | Reported Energy Savings (kWh) | Reported Demand Savings (kW) | Verified Energy Savings (kWh) | Verified Demand Savings (kW) | Energy Realization Rate (%) | Demand Realization Rate (%) | % of Total Verified Energy (%) | % of Total Verified Demand (%)
Interior LED Linear Lamp Replacing 4ft T8, T12, or T5/T5HO Lamp | 166.3 | 2553408 | 467 | 2845580 | 583 | 111.4% | 124.8% | 27.4% | 32.21%
Interior LED 2X4 Troffer or Linear Ambient replacing T8, T12 or T5/T5HO fixture | 172 | 805587 | 183 | 471685 | 98 | 58.55% | 53.55% | 4.541% | 5.414%
Interior LED 2X4 Retrofit Kit replacing T8, T12 or T5/T5HO fixture | 169.3 | 941975 | 175 | 860708 | 170 | 91.37% | 97.14% | 8.286% | 9.392%
Interior LED 1X4 Retrofit Kit replacing T8, T12 or T5/T5HO fixture | 168.3 | 1142901 | 260 | 1044051 | 182 | 91.35% | 70% | 10.05% | 10.06%
LED Low/High Bay Fixture replacing 301W‐450W fixture | 221.4 | 279014 | 47 | 268100 | 50 | 96.09% | 106.4% | 2.581% | 2.762%
Exterior LED replacing > 400W Fixture or Mogul Screw-Base Lamp | 149.3 | 537405 | 0 | 626285 | 0 | 116.5% | #DIV/0! | 6.03% | 0%
Interior LED Linear Lamp Replacing 2ft T8, T12, or T5/T5HO Lamp | 167.2 | 416935 | 95 | 388104 | 87 | 93.09% | 91.58% | 3.736% | 4.807%
LED High Bay fixture replacing > 750W fixture | 223.3 | 523427 | 95 | 204791 | 38 | 39.13% | 40% | 1.972% | 2.099%
Networked Lighting Controls | 284.1 | 389783 | 73 | 459973 | 70 | 118% | 95.89% | 4.428% | 3.867%
Air-Cooled Chiller with Condenser ≥ 150 tons | 512 | 228136 | 225 | 50966 | 44 | 22.34% | 19.56% | 0.4907% | 2.431%
Packaged DX 240 - 760kbtu | 361.1 | 240202 | 59 | 211675 | 53 | 88.12% | 89.83% | 2.038% | 2.928%
Strip Curtains Cooler | 261.2 | 364059 | 42 | 364059 | 42 | 100% | 100% | 3.505% | 2.32%
Other Measures |  | 2739534 | 747 | 2590905 | 393 | 94.57% | 52.61% | 24.94% | 21.71%
TOTAL |  | 11162366 | 2468 | 10386882 | 1810 | 93.05% | 73.34% | 100% | 100%
Source: Program Tracking Database and Guidehouse analysis
Savings by Building Type
Program | Building Type | Total Number of Measures | Reported Energy Savings (kWh) | Verified Energy Savings (kWh) | Energy Realization Rate (%) | % of Total Verified Energy (%) | Reported Demand Savings (kW) | Verified Demand Savings (kW) | Demand Realization Rate | % of Total Verified Demand (%)
Standard- Evergy Metro | Exterior | 61 | 388347 | 438092 | 112.8% | 4.218% | 2 | 0 | 0% | 0%
| Industrial | 27 | 254212 | 198027 | 77.9% | 1.907% | 31 | 15 | 48.39% | 0.7712%
| Office | 262 | 3556418 | 3399527 | 95.59% | 32.73% | 731 | 707 | 96.72% | 36.35%
| Other | 42 | 318241 | 439460 | 138.1% | 4.231% | 59 | 71 | 120.3% | 3.65%
| Retail | 205 | 2181510 | 2198871 | 100.8% | 21.17% | 371 | 295 | 79.51% | 15.17%
| School | 159 | 1260265 | 1093521 | 86.77% | 10.53% | 694 | 455 | 65.56% | 23.39%
| Warehouse | 100 | 2963399 | 2307858 | 77.88% | 22.22% | 573 | 366 | 63.87% | 18.82%
| Parking Garage* | 23 | 239974 | 311525 | 129.8% | 2.999% | 33 | 36 | 109.1% | 1.851%
| Total | 879 | 11162366 | 10386881 | 93.05% | 100% | 2494 | 1945 | 77.99% | 100%
Source: C&I Standard Tracking Databases and Guidehouse analysis
*Lighting measures installed in parking garages were separated out from other projects since the waste heat factor for garages are 1.0, the coincidence factor is 1.0, and the HOU is assumed to be 8760
Evergy MO West Data Tables
Measures with 2% or more program level savings
Measure name | Primary Key | Reported Energy Savings (kWh) | Reported Demand Savings (kW) | Verified Energy Savings (kWh) | Verified Demand Savings (kW) | Energy Realization Rate (%) | Demand Realization Rate (%) | % of Total Verified Energy (%) | % of Total Verified Demand (%)
Interior LED Linear Lamp Replacing 4ft T8, T12, or T5/T5HO Lamp | 166 | 2329120 | 426 | 2527562 | 485 | 108.5% | 113.8% | 20.32% | 25.94%
Interior LED 2X4 Troffer or Linear Ambient replacing T8, T12 or T5/T5HO fixture | 172.3 | 1540001 | 350 | 826380 | 169 | 53.66% | 48.29% | 6.643% | 9.037%
Exterior LED replacing 251W-400W Fixture or Mogul Screw‐Base Lamp | 150.3 | 473293 | 0 | 608392 | 1 | 128.5% | #DIV/0! | 4.891% | 0.05348%
Interior LED 2X4 Retrofit Kit replacing T8, T12 or T5/T5HO fixture | 169.3 | 1884551 | 350 | 2278799 | 468 | 120.9% | 133.7% | 18.32% | 25.03%
Exterior LED replacing < 175W Fixture or Mogul Screw-Base Lamp | 152.3 | 273623 | 0 | 481225 | 0 | 175.9% | #DIV/0! | 3.868% | 0%
LED Low/High Bay Fixture replacing 301W‐450W fixture | 221.4 | 517220 | 87 | 496008 | 88 | 95.9% | 101.1% | 3.987% | 4.706%
Exterior LED replacing > 400W Fixture or Mogul Screw-Base Lamp | 149.3 | 2237910 | 0 | 2517518 | 0 | 112.5% | #DIV/0! | 20.24% | 0%
Air-Cooled Chiller with Condenser ≥ 150 tons | 512 | 272044 | 269 | 321838 | 55 | 118.3% | 20.45% | 2.587% | 2.941%
Other Measures |  | 2439886 | 826 | 2381989 | 604 | 97.63% | 73.12% | 19.15% | 32.3%
TOTAL |  | 11967648 | 2308 | 12439711 | 1870 | 103.9% | 81.02% | 100% | 100%
Source: Program Tracking Database and Guidehouse analysis
Savings by Building Type
Program | Building Type | Total Number of Measures | Reported Energy Savings (kWh) | Verified Energy Savings (kWh) | Energy Realization Rate (%) | % of Total Verified Energy (%) | Reported Demand Savings (kW) | Verified Demand Savings (kW) | Demand Realization Rate | % of Total Verified Demand (%)
Standard- Evergy MO West | Exterior | 21 | 267858 | 266630 | 99.54% | 2.143% | 1.7644 | 0 | 0% | 0%
| Industrial | 41 | 731509 | 616043 | 84.22% | 4.952% | 136.5579 | 84 | 61.51% | 4.492%
| Office | 263 | 2680431 | 2621403 | 97.8% | 21.07% | 419 | 340 | 81.15% | 18.18%
| Other | 38 | 110273 | 136162 | 123.5% | 1.095% | 11 | 12 | 109.1% | 0.6417%
| Retail | 368 | 4105174 | 5034514 | 122.6% | 40.47% | 554 | 536 | 96.75% | 28.66%
| School | 352 | 3068103 | 3350662 | 109.2% | 26.94% | 1007 | 854 | 84.81% | 45.67%
| Warehouse | 49 | 916918 | 271697 | 29.63% | 2.184% | 167 | 27 | 16.17% | 1.444%
| Parking Garage* | 27 | 87383 | 142600 | 163.2% | 1.146% | 13 | 17 | 130.8% | 0.9091%
| Total | 1159 | 11967649 | 12439711 | 103.9% | 100% | 2309.3223 | 1870 | 80.98% | 100%
Source: C&I Standard Tracking Databases and Guidehouse analysis
*Lighting measures installed in parking garages were separated out from other projects since the waste heat factor for garages are 1.0, the coincidence factor is 1.0, and the HOU is assumed to be 8760
Participant Satisfaction with Standard Program (on a scale of 1 through 5, 1 being the lowest, 5 being the highest)
Program Component | 5 | 4 | 3 | 2 | 1 | Not Sure | Average Satisfaction (1-5)
Amount of rebate | 51.92% | 34.62% | 3.846% | 5.769% | 0% | 3.846% | 4.375
Time to receive the rebate | 67.31% | 15.38% | 9.615% | 3.846% | 0% | 3.846% | 4.5208
Requirements to participate | 53.85% | 34.62% | 9.615% | 0% | 0% | 1.923% | 4.449
Application process | 48.08% | 40.38% | 9.615% | 0% | 1.923% | 0% | 4.36
Pre-approval process | 42.86% | 38.1% | 9.524% | 0% | 2.381% | 7.143% | 4.2895
Final approval process | 40% | 60% | 0% | 0% | 0% | 0% | 4.4444
Installation contractor | 80% | 20% | 0% | 0% | 0% | 0% | 4.8889
Program communications | 65.38% | 21.15% | 1.923% | 0% | 0% | 11.54% | 4.7045
Program Representative | 71.15% | 19.23% | 3.846% | 1.923% | 0% | 3.846% | 4.6667
Overall satisfaction | 65.38% | 30.77% | 1.923% | 0% | 1.923% | 0% | 4.58
Source: Guidehouse survey of participants; n = 52
Participant Satisfaction with Evergy (on a scale of 1 through 5, 1 being the lowest, 5 being the highest)
Program Component | 5 | 4 | 3 | 2 | 1 | Average Satisfaction (1-5)
Overall Satisfaction with Evergy | 71% | 22% | 6% | 0% | 0% | 4.6
Source: Guidehouse survey of participants; n = 113
Participant's Willingness to Participate in Evergy Rebate Program Again (on a scale of 1 through 5, 1 being "not at all likely", 5 being "very likely")
Program Component | 5 | 4 | 3 | 2 | 1 | Average Rating (1-5)
Willingness to Participate | 87% | 12% | 2% | 0% | 0% | 4.9
Source: Guidehouse survey of participants; n = 113
Participant's Agreement with Statements about Program Ease and Information (on a scale of 1 through 5, 1 being "Strongly disagree" and 5 being "Strongly agree")
Program Component | 5 | 4 | 3 | 2 | 1 | Average Agreement (1-5)
The program is easy to work with and understand | 50% | 38% | 8% | 0% | 4% | 4.3
When I had questions, I knew who to contact | 57% | 31% | 6% | 2% | 4% | 4.35
I had enough information about measure eligibility and rebates to make decisions about which equipment to install. | 49% | 33% | 10% | 4% | 4% | 4.19
Source: Guidehouse survey of participants; n = 52
Trade Ally Satisfaction with Standard Program (on a scale of 1 through 5, 1 being the lowest, 5 being the highest)
Program Component | 5 | 4 | 3 | 2 | 1 | Not Sure | Not Applicable | Average Satisfaction (1-5)
Marketing materials provided by the program | 50% | 25% | 8.33% | 0% | 0% | 4.17% | 12.5% | 4.5
Amount and type of communication and support received from the program | 62.5% | 25% | 8.33% | 0% | 0% | 0% | 4.17% | 4.5652
Amount and type of training provided by the program | 37.5% | 29.17% | 16.67% | 0% | 0% | 4.17% | 12.5% | 4.25
Project application process | 58.33% | 20.83% | 12.5% | 0% | 0% | 0% | 8.33% | 4.5
Time to complete a project the program | 66.67% | 16.67% | 8.33% | 0% | 0% | 0% | 8.33% | 4.6364
The amount of the program incentives | 37.5% | 37.5% | 12.5% | 8.33% | 0% |  | 4.17% | 4.087
The Program Representative | 62.5% | 25% | 0% | 0% | 0% | 4.17% | 8.33% | 4.7143
Overall satisfaction with Standard program | 62.5% | 37.5% | 0% | 0% | 0% | 0% | 0% | 4.625
Source: Guidehouse survey of trade allies; n = 23

## Business ESP - Custom
Evergy Services, Inc. (ESI) Evaluation, Measurement, and Verification Report – Commercial & Industrial Databook
Business Energy Savings Program - Custom: Data Tables
Executive Summary
Data is sourced to Guidehouse analysis unless otherwise noted.
Every Metro Program Savings Summary - PY2
| Gross |  |  | Net
| Reported Savings | Verified Savings | Realization Rate | MEEIA 3-Year Target | Verified Savings | % of MEEIA 3-Year Target Achieved
Energy at Customer Meter (kWh) | 13412567.0528 | 14563905.3716 | 108.6% | 30239803.0328 | 11884146.7832 | 39.3%
Coinc Demand at Customer Meter (kW) | 2451.2433 | 2768.3366 | 112.9% | 4833.6325 | 2258.9627 | 46.73%
Source: Program Tracking Database and Guidehouse analysis
Evergy Metro Program Savings Summary - Program to Date
| Gross |  |  | Net
| Reported Savings | Verified Savings | Realization Rate | MEEIA 3-Year Target | Verified Savings | % of MEEIA 3-Year Target Achieved
Energy at Customer Meter (kWh) | 25366754.0511 | 27364066.805 | 107.9% | 30239803.0328 | 22124275.9299 | 73.16%
Coinc Demand at Customer Meter (kW) | 4870.7861 | 5359.3482 | 110% | 4833.6325 | 4331.772 | 89.62%
Source: Program Tracking Database and Guidehouse analysis
Evergy MO West Program Savings Summary - PY2
| Gross |  |  | Net
| Reported Savings | Verified Savings | Realization Rate | MEEIA 3-Year Target | Verified Savings | % of MEEIA 3-Year Target Achieved
Energy at Customer Meter (kWh) | 16644699.1888 | 16081967.144 | 96.62% | 10016241.48 | 13122885.1895 | 131%
Coinc Demand at Customer Meter (kW) | 3773.9493 | 2893.6969 | 76.68% | 1586.6804 | 2361.2567 | 148.8%
Source: Program Tracking Database and Guidehouse analysis
Evergy MO West Program Savings Summary - Program to Date
| Gross |  |  | Net
| Reported Savings | Verified Savings | Realization Rate | MEEIA 3-Year Target | Verified Savings | % of MEEIA 3-Year Target Achieved
Energy at Customer Meter (kWh) | 21903610.9739 | 21175620.0608 | 96.68% | 10016241.48 | 17197807.5229 | 171.7%
Coinc Demand at Customer Meter (kW) | 4722.8164 | 3735.4598 | 79.09% | 1586.6804 | 3034.667 | 191.3%
Source: Program Tracking Database and Guidehouse analysis
Net to Gross Component Summary
Free Ridership | Participant Spillover | Non-Participant Spillover | NTGR
0.239 | 0.04 | 0.015 | 81.6%
Source: Guidehouse analysis PY2018
Evergy Metro Savings by Measure Type
Measure Type | Total Number of Projects | Reported Energy Savings (kWh) | Verified Energy Savings (kWh) | % of Total Verified Energy (%) | Reported Demand Savings (kW) | Verified Demand Savings (kW) | % of Total Verified Demand (%)
Air Conditioning and Heating | 41 | 366810 | 398156.7433 | 2.735% | 110.7232 | 124.8955 | 4.517%
Appliances | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Lighting System Upgrades | 72 | 2027302.2478 | 2200550.8594 | 15.11% | 363.0009 | 409.464 | 14.81%
Miscellaneous | 30 | 11018454.805 | 11960066.7425 | 82.15% | 1977.5192 | 2230.6362 | 80.67%
Total | 143 | 13412567.0528 | 14558774.3453 | 100% | 2451.2433 | 2764.9956 | 100%
Source: Program Tracking Database and Guidehouse analysis
Evergy MO West Savings by Measure Type
Measure Type | Total Number of Projects | Reported Energy Savings (kWh) | Verified Energy Savings (kWh) | % of Total Verified Energy (%) | Reported Demand Savings (kW) | Verified Demand Savings (kW) | % of Total Verified Demand (%)
Air Conditioning and Heating | 15 | 1439292 | 1390631.7196 | 8.647% | 300.3155 | 230.2686 | 7.958%
Appliances | 2 | 109488 | 105786.3767 | 0.6578% | 10.6534 | 8.1686 | 0.2823%
Lighting System Upgrades | 106 | 5255046.6409 | 5077381.4811 | 31.57% | 908.3196 | 696.4592 | 24.07%
Miscellaneous | 53 | 9840872.5479 | 9508167.5667 | 59.12% | 2554.6608 | 1958.8006 | 67.69%
Total | 176 | 16644699.1888 | 16081967.144 | 100% | 3773.9493 | 2893.6969 | 100%
Source: Program Tracking Database and Guidehouse analysis
Additional Detail
End-of-Year Population and Sample Sizes
Stratum | Reported Energy Savings (kWh) | Reported Peak Demand Savings (kW) | Total Number of Projects | Projects in Sample
Certainty | 21099296 | 4433.636 | 14 | 14
Large | 2303673 | 439.2404 | 10 | 5
Small | 331754 | 87.2614 | 82 | 2
Total | 23734723 | 4960.1378 | 106 | 21
Source: C&I Custom Rebate Program Tracking Database and Guidehouse analysis
Note: Large projects account for at least 75% of total energy savings while total energy savings of all small projects are no more than 25%.
Evergy Metro - Energy Impacts at the Customer Meter For Sampled Projects
Stratum | Total Reported Energy Savings (kWh) | Total Verified Energy Savings (kWh) | Energy RR | Relative Precision at 90% Confidence (one-tailed)
Certainty | 9646960 | 11103781.9293 | 115.1% | 0%
Large | 1862189.12 | 1551574.4832 | 83.32% | NA
Small | 1903417.9328 | 1903417.9328 | 100% | NA
Total | 13412567.0528 | 14558774.3453 | 108.5% | 6.463%
Source: C&I Custom Rebate Program Tracking Database and Guidehouse analysis
Evergy Metro - Coincident Demand Impacts at Customer Meter For Sampled Projects
Stratum | Total Reported Coincident Demand Savings (kW) | Total Verified Coincident Demand Savings (kW) | Coincident Demand RR | Relative Precision at 90% Confidence (one-tailed)
Certainty | 1561.3 | 1967.5125 | 126% | 0%
Large | 391.1604 | 466.17 | 119.2% | NA
Small | 498.7829 | 331.3132 | 66.42% | NA
Total | 2451.2433 | 2764.9956 | 112.8% | 28.72%
Evergy MO West - Energy Impacts at the Customer Meter For Sampled Projects
Stratum | Total Reported Energy Savings (kWh) | Total Verified Energy Savings (kWh) | Energy RR | Relative Precision at 90% Confidence (one-tailed)
Certainty | 11452336 | 10862906.0808 | 94.85% | 0%
Large | 2281655.5479 | 2402106.4614 | 105.3% | 5.174%
Small | 2910707.6409 | 2816954.6018 | 96.78% | NA
Total | 16644699.1888 | 16081967.144 | 96.62% | 1.319%
Source: C&I Custom Rebate Program Tracking Database and Guidehouse analysis
Evergy MO West - Coincident Demand Impacts at Customer Meter For Sampled Projects
Stratum | Total Reported Coincident Demand Savings (kW) | Total Verified Coincident Demand Savings (kW) | Coincident Demand RR | Relative Precision at 90% Confidence (one-tailed)
Certainty | 2872.336 | 2353.2191 | 81.93% | 0%
Large | 425.9342 | 255.282 | 59.93% | 42.67%
Small | 475.6791 | 285.1959 | 59.96% | NA
Total | 3773.9493 | 2893.6969 | 76.68% | 15.75%
Source: C&I Custom Rebate Program Tracking Database and Guidehouse analysis
Project-Level Energy and Demand Savings and RRs
Premise ID | Project ID(s) | Reported kWh | Verified kWh | Realization Rate (kWh) | Reported kW | Verified kW | Realization Rate (kW)
5433202654 | 3302, 3776, 3777, 3778, 3891 | 8145623 | 8038762.4951 | 98.69% | 2186.133 | 2111.164 | 96.57%
2463880909 | 2462, 3620 | 1918169 | 1435599.5857 | 74.84% | 397.7693 | 152.0551 | 38.23%
371650000 | 3243 | 1388544 | 1388544 | 100% | 288.4337 | 90 | 31.2%
810060000 | 2580 | 580618 | 580618 | 100% | 120.4023 | 0 | 0%
7963332701 | 3419 | 500741 | 500741 | 100% | 82.3576 | 33.5 | 40.68%
1431424911 | 3531 | 454248 | 437783.9399 | 96.38% | 73.9799 | 55.7146 | 75.31%
5651580000 | 3235 | 364128 | 480881 | 132.1% | 69.9958 | 118.6 | 169.4%
5783869983 | 2454 | 227695 | 220361.0109 | 96.78% | 42.5037 | 25.4833 | 59.96%
410978402 | 2905, 3306, 3307, 3308 | 7665774 | 9185495.9293 | 119.8% | 1411.3 | 1817.5125 | 128.8%
6207745538 | 1249, 1250 | 1981186 | 1918286 | 96.83% | 150 | 150 | 100%
8202435121 | 3246 | 403938 | 336560.8181 | 83.32% | 92.5048 | 110.2437 | 119.2%
6337630000 | 2770 | 104059 | 104059 | 100% | 44.7577 | 29.73 | 66.42%
Source: C&I Custom Rebate Program Tracking Database and Guidehouse analysis
Project-Level Results for Sampled Projects
Nav. Site ID | Project Type | Energy RR (%) | Effect on Energy RR (%) | Demand RR (%) | Effect on Demand RR (%) | Reason for Discrepancy
5433202654 | 3302, 3776, 3777, 3778, 3891 | 98.69% | 2.651% | 96.57% | -1.526% | Guidehouse reviewed the current Trace 3D model and made minor updates to the baseline lighting based on the application-listed PPF using the Guidehouse agriculture lighting baseline methodology.
2463880909 | 2462, 3620 | 74.84% | 2.543% | 38.23% | 4.918% | Guidehouse reviewed the Trace 3D model and made updates to both the baseline and proposed lighting in accrodance with the Guidehouse agriculture lighting baseline methodology. The primary flower fixture type was found to have low efficacy (1.58 vs 1.6), which resulted in a low realization rate. Minor updates were also made to fan powers and efficiencies (fan Power neutral).
371650000 | 3243 | 100% | 0.2338% | 31.2% | 3.916% | Guidehouse reviewed the ex ante savings, which were calculated using simulation software (proprietory to the implementer) which follows industry standards. Guidehouse was not able to get the actual simulation model for review, however, the model outputs and underlying assumptions were verified and Guidehouse was satisfied with the calculation process.
810060000 | 2580 | 100% | 0.09434% | 0% | 2.354% | Guidehouse verified that the ex ante assumptions were reasonable and assigned a 100% realization rate for energy savings. At 100% load, when typical peak demand occurs, equipment with a VFD consumes the same or more power than equipment without VFD, which results in no pead demand savings for this measure.
7963332701 | 3419 | 100% | 0.08109% | 40.68% | 0.911% | Guidehouse verified that the ex ante assumptions were reasonable for the compressed air calculations and the pump VFD calculations and assigned a 100% realization rate for energy savings for this measure. For the peak demand savings of the compressed air measure, Guidehouse used the peak demand values generated from the compressed air calculator for baseline and efficient case operations, which resulted in a lower demand realization rate for this measure. At 100% load, when typical peak demand occurs, equipment with a VFD consumes the same or more power than equipment without VFD, which results in no pead demand savings for the VFD measures.
1431424911 | 3531 | 96.38% | 0.1441% | 75.31% | 0.2926% | Guidehouse updated the waste heat and coincident factors to align with the IL TRM v9 for the lighting measures. Guidehouse calculated the refrigerated case savings using the department of energy TDA calculations and found that the ex ante calculations for the regular refrigerated cases were in alignment, however the specialty cases were found to have incorrect energy savings calculated despite the correct case formulas being referenced.
5651580000 | 3235 | 132.1% | -0.441% | 169.4% | -1.071% | Guidehouse calculated savings using chiller peak efficiencies and algorithms outlined in the IL TRM v9. The ex ante savings were calculated using a 30% decrease in power consumption due to a 30% decrease in actual load. However, since the pumps are operated using VFDs, a 30% decrease in load corresponds to a 59% decrease in power consumption, which resulted in a higher energy realization rate for the pump measures.
5783869983 | 2454 | 96.78% | 0.06764% | 59.96% | 0.2997% | Guidehouse found that the ex ante energy savings for heat pumps was calculated using a deemed value from MEEIA TRM, while the ex post savings were calculated using actual capacity and efficiency coefficient values and algorithms from the IL TRM v9.
410978402 | 2905, 3306, 3307, 3308 | 119.8% | -7.663% | 128.8% | -13.58% | Guidehouse updated the proposed and baseline LPD values based on lighting design guidance and the Guidehouse baseline agriculture lighting methodology. Additionally, changes were made to update fan powers and efficienies based on design data (fan power neutral).
6207745538 | 1249, 1250 | 96.83% | 0.6318% | 100% | -0.1673% | Guidehouse verified all model inputs were correct for the ex ante model simulation with the exception of one measure end use labeled in the application as "unknown savings", which received a RR of 0. All other baseline and efficient consumptions were consistent with the model output.
8202435121 | 3246 | 83.32% | 0.3539% | 119.2% | -0.4664% | Guidehouse found that ex ante savings for the air source heat pump measures were only claiming savings for the cooling component, whereas the ex post calculations sum the savings from both the cooling and heating components, resulting in a high energy realization rate for these measures. Guidehouse also aligned the agriculture grow lighting measure with the Guidehouse agriculture lighting baseline methodology, which resulted in a lower realization rate for this measure. All other measures were found to align between the ex ante and ex post calculated energy savings.
6337630000 | 2770 | 100% | 0.01657% | 66.42% | 0.2569% | Guidehouse reviewed the ex ante calculations and found the assumptions to be reasonable, thus resulting in a 100% energy realization rate. The demand savings were referenced from the ex ante analysis in lieu of using the demand savings factor, and the coincident demand savings for the heating measure was given a realization rate of 0% since there exists no coinciding load for heating with the utility peak period.
Source: C&I Custom Rebate Program Tracking Database and Guidehouse analysis
Trade Ally Satisfaction with Custom Program (on a scale of 1 through 5, 1 being the lowest, 5 being the highest)
Program Component | 5 | 4 | 3 | 2 | 1 | Not Sure | Not Applicable | Average Satisfaction (1-5)
Marketing materials provided by the program | 50% | 30% | 20% |  |  |  |  | 4.3333
Amount and type of communication and support received from the program | 60% | 40% | [5 empty] | 4.5556
Amount and type of training provided by the program | 50% | 20% | 20% |  |  |  | 10% | 4.375
Project application process | 50% | 40% | 10% |  |  |  |  | 4.4444
Time to complete a project the program | 60% | 20% | 20% |  |  |  |  | 4.4444
The amount of the program incentives | 20% | 60% | 10% | 10% |  |  |  | 3.8889
The Program Representative | 70% | 30% | [5 empty] | 4.6667
Overall satisfaction with Custom program | 30% | 20% | 10% | 10% |  | 30% |  | 4
Source: PY2 Guidehouse survey of trade allies; n = 10
Participant Satisfaction with Custom Program (on a scale of 1 through 5, 1 being the lowest, 5 being the highest)
Program Component | 5 | 4 | 3 | 2 | 1 | Average Satisfaction (1-5)
Amount of rebate | 31% | 62% | 8% | 0% | 0% | 4.2
Time to receive the rebate | 46% | 38% | 15% | 0% | 0% | 4.3
Requirements to participate | 38% | 62% | 0% | 0% | 0% | 4.4
Application process | 38% | 54% | 8% | 0% | 0% | 4.3
Pre-approval process | 50% | 50% | 0% | 0% | 0% | 4.5
Final approval process | 40% | 40% | 20% | 0% | 0% | 4.2
Installation contractor | 40% | 60% | 0% | 0% | 0% | 4.4
Program communications | 69% | 23% | 8% | 0% | 0% | 4.6
Program Representative | 77% | 15% | 8% | 0% | 0% | 4.7
Overall satisfaction | 54% | 46% | 0% | 0% | 0% | 4.5
Source: PY1 Guidehouse survey of participants; n = 13
Participant Satisfaction with Evergy (on a scale of 1 through 5, 1 being the lowest, 5 being the highest)
Program Component | 5 | 4 | 3 | 2 | 1 | Average Satisfaction (1-5)
Overall Satisfaction with Evergy | 72% | 21% | 5% | 3% | 0% | 4.7
Source: PY1 Guidehouse survey of participants; n = 39
Participant's Willingness to Participate in Evergy Rebate Program Again (on a scale of 1 through 5, 1 being "not at all likely", 5 being "very likely")
Program Component | 5 | 4 | 3 | 2 | 1 | Average Satisfaction (1-5)
Willingness to Participate | 85% | 15% | 0% | 0% | 0% | 4.9
Source: PY1 Guidehouse survey of participants; n = 39
Ease of completing Business Energy Efficiency Rebates Custom project
pre-approval application (on a scale of 1 through 5, 1 being "not at all easy", 5 being "extremely easy")
Program Component | 5 | 4 | 3 | 2 | 1 | Average Satisfaction (1-5)
Pre-approval application | 33% | 56% | 11% | 0% | 0% | 4.2
Source: PY1 Guidehouse survey of participants; n = 9
Participant's Agreement with Statements about Program Ease and Information
Program Component | 5 | 4 | 3 | 2 | 1 | Average Satisfaction (1-5)
The program is easy to work with and understand | 61% | 28% | 11% | 0% | 0% | 4.5
When I had questions, I knew who to contact | 72% | 17% | 6% | 6% | 0% | 4.6
I had enough information about measure eligibility and rebates to make decisions about which equipment to install. | 56% | 33% | 6% | 6% | 0% | 4.4
Source: PY1 Guidehouse survey of participants; n = 13

## Process Efficiency
Evergy Services, Inc. (ESI) Evaluation, Measurement, and Verification Report – Commercial & Industrial Databook
Process Efficiency: Data Tables
Executive Summary
Data is sourced to Guidehouse analysis unless otherwise noted. The program did not report savings in PY1 for either territory. The program did not report savings in PY2 for the Evergy Metro territory.
Evergy Metro Program Savings Summary - PY2
| Gross |  |  | Net
| Reported Savings | Verified Savings | Realization Rate | MEEIA 3-Year Target | Verified Savings | % of MEEIA Target Achieved
Energy at Customer Meter (kWh) | 0 | 0 | #DIV/0! | 19454539.392 | 0 | 0%
Coinc Demand at Customer Meter (kW) | 0 | 0 | #DIV/0! | 181.9584 | 0 | 0%
Source: Program Tracking Database and Guidehouse analysis
Evergy Metro Program Savings Summary - Program to Date
| Gross |  |  | Net
| Reported Savings | Verified Savings | Realization Rate | MEEIA 3-Year Target | Verified Savings | % of MEEIA Target Achieved
Energy at Customer Meter (kWh) | 0 | 0 | #DIV/0! | 19454539.392 | 0 | 0%
Coinc Demand at Customer Meter (kW) | 0 | 0 | #DIV/0! | 181.9584 | 0 | 0%
The program did not report savings in PY1 or PY2 for the Evergy Metro territory.
Source: Program Tracking Database and Guidehouse analysis
Evergy MO West Program Savings Summary - PY2
| Gross |  |  | Net
| Reported Savings | Verified Savings | Realization Rate | MEEIA 3-Year Target | Verified Savings | % of MEEIA Target Achieved
Energy at Customer Meter (kWh) | 467795 | 450363 | 96.27% | 20470674.24 | 450363 | 2.2%
Coinc Demand at Customer Meter (kW) | 73.5 | 66.31 | 90.22% | 227.448 | 66.31 | 29.15%
Source: Program Tracking Database and Guidehouse analysis
Evergy MO West Program Savings Summary - Program to Date
| Gross |  |  | Net
| Reported Savings | Verified Savings | Realization Rate | MEEIA 3-Year Target | Verified Savings | % of MEEIA Target Achieved
Energy at Customer Meter (kWh) | 467795 | 450363 | 96.27% | 20470674.24 | 450363 | 2.2%
Coinc Demand at Customer Meter (kW) | 73.5 | 66.31 | 90.22% | 227.448 | 66.31 | 29.15%
Source: Program Tracking Database and Guidehouse analysis
Net to Gross Component Summary
Free Ridership | Spillover | NTGR
0 | 0 | 1
Source: Deemed at 1, Guidehouse will conduct NTG research for this program in PY3
Evergy Metro Savings by Measure Type
Measure Type | Total Number of Projects | Reported Energy Savings (kWh) | Verified Energy Savings (kWh) | % of Total Verified Energy (%) | Reported Demand Savings (kW) | Verified Demand Savings (kW) | % of Total Verified Demand (%)
Compressed Air Leaks | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #DIV/0!
Total | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #DIV/0!
Source: Program Tracking Database and Guidehouse analysis
Evergy MO West Savings by Measure Type
Measure Type | Total Number of Projects | Reported Energy Savings (kWh) | Verified Energy Savings (kWh) | % of Total Verified Energy (%) | Reported Demand Savings (kW) | Verified Demand Savings (kW) | % of Total Verified Demand (%)
Compressed Air Leaks | 2 | 467795 | 450363 | 100% | 73.5 | 66.31 | 100%
Total | 2 | 467795 | 450363 | 100% | 73.5 | 66.31 | 100%

## OEA
Evergy Services, Inc. (ESI) Evaluation, Measurement, and Verification Report – Commercial & Industrial Databook
Energy Analyzer: Data Tables
Executive Summary
Data is sourced to Guidehouse analysis unless otherwise noted.
The Online Energy Analyzer program did not claim any savings in PY2.
The Online Energy Analyzer program did not report any savings in PY1 or PY2 of MEEIA Cycle 3.

## MEEIA 3 Targets
EVERGY MEEIA 3 Savings Targets
EVERGY Metro
kWh Savings | PY1 | PY2 | PY3 | Total
Business Standard | 14019242.584 | 19107931.2873 | 20850203.5583 | 53977377.4297
Business Custom | 5216972.5209 | 11114231.3937 | 13908599.1182 | 30239803.0328
Business Process Efficiency | 3273111.072 | 7191745.92 | 8989682.4 | 19454539.392
Online Business Energy Audit | 0 | 0 | 0 | 0
| 22509326.1769 | 37413908.601 | 43748485.0766 | 103671719.8545
kW Savings | PY1 | PY2 | PY3 | Total
Business Standard | 2181.3606 | 3012.8919 | 3328.3623 | 8522.6148
Business Custom | 833.8986 | 1776.5364 | 2223.1976 | 4833.6325
Business Process Efficiency | 24.4944 | 69.984 | 87.48 | 181.9584
Online Business Energy Audit |  |  |  | 0
| 3039.7536 | 4859.4122 | 5639.0399 | 13538.2057
EVERGY MO West
kWh Savings | PY1 | PY2 | PY3 | Total
Business Standard | 13647811.6702 | 16447376.8079 | 16551008.7209 | 46646197.1989
Business Custom | 2663601.48 | 3676320 | 3676320 | 10016241.48
Business Process Efficiency | 3618888.84 | 7639682.4 | 9212103 | 20470674.24
Online Business Energy Audit | 0 | 0 | 0 | 0
| 19930301.9902 | 27763379.2079 | 29439431.7209 | 77133112.9189
kW Savings | PY1 | PY2 | PY3 | Total
Business Standard | 2160.5438 | 2653.0255 | 2700.3204 | 7513.8897
Business Custom | 422.9424 | 581.869 | 581.869 | 1586.6804
Business Process Efficiency | 30.618 | 87.48 | 109.35 | 227.448
Online Business Energy Audit |  |  |  | 0
| 2614.1042 | 3322.3746 | 3391.5394 | 9328.0181