Before the Public Service Commission

Of the State of Missouri

| In the Matter of the Request of the City of Kennett, Missouri for a Waiver of Compliance from the Requirements of 4 CSR 240-40.030(15)(C) | )))) | Case No. GE-2003-0503 |
| --- | --- | --- |

## Staff Recommendation

COMES NOW the Staff (“Staff”) of the Missouri Public Service Commission (“Commission”) and respectfully states as follows:

1.	On May 20, 2003, the City of Kennett (“Kennett”), Missouri filed, pursuant to     4 CSR 240-40.030(16) and 4 CSR 240-2.060(4), a Request For Waiver from the requirements of 4 CSR 240-40.030(15)(C).

2.	In its Order And Notice, issued June 3, 2003, the Commission directed the Staff to file, by June 13, 2003, “a pleading stating when it will file its memorandum and recommendation.”  The Staff hereby files its Memorandum and Recommendation in lieu of that pleading.

3.  	Kennett desires a waiver from the requirement that a 6-inch steel yard line on the property of Emerson Electric Co. (“Emerson”) be replaced.  Emerson has installed insulators on the subject yard line and also applied cathodic protection.  In addition, Kennett leak surveys the line and surveys its cathodic protection on an annual basis.

4.	In the attached Memorandum (Appendix A), the Staff states that the 6-inch yard line need not be replaced and that safety will not be compromised provided that Kennett continues to conduct an annual leak survey and an annual cathodic protection survey on the line.

WHEREFORE, the Staff respectfully requests that the Commission grant the requested waiver, subject to the condition that the City of Kennett conduct an annual instrument leak survey and an annual cathodic protection survey on the subject 6-inch yard line.

Respectfully submitted,

DANA K. JOYCE

General Counsel

### Dennis L. Frey

Dennis L. Frey

Senior Counsel				Missouri Bar No. 44697

Attorney for the Staff of the

Missouri Public Service Commission

P. O. Box 360

Jefferson City, MO 65102

(573) 751-8700 (Telephone)

(573) 751-9285 (Fax)

e-mail:  dennyfrey@psc.state.mo.us

# Certificate of Service

I hereby certify that copies of the foregoing have been mailed, hand-delivered, transmitted by facsimile or emailed to all counsel of record this 6th day of June 2003.

### Dennis L. Frey