STAFF’S REPORT IN RESPONSE TO

# THE COMMISSION’S ORDER FOR STAFF TO CONTINUE ITS

ANNUAL REPORTING TO THE COMMISSION

## Case No. GO-99-155

BACKGROUND:

The Commission opened this case on October 30, 1998, as a general investigatory case to

receive information relevant to the adequacy of Laclede Gas Company’s direct-buried copper service line replacement program and the effectiveness of Laclede’s leak survey procedures.  On February 18, 2000, Laclede, Staff and the Office of the Public Counsel filed a Unanimous Stipulation and Agreement.  As part of the Agreement, Laclede agreed to submit annual reports to Staff detailing direct-buried copper service line renewal and relays completed, and agreed to submit additional reports confirming the achievement of other milestones under the Agreement.  The Agreement provided that after the third year of the program, Laclede and Staff would review the progress and results of the program to determine future relay/renewal plans, including the rate of such future actions, and potential modifications to leak survey techniques and other related matters.  On May 18, 2000, the Commission issued an order approving the Unanimous Stipulation and Agreement.

On August 1, 2003, Staff filed its Three-year Summary Report, which can be summarized as follows:

- Copper Service Line Relay/Renewals

Laclede replaced or eliminated a total of 26,246 direct-buried copper service lines during the first three years of the program, which represents approximately 34 percent of the program’s beginning total qualifying lines (76,966).  The Stipulation requires Laclede to replace or renew 8,000 lines annually and Laclede had exceeded the annual minimum rate of renewals.

Staff recommended, unless otherwise ordered by the Commission, that Laclede continue to renew a minimum of 8,000 direct-buried copper service lines annually.

2. 	Leak Surveys

Laclede successfully completed an annual bar-hole leak survey for each of the first three program years, with each survey completed by July 1st of that year.  In 1999, Laclede first completed a bar-hole leak survey producing a 3.4 percent leak rate.  Laclede’s 2002 bar-hole leak survey of approximately 60,000 direct-buried copper service lines produced a leak rate of 1.1 percent.  The reduction in leak rate from Year 1999 to Year 2002 was approximately a 68 percent (68%) reduction in discovery of new leaks during annual bar-hole leak surveys.  Laclede’s Year 2003 bar-hole leak survey of approximately 52,000 direct-buried copper service lines yielded a new leak discovery rate of slightly over 1 percent (1.06%), but below Year 2002 new leak rates.

The Guidelines of the Stipulation mandate practices that provide for early leak detection on direct-buried copper service lines.  Therefore, the Staff recommended that, as it pertains to leak surveys, Laclede continue to perform an annual bar-hole leak survey.  The Stipulation specifically states that an annual bar-hole survey shall be conducted for the first three program years.  Because at the time of Staff’s Three-Year Summary Report nothing had been shown to be superior in the detection of sub-surface leaks than strategically placing bar-holes over certain service line locations and conducting a leak survey, the Staff recommended that the annual bar-hole leak surveys continue.

- Leak Repairs

Any Class 1 or 2 leak is repaired immediately.  Otherwise, in accordance with the Agreement, leaks detected during an annual bar-hole leak survey are required to be repaired within six (6) months, or at the latest within a year of discovery, depending on whether the leaks are located in Pressure Regions I or II (Pressure Region I includes direct-buried copper service lines that can operate above 35 psig, while these same service lines in Pressure Region II operate below 35 psig).  These leak repair requirements are more stringent than MoPSC Pipeline Safety Regulations, which generally require that Class 3 leaks, which are not considered to be a hazard, be monitored every 6 months and repaired within 5 years.

For the first three years of the program, Laclede repaired most Class 3 leaks in Pressure Region I within an average time of three to four months after discovery, instead of the six months allowed under the Program.  While Class 3 leaks in Pressure Region II require repair within one year of discovery, Laclede averaged seven to nine months for these repairs.

Making timely repairs prior to the subsequent bar-hole leak survey:  (1) provides for more accurate studies of data; (2) facilitates determination of leak trends in leak totals; and (3) improves detection of differences in areas where corrosion may be more or less active.  For these reasons, Staff recommended maintaining the timely repair requirements of six months for Pressure Region I leaks, and one year for Pressure Region II leaks, as stated in the Stipulation.

INTRODUCTON:

Subsequent to the filing of Staff’s Three-Year Summary Report, on March 5, 2004, the Commission issued a REPORT AND ORDER in which the Commission approved Staff’s recommendation that the Commission continue the current requirements of the previously approved Stipulation and Agreement, with annual reporting from Staff to the Commission.

REPORT OVERVIEW:

The following report pertains to the Unanimous Stipulation and Agreement (Agreement) in Case No. GO-99-155, Laclede’s Gas Company’s direct-buried copper service line replacement program.  This update report summarizes data obtained (through August 2004) during Staff’s ongoing monitoring of the program’s progress, addresses information relevant to the adequacy of Laclede’s copper service line replacement program, and discusses the effectiveness of the Company’s leak surveys and investigations.  For purposes of this report, Staff will touch upon the major points of Laclede’s program.  Staff notes that this program does appear to be yielding a number of positive results.

It should be noted that, unless otherwise ordered by the Commission, Laclede is required to follow, at a minimum, the guidelines of the Agreement until completion of the entire program.  If, at any time, Staff determines that the program requirements are inadequate, Staff would immediately bring its concerns and recommendations to the Commission.

STAFF INVESTIGATION/ANNUAL REPORT

- Bar-hole Leak Surveys

Laclede conducted its 2004 bar-hole leak survey during the months of March – July 2004.  Laclede personnel conducted a bar-hole leak survey over 10,253 direct-buried copper service lines in Pressure Region I and conducted a bar-hole leak survey over 34,371 direct-buried copper service lines in Pressure Region II for a total of 44,624 direct-buried copper service line bar-hole leak surveys during the 2004 survey.   A total of 409 leaks were found during the 2004 bar-hole leak survey, which represents a 0.92 percent leak rate for the 2004 survey.  As reported in Staff’s August 2003 Three-Year Summary Report, results from bar-hole leak surveys have shown a downward trend in the actual total number of new leaks discovered on copper service lines.  Observations in the fourth year of Laclede’s program indicate that this downward trend is continuing with the new leak rate of 0.92 percent, which is an approximate 13 percent decrease from the leakage rates found during the 2003 leak survey.

While the bar-hole method for leak surveying demands more personnel time and effort, it is Staff’s opinion that this method is far superior to other methods in the detection of small leaks that previously might have gone undetected.  This superior method of leak detection, coupled with conducting the surveys on an annual basis, helps in achieving the program goals of early detection before the leak becomes hazardous and assists in prioritizing replacements.  As mentioned previously in this report, this guideline of the Agreement exceeds MoPSC minimum pipeline safety regulations that require 3-year leak surveys on most residential service lines.

For these reasons, the Staff recommends that Laclede continue to conduct an annual bar-hole leak survey of direct-buried copper service lines.

2.	Leak Repairs

Expediting the removal of all leaks found during a bar-hole leak survey prior to conducting the subsequent year’s bar-hole leak survey continues to enhance the downward trend in detected leaks during subsequent annual bar-hole leak surveys.  As mentioned previously in this report, in accordance with the Agreement, leaks detected during an annual bar-hole leak survey are required to be repaired within six months of discovery in Pressure Region I and within one year of discovery in Pressure Region II.  Laclede continues to exceed the requirements in the Agreement by repairing Class 3 leaks in Pressure Region I within an average time of three months (down from 3 to 4 months during the first 3 years of the program) from discovery and within an average time of seven months (down from 7 to 9 months during the first 3 years of the program) from discovery in Pressure Region II.  As mentioned earlier in this report, the guideline in the Agreement exceeds MoPSC minimum pipeline safety regulations that require Class 3 leaks to be monitored every 6 months until repaired (within 5 years of discovery).

All detected leaks, along with other historical information, are used in a prioritization model for identifying replacement areas in a consistent manner and prioritizing the scheduling of these areas for replacement.  It is critical that any upward trends in new leaks on replacement program pipelines be identified promptly, as upward trends can point to the need to refocus efforts to stiffen requirements to meet the program’s goals and objectives.

The Staff believes that timely repairs of observed leaks prior to the subsequent bar-hole leak survey provides better information to detect any upward trends in leakage rate totals and, therefore, that the requirements in the Agreement calling for Class 3 leaks in Pressure Region I to be repaired within six months and Class 3 leaks in Pressure Region II to be repaired within one year be continued.

3.	Copper Service Line Replacements

During program year four (12 months ending March 1, 2004), Laclede completed a total of 8,264 direct-buried copper service line replacements (main-to-meter).  During the first four years of the program, Laclede has completed a total of 33,616 direct-buried copper service line replacements, which represents approximately 43 percent of the program’s beginning total qualifying services.  Through the end of program year four, Laclede has averaged 8,404 direct-buried copper service line replacements each year, which exceeds the Agreement’s criteria of an annual replacement rate of 8,000 direct-buried copper service lines.

The Staff believes that an aggressive annual replacement rate (i.e. 10% annually), based upon priority, with increased frequencies of leak surveys, continues to be successful and, therefore, recommends that the annual requirement of 8,000 direct-buried copper service line replacements should be maintained at this time.  Current results of this portion of the program are a substantial reduction in the number of direct-buried copper service lines and a substantially reduced leakage rate in the lines that remain to be replaced.

FINAL SUMMARY

The Guidelines contained in the Stipulation are the three-point foundation of Laclede’s current direct-buried copper service line replacement program.  First, priority replacements.  Second, leak surveys.  Third, timely leak repairs.  All must be considered together in order to achieve the purpose of the Stipulation, which is protection of the public’s safety, and each, must therefore, complement the other.  At this time, Staff believes that the efforts of the parties in meeting the Stipulation requirements are achieving this purpose, and this is supported by the results discussed in the preceding report.  Based on these observations, the Staff recommends that the Commission continue with the current requirements of the Stipulation and Agreement.

For the term of this program, Staff has and will continue to monitor the effectiveness of Laclede’ direct-buried copper service line replacements and leak surveys.  If at any time, Staff determines that the program requirements should be enhanced, it will immediately bring its concerns and recommendations to the Commission.