GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511437 | COMANC-4 | 138 | 18.74 | 18.8 | 0.06
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511438 | DUKE---2 | 69 | 3.49 | 3.56 | 0.07
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511439 | LWSTAP 4 | 138 | 11.9 | 11.98 | 0.08
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511440 | ALTUSJT4 | 138 | 5 | 5.12 | 0.12
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511441 | ALTUSJT2 | 69 | 5.73 | 5.87 | 0.14
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511444 | ROSVTAP2 | 69 | 4.1 | 4.16 | 0.06
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511460 | FREDJC-2 | 69 | 2.89 | 2.98 | 0.09
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511462 | HEADRIK2 | 69 | 4.67 | 4.79 | 0.12
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511465 | HOBART-2 | 69 | 5.75 | 5.81 | 0.06
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511467 | L.E.S.-4 | 138 | 25.51 | 25.59 | 0.08
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511471 | LWS-NTP4 | 138 | 12.02 | 12.1 | 0.08
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511472 | TIPTE T2 | 69 | 3.78 | 3.89 | 0.11
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511475 | SNYDER-2 | 69 | 7.7 | 7.92 | 0.22
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511479 | TIPTCTY2 | 69 | 2.44 | 2.51 | 0.07
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511488 | 112GORE4 | 138 | 13.09 | 13.18 | 0.09
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511494 | COMMTAP4 | 138 | 22.29 | 22.36 | 0.07
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511495 | TOMSTEED2 | 69 | 4.33 | 4.42 | 0.09
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511500 | CACHE4 | 138 | 8.58 | 8.7 | 0.12
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511509 | 53CACHE4 | 138 | 12.06 | 12.13 | 0.07
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511510 | LAIRGST4 | 138 | 12.67 | 12.77 | 0.1
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511512 | RPPAPER4 | 138 | 12.33 | 12.42 | 0.09
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511520 | DAV TAP2 | 69 | 2.3 | 2.35 | 0.05
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511543 | TIPTN T2 | 69 | 4.66 | 4.79 | 0.13
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511545 | TIPTON 2 | 69 | 2.6 | 2.67 | 0.07
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 512101 | CHILD4WT | 138 | 1.74 | 1.77 | 0.03
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 512110 | LAKEP4WT | 138 | 2.24 | 2.29 | 0.05
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 512111 | LAKEP2WT | 69 | 3.23 | 3.29 | 0.06
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 520404 | MDCPRK4 | 138 | 5.81 | 5.87 | 0.06
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 520410 | CACHE4 | 138 | 5 | 5.1 | 0.1
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 520491 | NAVAJO 2 | 69 | 2.33 | 2.38 | 0.05
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 520528 | ROSEVLT2 | 69 | 3.98 | 4.07 | 0.09
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 520534 | DUKE 2 | 69 | 4.28 | 4.37 | 0.09
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 520803 | ALTUS_ 2 | 69 | 3.49 | 3.58 | 0.09
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 520805 | ALTUSSW2 | 69 | 3.52 | 3.61 | 0.09
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 520914 | FREDRIK2 | 69 | 3.65 | 3.73 | 0.08
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 520954 | INDHOMA4 | 138 | 4.37 | 4.45 | 0.08
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 521009 | NAVJOTP2 | 69 | 3.61 | 3.7 | 0.09
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 521024 | PARADSE4 | 138 | 6.2 | 6.25 | 0.05
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 521042 | RUSSELL2 | 69 | 4.28 | 4.37 | 0.09
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 521043 | RUSSELL4 | 138 | 3.74 | 3.83 | 0.09
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 521051 | SNYDER 2 | 69 | 7.08 | 7.29 | 0.21
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 521052 | SNYDER 4 | 138 | 6.42 | 6.62 | 0.2
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 521069 | TIPTON-2 | 69 | 1.5 | 1.54 | 0.04
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 521070 | TIPTONJ2 | 69 | 4.13 | 4.23 | 0.1
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 521081 | VERNON 2 | 69 | 2.48 | 2.54 | 0.06
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 521190 | CACHEJ4 | 138 | 5.4 | 5.51 | 0.11
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 529298 | OMPVET-4 | 138 | 4.65 | 4.75 | 0.1
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 529302 | OMALTUS4 | 138 | 4.56 | 4.65 | 0.09
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 529345 | OMPARK-4 | 138 | 4.82 | 4.93 | 0.11
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 584550 | GEN-2015-013 | 138 | 6.41 | 6.6 | 0.19
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 588780 | GEN-2017-036 | 138 | 6.65 | 6.87 | 0.22
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 588904 | G17-051-TAP | 69 | 3.2 | 3.25 | 0.05
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 999600 | TAP_G17-036 | 138 | 6.86 | 7.09 | 0.23
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 511435 | SNYDER-4 | 138 | 7.09 | 7.12 | 0.03
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 511438 | DUKE---2 | 69 | 3.49 | 3.56 | 0.07
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 511440 | ALTUSJT4 | 138 | 5.1 | 5.12 | 0.02
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 511441 | ALTUSJT2 | 69 | 5.85 | 5.87 | 0.02
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 511460 | FREDJC-2 | 69 | 2.96 | 2.98 | 0.02
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 511475 | SNYDER-2 | 69 | 7.89 | 7.92 | 0.03
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 511520 | DAV TAP2 | 69 | 2.33 | 2.35 | 0.02
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 511521 | DAVDSON2 | 69 | 1.85 | 1.87 | 0.02
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 511543 | TIPTN T2 | 69 | 4.77 | 4.79 | 0.02
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 512100 | CHLDR2WT | 69 | 2.39 | 2.4 | 0.01
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 512101 | CHILD4WT | 138 | 1.76 | 1.77 | 0.01
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 512103 | HOLTP4WT | 138 | 1.58 | 1.59 | 0.01
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 512110 | LAKEP4WT | 138 | 2.27 | 2.29 | 0.02
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 512111 | LAKEP2WT | 69 | 3.27 | 3.29 | 0.02
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 512113 | VRNMTAP2 | 69 | 2.5 | 2.54 | 0.04
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 520481 | DIVERSN2 | 69 | 1.39 | 1.4 | 0.01
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 520491 | NAVAJO 2 | 69 | 2.36 | 2.38 | 0.02
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 520499 | WHTECTY2 | 69 | 1.95 | 1.98 | 0.03
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 520504 | GOULD 2 | 69 | 2.04 | 2.07 | 0.03
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 520534 | DUKE 2 | 69 | 4.28 | 4.37 | 0.09
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 520803 | ALTUS_ 2 | 69 | 3.53 | 3.58 | 0.05
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 520804 | ALTUSAF2 | 69 | 2.92 | 2.96 | 0.04
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 520805 | ALTUSSW2 | 69 | 3.56 | 3.61 | 0.05
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 520846 | CARTERJ2 | 69 | 3.85 | 3.89 | 0.04
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 520876 | DILL JT2 | 69 | 4.58 | 4.61 | 0.03
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 520877 | DIVERSW2 | 69 | 1.86 | 1.88 | 0.02
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 520894 | ELCTRSW2 | 69 | 1.93 | 1.94 | 0.01
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 520895 | ELDORDJ2 | 69 | 2.44 | 2.47 | 0.03
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 520896 | ELDORDO2 | 69 | 2.22 | 2.24 | 0.02
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 520925 | GOTEBO 2 | 69 | 4.28 | 4.31 | 0.03
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 520927 | GRANITE2 | 69 | 3.2 | 3.3 | 0.1
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 520929 | GYPSUM 2 | 69 | 3.31 | 3.37 | 0.06
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 520978 | LKCREEK2 | 69 | 3.68 | 3.76 | 0.08
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 520980 | LOCKETT2 | 69 | 2 | 2.03 | 0.03
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 520982 | LONEWLF2 | 69 | 3.22 | 3.27 | 0.05
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 521009 | NAVJOTP2 | 69 | 3.66 | 3.7 | 0.04
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 521042 | RUSSELL2 | 69 | 4.28 | 4.37 | 0.09
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 521043 | RUSSELL4 | 138 | 3.8 | 3.83 | 0.03
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 521051 | SNYDER 2 | 69 | 7.25 | 7.29 | 0.04
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 521052 | SNYDER 4 | 138 | 6.59 | 6.62 | 0.03
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 521081 | VERNON 2 | 69 | 2.51 | 2.54 | 0.03
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 529298 | OMPVET-4 | 138 | 4.73 | 4.75 | 0.02
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 529342 | OMMANGM2 | 69 | 3.1 | 3.21 | 0.11
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 529345 | OMPARK-4 | 138 | 4.91 | 4.93 | 0.02
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 588900 | GEN-2017-051 | 69 | 3.11 | 3.25 | 0.14
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 588904 | G17-051-TAP | 69 | 3.11 | 3.25 | 0.14
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 999600 | TAP_G17-036 | 138 | 7.06 | 7.09 | 0.03
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508048 | PLEASHL2 | 69 | 7.06 | 7.08 | 0.02
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508052 | ATLANTA2 | 69 | 5.49 | 5.53 | 0.04
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508055 | BLOOMBG2 | 69 | 5.63 | 5.73 | 0.1
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508058 | IPC TAP2 | 69 | 5.61 | 5.64 | 0.03
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508089 | WATLANT2 | 69 | 8.29 | 8.31 | 0.02
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508092 | IPC 2 | 69 | 4.59 | 4.62 | 0.03
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508800 | BELCHER2 | 69 | 3.19 | 3.4 | 0.21
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508801 | BLANCH-2 | 69 | 6.8 | 6.86 | 0.06
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508803 | GILLIAM2 | 69 | 4.91 | 5.37 | 0.46
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508804 | HOSSTON2 | 69 | 5.55 | 6.3 | 0.75
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508805 | LIEBERM2 | 69 | 8.98 | 9.16 | 0.18
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508806 | LIEBERM4 | 138 | 16.85 | 16.95 | 0.1
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508807 | LINTNRD4 | 138 | 9 | 9.04 | 0.04
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508810 | NBENTON2 | 69 | 4.36 | 4.43 | 0.07
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508811 | NBENTON4 | 138 | 9.31 | 9.36 | 0.05
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508812 | OILCITY2 | 69 | 7.13 | 7.39 | 0.26
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508813 | PLAINDL2 | 69 | 3.71 | 3.88 | 0.17
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508814 | RODESSA2 | 69 | 4.3 | 4.54 | 0.24
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508815 | SUPEROR2 | 69 | 6.44 | 6.88 | 0.44
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508817 | VIVIAN 2 | 69 | 5.13 | 5.55 | 0.42
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508818 | MOTT TP2 | 69 | 3.71 | 3.86 | 0.15
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508828 | MOTT 2 | 69 | 3.29 | 3.42 | 0.13
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508830 | BALDWIN2 | 69 | 4.7 | 4.72 | 0.02
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508834 | JEFFRSN2 | 69 | 4.41 | 4.46 | 0.05
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508838 | NMARSHL2 | 69 | 9.9 | 9.91 | 0.01
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508842 | WOODLWN2 | 69 | 5.89 | 5.93 | 0.04
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508846 | GODFREYRDTP2 | 69 | 4.31 | 4.56 | 0.25
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 588404 | G16-167-TAP | 138 | 10.01 | 10.07 | 0.06
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 588950 | GEN-2017-057 | 69 | 4.9 | 5.66 | 0.76
GEN-2017-023 | South | 14 - South Central Oklahoma | 504124 | ASHDWN_W 4 | 138 | 9.97 | 9.98 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 505614 | BRKN BW4 | 138 | 7.62 | 7.64 | 0.02
GEN-2017-023 | South | 14 - South Central Oklahoma | 507419 | DEQUEEN4 | 138 | 4.25 | 4.26 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 507431 | PATTERS4 | 138 | 13.11 | 13.12 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 507454 | TURK 4 | 138 | 24.61 | 24.62 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 507455 | TURK 7 | 345 | 9.03 | 9.04 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 507461 | GORDON TAP 4 | 138 | 2.68 | 2.68 | 0
GEN-2017-023 | South | 14 - South Central Oklahoma | 508049 | NASH 4 | 138 | 19.53 | 19.55 | 0.02
GEN-2017-023 | South | 14 - South Central Oklahoma | 508070 | NWT-BNT4 | 138 | 24.01 | 24.03 | 0.02
GEN-2017-023 | South | 14 - South Central Oklahoma | 508071 | NWTXARK4 | 138 | 25.01 | 25.03 | 0.02
GEN-2017-023 | South | 14 - South Central Oklahoma | 508072 | NWTXARK7 | 345 | 13.38 | 13.4 | 0.02
GEN-2017-023 | South | 14 - South Central Oklahoma | 508080 | SUGARHL4 | 138 | 12.14 | 12.15 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 508298 | LYDIA 7 | 345 | 12.94 | 12.96 | 0.02
GEN-2017-023 | South | 14 - South Central Oklahoma | 508359 | WELSH 7 | 345 | 21.37 | 21.38 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 508832 | DIANA 7 | 345 | 19.23 | 19.24 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 508841 | WILKES 7 | 345 | 15.53 | 15.53 | 0
GEN-2017-023 | South | 14 - South Central Oklahoma | 510864 | B.BOW 4 | 138 | 6.36 | 6.37 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 510866 | V-WEYCO4 | 138 | 10.06 | 10.08 | 0.02
GEN-2017-023 | South | 14 - South Central Oklahoma | 510867 | KI PMPS2 | 69 | 3.19 | 3.2 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 510868 | GA PAC 2 | 69 | 2.58 | 2.58 | 0
GEN-2017-023 | South | 14 - South Central Oklahoma | 510869 | W CITY 2 | 69 | 3.98 | 3.99 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 510870 | WCITYTP2 | 69 | 6.57 | 6.59 | 0.02
GEN-2017-023 | South | 14 - South Central Oklahoma | 510875 | KI PMPN2 | 69 | 3.49 | 3.5 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 510876 | KIPUMPT2 | 69 | 4.89 | 4.91 | 0.02
GEN-2017-023 | South | 14 - South Central Oklahoma | 510886 | IDABEL-4 | 138 | 7.03 | 7.04 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 510888 | B.BOWTP4 | 138 | 7.39 | 7.4 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 510890 | CRAIGJT4 | 138 | 8.89 | 8.91 | 0.02
GEN-2017-023 | South | 14 - South Central Oklahoma | 510893 | HUGO---2 | 69 | 5.21 | 5.23 | 0.02
GEN-2017-023 | South | 14 - South Central Oklahoma | 510894 | VALYTIM2 | 69 | 2.78 | 2.79 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 510901 | HUGO---4 | 138 | 3.62 | 3.62 | 0
GEN-2017-023 | South | 14 - South Central Oklahoma | 510907 | PITTSB-7 | 345 | 14.18 | 14.19 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 510910 | VALIANT2 | 69 | 7.55 | 7.57 | 0.02
GEN-2017-023 | South | 14 - South Central Oklahoma | 510911 | VALIANT7 | 345 | 13.64 | 13.67 | 0.03
GEN-2017-023 | South | 14 - South Central Oklahoma | 510915 | ANTLTAP2 | 69 | 2.57 | 2.58 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 510917 | FTOWSON2 | 69 | 3.81 | 3.82 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 510918 | VALIANT4 | 138 | 15.37 | 15.41 | 0.04
GEN-2017-023 | South | 14 - South Central Oklahoma | 510920 | SAWYER 2 | 69 | 3.74 | 3.75 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 510925 | KIOWA 7 | 345 | 13.92 | 13.93 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 510946 | C-RIVER4 | 138 | 13.38 | 13.39 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 511468 | L.E.S.-7 | 345 | 13.59 | 13.59 | 0
GEN-2017-023 | South | 14 - South Central Oklahoma | 511568 | TERRYRD7 | 345 | 10.33 | 10.33 | 0
GEN-2017-023 | South | 14 - South Central Oklahoma | 511571 | RUSHSPR7 | 345 | 6.68 | 6.68 | 0
GEN-2017-023 | South | 14 - South Central Oklahoma | 514808 | JOHNCO 4 | 138 | 15.71 | 15.73 | 0.02
GEN-2017-023 | South | 14 - South Central Oklahoma | 514809 | JOHNCO 7 | 345 | 10.26 | 10.27 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 514908 | ARCADIA7 | 345 | 30.87 | 30.87 | 0
GEN-2017-023 | South | 14 - South Central Oklahoma | 514934 | DRAPER 7 | 345 | 21.39 | 21.39 | 0
GEN-2017-023 | South | 14 - South Central Oklahoma | 515044 | SEMINOL4 | 138 | 41.08 | 41.09 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 515045 | SEMINOL7 | 345 | 27.22 | 27.23 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 515135 | SUNNYSD4 | 138 | 19.3 | 19.31 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 515136 | SUNNYSD7 | 345 | 11.52 | 11.53 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 515137 | UNIROY 4 | 138 | 12.98 | 12.99 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 515144 | LONEGRV4 | 138 | 13.92 | 13.93 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 515164 | ROCKYPT4 | 138 | 10.82 | 10.83 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 515224 | MUSKOGE7 | 345 | 29.64 | 29.64 | 0
GEN-2017-023 | South | 14 - South Central Oklahoma | 515422 | C-RIVER7 | 345 | 10.29 | 10.3 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 515561 | CARTRCO4 | 138 | 10.1 | 10.1 | 0
GEN-2017-023 | South | 14 - South Central Oklahoma | 520411 | SAWYER4 | 138 | 10.92 | 10.97 | 0.05
GEN-2017-023 | South | 14 - South Central Oklahoma | 520419 | GARVIN4 | 138 | 6.2 | 6.22 | 0.02
GEN-2017-023 | South | 14 - South Central Oklahoma | 520466 | HAWORTH4 | 138 | 4.29 | 4.3 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 520497 | WSTBANK4 | 138 | 5.36 | 5.38 | 0.02
GEN-2017-023 | South | 14 - South Central Oklahoma | 520826 | BENNGTN4 | 138 | 4.86 | 4.87 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 520834 | BROKNBW4 | 138 | 7.04 | 7.05 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 520874 | DARWIN 4 | 138 | 4.98 | 4.99 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 520884 | DURANTP4 | 138 | 5.67 | 5.68 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 520918 | FROGVIL4 | 138 | 11.09 | 11.14 | 0.05
GEN-2017-023 | South | 14 - South Central Oklahoma | 520946 | HOLYCRK4 | 138 | 6.52 | 6.53 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 520948 | HUGO PP4 | 138 | 23.23 | 23.33 | 0.1
GEN-2017-023 | South | 14 - South Central Oklahoma | 520953 | IDABEL 4 | 138 | 6.27 | 6.29 | 0.02
GEN-2017-023 | South | 14 - South Central Oklahoma | 520968 | LANE 4 | 138 | 5.23 | 5.25 | 0.02
GEN-2017-023 | South | 14 - South Central Oklahoma | 521004 | MTRIVER4 | 138 | 8.55 | 8.56 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 521036 | RATTAN 4 | 138 | 7.12 | 7.14 | 0.02
GEN-2017-023 | South | 14 - South Central Oklahoma | 521077 | UNGER 4 | 138 | 5.18 | 5.2 | 0.02
GEN-2017-023 | South | 14 - South Central Oklahoma | 521079 | VALLANT4 | 138 | 8.92 | 8.96 | 0.04
GEN-2017-023 | South | 14 - South Central Oklahoma | 521098 | WSBNKTP4 | 138 | 6.88 | 6.91 | 0.03
GEN-2017-023 | South | 14 - South Central Oklahoma | 521115 | BENNSUB4 | 138 | 4.58 | 4.59 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 521157 | HUGO 7 | 345 | 11.58 | 11.61 | 0.03
GEN-2017-023 | South | 14 - South Central Oklahoma | 521187 | ATKEAST4 | 138 | 5.45 | 5.46 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 560088 | G16-063-TAP | 345 | 8.18 | 8.2 | 0.02
GEN-2017-023 | South | 14 - South Central Oklahoma | 584780 | GEN-2015-036 | 345 | 7.33 | 7.33 | 0
GEN-2017-023 | South | 14 - South Central Oklahoma | 587430 | GEN-2016-063 | 345 | 8.08 | 8.09 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 588670 | GEN-2017-023 | 138 | 19.23 | 19.35 | 0.12
GEN-2017-023 | South | 14 - South Central Oklahoma | 588680 | GEN-2017-024 | 138 | 10.68 | 10.72 | 0.04
GEN-2017-023 | South | 14 - South Central Oklahoma | 588839 | FIREWHL-TAP | 345 | 11.59 | 11.59 | 0
GEN-2017-023 | South | 14 - South Central Oklahoma | 589130 | GEN-2017-075 | 345 | 8.17 | 8.18 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 599892 | EASTDC 7 | 345 | 6.29 | 6.29 | 0
GEN-2017-024 | South | 14 - South Central Oklahoma | 507455 | TURK 7 | 345 | 9.03 | 9.04 | 0.01
GEN-2017-024 | South | 14 - South Central Oklahoma | 508071 | NWTXARK4 | 138 | 25.02 | 25.03 | 0.01
GEN-2017-024 | South | 14 - South Central Oklahoma | 508072 | NWTXARK7 | 345 | 13.39 | 13.4 | 0.01
GEN-2017-024 | South | 14 - South Central Oklahoma | 508298 | LYDIA 7 | 345 | 12.95 | 12.96 | 0.01
GEN-2017-024 | South | 14 - South Central Oklahoma | 508359 | WELSH 7 | 345 | 21.38 | 21.38 | 0
GEN-2017-024 | South | 14 - South Central Oklahoma | 510864 | B.BOW 4 | 138 | 6.36 | 6.37 | 0.01
GEN-2017-024 | South | 14 - South Central Oklahoma | 510866 | V-WEYCO4 | 138 | 10.07 | 10.08 | 0.01
GEN-2017-024 | South | 14 - South Central Oklahoma | 510868 | GA PAC 2 | 69 | 2.58 | 2.58 | 0
GEN-2017-024 | South | 14 - South Central Oklahoma | 510869 | W CITY 2 | 69 | 3.99 | 3.99 | 0
GEN-2017-024 | South | 14 - South Central Oklahoma | 510870 | WCITYTP2 | 69 | 6.58 | 6.59 | 0.01
GEN-2017-024 | South | 14 - South Central Oklahoma | 510875 | KI PMPN2 | 69 | 3.5 | 3.5 | 0
GEN-2017-024 | South | 14 - South Central Oklahoma | 510876 | KIPUMPT2 | 69 | 4.9 | 4.91 | 0.01
GEN-2017-024 | South | 14 - South Central Oklahoma | 510886 | IDABEL-4 | 138 | 7.04 | 7.04 | 0
GEN-2017-024 | South | 14 - South Central Oklahoma | 510888 | B.BOWTP4 | 138 | 7.39 | 7.4 | 0.01
GEN-2017-024 | South | 14 - South Central Oklahoma | 510890 | CRAIGJT4 | 138 | 8.9 | 8.91 | 0.01
GEN-2017-024 | South | 14 - South Central Oklahoma | 510893 | HUGO---2 | 69 | 5.22 | 5.23 | 0.01
GEN-2017-024 | South | 14 - South Central Oklahoma | 510894 | VALYTIM2 | 69 | 2.78 | 2.79 | 0.01
GEN-2017-024 | South | 14 - South Central Oklahoma | 510901 | HUGO---4 | 138 | 3.62 | 3.62 | 0
GEN-2017-024 | South | 14 - South Central Oklahoma | 510907 | PITTSB-7 | 345 | 14.18 | 14.19 | 0.01
GEN-2017-024 | South | 14 - South Central Oklahoma | 510910 | VALIANT2 | 69 | 7.56 | 7.57 | 0.01
GEN-2017-024 | South | 14 - South Central Oklahoma | 510911 | VALIANT7 | 345 | 13.65 | 13.67 | 0.02
GEN-2017-024 | South | 14 - South Central Oklahoma | 510917 | FTOWSON2 | 69 | 3.81 | 3.82 | 0.01
GEN-2017-024 | South | 14 - South Central Oklahoma | 510918 | VALIANT4 | 138 | 15.39 | 15.41 | 0.02
GEN-2017-024 | South | 14 - South Central Oklahoma | 510920 | SAWYER 2 | 69 | 3.75 | 3.75 | 0
GEN-2017-024 | South | 14 - South Central Oklahoma | 510925 | KIOWA 7 | 345 | 13.93 | 13.93 | 0
GEN-2017-024 | South | 14 - South Central Oklahoma | 511568 | TERRYRD7 | 345 | 10.33 | 10.33 | 0
GEN-2017-024 | South | 14 - South Central Oklahoma | 514809 | JOHNCO 7 | 345 | 10.26 | 10.27 | 0.01
GEN-2017-024 | South | 14 - South Central Oklahoma | 515045 | SEMINOL7 | 345 | 27.22 | 27.23 | 0.01
GEN-2017-024 | South | 14 - South Central Oklahoma | 515135 | SUNNYSD4 | 138 | 19.3 | 19.31 | 0.01
GEN-2017-024 | South | 14 - South Central Oklahoma | 515136 | SUNNYSD7 | 345 | 11.52 | 11.53 | 0.01
GEN-2017-024 | South | 14 - South Central Oklahoma | 515422 | C-RIVER7 | 345 | 10.29 | 10.3 | 0.01
GEN-2017-024 | South | 14 - South Central Oklahoma | 515568 | KEYSTNT4 | 138 | 3.93 | 3.94 | 0.01
GEN-2017-024 | South | 14 - South Central Oklahoma | 520411 | SAWYER4 | 138 | 10.94 | 10.97 | 0.03
GEN-2017-024 | South | 14 - South Central Oklahoma | 520419 | GARVIN4 | 138 | 6.2 | 6.22 | 0.02
GEN-2017-024 | South | 14 - South Central Oklahoma | 520466 | HAWORTH4 | 138 | 4.3 | 4.3 | 0
GEN-2017-024 | South | 14 - South Central Oklahoma | 520483 | DURANT 4 | 138 | 4.77 | 4.78 | 0.01
GEN-2017-024 | South | 14 - South Central Oklahoma | 520497 | WSTBANK4 | 138 | 5.35 | 5.38 | 0.03
GEN-2017-024 | South | 14 - South Central Oklahoma | 520826 | BENNGTN4 | 138 | 4.85 | 4.87 | 0.02
GEN-2017-024 | South | 14 - South Central Oklahoma | 520874 | DARWIN 4 | 138 | 4.98 | 4.99 | 0.01
GEN-2017-024 | South | 14 - South Central Oklahoma | 520884 | DURANTP4 | 138 | 5.66 | 5.68 | 0.02
GEN-2017-024 | South | 14 - South Central Oklahoma | 520918 | FROGVIL4 | 138 | 11.07 | 11.14 | 0.07
GEN-2017-024 | South | 14 - South Central Oklahoma | 520946 | HOLYCRK4 | 138 | 6.52 | 6.53 | 0.01
GEN-2017-024 | South | 14 - South Central Oklahoma | 520948 | HUGO PP4 | 138 | 23.27 | 23.33 | 0.06
GEN-2017-024 | South | 14 - South Central Oklahoma | 520953 | IDABEL 4 | 138 | 6.28 | 6.29 | 0.01
GEN-2017-024 | South | 14 - South Central Oklahoma | 520968 | LANE 4 | 138 | 5.24 | 5.25 | 0.01
GEN-2017-024 | South | 14 - South Central Oklahoma | 521036 | RATTAN 4 | 138 | 7.13 | 7.14 | 0.01
GEN-2017-024 | South | 14 - South Central Oklahoma | 521049 | SCLMNJC4 | 138 | 7.38 | 7.39 | 0.01
GEN-2017-024 | South | 14 - South Central Oklahoma | 521077 | UNGER 4 | 138 | 5.17 | 5.2 | 0.03
GEN-2017-024 | South | 14 - South Central Oklahoma | 521079 | VALLANT4 | 138 | 8.94 | 8.96 | 0.02
GEN-2017-024 | South | 14 - South Central Oklahoma | 521098 | WSBNKTP4 | 138 | 6.87 | 6.91 | 0.04
GEN-2017-024 | South | 14 - South Central Oklahoma | 521115 | BENNSUB4 | 138 | 4.57 | 4.59 | 0.02
GEN-2017-024 | South | 14 - South Central Oklahoma | 521157 | HUGO 7 | 345 | 11.59 | 11.61 | 0.02
GEN-2017-024 | South | 14 - South Central Oklahoma | 560088 | G16-063-TAP | 345 | 8.19 | 8.2 | 0.01
GEN-2017-024 | South | 14 - South Central Oklahoma | 587430 | GEN-2016-063 | 345 | 8.08 | 8.09 | 0.01
GEN-2017-024 | South | 14 - South Central Oklahoma | 588670 | GEN-2017-023 | 138 | 19.3 | 19.35 | 0.05
GEN-2017-024 | South | 14 - South Central Oklahoma | 588680 | GEN-2017-024 | 138 | 10.65 | 10.72 | 0.07
GEN-2017-024 | South | 14 - South Central Oklahoma | 589130 | GEN-2017-075 | 345 | 8.18 | 8.18 | 0
GEN-2017-027 | South | 14 - South Central Oklahoma | 510907 | PITTSB-7 | 345 | 14.15 | 14.19 | 0.04
GEN-2017-027 | South | 14 - South Central Oklahoma | 510911 | VALIANT7 | 345 | 13.65 | 13.67 | 0.02
GEN-2017-027 | South | 14 - South Central Oklahoma | 510925 | KIOWA 7 | 345 | 13.9 | 13.93 | 0.03
GEN-2017-027 | South | 14 - South Central Oklahoma | 511456 | O.K.U.-7 | 345 | 5.61 | 5.62 | 0.01
GEN-2017-027 | South | 14 - South Central Oklahoma | 511467 | L.E.S.-4 | 138 | 25.26 | 25.28 | 0.02
GEN-2017-027 | South | 14 - South Central Oklahoma | 511468 | L.E.S.-7 | 345 | 13.57 | 13.59 | 0.02
GEN-2017-027 | South | 14 - South Central Oklahoma | 511566 | PERNELL4 | 138 | 4.59 | 4.77 | 0.18
GEN-2017-027 | South | 14 - South Central Oklahoma | 511568 | TERRYRD7 | 345 | 10.28 | 10.33 | 0.05
GEN-2017-027 | South | 14 - South Central Oklahoma | 511571 | RUSHSPR7 | 345 | 6.67 | 6.68 | 0.01
GEN-2017-027 | South | 14 - South Central Oklahoma | 514808 | JOHNCO 4 | 138 | 15.63 | 15.73 | 0.1
GEN-2017-027 | South | 14 - South Central Oklahoma | 514809 | JOHNCO 7 | 345 | 10.18 | 10.27 | 0.09
GEN-2017-027 | South | 14 - South Central Oklahoma | 515045 | SEMINOL7 | 345 | 27.19 | 27.23 | 0.04
GEN-2017-027 | South | 14 - South Central Oklahoma | 515100 | PAOLI- 4 | 138 | 10.52 | 10.61 | 0.09
GEN-2017-027 | South | 14 - South Central Oklahoma | 515120 | RUSSET-4 | 138 | 11.72 | 11.79 | 0.07
GEN-2017-027 | South | 14 - South Central Oklahoma | 515122 | SXMLCKT4 | 138 | 11.47 | 11.52 | 0.05
GEN-2017-027 | South | 14 - South Central Oklahoma | 515124 | MAYSVIL4 | 138 | 6.3 | 6.42 | 0.12
GEN-2017-027 | South | 14 - South Central Oklahoma | 515125 | WILDHRS2 | 69 | 3.57 | 3.64 | 0.07
GEN-2017-027 | South | 14 - South Central Oklahoma | 515126 | CONTYLN2 | 69 | 4.94 | 5.08 | 0.14
GEN-2017-027 | South | 14 - South Central Oklahoma | 515127 | WLDHRST2 | 69 | 5.11 | 5.26 | 0.15
GEN-2017-027 | South | 14 - South Central Oklahoma | 515128 | RATLIFF2 | 69 | 5.21 | 5.36 | 0.15
GEN-2017-027 | South | 14 - South Central Oklahoma | 515129 | RATLIFF4 | 138 | 6.68 | 7.28 | 0.6
GEN-2017-027 | South | 14 - South Central Oklahoma | 515130 | POOLVIL4 | 138 | 8.48 | 9.82 | 1.34
GEN-2017-027 | South | 14 - South Central Oklahoma | 515131 | FOX 4 | 138 | 6.96 | 7.67 | 0.71
GEN-2017-027 | South | 14 - South Central Oklahoma | 515132 | DUNDEE 4 | 138 | 6.44 | 6.82 | 0.38
GEN-2017-027 | South | 14 - South Central Oklahoma | 515134 | PRARPNT4 | 138 | 5.55 | 5.81 | 0.26
GEN-2017-027 | South | 14 - South Central Oklahoma | 515135 | SUNNYSD4 | 138 | 18.61 | 19.31 | 0.7
GEN-2017-027 | South | 14 - South Central Oklahoma | 515136 | SUNNYSD7 | 345 | 11.33 | 11.53 | 0.2
GEN-2017-027 | South | 14 - South Central Oklahoma | 515137 | UNIROY 4 | 138 | 12.74 | 12.99 | 0.25
GEN-2017-027 | South | 14 - South Central Oklahoma | 515138 | CARTER 4 | 138 | 12.7 | 12.89 | 0.19
GEN-2017-027 | South | 14 - South Central Oklahoma | 515139 | HEALDTN2 | 69 | 4.45 | 4.54 | 0.09
GEN-2017-027 | South | 14 - South Central Oklahoma | 515140 | HLTNTAP2 | 69 | 5.23 | 5.35 | 0.12
GEN-2017-027 | South | 14 - South Central Oklahoma | 515141 | HLTNTAP4 | 138 | 6.77 | 7.12 | 0.35
GEN-2017-027 | South | 14 - South Central Oklahoma | 515142 | DILLARD4 | 138 | 7.83 | 8.14 | 0.31
GEN-2017-027 | South | 14 - South Central Oklahoma | 515143 | WOLFCRK4 | 138 | 9.78 | 10.13 | 0.35
GEN-2017-027 | South | 14 - South Central Oklahoma | 515144 | LONEGRV4 | 138 | 13.47 | 13.93 | 0.46
GEN-2017-027 | South | 14 - South Central Oklahoma | 515148 | MOBILOL2 | 69 | 3.27 | 3.33 | 0.06
GEN-2017-027 | South | 14 - South Central Oklahoma | 515150 | CANEYCK4 | 138 | 8.89 | 8.91 | 0.02
GEN-2017-027 | South | 14 - South Central Oklahoma | 515160 | MRIETA 2 | 69 | 2.09 | 2.1 | 0.01
GEN-2017-027 | South | 14 - South Central Oklahoma | 515162 | FNDTION4 | 138 | 11.88 | 12.04 | 0.16
GEN-2017-027 | South | 14 - South Central Oklahoma | 515163 | ROCKYPT2 | 69 | 8.01 | 8.05 | 0.04
GEN-2017-027 | South | 14 - South Central Oklahoma | 515164 | ROCKYPT4 | 138 | 10.66 | 10.83 | 0.17
GEN-2017-027 | South | 14 - South Central Oklahoma | 515166 | ARDMORE2 | 69 | 9.97 | 10.03 | 0.06
GEN-2017-027 | South | 14 - South Central Oklahoma | 515171 | CHIKSAW4 | 138 | 12.49 | 12.66 | 0.17
GEN-2017-027 | South | 14 - South Central Oklahoma | 515172 | SPRNDAL4 | 138 | 11.73 | 11.88 | 0.15
GEN-2017-027 | South | 14 - South Central Oklahoma | 515372 | ARDWEST4 | 138 | 12.58 | 12.81 | 0.23
GEN-2017-027 | South | 14 - South Central Oklahoma | 515415 | CHEEKTP4 | 138 | 12.2 | 12.61 | 0.41
GEN-2017-027 | South | 14 - South Central Oklahoma | 515419 | COMMRCT2 | 69 | 9.3 | 9.35 | 0.05
GEN-2017-027 | South | 14 - South Central Oklahoma | 515420 | SCMMRCT2 | 69 | 9.26 | 9.31 | 0.05
GEN-2017-027 | South | 14 - South Central Oklahoma | 515422 | C-RIVER7 | 345 | 10.29 | 10.3 | 0.01
GEN-2017-027 | South | 14 - South Central Oklahoma | 515561 | CARTRCO4 | 138 | 8.67 | 10.1 | 1.43
GEN-2017-027 | South | 14 - South Central Oklahoma | 515563 | ORIGINW4 | 138 | 5.59 | 5.9 | 0.31
GEN-2017-027 | South | 14 - South Central Oklahoma | 515570 | MAYSVLT4 | 138 | 5.93 | 6.05 | 0.12
GEN-2017-027 | South | 14 - South Central Oklahoma | 515643 | HONEYCK4 | 138 | 8.89 | 8.95 | 0.06
GEN-2017-027 | South | 14 - South Central Oklahoma | 515676 | MRIETAT2 | 69 | 2.27 | 2.27 | 0
GEN-2017-027 | South | 14 - South Central Oklahoma | 515805 | COUTYTP2 | 69 | 4.95 | 5.09 | 0.14
GEN-2017-027 | South | 14 - South Central Oklahoma | 515873 | DRPSPRG4 | 138 | 10.99 | 11.12 | 0.13
GEN-2017-027 | South | 14 - South Central Oklahoma | 515932 | STIRLNG4 | 138 | 10.13 | 10.22 | 0.09
GEN-2017-027 | South | 14 - South Central Oklahoma | 520445 | MAYSVLL4 | 138 | 5.86 | 5.98 | 0.12
GEN-2017-027 | South | 14 - South Central Oklahoma | 520948 | HUGO PP4 | 138 | 23.31 | 23.33 | 0.02
GEN-2017-027 | South | 14 - South Central Oklahoma | 521125 | CHEEK_4 | 138 | 8.63 | 8.83 | 0.2
GEN-2017-027 | South | 14 - South Central Oklahoma | 521157 | HUGO 7 | 345 | 11.59 | 11.61 | 0.02
GEN-2017-027 | South | 14 - South Central Oklahoma | 560088 | G16-063-TAP | 345 | 8.15 | 8.2 | 0.05
GEN-2017-027 | South | 14 - South Central Oklahoma | 563259 | GEN-2015-092 | 345 | 6.47 | 6.48 | 0.01
GEN-2017-027 | South | 14 - South Central Oklahoma | 584780 | GEN-2015-036 | 345 | 7.29 | 7.33 | 0.04
GEN-2017-027 | South | 14 - South Central Oklahoma | 587430 | GEN-2016-063 | 345 | 8.05 | 8.09 | 0.04
GEN-2017-027 | South | 14 - South Central Oklahoma | 587744 | G16-091-TAP | 345 | 15.02 | 15.03 | 0.01
GEN-2017-027 | South | 14 - South Central Oklahoma | 588710 | GEN-2017-027 | 138 | 8.67 | 10.1 | 1.43
GEN-2017-027 | South | 14 - South Central Oklahoma | 589130 | GEN-2017-075 | 345 | 8.14 | 8.18 | 0.04
GEN-2017-075 | South | 14 - South Central Oklahoma | 507431 | PATTERS4 | 138 | 13.11 | 13.12 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 507454 | TURK 4 | 138 | 24.61 | 24.62 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 507455 | TURK 7 | 345 | 9.03 | 9.04 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 508049 | NASH 4 | 138 | 19.53 | 19.55 | 0.02
GEN-2017-075 | South | 14 - South Central Oklahoma | 508070 | NWT-BNT4 | 138 | 24.01 | 24.03 | 0.02
GEN-2017-075 | South | 14 - South Central Oklahoma | 508071 | NWTXARK4 | 138 | 25 | 25.03 | 0.03
GEN-2017-075 | South | 14 - South Central Oklahoma | 508072 | NWTXARK7 | 345 | 13.37 | 13.4 | 0.03
GEN-2017-075 | South | 14 - South Central Oklahoma | 508080 | SUGARHL4 | 138 | 12.14 | 12.15 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 508298 | LYDIA 7 | 345 | 12.93 | 12.96 | 0.03
GEN-2017-075 | South | 14 - South Central Oklahoma | 508359 | WELSH 7 | 345 | 21.36 | 21.38 | 0.02
GEN-2017-075 | South | 14 - South Central Oklahoma | 508832 | DIANA 7 | 345 | 19.23 | 19.24 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 508841 | WILKES 7 | 345 | 15.53 | 15.53 | 0
GEN-2017-075 | South | 14 - South Central Oklahoma | 510866 | V-WEYCO4 | 138 | 10.06 | 10.08 | 0.02
GEN-2017-075 | South | 14 - South Central Oklahoma | 510870 | WCITYTP2 | 69 | 6.58 | 6.59 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 510876 | KIPUMPT2 | 69 | 4.9 | 4.91 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 510886 | IDABEL-4 | 138 | 7.03 | 7.04 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 510888 | B.BOWTP4 | 138 | 7.39 | 7.4 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 510893 | HUGO---2 | 69 | 5.22 | 5.23 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 510901 | HUGO---4 | 138 | 3.62 | 3.62 | 0
GEN-2017-075 | South | 14 - South Central Oklahoma | 510907 | PITTSB-7 | 345 | 14.14 | 14.19 | 0.05
GEN-2017-075 | South | 14 - South Central Oklahoma | 510910 | VALIANT2 | 69 | 7.56 | 7.57 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 510911 | VALIANT7 | 345 | 13.58 | 13.67 | 0.09
GEN-2017-075 | South | 14 - South Central Oklahoma | 510918 | VALIANT4 | 138 | 15.36 | 15.41 | 0.05
GEN-2017-075 | South | 14 - South Central Oklahoma | 510925 | KIOWA 7 | 345 | 13.89 | 13.93 | 0.04
GEN-2017-075 | South | 14 - South Central Oklahoma | 510946 | C-RIVER4 | 138 | 13.37 | 13.39 | 0.02
GEN-2017-075 | South | 14 - South Central Oklahoma | 511423 | FLE TAP4 | 138 | 9.07 | 9.07 | 0
GEN-2017-075 | South | 14 - South Central Oklahoma | 511437 | COMANC-4 | 138 | 18.52 | 18.54 | 0.02
GEN-2017-075 | South | 14 - South Central Oklahoma | 511439 | LWSTAP 4 | 138 | 11.75 | 11.75 | 0
GEN-2017-075 | South | 14 - South Central Oklahoma | 511456 | O.K.U.-7 | 345 | 5.61 | 5.62 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 511466 | L.E.S.-2 | 69 | 16.98 | 16.99 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 511467 | L.E.S.-4 | 138 | 25.26 | 25.28 | 0.02
GEN-2017-075 | South | 14 - South Central Oklahoma | 511468 | L.E.S.-7 | 345 | 13.56 | 13.59 | 0.03
GEN-2017-075 | South | 14 - South Central Oklahoma | 511474 | SHERID4 | 138 | 12.55 | 12.56 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 511486 | ELGINJT4 | 138 | 10.25 | 10.25 | 0
GEN-2017-075 | South | 14 - South Central Oklahoma | 511494 | COMMTAP4 | 138 | 22.06 | 22.08 | 0.02
GEN-2017-075 | South | 14 - South Central Oklahoma | 511565 | OKLAUN HVDC7 | 345 | 5.6 | 5.6 | 0
GEN-2017-075 | South | 14 - South Central Oklahoma | 511568 | TERRYRD7 | 345 | 10.28 | 10.33 | 0.05
GEN-2017-075 | South | 14 - South Central Oklahoma | 511571 | RUSHSPR7 | 345 | 6.66 | 6.68 | 0.02
GEN-2017-075 | South | 14 - South Central Oklahoma | 514808 | JOHNCO 4 | 138 | 15.66 | 15.73 | 0.07
GEN-2017-075 | South | 14 - South Central Oklahoma | 514809 | JOHNCO 7 | 345 | 10.19 | 10.27 | 0.08
GEN-2017-075 | South | 14 - South Central Oklahoma | 514908 | ARCADIA7 | 345 | 30.87 | 30.87 | 0
GEN-2017-075 | South | 14 - South Central Oklahoma | 514934 | DRAPER 7 | 345 | 21.38 | 21.39 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 515044 | SEMINOL4 | 138 | 41.06 | 41.09 | 0.03
GEN-2017-075 | South | 14 - South Central Oklahoma | 515045 | SEMINOL7 | 345 | 27.21 | 27.23 | 0.02
GEN-2017-075 | South | 14 - South Central Oklahoma | 515120 | RUSSET-4 | 138 | 11.75 | 11.79 | 0.04
GEN-2017-075 | South | 14 - South Central Oklahoma | 515121 | MILLCKT4 | 138 | 11.34 | 11.37 | 0.03
GEN-2017-075 | South | 14 - South Central Oklahoma | 515122 | SXMLCKT4 | 138 | 11.48 | 11.52 | 0.04
GEN-2017-075 | South | 14 - South Central Oklahoma | 515128 | RATLIFF2 | 69 | 5.36 | 5.36 | 0
GEN-2017-075 | South | 14 - South Central Oklahoma | 515129 | RATLIFF4 | 138 | 7.27 | 7.28 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 515130 | POOLVIL4 | 138 | 9.79 | 9.82 | 0.03
GEN-2017-075 | South | 14 - South Central Oklahoma | 515131 | FOX 4 | 138 | 7.65 | 7.67 | 0.02
GEN-2017-075 | South | 14 - South Central Oklahoma | 515134 | PRARPNT4 | 138 | 5.8 | 5.81 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 515135 | SUNNYSD4 | 138 | 19.15 | 19.31 | 0.16
GEN-2017-075 | South | 14 - South Central Oklahoma | 515136 | SUNNYSD7 | 345 | 11.35 | 11.53 | 0.18
GEN-2017-075 | South | 14 - South Central Oklahoma | 515137 | UNIROY 4 | 138 | 12.92 | 12.99 | 0.07
GEN-2017-075 | South | 14 - South Central Oklahoma | 515138 | CARTER 4 | 138 | 12.83 | 12.89 | 0.06
GEN-2017-075 | South | 14 - South Central Oklahoma | 515143 | WOLFCRK4 | 138 | 10.08 | 10.13 | 0.05
GEN-2017-075 | South | 14 - South Central Oklahoma | 515144 | LONEGRV4 | 138 | 13.85 | 13.93 | 0.08
GEN-2017-075 | South | 14 - South Central Oklahoma | 515147 | GLASSES4 | 138 | 8.43 | 8.46 | 0.03
GEN-2017-075 | South | 14 - South Central Oklahoma | 515149 | MADINDT4 | 138 | 8.42 | 8.45 | 0.03
GEN-2017-075 | South | 14 - South Central Oklahoma | 515150 | CANEYCK4 | 138 | 8.89 | 8.91 | 0.02
GEN-2017-075 | South | 14 - South Central Oklahoma | 515151 | LTLCITY4 | 138 | 7.46 | 7.47 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 515162 | FNDTION4 | 138 | 11.99 | 12.04 | 0.05
GEN-2017-075 | South | 14 - South Central Oklahoma | 515163 | ROCKYPT2 | 69 | 8.03 | 8.05 | 0.02
GEN-2017-075 | South | 14 - South Central Oklahoma | 515164 | ROCKYPT4 | 138 | 10.78 | 10.83 | 0.05
GEN-2017-075 | South | 14 - South Central Oklahoma | 515172 | SPRNDAL4 | 138 | 11.83 | 11.88 | 0.05
GEN-2017-075 | South | 14 - South Central Oklahoma | 515224 | MUSKOGE7 | 345 | 29.64 | 29.64 | 0
GEN-2017-075 | South | 14 - South Central Oklahoma | 515372 | ARDWEST4 | 138 | 12.75 | 12.81 | 0.06
GEN-2017-075 | South | 14 - South Central Oklahoma | 515415 | CHEEKTP4 | 138 | 12.54 | 12.61 | 0.07
GEN-2017-075 | South | 14 - South Central Oklahoma | 515420 | SCMMRCT2 | 69 | 9.28 | 9.31 | 0.03
GEN-2017-075 | South | 14 - South Central Oklahoma | 515422 | C-RIVER7 | 345 | 10.28 | 10.3 | 0.02
GEN-2017-075 | South | 14 - South Central Oklahoma | 515561 | CARTRCO4 | 138 | 10.07 | 10.1 | 0.03
GEN-2017-075 | South | 14 - South Central Oklahoma | 515563 | ORIGINW4 | 138 | 5.89 | 5.9 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 515676 | MRIETAT2 | 69 | 2.27 | 2.27 | 0
GEN-2017-075 | South | 14 - South Central Oklahoma | 515800 | GRACMNT7 | 345 | 17.39 | 17.4 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 515873 | DRPSPRG4 | 138 | 11.07 | 11.12 | 0.05
GEN-2017-075 | South | 14 - South Central Oklahoma | 515932 | STIRLNG4 | 138 | 10.18 | 10.22 | 0.04
GEN-2017-075 | South | 14 - South Central Oklahoma | 520411 | SAWYER4 | 138 | 10.94 | 10.97 | 0.03
GEN-2017-075 | South | 14 - South Central Oklahoma | 520419 | GARVIN4 | 138 | 6.21 | 6.22 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 520497 | WSTBANK4 | 138 | 5.37 | 5.38 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 520874 | DARWIN 4 | 138 | 4.99 | 4.99 | 0
GEN-2017-075 | South | 14 - South Central Oklahoma | 520918 | FROGVIL4 | 138 | 11.1 | 11.14 | 0.04
GEN-2017-075 | South | 14 - South Central Oklahoma | 520948 | HUGO PP4 | 138 | 23.22 | 23.33 | 0.11
GEN-2017-075 | South | 14 - South Central Oklahoma | 520953 | IDABEL 4 | 138 | 6.28 | 6.29 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 521036 | RATTAN 4 | 138 | 7.13 | 7.14 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 521044 | RUSSETT4 | 138 | 11.67 | 11.71 | 0.04
GEN-2017-075 | South | 14 - South Central Oklahoma | 521067 | TEXOMAJ4 | 138 | 8.79 | 8.81 | 0.02
GEN-2017-075 | South | 14 - South Central Oklahoma | 521077 | UNGER 4 | 138 | 5.19 | 5.2 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 521079 | VALLANT4 | 138 | 8.94 | 8.96 | 0.02
GEN-2017-075 | South | 14 - South Central Oklahoma | 521098 | WSBNKTP4 | 138 | 6.89 | 6.91 | 0.02
GEN-2017-075 | South | 14 - South Central Oklahoma | 521122 | HOWE 4 | 138 | 11.38 | 11.41 | 0.03
GEN-2017-075 | South | 14 - South Central Oklahoma | 521125 | CHEEK_4 | 138 | 8.79 | 8.83 | 0.04
GEN-2017-075 | South | 14 - South Central Oklahoma | 521157 | HUGO 7 | 345 | 11.49 | 11.61 | 0.12
GEN-2017-075 | South | 14 - South Central Oklahoma | 525832 | TUCO_INT 7 | 345 | 12.31 | 12.31 | 0
GEN-2017-075 | South | 14 - South Central Oklahoma | 560088 | G16-063-TAP | 345 | 7.8 | 8.2 | 0.4
GEN-2017-075 | South | 14 - South Central Oklahoma | 563259 | GEN-2015-092 | 345 | 6.46 | 6.48 | 0.02
GEN-2017-075 | South | 14 - South Central Oklahoma | 584780 | GEN-2015-036 | 345 | 7.29 | 7.33 | 0.04
GEN-2017-075 | South | 14 - South Central Oklahoma | 587430 | GEN-2016-063 | 345 | 7.71 | 8.09 | 0.38
GEN-2017-075 | South | 14 - South Central Oklahoma | 587740 | GEN-2016-091 | 345 | 13.33 | 13.34 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 587744 | G16-091-TAP | 345 | 15.02 | 15.03 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 587770 | GEN-2016-095 | 345 | 11.04 | 11.05 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 588670 | GEN-2017-023 | 138 | 19.27 | 19.35 | 0.08
GEN-2017-075 | South | 14 - South Central Oklahoma | 588680 | GEN-2017-024 | 138 | 10.69 | 10.72 | 0.03
GEN-2017-075 | South | 14 - South Central Oklahoma | 588710 | GEN-2017-027 | 138 | 10.07 | 10.1 | 0.03
GEN-2017-075 | South | 14 - South Central Oklahoma | 588760 | GEN-2017-033 | 345 | 4.11 | 4.12 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 588839 | FIREWHL-TAP | 345 | 11.59 | 11.59 | 0
GEN-2017-075 | South | 14 - South Central Oklahoma | 589030 | GEN-2017-065 | 345 | 5.13 | 5.13 | 0
GEN-2017-075 | South | 14 - South Central Oklahoma | 589130 | GEN-2017-075 | 345 | 7.79 | 8.18 | 0.39
GEN-2017-075 | South | 14 - South Central Oklahoma | 599891 | OKLAUN 7 | 345 | 4.36 | 4.36 | 0
GEN-2017-075 | South | 14 - South Central Oklahoma | 599892 | EASTDC 7 | 345 | 6.29 | 6.29 | 0
GEN-2017-011 | Central | 01 - Woodward | 526337 | JONES 6 | 230 | 19.271 | 19.271 | 0
GEN-2017-011 | Central | 01 - Woodward | 524296 | SPNSPUR_WND7 | 345 | 4.5325 | 4.5325 | 0
GEN-2017-011 | Central | 01 - Woodward | 523961 | POTTER_CO 7 | 345 | 7.4527 | 7.4527 | 0
GEN-2017-011 | Central | 01 - Woodward | 590001 | OKLEHV24 | 138 | 4.7903 | 4.7903 | 0
GEN-2017-011 | Central | 01 - Woodward | 590003 | OKLEHV14 | 138 | 4.8014 | 4.8014 | 0
GEN-2017-011 | Central | 01 - Woodward | 583370 | GEN-2012-024 | 345 | 11.3148 | 11.3148 | 0
GEN-2017-011 | Central | 01 - Woodward | 520430 | NOELSW 4 | 138 | 11.3345 | 11.3345 | 0
GEN-2017-011 | Central | 01 - Woodward | 520436 | ROSEVLY4 | 138 | 12.6971 | 12.6971 | 0
GEN-2017-011 | Central | 01 - Woodward | 532782 | BUFFALO7 | 345 | 20.7023 | 20.7023 | 0
GEN-2017-011 | Central | 01 - Woodward | 532783 | KINGMAN7 | 345 | 6.8327 | 6.8327 | 0
GEN-2017-011 | Central | 01 - Woodward | 532784 | NINN1WF7 | 345 | 5.6893 | 5.6893 | 0
GEN-2017-011 | Central | 01 - Woodward | 532796 | WICHITA7 | 345 | 24.3835 | 24.3835 | 0
GEN-2017-011 | Central | 01 - Woodward | 520529 | RSVLYSW4 | 138 | 13.677 | 13.677 | 0
GEN-2017-011 | Central | 01 - Woodward | 582008 | GEN-2011-008 | 345 | 10.5174 | 10.5174 | 0
GEN-2017-011 | Central | 01 - Woodward | 584060 | GEN-2015-057 | 345 | 9.1364 | 9.1364 | 0
GEN-2017-011 | Central | 01 - Woodward | 520601 | AVARD 4 | 138 | 6.9924 | 6.9924 | 0
GEN-2017-011 | Central | 01 - Woodward | 588190 | GEN-2016-128 | 345 | 7.9545 | 7.9545 | 0
GEN-2017-011 | Central | 01 - Woodward | 526935 | YOAKUM 6 | 230 | 16.8151 | 16.8151 | 0
GEN-2017-011 | Central | 01 - Woodward | 526936 | YOAKUM_345 | 345 | 8.5075 | 8.5075 | 0
GEN-2017-011 | Central | 01 - Woodward | 514715 | WOODRNG7 | 345 | 19.1426 | 19.1426 | 0
GEN-2017-011 | Central | 01 - Woodward | 515786 | FPLWIND4 | 138 | 6.8223 | 6.8223 | 0
GEN-2017-011 | Central | 01 - Woodward | 514771 | TANGIER2 | 69 | 3.6773 | 3.6773 | 0
GEN-2017-011 | Central | 01 - Woodward | 514773 | NEWMAN 2 | 69 | 1.5468 | 1.5468 | 0
GEN-2017-011 | Central | 01 - Woodward | 514775 | TANGRTP2 | 69 | 4.7834 | 4.7834 | 0
GEN-2017-011 | Central | 01 - Woodward | 514776 | NEWGRTP2 | 69 | 5.4632 | 5.4632 | 0
GEN-2017-011 | Central | 01 - Woodward | 514779 | WDNITRO2 | 69 | 4.7713 | 4.7713 | 0
GEN-2017-011 | Central | 01 - Woodward | 514781 | CEDARAV2 | 69 | 5.7047 | 5.7047 | 0
GEN-2017-011 | Central | 01 - Woodward | 514782 | WODWRD 2 | 69 | 10.9471 | 10.9471 | 0
GEN-2017-011 | Central | 01 - Woodward | 514785 | WOODWRD4 | 138 | 13.1308 | 13.1308 | 0
GEN-2017-011 | Central | 01 - Woodward | 514787 | DEWEY 4 | 138 | 7.7536 | 7.7536 | 0
GEN-2017-011 | Central | 01 - Woodward | 514794 | KNOBHIL2 | 69 | 9.1065 | 9.1065 | 0
GEN-2017-011 | Central | 01 - Woodward | 514795 | KNOBHIL4 | 138 | 11.3932 | 11.3932 | 0
GEN-2017-011 | Central | 01 - Woodward | 514796 | IODINE-4 | 138 | 7.3853 | 7.3853 | 0
GEN-2017-011 | Central | 01 - Woodward | 514801 | MINCO 7 | 345 | 18.2091 | 18.2091 | 0
GEN-2017-011 | Central | 01 - Woodward | 579370 | G06-044-MV1A | 115 | 8.2373 | 8.2373 | 0
GEN-2017-011 | Central | 01 - Woodward | 588560 | GEN-2017-011 | 345 | 12.2639 | 12.2639 | 0
GEN-2017-011 | Central | 01 - Woodward | 520999 | MOORLND4 | 138 | 20.5768 | 20.5768 | 0
GEN-2017-011 | Central | 01 - Woodward | 514879 | NORTWST4 | 138 | 44.4108 | 44.4108 | 0
GEN-2017-011 | Central | 01 - Woodward | 514880 | NORTWST7 | 345 | 33.063 | 33.063 | 0
GEN-2017-011 | Central | 01 - Woodward | 514881 | SPRNGCK7 | 345 | 23.857 | 23.857 | 0
GEN-2017-011 | Central | 01 - Woodward | 514898 | CIMARON4 | 138 | 43.3374 | 43.3374 | 0
GEN-2017-011 | Central | 01 - Woodward | 514901 | CIMARON7 | 345 | 34.6112 | 34.6112 | 0
GEN-2017-011 | Central | 01 - Woodward | 523097 | HITCHLAND 7 | 345 | 15.1013 | 15.1013 | 0
GEN-2017-011 | Central | 01 - Woodward | 514908 | ARCADIA7 | 345 | 30.6277 | 30.6277 | 0
GEN-2017-011 | Central | 01 - Woodward | 523103 | NOBLE_WND 3 | 115 | 10.6735 | 10.6735 | 0
GEN-2017-011 | Central | 01 - Woodward | 523111 | NOVUS1 3 | 115 | 19.4188 | 19.4188 | 0
GEN-2017-011 | Central | 01 - Woodward | 523112 | NOVUS1 7 | 345 | 14.8323 | 14.8323 | 0
GEN-2017-011 | Central | 01 - Woodward | 523118 | BUFF_DUNES 7 | 345 | 6.0476 | 6.0476 | 0
GEN-2017-011 | Central | 01 - Woodward | 514934 | DRAPER 7 | 345 | 21.066 | 21.066 | 0
GEN-2017-011 | Central | 01 - Woodward | 523130 | NBLWND-HV2 3 | 115 | 5.1334 | 5.1334 | 0
GEN-2017-011 | Central | 01 - Woodward | 523131 | NBLWND-HV3 3 | 115 | 8.0198 | 8.0198 | 0
GEN-2017-011 | Central | 01 - Woodward | 521096 | WOODWRD2 | 69 | 9.9388 | 9.9388 | 0
GEN-2017-011 | Central | 01 - Woodward | 576395 | GEN-2010-014 | 345 | 11.1504 | 11.1504 | 0
GEN-2017-011 | Central | 01 - Woodward | 576396 | G10-014-XFMR | 115 | 13.2853 | 13.2853 | 0
GEN-2017-011 | Central | 01 - Woodward | 576397 | G10-014-XF-1 | 115 | 9.2449 | 9.2449 | 0
GEN-2017-011 | Central | 01 - Woodward | 523155 | OCHILTREE 6 | 230 | 4.2744 | 4.2744 | 0
GEN-2017-011 | Central | 01 - Woodward | 576407 | G10-014-XF-2 | 115 | 12.512 | 12.512 | 0
GEN-2017-011 | Central | 01 - Woodward | 525213 | SWISHER 6 | 230 | 10.3091 | 10.3091 | 0
GEN-2017-011 | Central | 01 - Woodward | 900001 | TRAVERSE1 | 345 | 7.3845 | 7.3845 | 0
GEN-2017-011 | Central | 01 - Woodward | 900002 | TRAVERSE2 | 345 | 5.7168 | 5.7168 | 0
GEN-2017-011 | Central | 01 - Woodward | 900003 | TRAVERSE3 | 345 | 5.1975 | 5.1975 | 0
GEN-2017-011 | Central | 01 - Woodward | 523174 | GOODWELLWND3 | 115 | 6.6033 | 6.6033 | 0
GEN-2017-011 | Central | 01 - Woodward | 560071 | G16-003-TAP | 345 | 15.2408 | 15.2408 | 0
GEN-2017-011 | Central | 01 - Woodward | 588750 | GEN-2017-032 | 345 | 3.2299 | 3.2299 | 0
GEN-2017-011 | Central | 01 - Woodward | 523215 | FREWHELCOL17 | 345 | 9.1713 | 9.1713 | 0
GEN-2017-011 | Central | 01 - Woodward | 560080 | G16-046-TAP | 345 | 11.4323 | 11.4323 | 0
GEN-2017-011 | Central | 01 - Woodward | 588754 | G17-032-TAP | 345 | 3.2299 | 3.2299 | 0
GEN-2017-011 | Central | 01 - Woodward | 588760 | GEN-2017-033 | 345 | 4.0304 | 4.0304 | 0
GEN-2017-011 | Central | 01 - Woodward | 526161 | CARLISLE 6 | 230 | 13.2714 | 13.2714 | 0
GEN-2017-011 | Central | 01 - Woodward | 539631 | FLATRWD4 | 138 | 10.3664 | 10.3664 | 0
GEN-2017-011 | Central | 01 - Woodward | 539638 | FLATRDG4 | 138 | 15.5308 | 15.5308 | 0
GEN-2017-011 | Central | 01 - Woodward | 523093 | HITCHLAND 3 | 115 | 17.775 | 17.775 | 0
GEN-2017-011 | Central | 01 - Woodward | 588630 | GEN-2017-018 | 345 | 16.4054 | 16.4054 | 0
GEN-2017-011 | Central | 01 - Woodward | 523095 | HITCHLAND 6 | 230 | 14.7393 | 14.7393 | 0
GEN-2017-011 | Central | 01 - Woodward | 531469 | SPERVIL7 | 345 | 13.739 | 13.739 | 0
GEN-2017-011 | Central | 01 - Woodward | 525828 | TUCO_INT 3 | 115 | 19.3193 | 19.3193 | 0
GEN-2017-011 | Central | 01 - Woodward | 525830 | TUCO_INT 6 | 230 | 21.2069 | 21.2069 | 0
GEN-2017-011 | Central | 01 - Woodward | 523309 | MOORE_CNTY 6 | 230 | 6.8187 | 6.8187 | 0
GEN-2017-011 | Central | 01 - Woodward | 525832 | TUCO_INT 7 | 345 | 11.9885 | 11.9885 | 0
GEN-2017-011 | Central | 01 - Woodward | 582708 | G-2011-008-1 | 345 | 8.564 | 8.564 | 0
GEN-2017-011 | Central | 01 - Woodward | 531512 | HARBNGR7 | 345 | 6.5528 | 6.5528 | 0
GEN-2017-011 | Central | 01 - Woodward | 515600 | KNGFSHR7 | 345 | 11.9002 | 11.9002 | 0
GEN-2017-011 | Central | 01 - Woodward | 525826 | TUCO_INT 2 | 69 | 7.85 | 7.85 | 0
GEN-2017-011 | Central | 01 - Woodward | 515605 | CANADN7 | 345 | 12.9579 | 12.9579 | 0
GEN-2017-011 | Central | 01 - Woodward | 539800 | CLARKCOUNTY7 | 345 | 13.2652 | 13.2652 | 0
GEN-2017-011 | Central | 01 - Woodward | 539801 | THISTLE7 | 345 | 16.4054 | 16.4054 | 0
GEN-2017-011 | Central | 01 - Woodward | 539804 | THISTLE4 | 138 | 17.502 | 17.502 | 0
GEN-2017-011 | Central | 01 - Woodward | 525850 | ELK_CT1 | 345 | 11.8972 | 11.8972 | 0
GEN-2017-011 | Central | 01 - Woodward | 588970 | GEN-2017-059 | 230 | 8.547 | 8.547 | 0
GEN-2017-011 | Central | 01 - Woodward | 539852 | P1 MPT PRI | 345 | 10.7708 | 10.7708 | 0
GEN-2017-011 | Central | 01 - Woodward | 585250 | GEN-2015-090 | 345 | 5.0829 | 5.0829 | 0
GEN-2017-011 | Central | 01 - Woodward | 539857 | P2 MPT PRI | 345 | 9.1323 | 9.1323 | 0
GEN-2017-011 | Central | 01 - Woodward | 525524 | TOLK_EAST 6 | 230 | 26.995 | 26.995 | 0
GEN-2017-011 | Central | 01 - Woodward | 525860 | SP-BECTON +2 | 69 | 2.254 | 2.254 | 0
GEN-2017-011 | Central | 01 - Woodward | 589030 | GEN-2017-065 | 345 | 5.0163 | 5.0163 | 0
GEN-2017-011 | Central | 01 - Woodward | 582908 | G-2011-008-2 | 345 | 8.4371 | 8.4371 | 0
GEN-2017-011 | Central | 01 - Woodward | 589060 | GEN-2017-068 | 345 | 20.2698 | 20.2698 | 0
GEN-2017-011 | Central | 01 - Woodward | 587020 | GEN-2016-003 | 345 | 15.2408 | 15.2408 | 0
GEN-2017-011 | Central | 01 - Woodward | 515363 | CENT 4 | 138 | 3.1164 | 3.1164 | 0
GEN-2017-011 | Central | 01 - Woodward | 515375 | WWRDEHV7 | 345 | 19.8203 | 19.8204 | 5.0453e-06
GEN-2017-011 | Central | 01 - Woodward | 515376 | WWRDEHV4 | 138 | 24.1765 | 24.1765 | 0
GEN-2017-011 | Central | 01 - Woodward | 515390 | TLGAWND4 | 138 | 4.0402 | 4.0402 | 0
GEN-2017-011 | Central | 01 - Woodward | 515394 | KEENAN 4 | 138 | 8.9124 | 8.9124 | 0
GEN-2017-011 | Central | 01 - Woodward | 515398 | OUSPRT 4 | 138 | 9.4842 | 9.4842 | 0
GEN-2017-011 | Central | 01 - Woodward | 515407 | TATONGA7 | 345 | 16.7261 | 16.7261 | 0
GEN-2017-011 | Central | 01 - Woodward | 515425 | WWDPST 4 | 138 | 17.5451 | 17.5451 | 0
GEN-2017-011 | Central | 01 - Woodward | 515444 | MCNOWND7 | 345 | 18.1528 | 18.1528 | 0
GEN-2017-011 | Central | 01 - Woodward | 515448 | CRSRDSW7 | 345 | 11.7432 | 11.7432 | 0
GEN-2017-011 | Central | 01 - Woodward | 515458 | BORDER 7 | 345 | 4.496 | 4.496 | 0
GEN-2017-011 | Central | 01 - Woodward | 587140 | GEN-2016-020 | 138 | 7.483 | 7.483 | 0
GEN-2017-011 | Central | 01 - Woodward | 525723 | CNTYLINE_TP2 | 69 | 2.2011 | 2.2011 | 0
GEN-2017-011 | Central | 01 - Woodward | 525724 | COUNTYLINE 2 | 69 | 1.9277 | 1.9277 | 0
GEN-2017-011 | Central | 01 - Woodward | 525731 | SP-ABERNTHY2 | 69 | 3.0086 | 3.0086 | 0
GEN-2017-011 | Central | 01 - Woodward | 515497 | MATHWSN7 | 345 | 33.254 | 33.254 | 0
GEN-2017-011 | Central | 01 - Woodward | 525738 | HALECENTER 2 | 69 | 2.456 | 2.456 | 0
GEN-2017-011 | Central | 01 - Woodward | 525745 | LH-HALECTR 2 | 69 | 2.4284 | 2.4284 | 0
GEN-2017-011 | Central | 01 - Woodward | 525899 | SP-SHALLWTR2 | 69 | 2.0997 | 2.0997 | 0
GEN-2017-011 | Central | 01 - Woodward | 515533 | REDCLFT4 | 138 | 6.7371 | 6.7371 | 0
GEN-2017-011 | Central | 01 - Woodward | 523853 | FINNEY 7 | 345 | 9.8902 | 9.8902 | 0
GEN-2017-011 | Central | 01 - Woodward | 515549 | MNCWND37 | 345 | 12.468 | 12.468 | 0
GEN-2017-011 | Central | 01 - Woodward | 511456 | O.K.U.-7 | 345 | 5.4913 | 5.4913 | 0
GEN-2017-011 | Central | 01 - Woodward | 515554 | BVRCNTY7 | 345 | 14.759 | 14.759 | 0
GEN-2017-011 | Central | 01 - Woodward | 585190 | GEN-2015-082 | 345 | 7.1443 | 7.1443 | 0
GEN-2017-011 | Central | 01 - Woodward | 511468 | L.E.S.-7 | 345 | 13.2765 | 13.2765 | 0
GEN-2017-011 | Central | 01 - Woodward | 525816 | TUCO_INT2 2 | 69 | 4.6511 | 4.6511 | 0
GEN-2017-011 | Central | 01 - Woodward | 515582 | SLNGWND7 | 345 | 7.3463 | 7.3463 | 0
GEN-2017-011 | Central | 01 - Woodward | 515585 | MAMTHPW7 | 345 | 13.2801 | 13.2801 | 0
GEN-2017-011 | Central | 01 - Woodward | 515590 | PALDR2W7 | 345 | 12.8458 | 12.8458 | 0
GEN-2017-011 | Central | 01 - Woodward | 515599 | G07621119-20 | 345 | 13.2036 | 13.2036 | 0
GEN-2017-011 | Central | 01 - Woodward | 525840 | ANTELOPE_1 6 | 230 | 21.0433 | 21.0433 | 0
GEN-2017-011 | Central | 01 - Woodward | 527896 | HOBBS_INT 7 | 345 | 7.7348 | 7.7348 | 0
GEN-2017-011 | Central | 01 - Woodward | 515610 | FSHRTAP7 | 345 | 17.7292 | 17.7292 | 0
GEN-2017-011 | Central | 01 - Woodward | 525853 | LH-WIL&ELN+2 | 69 | 2.5398 | 2.5398 | 0
GEN-2017-011 | Central | 01 - Woodward | 515618 | BALKOW 7 | 345 | 12.2581 | 12.2581 | 0
GEN-2017-011 | Central | 01 - Woodward | 587310 | GEN-2016-046 | 345 | 9.8441 | 9.8441 | 0
GEN-2017-011 | Central | 01 - Woodward | 523823 | CARPENTER 7 | 345 | 6.5732 | 6.5732 | 0
GEN-2017-011 | Central | 01 - Woodward | 515634 | PALDR1W7 | 345 | 11.2735 | 11.2735 | 0
GEN-2017-011 | Central | 01 - Woodward | 525885 | SP-NEWDEAL 2 | 69 | 3.3064 | 3.3064 | 0
GEN-2017-011 | Central | 01 - Woodward | 525891 | WHITEHEAD 2 | 69 | 2.551 | 2.551 | 0
GEN-2017-011 | Central | 01 - Woodward | 525892 | MONROE 2 | 69 | 2.6469 | 2.6469 | 0
GEN-2017-011 | Central | 01 - Woodward | 511565 | OKLAUN HVDC7 | 345 | 5.4749 | 5.4749 | 0
GEN-2017-011 | Central | 01 - Woodward | 585300 | GEN-2015-095 | 138 | 11.314 | 11.314 | 0
GEN-2017-011 | Central | 01 - Woodward | 515677 | BADGER 7 | 345 | 14.1624 | 14.1624 | 0
GEN-2017-011 | Central | 01 - Woodward | 515686 | GEN-2011-014 | 345 | 12.7624 | 12.7624 | 0
GEN-2017-011 | Central | 01 - Woodward | 583340 | GEN-2012-020 | 230 | 9.8745 | 9.8745 | 0
GEN-2017-011 | Central | 01 - Woodward | 523959 | POTTER_CO 6 | 230 | 20.0753 | 20.0753 | 0
GEN-2017-011 | Central | 01 - Woodward | 585410 | GREAT_WESTRN | 345 | 9.9473 | 9.9473 | 0
GEN-2017-011 | Central | 01 - Woodward | 587460 | GEN-2016-068 | 345 | 6.5319 | 6.5319 | 0
GEN-2017-011 | Central | 01 - Woodward | 515785 | WINDFRM4 | 138 | 20.1178 | 20.1178 | 0
GEN-2017-011 | Central | 01 - Woodward | 585420 | COWBOY_RIDGE | 345 | 7.6727 | 7.6727 | 0
GEN-2017-011 | Central | 01 - Woodward | 585430 | PRSIMN_CRK1 | 345 | 11.6188 | 11.6188 | 0
GEN-2017-011 | Central | 01 - Woodward | 585440 | PRSIMN_CRK2 | 345 | 10.6096 | 10.6096 | 0
GEN-2017-011 | Central | 01 - Woodward | 587500 | GEN-2016-073 | 345 | 15.1939 | 15.1939 | 0
GEN-2017-011 | Central | 01 - Woodward | 526073 | STANTON_N 2 | 69 | 1.6642 | 1.6642 | 0
GEN-2017-011 | Central | 01 - Woodward | 515852 | DGRASSE7 | 345 | 14.5578 | 14.5578 | 0
GEN-2017-011 | Central | 01 - Woodward | 515853 | DGRASSE4 | 138 | 15.3923 | 15.3923 | 0
GEN-2017-011 | Central | 01 - Woodward | 515863 | REDCLF 4 | 138 | 6.7225 | 6.7225 | 0
GEN-2017-011 | Central | 01 - Woodward | 515875 | REDNGTN7 | 345 | 18.0758 | 18.0758 | 0
GEN-2017-011 | Central | 01 - Woodward | 515877 | REDDIRT7 | 345 | 18.0716 | 18.0716 | 0
GEN-2017-011 | Central | 01 - Woodward | 579377 | G06-044-MV2B | 115 | 10.2533 | 10.2533 | 0
GEN-2017-011 | Central | 01 - Woodward | 599891 | OKLAUN 7 | 345 | 4.0421 | 4.0421 | 0
GEN-2017-011 | Central | 01 - Woodward | 515939 | MNCWND47 | 345 | 6.8069 | 6.8069 | 0
GEN-2017-011 | Central | 01 - Woodward | 599950 | LAMAR7 | 345 | 2.5722 | 2.5722 | 0
GEN-2017-028 | Central | 01 - Woodward | 511489 | WTH_JCT4 | 138 | 4.7764 | 4.7764 | 0
GEN-2017-028 | Central | 01 - Woodward | 511497 | WTH_SE 4 | 138 | 4.8078 | 4.8078 | 0
GEN-2017-028 | Central | 01 - Woodward | 511501 | TUTTLE4 | 138 | 10.1981 | 10.1981 | 0
GEN-2017-028 | Central | 01 - Woodward | 515600 | KNGFSHR7 | 345 | 11.9002 | 11.9002 | 0
GEN-2017-028 | Central | 01 - Woodward | 515605 | CANADN7 | 345 | 12.9579 | 12.9579 | 0
GEN-2017-028 | Central | 01 - Woodward | 515610 | FSHRTAP7 | 345 | 17.7292 | 17.7292 | 0
GEN-2017-028 | Central | 01 - Woodward | 515625 | KNGINDT2 | 69 | 3.4481 | 3.4481 | 0
GEN-2017-028 | Central | 01 - Woodward | 511540 | CAN_GAS4 | 138 | 7.8272 | 7.8272 | 0
GEN-2017-028 | Central | 01 - Woodward | 511548 | REDROCKRD4 | 138 | 7.6998 | 7.6998 | 0
GEN-2017-028 | Central | 01 - Woodward | 511559 | DARLINGTNRD4 | 138 | 6.1918 | 6.1918 | 0
GEN-2017-028 | Central | 01 - Woodward | 511573 | REDBDPLN4 | 138 | 4.4828 | 4.4828 | 0
GEN-2017-028 | Central | 01 - Woodward | 511575 | LEONARD4 | 138 | 10.0792 | 10.0792 | 0
GEN-2017-028 | Central | 01 - Woodward | 511576 | CEMRD_TP4 | 138 | 6.8146 | 6.8146 | 0
GEN-2017-028 | Central | 01 - Woodward | 563269 | GEN-2015-093 | 345 | 9.867 | 9.867 | 0
GEN-2017-028 | Central | 01 - Woodward | 520839 | CALUMET2 | 69 | 3.2242 | 3.2242 | 0
GEN-2017-028 | Central | 01 - Woodward | 520859 | COGAR 2 | 69 | 3.9677 | 3.9677 | 0
GEN-2017-028 | Central | 01 - Woodward | 520865 | CONCHO 2 | 69 | 1.9201 | 1.9201 | 0
GEN-2017-028 | Central | 01 - Woodward | 520892 | EL RENO2 | 69 | 6.458 | 6.458 | 0
GEN-2017-028 | Central | 01 - Woodward | 520893 | EL RENO4 | 138 | 9.2211 | 9.2211 | 0
GEN-2017-028 | Central | 01 - Woodward | 520899 | ELRENOJ2 | 69 | 5.152 | 5.152 | 0
GEN-2017-028 | Central | 01 - Woodward | 515800 | GRACMNT7 | 345 | 17.2218 | 17.2218 | 0
GEN-2017-028 | Central | 01 - Woodward | 520412 | MUSTANG2 | 69 | 3.2766 | 3.2766 | 0
GEN-2017-028 | Central | 01 - Woodward | 515877 | REDDIRT7 | 345 | 18.0716 | 18.0716 | 0
GEN-2017-028 | Central | 01 - Woodward | 514787 | DEWEY 4 | 138 | 7.7536 | 7.7536 | 0
GEN-2017-028 | Central | 01 - Woodward | 514801 | MINCO 7 | 345 | 18.2091 | 18.2091 | 0
GEN-2017-028 | Central | 01 - Woodward | 514811 | OKARCHE2 | 69 | 3.6291 | 3.6291 | 0
GEN-2017-028 | Central | 01 - Woodward | 514816 | YUKON 2 | 69 | 7.2786 | 7.2786 | 0
GEN-2017-028 | Central | 01 - Woodward | 514817 | SVCELRN2 | 69 | 6.3912 | 6.3912 | 0
GEN-2017-028 | Central | 01 - Woodward | 514818 | ELRENO 2 | 69 | 7.3305 | 7.3305 | 0
GEN-2017-028 | Central | 01 - Woodward | 514819 | EL-RENO4 | 138 | 15.4558 | 15.4558 | 0
GEN-2017-028 | Central | 01 - Woodward | 514820 | JENSENT4 | 138 | 15.3198 | 15.3198 | 0
GEN-2017-028 | Central | 01 - Woodward | 514821 | JENSEN 4 | 138 | 11.1068 | 11.1068 | 0
GEN-2017-028 | Central | 01 - Woodward | 514822 | SOUTHRD4 | 138 | 4.6186 | 4.6186 | 0
GEN-2017-028 | Central | 01 - Woodward | 514823 | ROMNOSE4 | 138 | 5.9231 | 5.9231 | 0
GEN-2017-028 | Central | 01 - Woodward | 520460 | GEARY 4 | 138 | 4.7128 | 4.7128 | 0
GEN-2017-028 | Central | 01 - Woodward | 514861 | MUSTANG4 | 138 | 36.8094 | 36.8094 | 0
GEN-2017-028 | Central | 01 - Woodward | 515585 | MAMTHPW7 | 345 | 13.2801 | 13.2801 | 0
GEN-2017-028 | Central | 01 - Woodward | 515864 | CMTRYRD4 | 138 | 6.6182 | 6.6182 | 0
GEN-2017-028 | Central | 01 - Woodward | 514849 | LAKESID4 | 138 | 24.8145 | 24.8146 | 4.0299e-06
GEN-2017-028 | Central | 01 - Woodward | 515875 | REDNGTN7 | 345 | 18.0758 | 18.0758 | 0
GEN-2017-028 | Central | 01 - Woodward | 514852 | SLVRLAK4 | 138 | 32.8246 | 32.8246 | 0
GEN-2017-028 | Central | 01 - Woodward | 514853 | DVISION4 | 138 | 36.0432 | 36.0432 | 0
GEN-2017-028 | Central | 01 - Woodward | 521005 | SARAROAD2 | 69 | 3.3735 | 3.3735 | 0
GEN-2017-028 | Central | 01 - Woodward | 514862 | RICHRDS4 | 138 | 21.7808 | 21.7808 | 0
GEN-2017-028 | Central | 01 - Woodward | 514863 | HAYMAKR4 | 138 | 26.3763 | 26.3763 | 0
GEN-2017-028 | Central | 01 - Woodward | 520502 | CANA 2 | 69 | 4.2497 | 4.2497 | 0
GEN-2017-028 | Central | 01 - Woodward | 520508 | CLVJCTN2 | 69 | 4.9185 | 4.9185 | 0
GEN-2017-028 | Central | 01 - Woodward | 515390 | TLGAWND4 | 138 | 4.0402 | 4.0402 | 0
GEN-2017-028 | Central | 01 - Woodward | 514879 | NORTWST4 | 138 | 44.4108 | 44.4108 | 0
GEN-2017-028 | Central | 01 - Woodward | 514880 | NORTWST7 | 345 | 33.063 | 33.063 | 0
GEN-2017-028 | Central | 01 - Woodward | 514881 | SPRNGCK7 | 345 | 23.857 | 23.857 | 0
GEN-2017-028 | Central | 01 - Woodward | 514893 | XEROX 4 | 138 | 28.9961 | 28.9961 | 0
GEN-2017-028 | Central | 01 - Woodward | 514894 | CZECHAL4 | 138 | 27.8317 | 27.8317 | 0
GEN-2017-028 | Central | 01 - Woodward | 514895 | SARA 4 | 138 | 18.7296 | 18.7296 | 0
GEN-2017-028 | Central | 01 - Woodward | 514896 | MORGAN 4 | 138 | 31.9433 | 31.9433 | 0
GEN-2017-028 | Central | 01 - Woodward | 514898 | CIMARON4 | 138 | 43.3374 | 43.3374 | 0
GEN-2017-028 | Central | 01 - Woodward | 514901 | CIMARON7 | 345 | 34.6112 | 34.6112 | 0
GEN-2017-028 | Central | 01 - Woodward | 514902 | MCCLAIN4 | 138 | 28.4224 | 28.4224 | 0
GEN-2017-028 | Central | 01 - Woodward | 515931 | GEARYTP4 | 138 | 5.3957 | 5.3957 | 0
GEN-2017-028 | Central | 01 - Woodward | 514908 | ARCADIA7 | 345 | 30.6277 | 30.6277 | 0
GEN-2017-028 | Central | 01 - Woodward | 515933 | MLCLMRD4 | 138 | 9.6701 | 9.6701 | 0
GEN-2017-028 | Central | 01 - Woodward | 521058 | SUNSHIN2 | 69 | 4.9831 | 4.9831 | 0
GEN-2017-028 | Central | 01 - Woodward | 515939 | MNCWND47 | 345 | 6.8069 | 6.8069 | 0
GEN-2017-028 | Central | 01 - Woodward | 515444 | MCNOWND7 | 345 | 18.1528 | 18.1528 | 0
GEN-2017-028 | Central | 01 - Woodward | 514933 | DRAPER 4 | 138 | 39.3998 | 39.3998 | 0
GEN-2017-028 | Central | 01 - Woodward | 514934 | DRAPER 7 | 345 | 21.066 | 21.066 | 0
GEN-2017-028 | Central | 01 - Woodward | 515448 | CRSRDSW7 | 345 | 11.7432 | 11.7432 | 0
GEN-2017-028 | Central | 01 - Woodward | 584060 | GEN-2015-057 | 345 | 9.1364 | 9.1364 | 0
GEN-2017-028 | Central | 01 - Woodward | 529281 | OMKFIND2 | 69 | 3.3878 | 3.3878 | 0
GEN-2017-028 | Central | 01 - Woodward | 515460 | TALBEAR4 | 138 | 6.9954 | 6.9955 | 1.4295e-05
GEN-2017-028 | Central | 01 - Woodward | 515472 | TLBEART4 | 138 | 7.7864 | 7.7864 | 0
GEN-2017-028 | Central | 01 - Woodward | 515481 | STHLAKE4 | 138 | 20.7116 | 20.7116 | 0
GEN-2017-028 | Central | 01 - Woodward | 900001 | TRAVERSE1 | 345 | 7.3845 | 7.3845 | 0
GEN-2017-028 | Central | 01 - Woodward | 900002 | TRAVERSE2 | 345 | 5.7168 | 5.7168 | 0
GEN-2017-028 | Central | 01 - Woodward | 900003 | TRAVERSE3 | 345 | 5.1975 | 5.1975 | 0
GEN-2017-028 | Central | 01 - Woodward | 515497 | MATHWSN7 | 345 | 33.254 | 33.254 | 0
GEN-2017-028 | Central | 01 - Woodward | 588720 | GEN-2017-028 | 138 | 9.2258 | 9.2258 | 0
GEN-2017-028 | Central | 01 - Woodward | 515506 | OKRCHET2 | 69 | 3.6349 | 3.6349 | 0
GEN-2017-028 | Central | 01 - Woodward | 511424 | T-CONCO4 | 138 | 6.7748 | 6.7748 | 0
GEN-2017-028 | Central | 01 - Woodward | 511425 | TUTCONT4 | 138 | 10.3426 | 10.3426 | 0
GEN-2017-028 | Central | 01 - Woodward | 511433 | HINTON 4 | 138 | 5.3228 | 5.3228 | 0
GEN-2017-028 | Central | 01 - Woodward | 515407 | TATONGA7 | 345 | 16.7261 | 16.7261 | 0
GEN-2017-028 | Central | 01 - Woodward | 515549 | MNCWND37 | 345 | 12.468 | 12.468 | 0
GEN-2017-028 | Central | 01 - Woodward | 515045 | SEMINOL7 | 345 | 26.7438 | 26.7438 | 0
GEN-2017-028 | Central | 01 - Woodward | 515582 | SLNGWND7 | 345 | 7.3463 | 7.3463 | 0
GEN-2017-018 | Central | 03 - Spearville | 588750 | GEN-2017-032 | 345 | 2.9216 | 3.2299 | 0.10552
GEN-2017-018 | Central | 03 - Spearville | 588754 | G17-032-TAP | 345 | 2.9216 | 3.2299 | 0.10552
GEN-2017-018 | Central | 03 - Spearville | 588650 | GEN-2017-021 | 345 | 8.859 | 9.6649 | 0.09097
GEN-2017-018 | Central | 03 - Spearville | 588654 | G17-021-TAP | 345 | 9.2902 | 10.1312 | 0.090525
GEN-2017-018 | Central | 03 - Spearville | 589370 | GEN-2017-099 | 345 | 8.859 | 9.6568 | 0.090055
GEN-2017-018 | Central | 03 - Spearville | 599950 | LAMAR7 | 345 | 2.3728 | 2.5722 | 0.084036
GEN-2017-018 | Central | 03 - Spearville | 531469 | SPERVIL7 | 345 | 13.1153 | 13.739 | 0.047555
GEN-2017-018 | Central | 03 - Spearville | 539803 | IRONWOOD7 | 345 | 12.5911 | 13.1405 | 0.043634
GEN-2017-018 | Central | 03 - Spearville | 579480 | GEN-2008-124 | 345 | 12.1777 | 12.6897 | 0.042044
GEN-2017-018 | Central | 03 - Spearville | 523853 | FINNEY 7 | 345 | 9.544 | 9.8902 | 0.036274
GEN-2017-018 | Central | 03 - Spearville | 531449 | HOLCOMB7 | 345 | 9.6562 | 10.0016 | 0.03577
GEN-2017-018 | Central | 03 - Spearville | 589484 | G16-049-TAP | 345 | 8.6792 | 8.9146 | 0.027122
GEN-2017-018 | Central | 03 - Spearville | 531501 | BUCKNER7 | 345 | 8.8014 | 9.0375 | 0.026825
GEN-2017-018 | Central | 03 - Spearville | 560080 | G16-046-TAP | 345 | 11.1556 | 11.4323 | 0.024804
GEN-2017-018 | Central | 03 - Spearville | 539800 | CLARKCOUNTY7 | 345 | 12.9764 | 13.2652 | 0.022256
GEN-2017-018 | Central | 03 - Spearville | 539695 | SPEARVL6 | 230 | 12.2036 | 12.4729 | 0.022067
GEN-2017-018 | Central | 03 - Spearville | 539117 | SPRVILL-EHVB | 230 | 11.8903 | 12.1451 | 0.021429
GEN-2017-018 | Central | 03 - Spearville | 531502 | CIMRRN 7 | 345 | 7.0225 | 7.172 | 0.021289
GEN-2017-018 | Central | 03 - Spearville | 531504 | CIMWD2 7 | 345 | 7.0225 | 7.172 | 0.021289
GEN-2017-018 | Central | 03 - Spearville | 587310 | GEN-2016-046 | 345 | 9.641 | 9.8441 | 0.021066
GEN-2017-018 | Central | 03 - Spearville | 523118 | BUFF_DUNES 7 | 345 | 5.9244 | 6.0476 | 0.020795
GEN-2017-018 | Central | 03 - Spearville | 530583 | POSTROCK7 | 345 | 9.5651 | 9.7633 | 0.020721
GEN-2017-018 | Central | 03 - Spearville | 583370 | GEN-2012-024 | 345 | 11.1056 | 11.3148 | 0.018837
GEN-2017-018 | Central | 03 - Spearville | 539852 | P1 MPT PRI | 345 | 10.5849 | 10.7708 | 0.017563
GEN-2017-018 | Central | 03 - Spearville | 582008 | GEN-2011-008 | 345 | 10.3495 | 10.5174 | 0.016223
GEN-2017-018 | Central | 03 - Spearville | 531465 | SETAB 7 | 345 | 7.0502 | 7.1573 | 0.015191
GEN-2017-018 | Central | 03 - Spearville | 539857 | P2 MPT PRI | 345 | 9.0022 | 9.1323 | 0.014452
GEN-2017-018 | Central | 03 - Spearville | 582908 | G-2011-008-2 | 345 | 8.3279 | 8.4371 | 0.013113
GEN-2017-018 | Central | 03 - Spearville | 582708 | G-2011-008-1 | 345 | 8.457 | 8.564 | 0.012652
GEN-2017-018 | Central | 03 - Spearville | 539759 | SPRVL 3 | 115 | 11.4523 | 11.5615 | 0.0095352
GEN-2017-018 | Central | 03 - Spearville | 531448 | HOLCOMB3 | 115 | 21.3888 | 21.5721 | 0.0085699
GEN-2017-018 | Central | 03 - Spearville | 539694 | SPEARVL3 | 115 | 10.2986 | 10.3686 | 0.006797
GEN-2017-018 | Central | 03 - Spearville | 530582 | S HAYS6 | 230 | 9.7644 | 9.8282 | 0.0065339
GEN-2017-018 | Central | 03 - Spearville | 588630 | GEN-2017-018 | 345 | 16.3278 | 16.4054 | 0.0047526
GEN-2017-018 | Central | 03 - Spearville | 539801 | THISTLE7 | 345 | 16.3278 | 16.4054 | 0.0047526
GEN-2017-018 | Central | 03 - Spearville | 539679 | GRTBEND6 | 230 | 8.4778 | 8.513 | 0.004152
GEN-2017-018 | Central | 03 - Spearville | 530680 | HEIZER 6 | 230 | 8.4277 | 8.4625 | 0.0041292
GEN-2017-018 | Central | 03 - Spearville | 539771 | NFTDODG3 | 115 | 12.214 | 12.2642 | 0.00411
GEN-2017-018 | Central | 03 - Spearville | 539671 | FTDODGE3 | 115 | 12.1733 | 12.2228 | 0.0040663
GEN-2017-018 | Central | 03 - Spearville | 539645 | DCBEEF3 | 115 | 8.1294 | 8.1515 | 0.0027185
GEN-2017-018 | Central | 03 - Spearville | 539688 | S-DODGE3 | 115 | 8.1466 | 8.1667 | 0.0024673
GEN-2017-018 | Central | 03 - Spearville | 539740 | EDODGE 3 | 115 | 7.2953 | 7.3131 | 0.0024399
GEN-2017-018 | Central | 03 - Spearville | 539678 | GRTBEND3 | 115 | 12.9225 | 12.9518 | 0.0022674
GEN-2017-018 | Central | 03 - Spearville | 539804 | THISTLE4 | 138 | 17.4711 | 17.502 | 0.0017686
GEN-2017-018 | Central | 03 - Spearville | 515852 | DGRASSE7 | 345 | 14.5329 | 14.5578 | 0.0017134
GEN-2017-018 | Central | 03 - Spearville | 539680 | N-DODGE3 | 115 | 5.1229 | 5.1316 | 0.0016983
GEN-2017-018 | Central | 03 - Spearville | 530610 | SHAYS_230 | 230 | 4.2554 | 4.2625 | 0.0016685
GEN-2017-018 | Central | 03 - Spearville | 539638 | FLATRDG4 | 138 | 15.5075 | 15.5308 | 0.0015025
GEN-2017-018 | Central | 03 - Spearville | 539758 | FORD 3 | 115 | 5.5694 | 5.5777 | 0.0014903
GEN-2017-018 | Central | 03 - Spearville | 539681 | N-GBEND3 | 115 | 8.3462 | 8.3584 | 0.0014617
GEN-2017-018 | Central | 03 - Spearville | 539641 | NW-DODG3 | 115 | 3.8709 | 3.8759 | 0.0012917
GEN-2017-018 | Central | 03 - Spearville | 539699 | W-DODGE3 | 115 | 5.2105 | 5.2171 | 0.0012667
GEN-2017-018 | Central | 03 - Spearville | 532782 | BUFFALO7 | 345 | 20.6769 | 20.7023 | 0.0012284
GEN-2017-018 | Central | 03 - Spearville | 539661 | 24-FREY3 | 115 | 5.6199 | 5.6255 | 0.00099646
GEN-2017-018 | Central | 03 - Spearville | 539628 | NW-DGTP3 | 115 | 4.063 | 4.067 | 0.00098449
GEN-2017-018 | Central | 03 - Spearville | 539631 | FLATRWD4 | 138 | 10.3564 | 10.3664 | 0.00096559
GEN-2017-018 | Central | 03 - Spearville | 532796 | WICHITA7 | 345 | 24.3601 | 24.3835 | 0.00096059
GEN-2017-018 | Central | 03 - Spearville | 539689 | 2ND-KS 3 | 115 | 5.0444 | 5.0489 | 0.00089208
GEN-2017-018 | Central | 03 - Spearville | 539944 | LOCHS | 115 | 3.6994 | 3.7027 | 0.00089204
GEN-2017-018 | Central | 03 - Spearville | 587500 | GEN-2016-073 | 345 | 15.1804 | 15.1939 | 0.0008893
GEN-2017-018 | Central | 03 - Spearville | 539674 | BARBER 4 | 138 | 8.2161 | 8.2231 | 0.00085199
GEN-2017-018 | Central | 03 - Spearville | 515554 | BVRCNTY7 | 345 | 14.7467 | 14.759 | 0.00083408
GEN-2017-018 | Central | 03 - Spearville | 589060 | GEN-2017-068 | 345 | 20.2535 | 20.2698 | 0.0008048
GEN-2017-018 | Central | 03 - Spearville | 515375 | WWRDEHV7 | 345 | 19.805 | 19.8204 | 0.00077758
GEN-2017-018 | Central | 03 - Spearville | 539760 | BARBER 3 | 115 | 8.0545 | 8.0604 | 0.00073251
GEN-2017-018 | Central | 03 - Spearville | 539673 | MED-LDG3 | 115 | 7.8793 | 7.8849 | 0.00071072
GEN-2017-018 | Central | 03 - Spearville | 515590 | PALDR2W7 | 345 | 12.8368 | 12.8458 | 0.00070111
GEN-2017-018 | Central | 03 - Spearville | 515677 | BADGER 7 | 345 | 14.1527 | 14.1624 | 0.00068538
GEN-2017-018 | Central | 03 - Spearville | 515618 | BALKOW 7 | 345 | 12.2498 | 12.2581 | 0.00067756
GEN-2017-018 | Central | 03 - Spearville | 560071 | G16-003-TAP | 345 | 15.2315 | 15.2408 | 0.00061058
GEN-2017-018 | Central | 03 - Spearville | 587020 | GEN-2016-003 | 345 | 15.2315 | 15.2408 | 0.00061058
GEN-2017-018 | Central | 03 - Spearville | 532871 | CIRCLE 6 | 230 | 10.0517 | 10.0578 | 0.00060686
GEN-2017-018 | Central | 03 - Spearville | 515686 | GEN-2011-014 | 345 | 12.7547 | 12.7624 | 0.0006037
GEN-2017-018 | Central | 03 - Spearville | 515634 | PALDR1W7 | 345 | 11.2669 | 11.2735 | 0.00058579
GEN-2017-018 | Central | 03 - Spearville | 539684 | OTISSUB3 | 115 | 2.9576 | 2.9591 | 0.00050717
GEN-2017-018 | Central | 03 - Spearville | 588560 | GEN-2017-011 | 345 | 12.2579 | 12.2639 | 0.00048948
GEN-2017-018 | Central | 03 - Spearville | 515599 | G07621119-20 | 345 | 13.1976 | 13.2036 | 0.00045463
GEN-2017-018 | Central | 03 - Spearville | 539779 | GRAY CO3 | 115 | 3.5101 | 3.5116 | 0.00042734
GEN-2017-018 | Central | 03 - Spearville | 539667 | HAGGARD3 | 115 | 3.5101 | 3.5116 | 0.00042734
GEN-2017-018 | Central | 03 - Spearville | 539778 | GYCOTAP3 | 115 | 3.5101 | 3.5116 | 0.00042734
GEN-2017-018 | Central | 03 - Spearville | 515853 | DGRASSE4 | 138 | 15.3859 | 15.3923 | 0.00041597
GEN-2017-018 | Central | 03 - Spearville | 532771 | RENO 7 | 345 | 12.6407 | 12.6459 | 0.00041137
GEN-2017-018 | Central | 03 - Spearville | 533413 | CIRCLE 3 | 115 | 23.6141 | 23.6235 | 0.00039807
GEN-2017-018 | Central | 03 - Spearville | 585430 | PRSIMN_CRK1 | 345 | 11.6142 | 11.6188 | 0.00039607
GEN-2017-018 | Central | 03 - Spearville | 539649 | SAWYER 3 | 115 | 4.5887 | 4.5905 | 0.00039227
GEN-2017-018 | Central | 03 - Spearville | 533416 | RENO 3 | 115 | 26.7924 | 26.8023 | 0.00036951
GEN-2017-018 | Central | 03 - Spearville | 585440 | PRSIMN_CRK2 | 345 | 10.6058 | 10.6096 | 0.00035829
GEN-2017-018 | Central | 03 - Spearville | 532791 | BENTON 7 | 345 | 19.74 | 19.7468 | 0.00034448
GEN-2017-018 | Central | 03 - Spearville | 533040 | EVANS N4 | 138 | 33.521 | 33.5322 | 0.00033412
GEN-2017-018 | Central | 03 - Spearville | 533041 | EVANS S4 | 138 | 33.521 | 33.5322 | 0.00033412
GEN-2017-018 | Central | 03 - Spearville | 585190 | GEN-2015-082 | 345 | 7.142 | 7.1443 | 0.00032204
GEN-2017-018 | Central | 03 - Spearville | 520529 | RSVLYSW4 | 138 | 13.6726 | 13.677 | 0.00032181
GEN-2017-018 | Central | 03 - Spearville | 585410 | GREAT_WESTRN | 345 | 9.9442 | 9.9473 | 0.00031174
GEN-2017-018 | Central | 03 - Spearville | 532783 | KINGMAN7 | 345 | 6.8306 | 6.8327 | 0.00030744
GEN-2017-018 | Central | 03 - Spearville | 539668 | HARPER 4 | 138 | 7.2222 | 7.2244 | 0.00030462
GEN-2017-018 | Central | 03 - Spearville | 520436 | ROSEVLY4 | 138 | 12.6934 | 12.6971 | 0.00029149
GEN-2017-018 | Central | 03 - Spearville | 587884 | G16-111-TAP | 345 | 11.3842 | 11.3875 | 0.00028988
GEN-2017-018 | Central | 03 - Spearville | 532798 | VIOLA 7 | 345 | 14.4584 | 14.4624 | 0.00027666
GEN-2017-018 | Central | 03 - Spearville | 515376 | WWRDEHV4 | 138 | 24.17 | 24.1765 | 0.00026893
GEN-2017-018 | Central | 03 - Spearville | 587894 | G16-112-TAP | 345 | 11.182 | 11.1849 | 0.00025935
GEN-2017-018 | Central | 03 - Spearville | 587910 | GEN-2016-114 | 345 | 10.1524 | 10.155 | 0.0002561
GEN-2017-018 | Central | 03 - Spearville | 532784 | NINN1WF7 | 345 | 5.6879 | 5.6893 | 0.00024614
GEN-2017-018 | Central | 03 - Spearville | 533074 | 45TH ST4 | 138 | 24.2551 | 24.2608 | 0.000235
GEN-2017-018 | Central | 03 - Spearville | 585420 | COWBOY_RIDGE | 345 | 7.6709 | 7.6727 | 0.00023465
GEN-2017-018 | Central | 03 - Spearville | 533075 | VIOLA 4 | 138 | 24.4694 | 24.4751 | 0.00023294
GEN-2017-018 | Central | 03 - Spearville | 515407 | TATONGA7 | 345 | 16.7223 | 16.7261 | 0.00022724
GEN-2017-018 | Central | 03 - Spearville | 585250 | GEN-2015-090 | 345 | 5.0818 | 5.0829 | 0.00021646
GEN-2017-018 | Central | 03 - Spearville | 562476 | G14-001-TAP | 345 | 10.626 | 10.6282 | 0.00020704
GEN-2017-018 | Central | 03 - Spearville | 520430 | NOELSW 4 | 138 | 11.3322 | 11.3345 | 0.00020296
GEN-2017-018 | Central | 03 - Spearville | 514795 | KNOBHIL4 | 138 | 11.3909 | 11.3932 | 0.00020192
GEN-2017-018 | Central | 03 - Spearville | 532794 | ROSEHIL7 | 345 | 19.0627 | 19.0665 | 0.00019934
GEN-2017-018 | Central | 03 - Spearville | 589240 | GEN-2017-086 | 345 | 10.5531 | 10.5552 | 0.00019899
GEN-2017-018 | Central | 03 - Spearville | 533065 | SG12COL4 | 138 | 19.7802 | 19.7841 | 0.00019717
GEN-2017-018 | Central | 03 - Spearville | 585300 | GEN-2015-095 | 138 | 11.3118 | 11.314 | 0.00019449
GEN-2017-018 | Central | 03 - Spearville | 532986 | BENTON 4 | 138 | 27.9826 | 27.9879 | 0.0001894
GEN-2017-018 | Central | 03 - Spearville | 533054 | MAIZE 4 | 138 | 21.1222 | 21.1262 | 0.00018937
GEN-2017-018 | Central | 03 - Spearville | 515585 | MAMTHPW7 | 345 | 13.2777 | 13.2801 | 0.00018075
GEN-2017-018 | Central | 03 - Spearville | 539001 | ANTHONY4 | 138 | 5.0259 | 5.0268 | 0.00017907
GEN-2017-018 | Central | 03 - Spearville | 533047 | GILL 4 | 138 | 22.0305 | 22.0344 | 0.00017703
GEN-2017-018 | Central | 03 - Spearville | 533438 | WMCPHER3 | 115 | 15.7546 | 15.7573 | 0.00017138
GEN-2017-018 | Central | 03 - Spearville | 587880 | GEN-2016-111 | 345 | 7.1269 | 7.1281 | 0.00016838
GEN-2017-018 | Central | 03 - Spearville | 515425 | WWDPST 4 | 138 | 17.5422 | 17.5451 | 0.00016532
GEN-2017-018 | Central | 03 - Spearville | 533035 | CHISHLM4 | 138 | 21.3532 | 21.3567 | 0.00016391
GEN-2017-018 | Central | 03 - Spearville | 520601 | AVARD 4 | 138 | 6.9913 | 6.9924 | 0.00015734
GEN-2017-018 | Central | 03 - Spearville | 539009 | CONWAY | 138 | 12.7335 | 12.7355 | 0.00015707
GEN-2017-018 | Central | 03 - Spearville | 533053 | LAKERDG4 | 138 | 17.3481 | 17.3508 | 0.00015564
GEN-2017-018 | Central | 03 - Spearville | 533052 | PARKCTY4 | 138 | 20.1237 | 20.1268 | 0.00015405
GEN-2017-018 | Central | 03 - Spearville | 588320 | GEN-2016-162 | 345 | 9.7753 | 9.7768 | 0.00015345
GEN-2017-018 | Central | 03 - Spearville | 515448 | CRSRDSW7 | 345 | 11.7414 | 11.7432 | 0.0001533
GEN-2017-018 | Central | 03 - Spearville | 539000 | RAGO 4 | 138 | 3.95 | 3.9506 | 0.0001519
GEN-2017-018 | Central | 03 - Spearville | 533062 | ROSEHIL4 | 138 | 31.0086 | 31.0133 | 0.00015157
GEN-2017-018 | Central | 03 - Spearville | 539675 | MILANTP4 | 138 | 9.9211 | 9.9226 | 0.00015119
GEN-2017-018 | Central | 03 - Spearville | 588330 | GEN-2016-163 | 345 | 8.6372 | 8.6384 | 0.00013893
GEN-2017-018 | Central | 03 - Spearville | 539008 | MILAN_GOAB | 138 | 11.9456 | 11.9472 | 0.00013394
GEN-2017-018 | Central | 03 - Spearville | 533024 | 29TH 4 | 138 | 19.423 | 19.4255 | 0.00012871
GEN-2017-018 | Central | 03 - Spearville | 583850 | GEN-2014-001 | 345 | 7.0897 | 7.0906 | 0.00012694
GEN-2017-018 | Central | 03 - Spearville | 533415 | DAVIS 3 | 115 | 8.7135 | 8.7146 | 0.00012624
GEN-2017-018 | Central | 03 - Spearville | 532988 | BELAIRE4 | 138 | 18.7913 | 18.7936 | 0.0001224
GEN-2017-018 | Central | 03 - Spearville | 533036 | CLEARWT4 | 138 | 14.1688 | 14.1705 | 0.00011998
GEN-2017-018 | Central | 03 - Spearville | 539676 | MILAN 4 | 138 | 10.5417 | 10.5429 | 0.00011383
GEN-2017-018 | Central | 03 - Spearville | 515543 | RENFROW7 | 345 | 12.5417 | 12.5431 | 0.00011163
GEN-2017-018 | Central | 03 - Spearville | 533015 | BENTLEY4 | 138 | 10.8174 | 10.8186 | 0.00011093
GEN-2017-018 | Central | 03 - Spearville | 588360 | GEN-2016-153 | 345 | 7.2616 | 7.2624 | 0.00011017
GEN-2017-018 | Central | 03 - Spearville | 539002 | BLF-CRK4 | 138 | 4.7102 | 4.7107 | 0.00010615
GEN-2017-018 | Central | 03 - Spearville | 588364 | G16-153-TAP | 345 | 7.5916 | 7.5924 | 0.00010538
GEN-2017-018 | Central | 03 - Spearville | 532792 | FR2EAST7 | 345 | 6.8423 | 6.843 | 0.0001023
GEN-2017-018 | Central | 03 - Spearville | 587980 | GEN-2016-122 | 345 | 5.2094 | 5.2099 | 9.598e-05
GEN-2017-018 | Central | 03 - Spearville | 515582 | SLNGWND7 | 345 | 7.3456 | 7.3463 | 9.5295e-05
GEN-2017-018 | Central | 03 - Spearville | 515398 | OUSPRT 4 | 138 | 9.4833 | 9.4842 | 9.4904e-05
GEN-2017-018 | Central | 03 - Spearville | 520437 | SALTPLN4 | 138 | 6.5467 | 6.5473 | 9.1649e-05
GEN-2017-018 | Central | 03 - Spearville | 515646 | GRNTWD 7 | 345 | 11.0032 | 11.0042 | 9.0883e-05
GEN-2017-018 | Central | 03 - Spearville | 515394 | KEENAN 4 | 138 | 8.9116 | 8.9124 | 8.9771e-05
GEN-2017-018 | Central | 03 - Spearville | 515458 | BORDER 7 | 345 | 4.4956 | 4.496 | 8.8976e-05
GEN-2017-018 | Central | 03 - Spearville | 533016 | WWUPLNT4 | 138 | 8.1589 | 8.1596 | 8.5796e-05
GEN-2017-018 | Central | 03 - Spearville | 587890 | GEN-2016-112 | 345 | 4.6689 | 4.6693 | 8.5673e-05
GEN-2017-018 | Central | 03 - Spearville | 533429 | MOUNDRG3 | 115 | 8.6504 | 8.6511 | 8.0921e-05
GEN-2017-018 | Central | 03 - Spearville | 578530 | FR3HV | 345 | 4.9911 | 4.9915 | 8.0143e-05
GEN-2017-018 | Central | 03 - Spearville | 514785 | WOODWRD4 | 138 | 13.1298 | 13.1308 | 7.6163e-05
GEN-2017-018 | Central | 03 - Spearville | 532795 | FR2WEST7 | 345 | 5.4502 | 5.4506 | 7.3392e-05
GEN-2017-018 | Central | 03 - Spearville | 584900 | GEN-2015-052 | 345 | 13.0806 | 13.0815 | 6.8804e-05
GEN-2017-018 | Central | 03 - Spearville | 560053 | G15-052T | 345 | 13.1309 | 13.1318 | 6.8541e-05
GEN-2017-018 | Central | 03 - Spearville | 515477 | CHSHLMV7 | 345 | 13.5537 | 13.5546 | 6.6403e-05
GEN-2017-018 | Central | 03 - Spearville | 515476 | HUNTERS7 | 345 | 13.5721 | 13.573 | 6.6313e-05
GEN-2017-018 | Central | 03 - Spearville | 532768 | EMPEC 7 | 345 | 17.6048 | 17.6059 | 6.2483e-05
GEN-2017-018 | Central | 03 - Spearville | 515497 | MATHWSN7 | 345 | 33.252 | 33.254 | 6.0147e-05
GEN-2017-018 | Central | 03 - Spearville | 532769 | LANG 7 | 345 | 17.3857 | 17.3867 | 5.7519e-05
GEN-2017-018 | Central | 03 - Spearville | 532800 | LATHAMS7 | 345 | 10.5077 | 10.5083 | 5.7101e-05
GEN-2017-018 | Central | 03 - Spearville | 532990 | MIDIAN 4 | 138 | 10.5583 | 10.5589 | 5.6827e-05
GEN-2017-018 | Central | 03 - Spearville | 515544 | RENFROW4 | 138 | 14.4233 | 14.4241 | 5.5466e-05
GEN-2017-018 | Central | 03 - Spearville | 514794 | KNOBHIL2 | 69 | 9.106 | 9.1065 | 5.4909e-05
GEN-2017-018 | Central | 03 - Spearville | 532801 | ELKRVR17 | 345 | 9.264 | 9.2645 | 5.3972e-05
GEN-2017-018 | Central | 03 - Spearville | 514792 | ALVAOGE2 | 69 | 7.6425 | 7.6429 | 5.2339e-05
GEN-2017-018 | Central | 03 - Spearville | 532984 | SUMNER 4 | 138 | 10.2472 | 10.2477 | 4.8794e-05
GEN-2017-018 | Central | 03 - Spearville | 520462 | ASPEN 4 | 138 | 19.8344 | 19.8353 | 4.5376e-05
GEN-2017-018 | Central | 03 - Spearville | 585100 | GEN-2015-073 | 345 | 13.3996 | 13.4002 | 4.4777e-05
GEN-2017-018 | Central | 03 - Spearville | 515785 | WINDFRM4 | 138 | 20.1169 | 20.1178 | 4.4739e-05
GEN-2017-018 | Central | 03 - Spearville | 515863 | REDCLF 4 | 138 | 6.7222 | 6.7225 | 4.4628e-05
GEN-2017-018 | Central | 03 - Spearville | 520999 | MOORLND4 | 138 | 20.5759 | 20.5768 | 4.374e-05
GEN-2017-018 | Central | 03 - Spearville | 514796 | IODINE-4 | 138 | 7.385 | 7.3853 | 4.0623e-05
GEN-2017-018 | Central | 03 - Spearville | 532770 | MORRIS 7 | 345 | 12.8684 | 12.8689 | 3.8855e-05
GEN-2017-018 | Central | 03 - Spearville | 532797 | WOLFCRK7 | 345 | 18.1147 | 18.1154 | 3.8643e-05
GEN-2017-018 | Central | 03 - Spearville | 514901 | CIMARON7 | 345 | 34.6099 | 34.6112 | 3.7562e-05
GEN-2017-018 | Central | 03 - Spearville | 515877 | REDDIRT7 | 345 | 18.071 | 18.0716 | 3.3202e-05
GEN-2017-018 | Central | 03 - Spearville | 515875 | REDNGTN7 | 345 | 18.0752 | 18.0758 | 3.3195e-05
GEN-2017-018 | Central | 03 - Spearville | 515363 | CENT 4 | 138 | 3.1163 | 3.1164 | 3.2089e-05
GEN-2017-018 | Central | 03 - Spearville | 532799 | WAVERLY7 | 345 | 16.0603 | 16.0608 | 3.1133e-05
GEN-2017-018 | Central | 03 - Spearville | 515560 | CZYCRVT2 | 69 | 3.2561 | 3.2562 | 3.0712e-05
GEN-2017-018 | Central | 03 - Spearville | 514880 | NORTWST7 | 345 | 33.062 | 33.063 | 3.0246e-05
GEN-2017-018 | Central | 03 - Spearville | 515533 | REDCLFT4 | 138 | 6.7369 | 6.7371 | 2.9687e-05
GEN-2017-018 | Central | 03 - Spearville | 514782 | WODWRD 2 | 69 | 10.9468 | 10.9471 | 2.7405e-05
GEN-2017-018 | Central | 03 - Spearville | 532802 | WAVERTX7 | 345 | 13.4367 | 13.437 | 2.2327e-05
GEN-2017-018 | Central | 03 - Spearville | 514779 | WDNITRO2 | 69 | 4.7712 | 4.7713 | 2.0959e-05
GEN-2017-018 | Central | 03 - Spearville | 514775 | TANGRTP2 | 69 | 4.7833 | 4.7834 | 2.0906e-05
GEN-2017-018 | Central | 03 - Spearville | 514788 | GLASMTN4 | 138 | 5.1336 | 5.1337 | 1.948e-05
GEN-2017-018 | Central | 03 - Spearville | 532774 | SWISVAL7 | 345 | 16.1666 | 16.1669 | 1.8557e-05
GEN-2017-018 | Central | 03 - Spearville | 514776 | NEWGRTP2 | 69 | 5.4631 | 5.4632 | 1.8305e-05
GEN-2017-018 | Central | 03 - Spearville | 514781 | CEDARAV2 | 69 | 5.7046 | 5.7047 | 1.753e-05
GEN-2017-018 | Central | 03 - Spearville | 515610 | FSHRTAP7 | 345 | 17.7289 | 17.7292 | 1.6922e-05
GEN-2017-018 | Central | 03 - Spearville | 515786 | FPLWIND4 | 138 | 6.8222 | 6.8223 | 1.4658e-05
GEN-2017-018 | Central | 03 - Spearville | 900001 | TRAVERSE1 | 345 | 7.3844 | 7.3845 | 1.3542e-05
GEN-2017-018 | Central | 03 - Spearville | 521065 | TALOGA 4 | 138 | 7.4782 | 7.4783 | 1.3372e-05
GEN-2017-018 | Central | 03 - Spearville | 587140 | GEN-2016-020 | 138 | 7.4829 | 7.483 | 1.3364e-05
GEN-2017-018 | Central | 03 - Spearville | 520425 | PIC4 | 138 | 7.8452 | 7.8453 | 1.2747e-05
GEN-2017-018 | Central | 03 - Spearville | 520957 | IODINE 4 | 138 | 7.8901 | 7.8902 | 1.2674e-05
GEN-2017-018 | Central | 03 - Spearville | 520995 | MOORLND2 | 69 | 8.5665 | 8.5666 | 1.1673e-05
GEN-2017-018 | Central | 03 - Spearville | 583340 | GEN-2012-020 | 230 | 9.8744 | 9.8745 | 1.0127e-05
GEN-2017-018 | Central | 03 - Spearville | 525850 | ELK_CT1 | 345 | 11.8971 | 11.8972 | 8.4054e-06
GEN-2017-018 | Central | 03 - Spearville | 515600 | KNGFSHR7 | 345 | 11.9001 | 11.9002 | 8.4033e-06
GEN-2017-018 | Central | 03 - Spearville | 525832 | TUCO_INT 7 | 345 | 11.9884 | 11.9885 | 8.3414e-06
GEN-2017-018 | Central | 03 - Spearville | 515605 | CANADN7 | 345 | 12.9578 | 12.9579 | 7.7174e-06
GEN-2017-018 | Central | 03 - Spearville | 525840 | ANTELOPE_1 6 | 230 | 21.0432 | 21.0433 | 4.7521e-06
GEN-2017-018 | Central | 03 - Spearville | 525830 | TUCO_INT 6 | 230 | 21.2068 | 21.2069 | 4.7155e-06
GEN-2017-018 | Central | 03 - Spearville | 526936 | YOAKUM_345 | 345 | 8.5075 | 8.5075 | 0
GEN-2017-018 | Central | 03 - Spearville | 514771 | TANGIER2 | 69 | 3.6773 | 3.6773 | 0
GEN-2017-018 | Central | 03 - Spearville | 514773 | NEWMAN 2 | 69 | 1.5468 | 1.5468 | 0
GEN-2017-018 | Central | 03 - Spearville | 533629 | CC2SHAR2 | 69 | 4.5461 | 4.5461 | 0
GEN-2017-018 | Central | 03 - Spearville | 900002 | TRAVERSE2 | 345 | 5.7168 | 5.7168 | 0
GEN-2017-018 | Central | 03 - Spearville | 900003 | TRAVERSE3 | 345 | 5.1975 | 5.1975 | 0
GEN-2017-018 | Central | 03 - Spearville | 588760 | GEN-2017-033 | 345 | 4.0304 | 4.0304 | 0
GEN-2017-018 | Central | 03 - Spearville | 533653 | WOLFCRK2 | 69 | 5.8601 | 5.8601 | 0
GEN-2017-018 | Central | 03 - Spearville | 588970 | GEN-2017-059 | 230 | 8.547 | 8.547 | 0
GEN-2017-018 | Central | 03 - Spearville | 589030 | GEN-2017-065 | 345 | 5.0163 | 5.0163 | 0
GEN-2017-018 | Central | 03 - Spearville | 511565 | OKLAUN HVDC7 | 345 | 5.4749 | 5.4749 | 0
GEN-2017-018 | Central | 03 - Spearville | 511456 | O.K.U.-7 | 345 | 5.4913 | 5.4913 | 0
GEN-2017-021 | Central | 03 - Spearville | 588750 | GEN-2017-032 | 345 | 2.9216 | 3.2299 | 0.10552
GEN-2017-021 | Central | 03 - Spearville | 588754 | G17-032-TAP | 345 | 2.9216 | 3.2299 | 0.10552
GEN-2017-021 | Central | 03 - Spearville | 588650 | GEN-2017-021 | 345 | 8.859 | 9.6649 | 0.09097
GEN-2017-021 | Central | 03 - Spearville | 588654 | G17-021-TAP | 345 | 9.2902 | 10.1312 | 0.090525
GEN-2017-021 | Central | 03 - Spearville | 589370 | GEN-2017-099 | 345 | 8.859 | 9.6568 | 0.090055
GEN-2017-021 | Central | 03 - Spearville | 599950 | LAMAR7 | 345 | 2.3728 | 2.5722 | 0.084036
GEN-2017-021 | Central | 03 - Spearville | 531469 | SPERVIL7 | 345 | 13.1153 | 13.739 | 0.047555
GEN-2017-021 | Central | 03 - Spearville | 539803 | IRONWOOD7 | 345 | 12.5911 | 13.1405 | 0.043634
GEN-2017-021 | Central | 03 - Spearville | 579480 | GEN-2008-124 | 345 | 12.1777 | 12.6897 | 0.042044
GEN-2017-021 | Central | 03 - Spearville | 523853 | FINNEY 7 | 345 | 9.544 | 9.8902 | 0.036274
GEN-2017-021 | Central | 03 - Spearville | 531449 | HOLCOMB7 | 345 | 9.6562 | 10.0016 | 0.03577
GEN-2017-021 | Central | 03 - Spearville | 589484 | G16-049-TAP | 345 | 8.6792 | 8.9146 | 0.027122
GEN-2017-021 | Central | 03 - Spearville | 531501 | BUCKNER7 | 345 | 8.8014 | 9.0375 | 0.026825
GEN-2017-021 | Central | 03 - Spearville | 560080 | G16-046-TAP | 345 | 11.1556 | 11.4323 | 0.024804
GEN-2017-021 | Central | 03 - Spearville | 539800 | CLARKCOUNTY7 | 345 | 12.9764 | 13.2652 | 0.022256
GEN-2017-021 | Central | 03 - Spearville | 539695 | SPEARVL6 | 230 | 12.2036 | 12.4729 | 0.022067
GEN-2017-021 | Central | 03 - Spearville | 539117 | SPRVILL-EHVB | 230 | 11.8903 | 12.1451 | 0.021429
GEN-2017-021 | Central | 03 - Spearville | 531502 | CIMRRN 7 | 345 | 7.0225 | 7.172 | 0.021289
GEN-2017-021 | Central | 03 - Spearville | 531504 | CIMWD2 7 | 345 | 7.0225 | 7.172 | 0.021289
GEN-2017-021 | Central | 03 - Spearville | 587310 | GEN-2016-046 | 345 | 9.641 | 9.8441 | 0.021066
GEN-2017-021 | Central | 03 - Spearville | 523118 | BUFF_DUNES 7 | 345 | 5.9244 | 6.0476 | 0.020795
GEN-2017-021 | Central | 03 - Spearville | 530583 | POSTROCK7 | 345 | 9.5651 | 9.7633 | 0.020721
GEN-2017-021 | Central | 03 - Spearville | 583370 | GEN-2012-024 | 345 | 11.1056 | 11.3148 | 0.018837
GEN-2017-021 | Central | 03 - Spearville | 539852 | P1 MPT PRI | 345 | 10.5849 | 10.7708 | 0.017563
GEN-2017-021 | Central | 03 - Spearville | 582008 | GEN-2011-008 | 345 | 10.3495 | 10.5174 | 0.016223
GEN-2017-021 | Central | 03 - Spearville | 531465 | SETAB 7 | 345 | 7.0502 | 7.1573 | 0.015191
GEN-2017-021 | Central | 03 - Spearville | 539857 | P2 MPT PRI | 345 | 9.0022 | 9.1323 | 0.014452
GEN-2017-021 | Central | 03 - Spearville | 582908 | G-2011-008-2 | 345 | 8.3279 | 8.4371 | 0.013113
GEN-2017-021 | Central | 03 - Spearville | 582708 | G-2011-008-1 | 345 | 8.457 | 8.564 | 0.012652
GEN-2017-021 | Central | 03 - Spearville | 530584 | POSTROCK6 | 230 | 12.8772 | 13.0179 | 0.010926
GEN-2017-021 | Central | 03 - Spearville | 530558 | KNOLL 6 | 230 | 12.7371 | 12.8736 | 0.010717
GEN-2017-021 | Central | 03 - Spearville | 539759 | SPRVL 3 | 115 | 11.4523 | 11.5615 | 0.0095352
GEN-2017-021 | Central | 03 - Spearville | 531448 | HOLCOMB3 | 115 | 21.3888 | 21.5721 | 0.0085699
GEN-2017-021 | Central | 03 - Spearville | 530702 | BUCKEYE_230 | 230 | 9.2881 | 9.3543 | 0.0071274
GEN-2017-021 | Central | 03 - Spearville | 539694 | SPEARVL3 | 115 | 10.2986 | 10.3686 | 0.006797
GEN-2017-021 | Central | 03 - Spearville | 530582 | S HAYS6 | 230 | 9.7644 | 9.8282 | 0.0065339
GEN-2017-021 | Central | 03 - Spearville | 531451 | MINGO 7 | 345 | 6.8482 | 6.8898 | 0.0060746
GEN-2017-021 | Central | 03 - Spearville | 531632 | GEN-2016-067 | 345 | 6.8482 | 6.8898 | 0.0060746
GEN-2017-021 | Central | 03 - Spearville | 588580 | GEN-2017-013 | 345 | 6.7841 | 6.8249 | 0.0060141
GEN-2017-021 | Central | 03 - Spearville | 523823 | CARPENTER 7 | 345 | 6.5344 | 6.5732 | 0.0059378
GEN-2017-021 | Central | 03 - Spearville | 531464 | SETAB 3 | 115 | 10.2918 | 10.3483 | 0.0054898
GEN-2017-021 | Central | 03 - Spearville | 585030 | GEN-2015-065 | 345 | 6.1591 | 6.1922 | 0.0053742
GEN-2017-021 | Central | 03 - Spearville | 588630 | GEN-2017-018 | 345 | 16.3278 | 16.4054 | 0.0047526
GEN-2017-021 | Central | 03 - Spearville | 539801 | THISTLE7 | 345 | 16.3278 | 16.4054 | 0.0047526
GEN-2017-021 | Central | 03 - Spearville | 539679 | GRTBEND6 | 230 | 8.4778 | 8.513 | 0.004152
GEN-2017-021 | Central | 03 - Spearville | 530680 | HEIZER 6 | 230 | 8.4277 | 8.4625 | 0.0041292
GEN-2017-021 | Central | 03 - Spearville | 539771 | NFTDODG3 | 115 | 12.214 | 12.2642 | 0.00411
GEN-2017-021 | Central | 03 - Spearville | 539671 | FTDODGE3 | 115 | 12.1733 | 12.2228 | 0.0040663
GEN-2017-021 | Central | 03 - Spearville | 531379 | JONES3 | 115 | 10.8669 | 10.9085 | 0.0038281
GEN-2017-021 | Central | 03 - Spearville | 531445 | GRDNCTY3 | 115 | 14.0365 | 14.0881 | 0.0036761
GEN-2017-021 | Central | 03 - Spearville | 530561 | KNOLL 3 | 115 | 12.1272 | 12.168 | 0.0033643
GEN-2017-021 | Central | 03 - Spearville | 531429 | MINGO 3 | 115 | 12.9898 | 13.033 | 0.0033257
GEN-2017-021 | Central | 03 - Spearville | 530676 | GMEC 3 | 115 | 11.5228 | 11.5588 | 0.0031242
GEN-2017-021 | Central | 03 - Spearville | 640325 | REDWILO3 | 345 | 9.3783 | 9.4068 | 0.0030389
GEN-2017-021 | Central | 03 - Spearville | 560082 | G16-050-TAP | 345 | 7.1649 | 7.1859 | 0.002931
GEN-2017-021 | Central | 03 - Spearville | 530553 | S HAYS 3 | 115 | 9.13 | 9.1552 | 0.0027601
GEN-2017-021 | Central | 03 - Spearville | 539645 | DCBEEF3 | 115 | 8.1294 | 8.1515 | 0.0027185
GEN-2017-021 | Central | 03 - Spearville | 587350 | GEN-2016-050 | 345 | 6.4203 | 6.4369 | 0.0025855
GEN-2017-021 | Central | 03 - Spearville | 539688 | S-DODGE3 | 115 | 8.1466 | 8.1667 | 0.0024673
GEN-2017-021 | Central | 03 - Spearville | 539740 | EDODGE 3 | 115 | 7.2953 | 7.3131 | 0.0024399
GEN-2017-021 | Central | 03 - Spearville | 585020 | GEN-2015-064 | 115 | 10.1386 | 10.1633 | 0.0024362
GEN-2017-021 | Central | 03 - Spearville | 531393 | PLYMELL3 | 115 | 7.569 | 7.5869 | 0.0023649
GEN-2017-021 | Central | 03 - Spearville | 531420 | FLETCHR3 | 115 | 6.7413 | 6.7567 | 0.0022844
GEN-2017-021 | Central | 03 - Spearville | 530601 | HEIZER 3 | 115 | 12.7456 | 12.7746 | 0.0022753
GEN-2017-021 | Central | 03 - Spearville | 539678 | GRTBEND3 | 115 | 12.9225 | 12.9518 | 0.0022674
GEN-2017-021 | Central | 03 - Spearville | 539804 | THISTLE4 | 138 | 17.4711 | 17.502 | 0.0017686
GEN-2017-021 | Central | 03 - Spearville | 515852 | DGRASSE7 | 345 | 14.5329 | 14.5578 | 0.0017134
GEN-2017-021 | Central | 03 - Spearville | 539680 | N-DODGE3 | 115 | 5.1229 | 5.1316 | 0.0016983
GEN-2017-021 | Central | 03 - Spearville | 530610 | SHAYS_230 | 230 | 4.2554 | 4.2625 | 0.0016685
GEN-2017-021 | Central | 03 - Spearville | 640065 | AXTELL 3 | 345 | 9.6103 | 9.6255 | 0.0015816
GEN-2017-021 | Central | 03 - Spearville | 539638 | FLATRDG4 | 138 | 15.5075 | 15.5308 | 0.0015025
GEN-2017-021 | Central | 03 - Spearville | 539758 | FORD 3 | 115 | 5.5694 | 5.5777 | 0.0014903
GEN-2017-021 | Central | 03 - Spearville | 539681 | N-GBEND3 | 115 | 8.3462 | 8.3584 | 0.0014617
GEN-2017-021 | Central | 03 - Spearville | 530609 | HZRNGPL3 | 115 | 8.0052 | 8.0167 | 0.0014366
GEN-2017-021 | Central | 03 - Spearville | 539641 | NW-DODG3 | 115 | 3.8709 | 3.8759 | 0.0012917
GEN-2017-021 | Central | 03 - Spearville | 539699 | W-DODGE3 | 115 | 5.2105 | 5.2171 | 0.0012667
GEN-2017-021 | Central | 03 - Spearville | 532782 | BUFFALO7 | 345 | 20.6769 | 20.7023 | 0.0012284
GEN-2017-021 | Central | 03 - Spearville | 539666 | GBENDTP3 | 115 | 7.6967 | 7.7061 | 0.0012213
GEN-2017-021 | Central | 03 - Spearville | 531408 | PIERCVL3 | 115 | 3.8381 | 3.8427 | 0.0011985
GEN-2017-021 | Central | 03 - Spearville | 539783 | CRKCK 3 | 115 | 4.1956 | 4.2001 | 0.0010726
GEN-2017-021 | Central | 03 - Spearville | 539661 | 24-FREY3 | 115 | 5.6199 | 5.6255 | 0.00099646
GEN-2017-021 | Central | 03 - Spearville | 539628 | NW-DGTP3 | 115 | 4.063 | 4.067 | 0.00098449
GEN-2017-021 | Central | 03 - Spearville | 530552 | GORHAM 3 | 115 | 3.171 | 3.1741 | 0.00097761
GEN-2017-021 | Central | 03 - Spearville | 539631 | FLATRWD4 | 138 | 10.3564 | 10.3664 | 0.00096559
GEN-2017-021 | Central | 03 - Spearville | 532796 | WICHITA7 | 345 | 24.3601 | 24.3835 | 0.00096059
GEN-2017-021 | Central | 03 - Spearville | 530592 | SMOKYHL6 | 230 | 7.1343 | 7.1409 | 0.00092511
GEN-2017-021 | Central | 03 - Spearville | 539689 | 2ND-KS 3 | 115 | 5.0444 | 5.0489 | 0.00089208
GEN-2017-021 | Central | 03 - Spearville | 539944 | LOCHS | 115 | 3.6994 | 3.7027 | 0.00089204
GEN-2017-021 | Central | 03 - Spearville | 587500 | GEN-2016-073 | 345 | 15.1804 | 15.1939 | 0.0008893
GEN-2017-021 | Central | 03 - Spearville | 640326 | REDWILO7 | 115 | 12.6507 | 12.6619 | 0.00088533
GEN-2017-021 | Central | 03 - Spearville | 640183 | GENTLMN3 | 345 | 18.2387 | 18.2548 | 0.00088274
GEN-2017-021 | Central | 03 - Spearville | 531407 | INGALLS3 | 115 | 2.6792 | 2.6814 | 0.00082114
GEN-2017-021 | Central | 03 - Spearville | 531213 | SANTAFE3 | 115 | 2.6806 | 2.6828 | 0.00082071
GEN-2017-021 | Central | 03 - Spearville | 530599 | SMKYP2 6 | 230 | 6.6055 | 6.6109 | 0.0008175
GEN-2017-021 | Central | 03 - Spearville | 589060 | GEN-2017-068 | 345 | 20.2535 | 20.2698 | 0.0008048
GEN-2017-021 | Central | 03 - Spearville | 515375 | WWRDEHV7 | 345 | 19.805 | 19.8204 | 0.00077758
GEN-2017-021 | Central | 03 - Spearville | 530593 | SMKYP1 6 | 230 | 6.1703 | 6.175 | 0.00076171
GEN-2017-021 | Central | 03 - Spearville | 640252 | KEYSTON3 | 345 | 12.7746 | 12.7842 | 0.00075149
GEN-2017-021 | Central | 03 - Spearville | 530677 | OGALATP3 | 115 | 2.6344 | 2.6363 | 0.00072123
GEN-2017-021 | Central | 03 - Spearville | 539763 | SSTARTP3 | 115 | 4.0724 | 4.0753 | 0.00071211
GEN-2017-021 | Central | 03 - Spearville | 640374 | SWEET W3 | 345 | 10.9794 | 10.9872 | 0.00071042
GEN-2017-021 | Central | 03 - Spearville | 539784 | ENSNGW 3 | 115 | 2.8424 | 2.8444 | 0.00070363
GEN-2017-021 | Central | 03 - Spearville | 531211 | CHRLSTN3 | 115 | 2.2297 | 2.2312 | 0.00067274
GEN-2017-021 | Central | 03 - Spearville | 531210 | BLUEJAY3 | 115 | 2.1032 | 2.1046 | 0.00066565
GEN-2017-021 | Central | 03 - Spearville | 530684 | RUSLPMP3 | 115 | 2.0504 | 2.0517 | 0.00063402
GEN-2017-021 | Central | 03 - Spearville | 531492 | OG ONEOK | 115 | 2.1303 | 2.1316 | 0.00061024
GEN-2017-021 | Central | 03 - Spearville | 532871 | CIRCLE 6 | 230 | 10.0517 | 10.0578 | 0.00060686
GEN-2017-021 | Central | 03 - Spearville | 530560 | WKNNY 3 | 115 | 2.2105 | 2.2118 | 0.0005881
GEN-2017-021 | Central | 03 - Spearville | 531423 | GARDNCY2 | 69 | 3.6434 | 3.6455 | 0.00057638
GEN-2017-021 | Central | 03 - Spearville | 539761 | SSTARW 3 | 115 | 3.4163 | 3.4182 | 0.00055616
GEN-2017-021 | Central | 03 - Spearville | 640269 | MCCOOK 7 | 115 | 9.3182 | 9.3232 | 0.00053658
GEN-2017-021 | Central | 03 - Spearville | 539684 | OTISSUB3 | 115 | 2.9576 | 2.9591 | 0.00050717
GEN-2017-021 | Central | 03 - Spearville | 640312 | PAULINE3 | 345 | 8.4521 | 8.4562 | 0.00048509
GEN-2017-021 | Central | 03 - Spearville | 531212 | TWNSPRG3 | 115 | 1.6677 | 1.6685 | 0.0004797
GEN-2017-021 | Central | 03 - Spearville | 640066 | AXTELL 7 | 115 | 14.2198 | 14.2265 | 0.00047117
GEN-2017-021 | Central | 03 - Spearville | 515599 | G07621119-20 | 345 | 13.1976 | 13.2036 | 0.00045463
GEN-2017-021 | Central | 03 - Spearville | 588530 | GEN-2017-008 | 345 | 7.853 | 7.8565 | 0.00044569
GEN-2017-021 | Central | 03 - Spearville | 539779 | GRAY CO3 | 115 | 3.5101 | 3.5116 | 0.00042734
GEN-2017-021 | Central | 03 - Spearville | 539667 | HAGGARD3 | 115 | 3.5101 | 3.5116 | 0.00042734
GEN-2017-021 | Central | 03 - Spearville | 539778 | GYCOTAP3 | 115 | 3.5101 | 3.5116 | 0.00042734
GEN-2017-021 | Central | 03 - Spearville | 515853 | DGRASSE4 | 138 | 15.3859 | 15.3923 | 0.00041597
GEN-2017-021 | Central | 03 - Spearville | 640184 | GENTLMN4 | 230 | 20.0055 | 20.0136 | 0.00040489
GEN-2017-021 | Central | 03 - Spearville | 533413 | CIRCLE 3 | 115 | 23.6141 | 23.6235 | 0.00039807
GEN-2017-021 | Central | 03 - Spearville | 585430 | PRSIMN_CRK1 | 345 | 11.6142 | 11.6188 | 0.00039607
GEN-2017-021 | Central | 03 - Spearville | 587680 | GEN-2016-074 | 345 | 6.4721 | 6.4745 | 0.00037082
GEN-2017-021 | Central | 03 - Spearville | 585440 | PRSIMN_CRK2 | 345 | 10.6058 | 10.6096 | 0.00035829
GEN-2017-021 | Central | 03 - Spearville | 539642 | ELLSWTP3 | 115 | 3.9821 | 3.9835 | 0.00035157
GEN-2017-021 | Central | 03 - Spearville | 532872 | EMCPHER6 | 230 | 9.3729 | 9.3761 | 0.00034141
GEN-2017-021 | Central | 03 - Spearville | 587850 | GEN-2016-106 | 345 | 8.8132 | 8.8161 | 0.00032905
GEN-2017-021 | Central | 03 - Spearville | 585410 | GREAT_WESTRN | 345 | 9.9442 | 9.9473 | 0.00031174
GEN-2017-021 | Central | 03 - Spearville | 532783 | KINGMAN7 | 345 | 6.8306 | 6.8327 | 0.00030744
GEN-2017-021 | Central | 03 - Spearville | 640082 | BEVERLY7 | 115 | 4.8655 | 4.8669 | 0.00028774
GEN-2017-021 | Central | 03 - Spearville | 659425 | SD.LS-KS-MB3 | 345 | 7.6812 | 7.6833 | 0.00027339
GEN-2017-021 | Central | 03 - Spearville | 659426 | SD.LS-LR-MB3 | 345 | 7.6812 | 7.6833 | 0.00027339
GEN-2017-021 | Central | 03 - Spearville | 640253 | KEYSTON7 | 115 | 15.6225 | 15.6265 | 0.00025604
GEN-2017-021 | Central | 03 - Spearville | 532784 | NINN1WF7 | 345 | 5.6879 | 5.6893 | 0.00024614
GEN-2017-021 | Central | 03 - Spearville | 585420 | COWBOY_RIDGE | 345 | 7.6709 | 7.6727 | 0.00023465
GEN-2017-021 | Central | 03 - Spearville | 585250 | GEN-2015-090 | 345 | 5.0818 | 5.0829 | 0.00021646
GEN-2017-021 | Central | 03 - Spearville | 530686 | RICE 6 | 230 | 4.9172 | 4.9182 | 0.00020337
GEN-2017-021 | Central | 03 - Spearville | 640365 | STOCKVL7 | 115 | 4.5853 | 4.5862 | 0.00019628
GEN-2017-021 | Central | 03 - Spearville | 640083 | BEVERLY8 | 69 | 4.356 | 4.3567 | 0.0001607
GEN-2017-021 | Central | 03 - Spearville | 640270 | MCCOOK 8 | 69 | 4.5246 | 4.5253 | 0.00015471
GEN-2017-021 | Central | 03 - Spearville | 640255 | KINGSLY7 | 115 | 9.3401 | 9.3414 | 0.00013918
GEN-2017-021 | Central | 03 - Spearville | 640500 | THEDFRD3 | 345 | 5.2771 | 5.2777 | 0.0001137
GEN-2017-021 | Central | 03 - Spearville | 640366 | STOCKVL8 | 69 | 3.2872 | 3.2875 | 9.1263e-05
GEN-2017-021 | Central | 03 - Spearville | 530688 | BUFLOCRK6 | 230 | 3.6479 | 3.6482 | 8.2239e-05
GEN-2017-032 | Central | 03 - Spearville | 588750 | GEN-2017-032 | 345 | 2.9216 | 3.2299 | 0.10552
GEN-2017-032 | Central | 03 - Spearville | 588754 | G17-032-TAP | 345 | 2.9216 | 3.2299 | 0.10552
GEN-2017-032 | Central | 03 - Spearville | 588650 | GEN-2017-021 | 345 | 8.859 | 9.6649 | 0.09097
GEN-2017-032 | Central | 03 - Spearville | 588654 | G17-021-TAP | 345 | 9.2902 | 10.1312 | 0.090525
GEN-2017-032 | Central | 03 - Spearville | 589370 | GEN-2017-099 | 345 | 8.859 | 9.6568 | 0.090055
GEN-2017-032 | Central | 03 - Spearville | 599950 | LAMAR7 | 345 | 2.3728 | 2.5722 | 0.084036
GEN-2017-032 | Central | 03 - Spearville | 531469 | SPERVIL7 | 345 | 13.1153 | 13.739 | 0.047555
GEN-2017-032 | Central | 03 - Spearville | 539803 | IRONWOOD7 | 345 | 12.5911 | 13.1405 | 0.043634
GEN-2017-032 | Central | 03 - Spearville | 579480 | GEN-2008-124 | 345 | 12.1777 | 12.6897 | 0.042044
GEN-2017-032 | Central | 03 - Spearville | 523853 | FINNEY 7 | 345 | 9.544 | 9.8902 | 0.036274
GEN-2017-032 | Central | 03 - Spearville | 531449 | HOLCOMB7 | 345 | 9.6562 | 10.0016 | 0.03577
GEN-2017-032 | Central | 03 - Spearville | 531501 | BUCKNER7 | 345 | 8.8014 | 9.0375 | 0.026825
GEN-2017-032 | Central | 03 - Spearville | 539800 | CLARKCOUNTY7 | 345 | 12.9764 | 13.2652 | 0.022256
GEN-2017-032 | Central | 03 - Spearville | 539695 | SPEARVL6 | 230 | 12.2036 | 12.4729 | 0.022067
GEN-2017-032 | Central | 03 - Spearville | 539117 | SPRVILL-EHVB | 230 | 11.8903 | 12.1451 | 0.021429
GEN-2017-032 | Central | 03 - Spearville | 531502 | CIMRRN 7 | 345 | 7.0225 | 7.172 | 0.021289
GEN-2017-032 | Central | 03 - Spearville | 531504 | CIMWD2 7 | 345 | 7.0225 | 7.172 | 0.021289
GEN-2017-032 | Central | 03 - Spearville | 523118 | BUFF_DUNES 7 | 345 | 5.9244 | 6.0476 | 0.020795
GEN-2017-032 | Central | 03 - Spearville | 583370 | GEN-2012-024 | 345 | 11.1056 | 11.3148 | 0.018837
GEN-2017-032 | Central | 03 - Spearville | 539852 | P1 MPT PRI | 345 | 10.5849 | 10.7708 | 0.017563
GEN-2017-032 | Central | 03 - Spearville | 582008 | GEN-2011-008 | 345 | 10.3495 | 10.5174 | 0.016223
GEN-2017-032 | Central | 03 - Spearville | 531465 | SETAB 7 | 345 | 7.0502 | 7.1573 | 0.015191
GEN-2017-032 | Central | 03 - Spearville | 539857 | P2 MPT PRI | 345 | 9.0022 | 9.1323 | 0.014452
GEN-2017-032 | Central | 03 - Spearville | 582908 | G-2011-008-2 | 345 | 8.3279 | 8.4371 | 0.013113
GEN-2017-032 | Central | 03 - Spearville | 582708 | G-2011-008-1 | 345 | 8.457 | 8.564 | 0.012652
GEN-2017-032 | Central | 03 - Spearville | 539759 | SPRVL 3 | 115 | 11.4523 | 11.5615 | 0.0095352
GEN-2017-032 | Central | 03 - Spearville | 531448 | HOLCOMB3 | 115 | 21.3888 | 21.5721 | 0.0085699
GEN-2017-032 | Central | 03 - Spearville | 531632 | GEN-2016-067 | 345 | 6.8482 | 6.8898 | 0.0060746
GEN-2017-032 | Central | 03 - Spearville | 531451 | MINGO 7 | 345 | 6.8482 | 6.8898 | 0.0060746
GEN-2017-032 | Central | 03 - Spearville | 588580 | GEN-2017-013 | 345 | 6.7841 | 6.8249 | 0.0060141
GEN-2017-032 | Central | 03 - Spearville | 523823 | CARPENTER 7 | 345 | 6.5344 | 6.5732 | 0.0059378
GEN-2017-032 | Central | 03 - Spearville | 531512 | HARBNGR7 | 345 | 6.5143 | 6.5528 | 0.0059101
GEN-2017-032 | Central | 03 - Spearville | 531464 | SETAB 3 | 115 | 10.2918 | 10.3483 | 0.0054898
GEN-2017-032 | Central | 03 - Spearville | 585030 | GEN-2015-065 | 345 | 6.1591 | 6.1922 | 0.0053742
GEN-2017-032 | Central | 03 - Spearville | 531433 | SCOTCTY3 | 115 | 8.7819 | 8.82 | 0.0043385
GEN-2017-032 | Central | 03 - Spearville | 531379 | JONES3 | 115 | 10.8669 | 10.9085 | 0.0038281
GEN-2017-032 | Central | 03 - Spearville | 531445 | GRDNCTY3 | 115 | 14.0365 | 14.0881 | 0.0036761
GEN-2017-032 | Central | 03 - Spearville | 531480 | KSAVWTP3 | 115 | 13.5136 | 13.5621 | 0.003589
GEN-2017-032 | Central | 03 - Spearville | 531426 | JAMESON3 | 115 | 10.363 | 10.3994 | 0.0035125
GEN-2017-032 | Central | 03 - Spearville | 531429 | MINGO 3 | 115 | 12.9898 | 13.033 | 0.0033257
GEN-2017-032 | Central | 03 - Spearville | 640325 | REDWILO3 | 345 | 9.3783 | 9.4068 | 0.0030389
GEN-2017-032 | Central | 03 - Spearville | 531510 | HARBNGR3 | 115 | 9.5207 | 9.5445 | 0.0024998
GEN-2017-032 | Central | 03 - Spearville | 531485 | CNTRLPL3 | 115 | 5.5886 | 5.6025 | 0.0024872
GEN-2017-032 | Central | 03 - Spearville | 585020 | GEN-2015-064 | 115 | 10.1386 | 10.1633 | 0.0024362
GEN-2017-032 | Central | 03 - Spearville | 531405 | WALKMYR3 | 115 | 9.1635 | 9.1852 | 0.0023681
GEN-2017-032 | Central | 03 - Spearville | 531393 | PLYMELL3 | 115 | 7.569 | 7.5869 | 0.0023649
GEN-2017-032 | Central | 03 - Spearville | 531420 | FLETCHR3 | 115 | 6.7413 | 6.7567 | 0.0022844
GEN-2017-032 | Central | 03 - Spearville | 531476 | SWNDTAP3 | 115 | 7.603 | 7.6182 | 0.0019992
GEN-2017-032 | Central | 03 - Spearville | 531477 | S. WIND3 | 115 | 6.9695 | 6.9823 | 0.0018366
GEN-2017-032 | Central | 03 - Spearville | 531392 | PIONTAP3 | 115 | 6.4742 | 6.4831 | 0.0013747
GEN-2017-032 | Central | 03 - Spearville | 531400 | PK_GOAB3 | 115 | 4.8387 | 4.8451 | 0.0013227
GEN-2017-032 | Central | 03 - Spearville | 531375 | PUCKET 3 | 115 | 4.8253 | 4.8316 | 0.0013056
GEN-2017-032 | Central | 03 - Spearville | 523097 | HITCHLAND 7 | 345 | 15.0825 | 15.1013 | 0.0012465
GEN-2017-032 | Central | 03 - Spearville | 531398 | SUBLETE3 | 115 | 5.7966 | 5.8038 | 0.0012421
GEN-2017-032 | Central | 03 - Spearville | 531404 | WALKMYR2 | 69 | 8.0166 | 8.0265 | 0.0012349
GEN-2017-032 | Central | 03 - Spearville | 531440 | WILLIAM3 | 115 | 3.7332 | 3.7378 | 0.0012322
GEN-2017-032 | Central | 03 - Spearville | 523112 | NOVUS1 7 | 345 | 14.8143 | 14.8323 | 0.001215
GEN-2017-032 | Central | 03 - Spearville | 531408 | PIERCVL3 | 115 | 3.8381 | 3.8427 | 0.0011985
GEN-2017-032 | Central | 03 - Spearville | 531406 | WOODS 2 | 69 | 5.9432 | 5.9487 | 0.00092543
GEN-2017-032 | Central | 03 - Spearville | 576395 | GEN-2010-014 | 345 | 11.1406 | 11.1504 | 0.00087967
GEN-2017-032 | Central | 03 - Spearville | 515554 | BVRCNTY7 | 345 | 14.7467 | 14.759 | 0.00083408
GEN-2017-032 | Central | 03 - Spearville | 531407 | INGALLS3 | 115 | 2.6792 | 2.6814 | 0.00082114
GEN-2017-032 | Central | 03 - Spearville | 531213 | SANTAFE3 | 115 | 2.6806 | 2.6828 | 0.00082071
GEN-2017-032 | Central | 03 - Spearville | 523215 | FREWHELCOL17 | 345 | 9.1648 | 9.1713 | 0.00070924
GEN-2017-032 | Central | 03 - Spearville | 515590 | PALDR2W7 | 345 | 12.8368 | 12.8458 | 0.00070111
GEN-2017-032 | Central | 03 - Spearville | 515677 | BADGER 7 | 345 | 14.1527 | 14.1624 | 0.00068538
GEN-2017-032 | Central | 03 - Spearville | 515618 | BALKOW 7 | 345 | 12.2498 | 12.2581 | 0.00067756
GEN-2017-032 | Central | 03 - Spearville | 531211 | CHRLSTN3 | 115 | 2.2297 | 2.2312 | 0.00067274
GEN-2017-032 | Central | 03 - Spearville | 531210 | BLUEJAY3 | 115 | 2.1032 | 2.1046 | 0.00066565
GEN-2017-032 | Central | 03 - Spearville | 523095 | HITCHLAND 6 | 230 | 14.7297 | 14.7393 | 0.00065174
GEN-2017-032 | Central | 03 - Spearville | 515686 | GEN-2011-014 | 345 | 12.7547 | 12.7624 | 0.0006037
GEN-2017-032 | Central | 03 - Spearville | 515634 | PALDR1W7 | 345 | 11.2669 | 11.2735 | 0.00058579
GEN-2017-032 | Central | 03 - Spearville | 531423 | GARDNCY2 | 69 | 3.6434 | 3.6455 | 0.00057638
GEN-2017-032 | Central | 03 - Spearville | 531212 | TWNSPRG3 | 115 | 1.6677 | 1.6685 | 0.0004797
GEN-2017-032 | Central | 03 - Spearville | 531389 | NORTH6T2 | 69 | 2.9234 | 2.9247 | 0.00044469
GEN-2017-032 | Central | 03 - Spearville | 531388 | NORTH6 2 | 69 | 2.5026 | 2.5035 | 0.00035963
GEN-2017-032 | Central | 03 - Spearville | 531384 | MOSCOW 2 | 69 | 2.1181 | 2.1188 | 0.00033048
GEN-2017-032 | Central | 03 - Spearville | 523111 | NOVUS1 3 | 115 | 19.4124 | 19.4188 | 0.00032969
GEN-2017-032 | Central | 03 - Spearville | 585190 | GEN-2015-082 | 345 | 7.142 | 7.1443 | 0.00032204
GEN-2017-032 | Central | 03 - Spearville | 531385 | MOSCOWT2 | 69 | 2.2272 | 2.2279 | 0.0003143
GEN-2017-032 | Central | 03 - Spearville | 523093 | HITCHLAND 3 | 115 | 17.7697 | 17.775 | 0.00029826
GEN-2017-032 | Central | 03 - Spearville | 576396 | G10-014-XFMR | 115 | 13.2816 | 13.2853 | 0.00027858
GEN-2017-032 | Central | 03 - Spearville | 576407 | G10-014-XF-2 | 115 | 12.5088 | 12.512 | 0.00025582
GEN-2017-032 | Central | 03 - Spearville | 523103 | NOBLE_WND 3 | 115 | 10.6709 | 10.6735 | 0.00024365
GEN-2017-032 | Central | 03 - Spearville | 523131 | NBLWND-HV3 3 | 115 | 8.0184 | 8.0198 | 0.0001746
GEN-2017-032 | Central | 03 - Spearville | 576397 | G10-014-XF-1 | 115 | 9.2433 | 9.2449 | 0.0001731
GEN-2017-032 | Central | 03 - Spearville | 523155 | OCHILTREE 6 | 230 | 4.2738 | 4.2744 | 0.00014039
GEN-2017-032 | Central | 03 - Spearville | 579377 | G06-044-MV2B | 115 | 10.2519 | 10.2533 | 0.00013656
GEN-2017-032 | Central | 03 - Spearville | 523961 | POTTER_CO 7 | 345 | 7.4518 | 7.4527 | 0.00012078
GEN-2017-032 | Central | 03 - Spearville | 523130 | NBLWND-HV2 3 | 115 | 5.1328 | 5.1334 | 0.0001169
GEN-2017-032 | Central | 03 - Spearville | 579370 | G06-044-MV1A | 115 | 8.2364 | 8.2373 | 0.00010927
GEN-2017-032 | Central | 03 - Spearville | 523309 | MOORE_CNTY 6 | 230 | 6.8181 | 6.8187 | 8.8001e-05
GEN-2017-032 | Central | 03 - Spearville | 523174 | GOODWELLWND3 | 115 | 6.6028 | 6.6033 | 7.5725e-05
GEN-2017-032 | Central | 03 - Spearville | 523959 | POTTER_CO 6 | 230 | 20.0739 | 20.0753 | 6.9742e-05
GEN-2017-032 | Central | 03 - Spearville | 524296 | SPNSPUR_WND7 | 345 | 4.5322 | 4.5325 | 6.6193e-05
GEN-2017-032 | Central | 03 - Spearville | 524909 | ROSEVELT_N 6 | 230 | 9.3752 | 9.3752 | 0
GEN-2017-032 | Central | 03 - Spearville | 599955 | PNM-DC6 | 230 | 9.3752 | 9.3752 | 0
GEN-2017-032 | Central | 03 - Spearville | 599951 | LAMAR 6 | 345 | 57.859 | 57.859 | 0
GEN-2017-032 | Central | 03 - Spearville | 599960 | EPTNP-D6 | 230 | 7.7768 | 7.7768 | 0
GEN-2017-099 | Central | 03 - Spearville | 588750 | GEN-2017-032 | 345 | 2.9216 | 3.2299 | 0.10552
GEN-2017-099 | Central | 03 - Spearville | 588754 | G17-032-TAP | 345 | 2.9216 | 3.2299 | 0.10552
GEN-2017-099 | Central | 03 - Spearville | 588650 | GEN-2017-021 | 345 | 8.859 | 9.6649 | 0.09097
GEN-2017-099 | Central | 03 - Spearville | 588654 | G17-021-TAP | 345 | 9.2902 | 10.1312 | 0.090525
GEN-2017-099 | Central | 03 - Spearville | 589370 | GEN-2017-099 | 345 | 8.859 | 9.6568 | 0.090055
GEN-2017-099 | Central | 03 - Spearville | 599950 | LAMAR7 | 345 | 2.3728 | 2.5722 | 0.084036
GEN-2017-099 | Central | 03 - Spearville | 531469 | SPERVIL7 | 345 | 13.1153 | 13.739 | 0.047555
GEN-2017-099 | Central | 03 - Spearville | 539803 | IRONWOOD7 | 345 | 12.5911 | 13.1405 | 0.043634
GEN-2017-099 | Central | 03 - Spearville | 579480 | GEN-2008-124 | 345 | 12.1777 | 12.6897 | 0.042044
GEN-2017-099 | Central | 03 - Spearville | 523853 | FINNEY 7 | 345 | 9.544 | 9.8902 | 0.036274
GEN-2017-099 | Central | 03 - Spearville | 531449 | HOLCOMB7 | 345 | 9.6562 | 10.0016 | 0.03577
GEN-2017-099 | Central | 03 - Spearville | 531501 | BUCKNER7 | 345 | 8.8014 | 9.0375 | 0.026825
GEN-2017-099 | Central | 03 - Spearville | 539800 | CLARKCOUNTY7 | 345 | 12.9764 | 13.2652 | 0.022256
GEN-2017-099 | Central | 03 - Spearville | 539695 | SPEARVL6 | 230 | 12.2036 | 12.4729 | 0.022067
GEN-2017-099 | Central | 03 - Spearville | 539117 | SPRVILL-EHVB | 230 | 11.8903 | 12.1451 | 0.021429
GEN-2017-099 | Central | 03 - Spearville | 531502 | CIMRRN 7 | 345 | 7.0225 | 7.172 | 0.021289
GEN-2017-099 | Central | 03 - Spearville | 531504 | CIMWD2 7 | 345 | 7.0225 | 7.172 | 0.021289
GEN-2017-099 | Central | 03 - Spearville | 523118 | BUFF_DUNES 7 | 345 | 5.9244 | 6.0476 | 0.020795
GEN-2017-099 | Central | 03 - Spearville | 583370 | GEN-2012-024 | 345 | 11.1056 | 11.3148 | 0.018837
GEN-2017-099 | Central | 03 - Spearville | 539852 | P1 MPT PRI | 345 | 10.5849 | 10.7708 | 0.017563
GEN-2017-099 | Central | 03 - Spearville | 582008 | GEN-2011-008 | 345 | 10.3495 | 10.5174 | 0.016223
GEN-2017-099 | Central | 03 - Spearville | 531465 | SETAB 7 | 345 | 7.0502 | 7.1573 | 0.015191
GEN-2017-099 | Central | 03 - Spearville | 539857 | P2 MPT PRI | 345 | 9.0022 | 9.1323 | 0.014452
GEN-2017-099 | Central | 03 - Spearville | 582908 | G-2011-008-2 | 345 | 8.3279 | 8.4371 | 0.013113
GEN-2017-099 | Central | 03 - Spearville | 582708 | G-2011-008-1 | 345 | 8.457 | 8.564 | 0.012652
GEN-2017-099 | Central | 03 - Spearville | 539759 | SPRVL 3 | 115 | 11.4523 | 11.5615 | 0.0095352
GEN-2017-099 | Central | 03 - Spearville | 531448 | HOLCOMB3 | 115 | 21.3888 | 21.5721 | 0.0085699
GEN-2017-099 | Central | 03 - Spearville | 531632 | GEN-2016-067 | 345 | 6.8482 | 6.8898 | 0.0060746
GEN-2017-099 | Central | 03 - Spearville | 531451 | MINGO 7 | 345 | 6.8482 | 6.8898 | 0.0060746
GEN-2017-099 | Central | 03 - Spearville | 588580 | GEN-2017-013 | 345 | 6.7841 | 6.8249 | 0.0060141
GEN-2017-099 | Central | 03 - Spearville | 523823 | CARPENTER 7 | 345 | 6.5344 | 6.5732 | 0.0059378
GEN-2017-099 | Central | 03 - Spearville | 531512 | HARBNGR7 | 345 | 6.5143 | 6.5528 | 0.0059101
GEN-2017-099 | Central | 03 - Spearville | 531464 | SETAB 3 | 115 | 10.2918 | 10.3483 | 0.0054898
GEN-2017-099 | Central | 03 - Spearville | 585030 | GEN-2015-065 | 345 | 6.1591 | 6.1922 | 0.0053742
GEN-2017-099 | Central | 03 - Spearville | 531433 | SCOTCTY3 | 115 | 8.7819 | 8.82 | 0.0043385
GEN-2017-099 | Central | 03 - Spearville | 531379 | JONES3 | 115 | 10.8669 | 10.9085 | 0.0038281
GEN-2017-099 | Central | 03 - Spearville | 531445 | GRDNCTY3 | 115 | 14.0365 | 14.0881 | 0.0036761
GEN-2017-099 | Central | 03 - Spearville | 531480 | KSAVWTP3 | 115 | 13.5136 | 13.5621 | 0.003589
GEN-2017-099 | Central | 03 - Spearville | 531426 | JAMESON3 | 115 | 10.363 | 10.3994 | 0.0035125
GEN-2017-099 | Central | 03 - Spearville | 531429 | MINGO 3 | 115 | 12.9898 | 13.033 | 0.0033257
GEN-2017-099 | Central | 03 - Spearville | 640325 | REDWILO3 | 345 | 9.3783 | 9.4068 | 0.0030389
GEN-2017-099 | Central | 03 - Spearville | 531510 | HARBNGR3 | 115 | 9.5207 | 9.5445 | 0.0024998
GEN-2017-099 | Central | 03 - Spearville | 531485 | CNTRLPL3 | 115 | 5.5886 | 5.6025 | 0.0024872
GEN-2017-099 | Central | 03 - Spearville | 585020 | GEN-2015-064 | 115 | 10.1386 | 10.1633 | 0.0024362
GEN-2017-099 | Central | 03 - Spearville | 531405 | WALKMYR3 | 115 | 9.1635 | 9.1852 | 0.0023681
GEN-2017-099 | Central | 03 - Spearville | 531393 | PLYMELL3 | 115 | 7.569 | 7.5869 | 0.0023649
GEN-2017-099 | Central | 03 - Spearville | 531420 | FLETCHR3 | 115 | 6.7413 | 6.7567 | 0.0022844
GEN-2017-099 | Central | 03 - Spearville | 531476 | SWNDTAP3 | 115 | 7.603 | 7.6182 | 0.0019992
GEN-2017-099 | Central | 03 - Spearville | 531477 | S. WIND3 | 115 | 6.9695 | 6.9823 | 0.0018366
GEN-2017-099 | Central | 03 - Spearville | 531392 | PIONTAP3 | 115 | 6.4742 | 6.4831 | 0.0013747
GEN-2017-099 | Central | 03 - Spearville | 531400 | PK_GOAB3 | 115 | 4.8387 | 4.8451 | 0.0013227
GEN-2017-099 | Central | 03 - Spearville | 531375 | PUCKET 3 | 115 | 4.8253 | 4.8316 | 0.0013056
GEN-2017-099 | Central | 03 - Spearville | 523097 | HITCHLAND 7 | 345 | 15.0825 | 15.1013 | 0.0012465
GEN-2017-099 | Central | 03 - Spearville | 531398 | SUBLETE3 | 115 | 5.7966 | 5.8038 | 0.0012421
GEN-2017-099 | Central | 03 - Spearville | 531404 | WALKMYR2 | 69 | 8.0166 | 8.0265 | 0.0012349
GEN-2017-099 | Central | 03 - Spearville | 531440 | WILLIAM3 | 115 | 3.7332 | 3.7378 | 0.0012322
GEN-2017-099 | Central | 03 - Spearville | 523112 | NOVUS1 7 | 345 | 14.8143 | 14.8323 | 0.001215
GEN-2017-099 | Central | 03 - Spearville | 531408 | PIERCVL3 | 115 | 3.8381 | 3.8427 | 0.0011985
GEN-2017-099 | Central | 03 - Spearville | 531406 | WOODS 2 | 69 | 5.9432 | 5.9487 | 0.00092543
GEN-2017-099 | Central | 03 - Spearville | 576395 | GEN-2010-014 | 345 | 11.1406 | 11.1504 | 0.00087967
GEN-2017-099 | Central | 03 - Spearville | 515554 | BVRCNTY7 | 345 | 14.7467 | 14.759 | 0.00083408
GEN-2017-099 | Central | 03 - Spearville | 531407 | INGALLS3 | 115 | 2.6792 | 2.6814 | 0.00082114
GEN-2017-099 | Central | 03 - Spearville | 531213 | SANTAFE3 | 115 | 2.6806 | 2.6828 | 0.00082071
GEN-2017-099 | Central | 03 - Spearville | 523215 | FREWHELCOL17 | 345 | 9.1648 | 9.1713 | 0.00070924
GEN-2017-099 | Central | 03 - Spearville | 515590 | PALDR2W7 | 345 | 12.8368 | 12.8458 | 0.00070111
GEN-2017-099 | Central | 03 - Spearville | 515677 | BADGER 7 | 345 | 14.1527 | 14.1624 | 0.00068538
GEN-2017-099 | Central | 03 - Spearville | 515618 | BALKOW 7 | 345 | 12.2498 | 12.2581 | 0.00067756
GEN-2017-099 | Central | 03 - Spearville | 531211 | CHRLSTN3 | 115 | 2.2297 | 2.2312 | 0.00067274
GEN-2017-099 | Central | 03 - Spearville | 531210 | BLUEJAY3 | 115 | 2.1032 | 2.1046 | 0.00066565
GEN-2017-099 | Central | 03 - Spearville | 523095 | HITCHLAND 6 | 230 | 14.7297 | 14.7393 | 0.00065174
GEN-2017-099 | Central | 03 - Spearville | 515686 | GEN-2011-014 | 345 | 12.7547 | 12.7624 | 0.0006037
GEN-2017-099 | Central | 03 - Spearville | 515634 | PALDR1W7 | 345 | 11.2669 | 11.2735 | 0.00058579
GEN-2017-099 | Central | 03 - Spearville | 531423 | GARDNCY2 | 69 | 3.6434 | 3.6455 | 0.00057638
GEN-2017-099 | Central | 03 - Spearville | 531212 | TWNSPRG3 | 115 | 1.6677 | 1.6685 | 0.0004797
GEN-2017-099 | Central | 03 - Spearville | 531389 | NORTH6T2 | 69 | 2.9234 | 2.9247 | 0.00044469
GEN-2017-099 | Central | 03 - Spearville | 531388 | NORTH6 2 | 69 | 2.5026 | 2.5035 | 0.00035963
GEN-2017-099 | Central | 03 - Spearville | 531384 | MOSCOW 2 | 69 | 2.1181 | 2.1188 | 0.00033048
GEN-2017-099 | Central | 03 - Spearville | 523111 | NOVUS1 3 | 115 | 19.4124 | 19.4188 | 0.00032969
GEN-2017-099 | Central | 03 - Spearville | 585190 | GEN-2015-082 | 345 | 7.142 | 7.1443 | 0.00032204
GEN-2017-099 | Central | 03 - Spearville | 531385 | MOSCOWT2 | 69 | 2.2272 | 2.2279 | 0.0003143
GEN-2017-099 | Central | 03 - Spearville | 523093 | HITCHLAND 3 | 115 | 17.7697 | 17.775 | 0.00029826
GEN-2017-099 | Central | 03 - Spearville | 576396 | G10-014-XFMR | 115 | 13.2816 | 13.2853 | 0.00027858
GEN-2017-099 | Central | 03 - Spearville | 576407 | G10-014-XF-2 | 115 | 12.5088 | 12.512 | 0.00025582
GEN-2017-099 | Central | 03 - Spearville | 523103 | NOBLE_WND 3 | 115 | 10.6709 | 10.6735 | 0.00024365
GEN-2017-099 | Central | 03 - Spearville | 523131 | NBLWND-HV3 3 | 115 | 8.0184 | 8.0198 | 0.0001746
GEN-2017-099 | Central | 03 - Spearville | 576397 | G10-014-XF-1 | 115 | 9.2433 | 9.2449 | 0.0001731
GEN-2017-099 | Central | 03 - Spearville | 523155 | OCHILTREE 6 | 230 | 4.2738 | 4.2744 | 0.00014039
GEN-2017-099 | Central | 03 - Spearville | 579377 | G06-044-MV2B | 115 | 10.2519 | 10.2533 | 0.00013656
GEN-2017-099 | Central | 03 - Spearville | 523961 | POTTER_CO 7 | 345 | 7.4518 | 7.4527 | 0.00012078
GEN-2017-099 | Central | 03 - Spearville | 523130 | NBLWND-HV2 3 | 115 | 5.1328 | 5.1334 | 0.0001169
GEN-2017-099 | Central | 03 - Spearville | 579370 | G06-044-MV1A | 115 | 8.2364 | 8.2373 | 0.00010927
GEN-2017-099 | Central | 03 - Spearville | 523309 | MOORE_CNTY 6 | 230 | 6.8181 | 6.8187 | 8.8001e-05
GEN-2017-099 | Central | 03 - Spearville | 523174 | GOODWELLWND3 | 115 | 6.6028 | 6.6033 | 7.5725e-05
GEN-2017-099 | Central | 03 - Spearville | 523959 | POTTER_CO 6 | 230 | 20.0739 | 20.0753 | 6.9742e-05
GEN-2017-099 | Central | 03 - Spearville | 524296 | SPNSPUR_WND7 | 345 | 4.5322 | 4.5325 | 6.6193e-05
GEN-2017-099 | Central | 03 - Spearville | 524909 | ROSEVELT_N 6 | 230 | 9.3752 | 9.3752 | 0
GEN-2017-099 | Central | 03 - Spearville | 599955 | PNM-DC6 | 230 | 9.3752 | 9.3752 | 0
GEN-2017-099 | Central | 03 - Spearville | 599951 | LAMAR 6 | 345 | 57.859 | 57.859 | 0
GEN-2017-099 | Central | 03 - Spearville | 599960 | EPTNP-D6 | 230 | 7.7768 | 7.7768 | 0
GEN-2017-052 | Central | 03 - Spearville | 531448 | HOLCOMB3 | 115 | 21.3888 | 21.5721 | 0.0085699 |  |  | X
GEN-2017-052 | Central | 03 - Spearville | 531420 | FLETCHR3 | 115 | 6.7413 | 6.7567 | 0.0022844 |  |  | X
GEN-2017-052 | Central | 03 - Spearville | 531434 | SELKIRK3 | 115 | 3.7543 | 3.7599 | 0.0014916 |  |  | X
GEN-2017-052 | Central | 03 - Spearville | 531391 | PIONEER3 | 115 | 5.8179 | 5.8258 | 0.0013579 |  |  | X
GEN-2017-052 | Central | 03 - Spearville | 531400 | PK_GOAB3 | 115 | 4.8387 | 4.8451 | 0.0013227 |  |  | X
GEN-2017-052 | Central | 03 - Spearville | 531375 | PUCKET 3 | 115 | 4.8253 | 4.8316 | 0.0013056 |  |  | X
GEN-2017-052 | Central | 03 - Spearville | 531438 | TRIB SW3 | 115 | 3.4766 | 3.481 | 0.0012656 |  |  | X
GEN-2017-052 | Central | 03 - Spearville | 531439 | TRIBUNE3 | 115 | 3.4073 | 3.4116 | 0.001262 |  |  | X
GEN-2017-052 | Central | 03 - Spearville | 531440 | WILLIAM3 | 115 | 3.7332 | 3.7378 | 0.0012322 |  |  | X
GEN-2017-052 | Central | 03 - Spearville | 531437 | SYRACUS3 | 115 | 3.5583 | 3.5624 | 0.0011522 |  |  | X
GEN-2017-052 | Central | 03 - Spearville | 531431 | PALMER3 | 115 | 3.0073 | 3.0105 | 0.0010641 |  |  | X
GEN-2017-052 | Central | 03 - Spearville | 531490 | ULYSPLT3 | 115 | 3.8634 | 3.867 | 0.00093182 |  |  | X
GEN-2017-052 | Central | 03 - Spearville | 531473 | BEARCRK3 | 115 | 2.7512 | 2.7535 | 0.000836 |  |  | X
GEN-2017-052 | Central | 03 - Spearville | 531491 | BIG BOW 3 | 115 | 3.0259 | 3.0283 | 0.00079315 |  |  | X
GEN-2017-052 | Central | 03 - Spearville | 588910 | GEN-2017-052 | 115 | 2.6705 | 2.6726 | 0.00078637 |  |  | X
GEN-2017-052 | Central | 03 - Spearville | 588914 | G17-052-TAP | 115 | 2.6705 | 2.6726 | 0.00078637 |  |  | X
GEN-2017-052 | Central | 03 - Spearville | 531381 | JOHNSON2 | 115 | 2.7549 | 2.757 | 0.00076228 |  |  | X
GEN-2017-052 | Central | 03 - Spearville | 584630 | GEN-2015-021 | 115 | 2.7043 | 2.7063 | 0.00073956 |  |  | X
GEN-2017-052 | Central | 03 - Spearville | 531424 | JOHNCR 3 | 115 | 2.7078 | 2.7098 | 0.00073861 |  |  | X
GEN-2017-052 | Central | 03 - Spearville | 531390 | PIONEER2 | 69 | 3.8793 | 3.8814 | 0.00054133 |  |  | X
GEN-2017-052 | Central | 03 - Spearville | 531401 | ULU E 2 | 69 | 3.6374 | 3.6393 | 0.00052235 |  |  | X
GEN-2017-052 | Central | 03 - Spearville | 531402 | ULU NW 2 | 69 | 3.0651 | 3.0664 | 0.00042413 |  |  | X
GEN-2017-052 | Central | 03 - Spearville | 531403 | ULU PLT2 | 69 | 2.9845 | 2.9857 | 0.00040208 |  |  | X
GEN-2017-052 | Central | 03 - Spearville | 531475 | MANTERT2 | 69 | 1.9645 | 1.9652 | 0.00035632 |  |  | X
GEN-2017-052 | Central | 03 - Spearville | 531383 | JOHNCR 2 | 69 | 2.2469 | 2.2477 | 0.00035605 |  |  | X
GEN-2017-052 | Central | 03 - Spearville | 531382 | MANTER 2 | 69 | 1.6213 | 1.6217 | 0.00024672 |  |  | X
GEN-2017-052 | Central | 03 - Spearville | 531474 | RICHFLD2 | 69 | 1.2587 | 1.259 | 0.00023834 |  |  | X
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 588500 | GEN-2017-005 | 161 | 6.1239 | 6.7684 | 0.10524
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 588504 | G17-005-TAP | 161 | 6.2091 | 6.8529 | 0.10369
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 588540 | GEN-2017-009 | 345 | 9.9978 | 10.5633 | 0.056562
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 588544 | G17-009-TAP | 345 | 10.8451 | 11.4101 | 0.052097
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 532934 | MARMTNE5 | 161 | 8.0271 | 8.3996 | 0.046405
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 532935 | MARMTNW5 | 161 | 8.0271 | 8.3996 | 0.046405
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 532938 | FRANKLIN5 | 161 | 7.3574 | 7.6097 | 0.034292
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 532793 | NEOSHO 7 | 345 | 16.4472 | 16.8864 | 0.026704
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 532932 | LITCH 5 | 161 | 8.4404 | 8.6426 | 0.023956
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 543650 | DAKOTA_5 | 161 | 7.5109 | 7.6868 | 0.023419
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 543651 | PRQN_WIND5 | 161 | 6.4747 | 6.5832 | 0.016758
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 547476 | ASB349 5 | 161 | 10.2736 | 10.4272 | 0.014951
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533876 | FRANKLIN2 | 69 | 10.8139 | 10.9702 | 0.014454
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533765 | LITCH N2 | 69 | 12.258 | 12.4335 | 0.014317
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533766 | LITCH S2 | 69 | 12.258 | 12.4335 | 0.014317
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533639 | MARMATN2 | 69 | 8.3602 | 8.4769 | 0.013959
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 532937 | NEOSHO 5 | 161 | 21.0898 | 21.3739 | 0.013471
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533769 | PITNAC 2 | 69 | 10.791 | 10.9282 | 0.012714
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533020 | NEOSHOS4 | 138 | 22.8316 | 23.1093 | 0.012163
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533021 | NEOSHO 4 | 138 | 22.8316 | 23.1093 | 0.012163
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533022 | NEOSHON4 | 138 | 22.8316 | 23.1093 | 0.012163
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533647 | UN1ELSM2 | 69 | 7.4596 | 7.5451 | 0.011462
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533771 | ROUSE 2 | 69 | 9.1923 | 9.2932 | 0.010977
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533759 | DEPAUL 2 | 69 | 9.0629 | 9.1617 | 0.010902
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533775 | FRONTEN2 | 69 | 8.3303 | 8.4155 | 0.010228
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533767 | MULBERY2 | 69 | 7.9288 | 8.0076 | 0.0099385
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533770 | PITTSBG2 | 69 | 8.2594 | 8.3412 | 0.0099039
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 589200 | GEN-2017-082 | 161 | 7.1442 | 7.2138 | 0.0097422
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533764 | HUDSJCT2 | 69 | 7.8793 | 7.9533 | 0.0093917
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533756 | AQUARS 2 | 69 | 7.837 | 7.9101 | 0.0093275
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 543065 | CNTRVIL5 | 161 | 6.1989 | 6.2554 | 0.0091145
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 300739 | 7BLACKBERRY | 345 | 14.7665 | 14.8807 | 0.0077337
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533763 | HUDSON-2 | 69 | 6.2651 | 6.312 | 0.0074859
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 547491 | PUR421 5 | 161 | 9.0186 | 9.0825 | 0.0070854
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 547477 | CJ 366 5 | 161 | 11.7457 | 11.8216 | 0.0064619
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533640 | MCKEE 2 | 69 | 4.1424 | 4.1691 | 0.0064455
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533778 | NEOSHOS2 | 69 | 22.2897 | 22.4333 | 0.0064424
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533762 | GIR JCT2 | 69 | 6.3031 | 6.3413 | 0.0060605
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533774 | SHEFFLD2 | 69 | 4.4112 | 4.4364 | 0.0057127
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 510380 | DELWARE7 | 345 | 10.9307 | 10.9927 | 0.0056721
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 547490 | FIR417 5 | 161 | 13.5186 | 13.595 | 0.0056515
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533645 | SE9HIAT2 | 69 | 3.7003 | 3.7211 | 0.0056212
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533654 | ZILAJCT2 | 69 | 5.6188 | 5.6478 | 0.0051612
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 547467 | ORO110 5 | 161 | 18.3996 | 18.4918 | 0.005011
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533635 | FTSCOTT2 | 69 | 3.4075 | 3.4241 | 0.0048716
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533652 | WARE 2 | 69 | 3.4346 | 3.4512 | 0.0048332
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 547485 | CAR395 5 | 161 | 11.5223 | 11.576 | 0.0046605
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533761 | GIRARD 2 | 69 | 4.4111 | 4.4296 | 0.004194
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533650 | UN8HUMB2 | 69 | 4.0623 | 4.0775 | 0.0037417
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 547469 | RIV4525 | 161 | 23.1554 | 23.2407 | 0.0036838
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 547503 | RIV452T 5 | 161 | 22.7618 | 22.8433 | 0.0035806
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 547502 | RIV167 5 | 161 | 21.5053 | 21.578 | 0.0033806
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 547501 | RIV453 5 | 161 | 21.9817 | 22.056 | 0.0033801
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 532926 | BAKER 2 | 69 | 4.8595 | 4.8748 | 0.0031485
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 547498 | STL439 5 | 161 | 23.7884 | 23.8627 | 0.0031234
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533772 | SE1GREE2 | 69 | 5.9484 | 5.9667 | 0.0030765
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533758 | CRAWFOR2 | 69 | 7.108 | 7.129 | 0.0029544
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 547459 | WWR477 | 161 | 21.7196 | 21.7815 | 0.00285
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 543069 | PAOLA 5 | 161 | 10.4536 | 10.4773 | 0.0022672
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 543112 | OSAWAT 5 | 161 | 10.3659 | 10.3892 | 0.0022478
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 547487 | HOC404 5 | 161 | 12.8473 | 12.8753 | 0.0021794
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533008 | TV1MNDV4 | 138 | 6.9074 | 6.9223 | 0.0021571
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 543067 | CENTENL5 | 161 | 10.3128 | 10.3315 | 0.0018133
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 542981 | LACYGNE7 | 345 | 24.761 | 24.8029 | 0.0016922
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 543629 | LACYGNE11_7 | 345 | 24.1469 | 24.1868 | 0.0016524
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 543632 | LACYGNE22_7 | 345 | 24.1469 | 24.1868 | 0.0016524
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 547541 | RIV167 2 | 69 | 18.4455 | 18.47 | 0.0013282
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 543066 | S.OTTWA5 | 161 | 7.6022 | 7.6068 | 0.00060509
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 547690 | GLF339 2 | 69 | 9.0983 | 9.1038 | 0.00060451
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 543659 | LACYGNE2 | 69 | 8.4733 | 8.4743 | 0.00011802
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 543667 | LAC3_STAR7 | 345 | 0.6403 | 0.6403 | 0
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 543669 | LAC8_STAR7 | 345 | 0.6133 | 0.6133 | 0
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 588500 | GEN-2017-005 | 161 | 6.1239 | 6.7684 | 0.10524
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 588504 | G17-005-TAP | 161 | 6.2091 | 6.8529 | 0.10369
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 588540 | GEN-2017-009 | 345 | 9.9978 | 10.5633 | 0.056562
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 588544 | G17-009-TAP | 345 | 10.8451 | 11.4101 | 0.052097
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532934 | MARMTNE5 | 161 | 8.0271 | 8.3996 | 0.046405
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532935 | MARMTNW5 | 161 | 8.0271 | 8.3996 | 0.046405
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532793 | NEOSHO 7 | 345 | 16.4472 | 16.8864 | 0.026704
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 543650 | DAKOTA_5 | 161 | 7.5109 | 7.6868 | 0.023419
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 543651 | PRQN_WIND5 | 161 | 6.4747 | 6.5832 | 0.016758
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 512656 | GRDA1 5 | 161 | 41.696 | 42.3541 | 0.015783
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533766 | LITCH S2 | 69 | 12.258 | 12.4335 | 0.014317
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533639 | MARMATN2 | 69 | 8.3602 | 8.4769 | 0.013959
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532937 | NEOSHO 5 | 161 | 21.0898 | 21.3739 | 0.013471
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533020 | NEOSHOS4 | 138 | 22.8316 | 23.1093 | 0.012163
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533021 | NEOSHO 4 | 138 | 22.8316 | 23.1093 | 0.012163
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533022 | NEOSHON4 | 138 | 22.8316 | 23.1093 | 0.012163
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533647 | UN1ELSM2 | 69 | 7.4596 | 7.5451 | 0.011462
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532780 | CANEYRV7 | 345 | 9.847 | 9.9559 | 0.011059
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532781 | CANEYWF7 | 345 | 9.5894 | 9.692 | 0.010699
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532796 | WICHITA7 | 345 | 24.1532 | 24.3835 | 0.009535
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532800 | LATHAMS7 | 345 | 10.4136 | 10.5083 | 0.0090939
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532801 | ELKRVR17 | 345 | 9.1912 | 9.2645 | 0.007975
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 589060 | GEN-2017-068 | 345 | 20.1103 | 20.2698 | 0.0079313
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 300739 | 7BLACKBERRY | 345 | 14.7665 | 14.8807 | 0.0077337
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533640 | MCKEE 2 | 69 | 4.1424 | 4.1691 | 0.0064455
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533768 | NEOSHON2 | 69 | 22.2897 | 22.4333 | 0.0064424
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533778 | NEOSHOS2 | 69 | 22.2897 | 22.4333 | 0.0064424
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 512650 | GRDA1 7 | 345 | 25.9865 | 26.1539 | 0.0064418
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 512865 | GREC TAP5 | 345 | 24.9005 | 25.0478 | 0.0059155
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532794 | ROSEHIL7 | 345 | 18.9572 | 19.0665 | 0.0057656
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 300740 | 7SPORTSMAN | 345 | 23.6136 | 23.749 | 0.005734
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 510380 | DELWARE7 | 345 | 10.9307 | 10.9927 | 0.0056721
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547490 | FIR417 5 | 161 | 13.5186 | 13.595 | 0.0056515
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532791 | BENTON 7 | 345 | 19.6359 | 19.7468 | 0.0056478
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533005 | NEPARSN4 | 138 | 11.9276 | 11.9931 | 0.0054915
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547467 | ORO110 5 | 161 | 18.3996 | 18.4918 | 0.005011
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547494 | OAK432 5 | 161 | 16.7249 | 16.8003 | 0.0045082
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 300949 | 7JASPER | 345 | 12.0507 | 12.1045 | 0.0044645
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 301348 | 5CHOTEAU2 | 161 | 40.4609 | 40.6388 | 0.0043968
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 300741 | 5SPORTSMAN | 161 | 38.9761 | 39.1423 | 0.0042642
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533062 | ROSEHIL4 | 138 | 30.8868 | 31.0133 | 0.0040956
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 509745 | CLARKSV7 | 345 | 19.5998 | 19.6788 | 0.0040307
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533039 | ELPASO 4 | 138 | 24.1926 | 24.2863 | 0.0038731
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547469 | RIV4525 | 161 | 23.1554 | 23.2407 | 0.0036838
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547503 | RIV452T 5 | 161 | 22.7618 | 22.8433 | 0.0035806
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532986 | BENTON 4 | 138 | 27.8896 | 27.9879 | 0.0035246
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547502 | RIV167 5 | 161 | 21.5053 | 21.578 | 0.0033806
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547501 | RIV453 5 | 161 | 21.9817 | 22.056 | 0.0033801
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 509782 | R.S.S.-7 | 345 | 28.8139 | 28.9088 | 0.0032935
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 509807 | ONETA--7 | 345 | 26.6084 | 26.6954 | 0.0032696
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547470 | JOP145 5 | 161 | 16.9579 | 17.0133 | 0.0032669
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 510406 | N.E.S.-7 | 345 | 15.8275 | 15.8785 | 0.0032222
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 509852 | T.NO.--7 | 345 | 22.5867 | 22.6594 | 0.0032187
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 509836 | OEC 7 | 345 | 26.3545 | 26.4393 | 0.0032177
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532926 | BAKER 2 | 69 | 4.8595 | 4.8748 | 0.0031485
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547498 | STL439 5 | 161 | 23.7884 | 23.8627 | 0.0031234
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533772 | SE1GREE2 | 69 | 5.9484 | 5.9667 | 0.0030765
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 509834 | COGENT 7 | 345 | 26.6803 | 26.7611 | 0.0030285
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532991 | WEAVER 4 | 138 | 21.7367 | 21.8021 | 0.0030087
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533758 | CRAWFOR2 | 69 | 7.108 | 7.129 | 0.0029544
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547459 | WWR477 | 161 | 21.7196 | 21.7815 | 0.00285
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533068 | STEARMN4 | 138 | 19.1751 | 19.2296 | 0.0028422
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 509895 | T.NO.2-4 | 138 | 33.6374 | 33.7265 | 0.0026488
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 509806 | ONETA--4 | 138 | 47.2399 | 47.3648 | 0.002644
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 588664 | G17-022-TAP | 138 | 8.0166 | 8.0375 | 0.0026071
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547483 | JOP389 5 | 161 | 19.3374 | 19.3878 | 0.0026063
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 588660 | GEN-2017-022 | 138 | 7.7289 | 7.7484 | 0.002523
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 588320 | GEN-2016-162 | 345 | 9.7523 | 9.7768 | 0.0025122
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 509755 | WEKIWA-7 | 345 | 18.6818 | 18.7267 | 0.0024034
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533703 | ORDNJCT2 | 69 | 8.2682 | 8.2867 | 0.0022375
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 512750 | TONECE7 | 345 | 14.5005 | 14.5329 | 0.0022344
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 588330 | GEN-2016-163 | 345 | 8.6195 | 8.6384 | 0.0021927
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547487 | HOC404 5 | 161 | 12.8473 | 12.8753 | 0.0021794
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 560053 | G15-052T | 345 | 13.1034 | 13.1318 | 0.0021674
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533008 | TV1MNDV4 | 138 | 6.9074 | 6.9223 | 0.0021571
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 584900 | GEN-2015-052 | 345 | 13.0534 | 13.0815 | 0.0021527
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 512631 | MIAMI 5 | 161 | 9.1774 | 9.196 | 0.0020267
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 510379 | DELWARE4 | 138 | 10.8834 | 10.905 | 0.0019847
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532797 | WOLFCRK7 | 345 | 18.0814 | 18.1154 | 0.0018804
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533003 | LIBERTY4 | 138 | 7.3341 | 7.3476 | 0.0018407
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 300950 | 5JASPER | 161 | 12.2916 | 12.3134 | 0.0017736
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 542981 | LACYGNE7 | 345 | 24.761 | 24.8029 | 0.0016922
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 543629 | LACYGNE11_7 | 345 | 24.1469 | 24.1868 | 0.0016524
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 543632 | LACYGNE22_7 | 345 | 24.1469 | 24.1868 | 0.0016524
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533702 | ORDNCE 2 | 69 | 5.9863 | 5.9958 | 0.001587
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532799 | WAVERLY7 | 345 | 16.0356 | 16.0608 | 0.0015715
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533696 | LABETTS2 | 69 | 6.0496 | 6.0591 | 0.0015704
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547534 | ORO110 2 | 69 | 17.4344 | 17.4606 | 0.0015028
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 300045 | 7MORGAN | 345 | 12.7058 | 12.7243 | 0.001456
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547525 | JOP 59 2 | 69 | 18.9342 | 18.9602 | 0.0013732
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 512694 | CLEVLND7 | 345 | 14.9069 | 14.9267 | 0.0013282
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547541 | RIV167 2 | 69 | 18.4455 | 18.47 | 0.0013282
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532802 | WAVERTX7 | 345 | 13.4196 | 13.437 | 0.0012966
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 510378 | SCOFCTY4 | 138 | 8.6339 | 8.6447 | 0.0012509
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533704 | PARSONS2 | 69 | 4.8191 | 4.8251 | 0.001245
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547555 | GAL278 2 | 69 | 15.7673 | 15.7857 | 0.001167
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 514825 | KAYWIND7 | 345 | 12.6052 | 12.6199 | 0.0011662
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 515621 | OPENSKY7 | 345 | 12.64 | 12.6547 | 0.001163
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547602 | RIV406 2 | 69 | 16.1759 | 16.1946 | 0.001156
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 512734 | FARML 4 | 138 | 8.4258 | 8.4353 | 0.0011275
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533695 | LABETTE2 | 69 | 3.9998 | 4.004 | 0.0010501
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547486 | HOC404 4 | 138 | 6.4258 | 6.4319 | 0.0009493
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 549984 | BROOKLINE 7 | 345 | 11.278 | 11.2881 | 0.00089555
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 300794 | 5LAMAR | 161 | 8.3936 | 8.4008 | 0.0008578
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 300101 | 5MORGAN | 161 | 17.7718 | 17.7855 | 0.00077088
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547601 | HOC404 2 | 69 | 9.4214 | 9.4278 | 0.0006793
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 542968 | STILWEL7 | 345 | 23.1239 | 23.1391 | 0.00065733
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547690 | GLF339 2 | 69 | 9.0983 | 9.1038 | 0.00060451
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 543057 | BUCYRUS5 | 161 | 19.4621 | 19.4734 | 0.00058062
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 542965 | W.GRDNR7 | 345 | 24.8262 | 24.8406 | 0.00058003
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 542969 | STILWEL5 | 161 | 36.7533 | 36.773 | 0.00053601
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547530 | COL 94 2 | 69 | 6.3506 | 6.3532 | 0.00040941
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532768 | EMPEC 7 | 345 | 17.5987 | 17.6059 | 0.00040912
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 541198 | PECULR 7 | 345 | 18.8625 | 18.8701 | 0.00040292
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 300042 | 7HUBEN | 345 | 9.9412 | 9.9451 | 0.00039231
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 512735 | COFCTY2 | 69 | 10.0966 | 10.1003 | 0.00036646
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533653 | WOLFCRK2 | 69 | 5.8582 | 5.8601 | 0.00032433
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 542977 | CRAIG 7 | 345 | 21.4243 | 21.4312 | 0.00032206
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 542966 | WGARDNR5 | 161 | 23.42 | 23.4273 | 0.0003117
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547411 | COL282 2 | 69 | 4.5155 | 4.5169 | 0.00031004
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 585100 | GEN-2015-073 | 345 | 13.3961 | 13.4002 | 0.00030606
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 543077 | PLSTVAL5 | 161 | 14.6788 | 14.6832 | 0.00029975
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 543105 | BULLCRK5 | 161 | 22.4616 | 22.4683 | 0.00029829
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547455 | SCM66T 2 | 69 | 4.3392 | 4.3404 | 0.00027655
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 542978 | CRAIG 5 | 161 | 38.4477 | 38.4581 | 0.0002705
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 543053 | REDEL 5 | 161 | 22.9474 | 22.9535 | 0.00026583
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 543050 | ANTIOCH5 | 161 | 21.2541 | 21.2597 | 0.00026348
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 543058 | NLOUISB5 | 161 | 8.7738 | 8.7761 | 0.00026214
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 541200 | PHILL 7 | 345 | 17.2763 | 17.2807 | 0.00025468
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532775 | 87TH 7 | 345 | 20.0723 | 20.0774 | 0.00025408
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533629 | CC2SHAR2 | 69 | 4.545 | 4.5461 | 0.00024202
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532774 | SWISVAL7 | 345 | 16.163 | 16.1669 | 0.00024129
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 543132 | BNSF 5 | 161 | 18.2748 | 18.2791 | 0.0002353
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547412 | SEK225T2 | 69 | 3.4688 | 3.4696 | 0.00023063
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 541342 | PECULR 5 | 161 | 21.2998 | 21.3042 | 0.00020657
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 543049 | CEDRCRK5 | 161 | 27.3304 | 27.336 | 0.0002049
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547413 | SEK225 2 | 69 | 3.423 | 3.4237 | 0.0002045
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 541341 | S.HARP 5 | 161 | 19.2739 | 19.2777 | 0.00019716
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 543126 | LACKMAN5 | 161 | 12.9686 | 12.9708 | 0.00016964
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532856 | SWISVAL6 | 230 | 20.9983 | 21.0016 | 0.00015716
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547415 | SHR444 2 | 69 | 2.686 | 2.6864 | 0.00014892
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 542994 | HICKMAN5 | 161 | 18.3162 | 18.3189 | 0.00014741
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547409 | SCAM66 2 | 69 | 2.44 | 2.4403 | 0.00012295
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 543054 | CEDARNL5 | 161 | 8.9661 | 8.9672 | 0.00012268
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 543659 | LACYGNE2 | 69 | 8.4733 | 8.4743 | 0.00011802
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547414 | SMN425 2 | 69 | 1.946 | 1.9462 | 0.00010277
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 300071 | 5CLINTN | 161 | 11.477 | 11.478 | 8.7131e-05
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 588310 | GEN-2016-158 | 345 | 4.6245 | 4.6249 | 8.6496e-05
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 588300 | GEN-2016-157 | 345 | 4.8983 | 4.8987 | 8.1661e-05
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 543667 | LAC3_STAR7 | 345 | 0.6403 | 0.6403 | 0
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 543669 | LAC8_STAR7 | 345 | 0.6133 | 0.6133 | 0
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 588540 | GEN-2017-009 | 345 | 9.9978 | 10.5633 | 0.056562 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 588544 | G17-009-TAP | 345 | 10.8451 | 11.4101 | 0.052097 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 532935 | MARMTNW5 | 161 | 8.0271 | 8.3996 | 0.046405 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 532793 | NEOSHO 7 | 345 | 16.4472 | 16.8864 | 0.026704 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 532937 | NEOSHO 5 | 161 | 21.0898 | 21.3739 | 0.013471 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533020 | NEOSHOS4 | 138 | 22.8316 | 23.1093 | 0.012163 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533021 | NEOSHO 4 | 138 | 22.8316 | 23.1093 | 0.012163 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533022 | NEOSHON4 | 138 | 22.8316 | 23.1093 | 0.012163 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 300739 | 7BLACKBERRY | 345 | 14.7665 | 14.8807 | 0.0077337 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533768 | NEOSHON2 | 69 | 22.2897 | 22.4333 | 0.0064424 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533778 | NEOSHOS2 | 69 | 22.2897 | 22.4333 | 0.0064424 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 510380 | DELWARE7 | 345 | 10.9307 | 10.9927 | 0.0056721 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 532791 | BENTON 7 | 345 | 19.6359 | 19.7468 | 0.0056478 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533005 | NEPARSN4 | 138 | 11.9276 | 11.9931 | 0.0054915 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 547469 | RIV4525 | 161 | 23.1554 | 23.2407 | 0.0036838 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 547503 | RIV452T 5 | 161 | 22.7618 | 22.8433 | 0.0035806 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 532986 | BENTON 4 | 138 | 27.8896 | 27.9879 | 0.0035246 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 547502 | RIV167 5 | 161 | 21.5053 | 21.578 | 0.0033806 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 547501 | RIV453 5 | 161 | 21.9817 | 22.056 | 0.0033801 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 532926 | BAKER 2 | 69 | 4.8595 | 4.8748 | 0.0031485 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 532991 | WEAVER 4 | 138 | 21.7367 | 21.8021 | 0.0030087 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533758 | CRAWFOR2 | 69 | 7.108 | 7.129 | 0.0029544 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533052 | PARKCTY4 | 138 | 20.1019 | 20.1569 | 0.0027361 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533634 | ENA 2 | 69 | 5.2712 | 5.2854 | 0.0026939 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 588664 | G17-022-TAP | 138 | 8.0166 | 8.0375 | 0.0026071 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533001 | ALTOONA4 | 138 | 8.0292 | 8.0501 | 0.002603 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 588660 | GEN-2017-022 | 138 | 7.7289 | 7.7484 | 0.002523 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 588320 | GEN-2016-162 | 345 | 9.7523 | 9.7768 | 0.0025122 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533024 | 29TH 4 | 138 | 19.377 | 19.4255 | 0.002503 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533633 | COALCRK2 | 69 | 5.2439 | 5.2569 | 0.0024791 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 532988 | BELAIRE4 | 138 | 18.7482 | 18.7936 | 0.0024216 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533703 | ORDNJCT2 | 69 | 8.2682 | 8.2867 | 0.0022375 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 588330 | GEN-2016-163 | 345 | 8.6195 | 8.6384 | 0.0021927 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533008 | TV1MNDV4 | 138 | 6.9074 | 6.9223 | 0.0021571 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533003 | LIBERTY4 | 138 | 7.3341 | 7.3476 | 0.0018407 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533646 | TIOGA 2 | 69 | 6.9097 | 6.9223 | 0.0018235 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533002 | DEARING4 | 138 | 9.2078 | 9.2238 | 0.0017377 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 542981 | LACYGNE7 | 345 | 24.761 | 24.8029 | 0.0016922 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 532996 | TIOGA 4 | 138 | 4.3732 | 4.3806 | 0.0016921 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 543629 | LACYGNE11_7 | 345 | 24.1469 | 24.1868 | 0.0016524 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 543632 | LACYGNE22_7 | 345 | 24.1469 | 24.1868 | 0.0016524 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533702 | ORDNCE 2 | 69 | 5.9863 | 5.9958 | 0.001587 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533696 | LABETTS2 | 69 | 6.0496 | 6.0591 | 0.0015704 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533004 | MONTGOM4 | 138 | 6.7466 | 6.7571 | 0.0015563 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533006 | TAYLOR 4 | 138 | 6.5449 | 6.555 | 0.0015432 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533660 | ASHGRJ22 | 69 | 5.9685 | 5.9776 | 0.0015247 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 510422 | COFFEYT4 | 138 | 9.8765 | 9.8915 | 0.0015188 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533662 | CGENSUB2 | 69 | 5.8632 | 5.8719 | 0.0014838 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533658 | ASHGRV22 | 69 | 5.7386 | 5.747 | 0.0014638 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533666 | CHANTAP2 | 69 | 5.8503 | 5.8588 | 0.0014529 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533661 | CGENTAP2 | 69 | 5.5336 | 5.5414 | 0.0014096 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533659 | ASHGRJ12 | 69 | 5.4588 | 5.4663 | 0.0013739 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 532990 | MIDIAN 4 | 138 | 10.5446 | 10.5589 | 0.0013561 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 532993 | TALLGRS4 | 138 | 10.1282 | 10.1418 | 0.0013428 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 532987 | BUTLER 4 | 138 | 10.362 | 10.3759 | 0.0013414 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 532989 | BUTLERS4 | 138 | 10.362 | 10.3759 | 0.0013414 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533657 | ASHGRV12 | 69 | 5.2652 | 5.2722 | 0.0013295 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533663 | CHANP1 2 | 69 | 5.1713 | 5.1781 | 0.0013149 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533664 | CHANP2 2 | 69 | 5.1713 | 5.1781 | 0.0013149 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533665 | CHANP3 2 | 69 | 5.1071 | 5.1137 | 0.0012923 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533649 | UN7ROSE2 | 69 | 4.4513 | 4.4568 | 0.0012356 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533643 | ORCHARD2 | 69 | 3.8504 | 3.8548 | 0.0011427 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533695 | LABETTE2 | 69 | 3.9998 | 4.004 | 0.0010501 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533672 | ALTAMNS2 | 69 | 3.9875 | 3.9915 | 0.0010031 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533698 | MONTGOM2 | 69 | 7.6649 | 7.6718 | 0.00090021 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533597 | MIDIANW2 | 69 | 13.8298 | 13.8422 | 0.00089661 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533610 | MIDIANE2 | 69 | 13.8298 | 13.8422 | 0.00089661 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533583 | BUTLERN2 | 69 | 13.54 | 13.5517 | 0.00086411 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533609 | BUTLERS2 | 69 | 13.54 | 13.5517 | 0.00086411 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533713 | WILLJCT2 | 69 | 7.1968 | 7.2029 | 0.0008476 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533673 | ALTOO E2 | 69 | 5.4371 | 5.4416 | 0.00082765 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533694 | INDEPEN2 | 69 | 6.8515 | 6.8571 | 0.00081734 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533706 | RA5HIPR2 | 69 | 5.4019 | 5.4063 | 0.00081453 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533688 | DEARING2 | 69 | 7.8716 | 7.878 | 0.00081305 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533712 | WILLMS 2 | 69 | 6.8016 | 6.807 | 0.00079393 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533602 | SKELLY 2 | 69 | 12.2841 | 12.2937 | 0.0007815 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533700 | NEODJCT2 | 69 | 5.0391 | 5.0429 | 0.0007541 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533593 | FRNTR N2 | 69 | 11.8169 | 11.8258 | 0.00075316 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533592 | GETTY E2 | 69 | 11.6564 | 11.665 | 0.00073779 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533679 | CHERRYV2 | 69 | 5.3711 | 5.3748 | 0.00068887 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533671 | ALTAMNT2 | 69 | 2.7854 | 2.7873 | 0.00068213 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533587 | CHASJCT2 | 69 | 10.3806 | 10.3876 | 0.00067433 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533707 | RA6BROO2 | 69 | 4.613 | 4.6161 | 0.00067201 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533648 | UN6URBA2 | 69 | 3.469 | 3.4712 | 0.00063419 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533589 | CHESNEY2 | 69 | 8.9552 | 8.9604 | 0.00058067 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533675 | ARGO 2 | 69 | 3.8423 | 3.8445 | 0.00057257 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533603 | THUNBRD2 | 69 | 8.1334 | 8.1378 | 0.00054098 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533590 | ELDORAD2 | 69 | 8.4415 | 8.446 | 0.00053308 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533588 | CHASE 2 | 69 | 7.6935 | 7.6974 | 0.00050692 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533699 | NEODESH2 | 69 | 3.336 | 3.3376 | 0.00047962 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533674 | ALTOO W2 | 69 | 2.9702 | 2.9716 | 0.00047135 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533760 | ERIE 2 | 69 | 2.8041 | 2.8052 | 0.00039228 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533705 | STUDBKR2 | 69 | 1.7767 | 1.7772 | 0.00028142 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533601 | POTWIN 2 | 69 | 3.528 | 3.5288 | 0.00022676 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533692 | YELLOWJ2 | 69 | 1.3845 | 1.3848 | 0.00021668 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533701 | NEW ALB2 | 69 | 1.4684 | 1.4687 | 0.0002043 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533584 | BU6DEGR2 | 69 | 2.4872 | 2.4876 | 0.00016082 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 543659 | LACYGNE2 | 69 | 8.4733 | 8.4743 | 0.00011802 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533599 | PEABODY2 | 69 | 1.7306 | 1.7307 | 5.7783e-05 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533183 | WM BROS3 | 115 | 11.0007 | 11.0009 | 1.8181e-05 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 543667 | LAC3_STAR7 | 345 | 0.6403 | 0.6403 | 0 |  |  | X
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 543669 | LAC8_STAR7 | 345 | 0.6133 | 0.6133 | 0 |  |  | X
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 589300 | GEN-2017-092 | 345 | 9.3838 | 9.9032 | 0.055351
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 588810 | GEN-2017-040 | 345 | 10.5528 | 11.1329 | 0.054971
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 588839 | FIREWHL-TAP | 345 | 10.7008 | 11.2888 | 0.054949
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 588834 | FWL-WND-SWYD | 345 | 10.7008 | 11.2888 | 0.054949
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 588838 | G17-092-SWYD | 345 | 10.7008 | 11.2888 | 0.054949
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515422 | C-RIVER7 | 345 | 9.8234 | 9.9892 | 0.016878
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515224 | MUSKOGE7 | 345 | 28.6169 | 28.9683 | 0.012279
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515249 | BEGGS 4 | 138 | 5.4729 | 5.5141 | 0.007528
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515235 | PECANCK7 | 345 | 21.3829 | 21.5268 | 0.0067297
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510946 | C-RIVER4 | 138 | 12.8883 | 12.9719 | 0.0064865
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510907 | PITTSB-7 | 345 | 13.6566 | 13.7363 | 0.005836
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510925 | KIOWA 7 | 345 | 13.4158 | 13.4927 | 0.005732
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510380 | DELWARE7 | 345 | 10.9307 | 10.9927 | 0.0056721
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 509745 | CLARKSV7 | 345 | 19.5998 | 19.6788 | 0.0040307
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 588039 | G16133G16146 | 345 | 28.8139 | 28.9088 | 0.0032935
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 509782 | R.S.S.-7 | 345 | 28.8139 | 28.9088 | 0.0032935
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 509807 | ONETA--7 | 345 | 26.6084 | 26.6954 | 0.0032696
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510406 | N.E.S.-7 | 345 | 15.8275 | 15.8785 | 0.0032222
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 509852 | T.NO.--7 | 345 | 22.5867 | 22.6594 | 0.0032187
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 509836 | OEC 7 | 345 | 26.3545 | 26.4393 | 0.0032177
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 509834 | COGENT 7 | 345 | 26.6803 | 26.7611 | 0.0030285
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515234 | PECANCK5 | 161 | 20.9267 | 20.9845 | 0.002762
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 509783 | R.S.S.-4 | 138 | 59.4345 | 59.5979 | 0.0027492
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510951 | TALAWANDA 4 | 138 | 9.6276 | 9.6531 | 0.0026486
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 509806 | ONETA--4 | 138 | 47.2399 | 47.3648 | 0.002644
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 509870 | SAPLPRD7 | 345 | 22.2177 | 22.2751 | 0.0025835
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 509755 | WEKIWA-7 | 345 | 18.6818 | 18.7267 | 0.0024034
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 509875 | RSS T2 4 | 138 | 50.2851 | 50.4013 | 0.0023108
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 509773 | RSS T1 4 | 138 | 49.413 | 49.5251 | 0.0022686
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 509786 | BA.N-ST4 | 138 | 23.2255 | 23.2754 | 0.0021485
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 588040 | G16133_345GS | 345 | 19.6751 | 19.7156 | 0.0020584
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510908 | MCALEST4 | 138 | 9.8253 | 9.844 | 0.0019032
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515233 | PECANCK4 | 138 | 9.5555 | 9.5735 | 0.0018837
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515228 | 5TRIBES5 | 161 | 15.4215 | 15.4503 | 0.0018675
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 509871 | SAPLPRD4 | 138 | 32.0377 | 32.0936 | 0.0017448
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515230 | AGENCY 5 | 161 | 14.0106 | 14.0335 | 0.0016345
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515250 | HANCOK-5 | 161 | 14.1046 | 14.1276 | 0.0016307
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 506948 | SILOAM 5 | 161 | 21.0049 | 21.039 | 0.0016234
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515045 | SEMINOL7 | 345 | 26.7023 | 26.7438 | 0.0015542
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510909 | MCALESTIND 4 | 138 | 5.5912 | 5.5998 | 0.0015381
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515251 | EUCLID 5 | 161 | 13.7075 | 13.7284 | 0.0015247
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510906 | SMCALTP4 | 138 | 8.4625 | 8.4751 | 0.0014889
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 506944 | CHAMSPR5 | 161 | 21.9263 | 21.9572 | 0.0014093
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 588041 | G16133_765GS | 765 | 6.6077 | 6.6167 | 0.001362
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 506945 | CHAMSPR7 | 345 | 9.5419 | 9.5542 | 0.0012891
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 509891 | BA_71ST4 | 138 | 22.592 | 22.621 | 0.0012836
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 514803 | SOONER 7 | 345 | 27.048 | 27.0822 | 0.0012644
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 589140 | GEN-2017-076 | 161 | 19.6452 | 19.67 | 0.0012624
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 514809 | JOHNCO 7 | 345 | 9.7918 | 9.8039 | 0.0012357
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 504202 | SILOAMSP 5 | 161 | 18.7584 | 18.7808 | 0.0011941
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 506957 | TONTITN5 | 161 | 19.6592 | 19.6826 | 0.0011903
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 506978 | MATTISN5 | 161 | 19.1954 | 19.2178 | 0.0011669
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 506959 | TONTITN7 | 345 | 8.4933 | 8.5029 | 0.0011303
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510897 | LONEOAK4 | 138 | 8.7091 | 8.7189 | 0.0011253
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 509721 | BA.NO-S4 | 138 | 12.0065 | 12.0198 | 0.0011077
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 509769 | BA101-N4 | 138 | 19.1268 | 19.1477 | 0.0010927
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510865 | S-MCALT4 | 138 | 5.8211 | 5.8271 | 0.0010307
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 509869 | 121LYNN4 | 138 | 17.2637 | 17.2807 | 0.00098473
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 509768 | BA101ST4 | 138 | 18.3048 | 18.3223 | 0.00095603
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 509737 | BA101 S4 | 138 | 17.6486 | 17.6648 | 0.00091792
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 584780 | GEN-2015-036 | 345 | 6.9686 | 6.9744 | 0.0008323
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510911 | VALIANT7 | 345 | 13.1354 | 13.1462 | 0.00082221
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 514934 | DRAPER 7 | 345 | 21.0498 | 21.066 | 0.0007696
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 504020 | FARMNGTN 5 | 161 | 12.1769 | 12.1858 | 0.00073089
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515497 | MATHWSN7 | 345 | 33.2303 | 33.254 | 0.0007132
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515302 | FTSMITH7 | 345 | 10.0478 | 10.0548 | 0.00069667
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515136 | SUNNYSD7 | 345 | 11.0206 | 11.0282 | 0.00068962
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 514908 | ARCADIA7 | 345 | 30.6072 | 30.6277 | 0.00066978
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 514880 | NORTWST7 | 345 | 33.0413 | 33.063 | 0.00065675
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 514827 | CTNWOOD4 | 138 | 18.1397 | 18.1516 | 0.00065602
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515229 | AGENCY 2 | 69 | 12.9096 | 12.918 | 0.00065068
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515044 | SEMINOL4 | 138 | 40.0654 | 40.091 | 0.00063896
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515227 | 5TRIBES2 | 69 | 12.6248 | 12.6328 | 0.00063367
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 514901 | CIMARON7 | 345 | 34.5896 | 34.6112 | 0.00062447
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 514907 | ARCADIA4 | 138 | 43.807 | 43.8341 | 0.00061862
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 521157 | HUGO 7 | 345 | 11.1023 | 11.1089 | 0.00059447
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515461 | RNDBARN4 | 138 | 41.4854 | 41.5097 | 0.00058575
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 514909 | REDBUD 7 | 345 | 28.9155 | 28.9324 | 0.00058446
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 588043 | G16133_765MP | 765 | 4.0542 | 4.0565 | 0.00056731
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515075 | FRSTHIL4 | 138 | 13.8188 | 13.8266 | 0.00056445
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510921 | DUSTIN-4 | 138 | 9.3147 | 9.3198 | 0.00054752
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 514933 | DRAPER 4 | 138 | 39.3786 | 39.3998 | 0.00053836
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 514808 | JOHNCO 4 | 138 | 14.931 | 14.9389 | 0.0005291
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 587804 | G16-100-TAP | 345 | 21.9166 | 21.9281 | 0.00052472
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 514906 | JNSKAMO4 | 138 | 20.6591 | 20.6695 | 0.00050341
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515894 | THUNDER7 | 345 | 11.3237 | 11.329 | 0.00046804
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 514881 | SPRNGCK7 | 345 | 23.8462 | 23.857 | 0.0004529
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515305 | FTSMITH8 | 500 | 8.3973 | 8.4011 | 0.00045253
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515055 | MAUD 4 | 138 | 19.9584 | 19.9671 | 0.00043591
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515301 | FTSMTHW5 | 161 | 22.898 | 22.9076 | 0.00041925
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515300 | FTSMTHE5 | 161 | 23.0236 | 23.0332 | 0.00041696
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 514879 | NORTWST4 | 138 | 44.3924 | 44.4108 | 0.00041449
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 514946 | MIDWEST4 | 138 | 30.6139 | 30.6262 | 0.00040178
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515135 | SUNNYSD4 | 138 | 18.4585 | 18.4657 | 0.00039006
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 560088 | G16-063-TAP | 345 | 7.8302 | 7.8332 | 0.00038313
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 587430 | GEN-2016-063 | 345 | 7.7314 | 7.7343 | 0.00037509
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510899 | MCALEST2 | 69 | 4.8017 | 4.8035 | 0.00037487
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 589130 | GEN-2017-075 | 345 | 7.8196 | 7.8225 | 0.00037086
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515299 | BEVYTAP5 | 161 | 20.3431 | 20.3504 | 0.00035884
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515465 | LGARBER4 | 138 | 21.4859 | 21.4934 | 0.00034907
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 587800 | GEN-2016-100 | 345 | 14.9185 | 14.9237 | 0.00034856
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 504182 | BEVERLY5 | 161 | 19.5597 | 19.5664 | 0.00034254
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515345 | COLONY 5 | 161 | 18.2162 | 18.2223 | 0.00033487
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 520948 | HUGO PP4 | 138 | 22.1004 | 22.1078 | 0.00033484
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515122 | SXMLCKT4 | 138 | 10.9444 | 10.948 | 0.00032894
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515120 | RUSSET-4 | 138 | 11.1342 | 11.1378 | 0.00032333
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 521122 | HOWE 4 | 138 | 10.8417 | 10.8452 | 0.00032283
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515310 | QUANXTP5 | 161 | 17.5041 | 17.5096 | 0.00031421
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510918 | VALIANT4 | 138 | 14.7574 | 14.762 | 0.00031171
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515474 | QUANEXS5 | 161 | 16.5843 | 16.5893 | 0.00030149
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515178 | PARKLN 4 | 138 | 16.2138 | 16.2186 | 0.00029604
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515117 | ARBUCKL4 | 138 | 15.5845 | 15.5891 | 0.00029517
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515306 | ARKOMA 5 | 161 | 16.0234 | 16.0281 | 0.00029332
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 514898 | CIMARON4 | 138 | 43.3248 | 43.3374 | 0.00029083
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515308 | 3RDST 5 | 161 | 15.4222 | 15.4265 | 0.00027882
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 588670 | GEN-2017-023 | 138 | 18.3072 | 18.3123 | 0.00027858
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515003 | BARNES 4 | 138 | 15.8287 | 15.833 | 0.00027166
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515610 | FSHRTAP7 | 345 | 17.7246 | 17.7292 | 0.00025953
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 588045 | G16133_765CS | 765 | 3.5157 | 3.5166 | 0.00025599
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 508298 | LYDIA 7 | 345 | 12.5635 | 12.5666 | 0.00024675
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 588180 | GEN-2016-126 | 138 | 12.9061 | 12.9092 | 0.0002402
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515174 | VANOSS 4 | 138 | 13.1499 | 13.153 | 0.00023574
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 514961 | GM 4 | 138 | 19.1936 | 19.1981 | 0.00023445
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515531 | VANOSTP4 | 138 | 13.2751 | 13.2782 | 0.00023352
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 514949 | SOONRTP4 | 138 | 20.3707 | 20.3754 | 0.00023072
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 587950 | GEN-2016-119 | 345 | 11.7707 | 11.7734 | 0.00022938
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515150 | CANEYCK4 | 138 | 8.4199 | 8.4218 | 0.00022566
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515318 | SOTHADA4 | 138 | 11.2764 | 11.2789 | 0.0002217
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 511568 | TERRYRD7 | 345 | 9.9356 | 9.9378 | 0.00022143
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510866 | V-WEYCO4 | 138 | 9.6578 | 9.6598 | 0.00020709
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510948 | EARLSBORO 4 | 138 | 8.0011 | 8.0027 | 0.00019997
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 508072 | NWTXARK7 | 345 | 13.0046 | 13.0072 | 0.00019993
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 588080 | ZONE-4 SUB | 345 | 7.8057 | 7.8072 | 0.00019217
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 588046 | G16133_345CS | 345 | 7.9204 | 7.9219 | 0.00018938
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 514801 | MINCO 7 | 345 | 18.2057 | 18.2091 | 0.00018675
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515133 | BLUERIV4 | 138 | 10.4405 | 10.4424 | 0.00018198
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 587955 | GEN2016-119B | 345 | 9.8967 | 9.8985 | 0.00018188
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515444 | MCNOWND7 | 345 | 18.1495 | 18.1528 | 0.00018182
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515605 | CANADN7 | 345 | 12.9556 | 12.9579 | 0.00017753
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 588100 | ZONE-6 SUB | 345 | 7.0415 | 7.0427 | 0.00017042
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 504021 | FARM_1 2 | 69 | 8.0603 | 8.0616 | 0.00016128
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 588050 | ZONE-1 SUB | 345 | 6.3025 | 6.3035 | 0.00015867
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 587820 | GEN-2016-102 | 138 | 9.5679 | 9.5694 | 0.00015677
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 588090 | ZONE-5 SUB | 345 | 6.5065 | 6.5075 | 0.00015369
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 588070 | ZONE-3 SUB | 345 | 6.5318 | 6.5328 | 0.0001531
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515600 | KNGFSHR7 | 345 | 11.8984 | 11.9002 | 0.00015128
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515100 | PAOLI- 4 | 138 | 10.2996 | 10.3011 | 0.00014564
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 588060 | ZONE-2 SUB | 345 | 6.3129 | 6.3138 | 0.00014257
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515054 | MAUD 2 | 69 | 11.755 | 11.7566 | 0.00013611
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515114 | CHIGLEY4 | 138 | 8.0822 | 8.0833 | 0.0001361
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515177 | PARKLN 2 | 69 | 14.1839 | 14.1858 | 0.00013395
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510886 | IDABEL-4 | 138 | 6.7374 | 6.7383 | 0.00013358
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 508071 | NWTXARK4 | 138 | 24.3065 | 24.3096 | 0.00012754
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 511571 | RUSHSPR7 | 345 | 6.3575 | 6.3583 | 0.00012584
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515549 | MNCWND37 | 345 | 12.4665 | 12.468 | 0.00012032
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 563259 | GEN-2015-092 | 345 | 6.1634 | 6.1641 | 0.00011357
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515175 | IDEAL 2 | 69 | 11.8437 | 11.845 | 0.00010976
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 900001 | TRAVERSE1 | 345 | 7.3837 | 7.3845 | 0.00010835
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515097 | WLNUTCK4 | 138 | 9.2421 | 9.2431 | 0.0001082
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 507455 | TURK 7 | 345 | 8.7928 | 8.7937 | 0.00010236
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510901 | HUGO---4 | 138 | 3.4725 | 3.4728 | 8.6393e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 508359 | WELSH 7 | 345 | 20.8377 | 20.8395 | 8.6382e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 337909 | 8ANO% | 500 | 17.5426 | 17.5441 | 8.5506e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515124 | MAYSVIL4 | 138 | 6.2202 | 6.2207 | 8.0383e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 584060 | GEN-2015-057 | 345 | 9.1357 | 9.1364 | 7.6622e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 900002 | TRAVERSE2 | 345 | 5.7164 | 5.7168 | 6.9974e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510910 | VALIANT2 | 69 | 7.2552 | 7.2557 | 6.8916e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510870 | WCITYTP2 | 69 | 6.3166 | 6.317 | 6.3325e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515099 | PALIOGE2 | 69 | 8.0639 | 8.0644 | 6.2005e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515939 | MNCWND47 | 345 | 6.8065 | 6.8069 | 5.8767e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 900003 | TRAVERSE3 | 345 | 5.1972 | 5.1975 | 5.7723e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 337922 | 8P.HILL% | 500 | 15.1307 | 15.1314 | 4.6264e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515053 | PEARSNT2 | 69 | 4.4506 | 4.4508 | 4.4938e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510868 | GA PAC 2 | 69 | 2.4741 | 2.4742 | 4.0419e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515052 | TRIBBEY2 | 69 | 2.6015 | 2.6016 | 3.8439e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515637 | SRVCPLT2 | 69 | 2.6089 | 2.609 | 3.833e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515067 | PEARSON2 | 69 | 2.9482 | 2.9483 | 3.3919e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510867 | KI PMPS2 | 69 | 3.0643 | 3.0644 | 3.2634e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 511508 | BLANCHD4 | 138 | 6.5665 | 6.5667 | 3.0458e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 337912 | 5ANO% | 161 | 17.7035 | 17.704 | 2.8243e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 337811 | 8HAPPYVALY% | 500 | 24.9494 | 24.9501 | 2.8057e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510869 | W CITY 2 | 69 | 3.8276 | 3.8277 | 2.6126e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515095 | SRVCEPL2 | 69 | 2.3711 | 2.3711 | 0
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515636 | TRIBYTP2 | 69 | 2.6045 | 2.6045 | 0
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 589300 | GEN-2017-092 | 345 | 9.3838 | 9.9032 | 0.055351
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 588810 | GEN-2017-040 | 345 | 10.5528 | 11.1329 | 0.054971
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 588839 | FIREWHL-TAP | 345 | 10.7008 | 11.2888 | 0.054949
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 588834 | FWL-WND-SWYD | 345 | 10.7008 | 11.2888 | 0.054949
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 588838 | G17-092-SWYD | 345 | 10.7008 | 11.2888 | 0.054949
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515422 | C-RIVER7 | 345 | 9.8234 | 9.9892 | 0.016878
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515224 | MUSKOGE7 | 345 | 28.6169 | 28.9683 | 0.012279
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515249 | BEGGS 4 | 138 | 5.4729 | 5.5141 | 0.007528
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515235 | PECANCK7 | 345 | 21.3829 | 21.5268 | 0.0067297
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510946 | C-RIVER4 | 138 | 12.8883 | 12.9719 | 0.0064865
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510907 | PITTSB-7 | 345 | 13.6566 | 13.7363 | 0.005836
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510925 | KIOWA 7 | 345 | 13.4158 | 13.4927 | 0.005732
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510380 | DELWARE7 | 345 | 10.9307 | 10.9927 | 0.0056721
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 509745 | CLARKSV7 | 345 | 19.5998 | 19.6788 | 0.0040307
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 588039 | G16133G16146 | 345 | 28.8139 | 28.9088 | 0.0032935
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 509782 | R.S.S.-7 | 345 | 28.8139 | 28.9088 | 0.0032935
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 509807 | ONETA--7 | 345 | 26.6084 | 26.6954 | 0.0032696
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510406 | N.E.S.-7 | 345 | 15.8275 | 15.8785 | 0.0032222
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 509852 | T.NO.--7 | 345 | 22.5867 | 22.6594 | 0.0032187
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 509836 | OEC 7 | 345 | 26.3545 | 26.4393 | 0.0032177
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 509834 | COGENT 7 | 345 | 26.6803 | 26.7611 | 0.0030285
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515234 | PECANCK5 | 161 | 20.9267 | 20.9845 | 0.002762
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 509783 | R.S.S.-4 | 138 | 59.4345 | 59.5979 | 0.0027492
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510951 | TALAWANDA 4 | 138 | 9.6276 | 9.6531 | 0.0026486
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 509806 | ONETA--4 | 138 | 47.2399 | 47.3648 | 0.002644
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 509870 | SAPLPRD7 | 345 | 22.2177 | 22.2751 | 0.0025835
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 509755 | WEKIWA-7 | 345 | 18.6818 | 18.7267 | 0.0024034
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 509875 | RSS T2 4 | 138 | 50.2851 | 50.4013 | 0.0023108
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 509773 | RSS T1 4 | 138 | 49.413 | 49.5251 | 0.0022686
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 509786 | BA.N-ST4 | 138 | 23.2255 | 23.2754 | 0.0021485
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 588040 | G16133_345GS | 345 | 19.6751 | 19.7156 | 0.0020584
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510908 | MCALEST4 | 138 | 9.8253 | 9.844 | 0.0019032
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515233 | PECANCK4 | 138 | 9.5555 | 9.5735 | 0.0018837
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515228 | 5TRIBES5 | 161 | 15.4215 | 15.4503 | 0.0018675
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 509871 | SAPLPRD4 | 138 | 32.0377 | 32.0936 | 0.0017448
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515230 | AGENCY 5 | 161 | 14.0106 | 14.0335 | 0.0016345
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515250 | HANCOK-5 | 161 | 14.1046 | 14.1276 | 0.0016307
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 506948 | SILOAM 5 | 161 | 21.0049 | 21.039 | 0.0016234
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515045 | SEMINOL7 | 345 | 26.7023 | 26.7438 | 0.0015542
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510909 | MCALESTIND 4 | 138 | 5.5912 | 5.5998 | 0.0015381
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515251 | EUCLID 5 | 161 | 13.7075 | 13.7284 | 0.0015247
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510906 | SMCALTP4 | 138 | 8.4625 | 8.4751 | 0.0014889
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 506944 | CHAMSPR5 | 161 | 21.9263 | 21.9572 | 0.0014093
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 588041 | G16133_765GS | 765 | 6.6077 | 6.6167 | 0.001362
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 506945 | CHAMSPR7 | 345 | 9.5419 | 9.5542 | 0.0012891
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 509891 | BA_71ST4 | 138 | 22.592 | 22.621 | 0.0012836
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 514803 | SOONER 7 | 345 | 27.048 | 27.0822 | 0.0012644
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 589140 | GEN-2017-076 | 161 | 19.6452 | 19.67 | 0.0012624
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 514809 | JOHNCO 7 | 345 | 9.7918 | 9.8039 | 0.0012357
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 504202 | SILOAMSP 5 | 161 | 18.7584 | 18.7808 | 0.0011941
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 506957 | TONTITN5 | 161 | 19.6592 | 19.6826 | 0.0011903
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 506978 | MATTISN5 | 161 | 19.1954 | 19.2178 | 0.0011669
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 506959 | TONTITN7 | 345 | 8.4933 | 8.5029 | 0.0011303
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510897 | LONEOAK4 | 138 | 8.7091 | 8.7189 | 0.0011253
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 509721 | BA.NO-S4 | 138 | 12.0065 | 12.0198 | 0.0011077
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 509769 | BA101-N4 | 138 | 19.1268 | 19.1477 | 0.0010927
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510865 | S-MCALT4 | 138 | 5.8211 | 5.8271 | 0.0010307
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 509869 | 121LYNN4 | 138 | 17.2637 | 17.2807 | 0.00098473
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 509768 | BA101ST4 | 138 | 18.3048 | 18.3223 | 0.00095603
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 509737 | BA101 S4 | 138 | 17.6486 | 17.6648 | 0.00091792
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 584780 | GEN-2015-036 | 345 | 6.9686 | 6.9744 | 0.0008323
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510911 | VALIANT7 | 345 | 13.1354 | 13.1462 | 0.00082221
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 514934 | DRAPER 7 | 345 | 21.0498 | 21.066 | 0.0007696
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 504020 | FARMNGTN 5 | 161 | 12.1769 | 12.1858 | 0.00073089
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515497 | MATHWSN7 | 345 | 33.2303 | 33.254 | 0.0007132
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515302 | FTSMITH7 | 345 | 10.0478 | 10.0548 | 0.00069667
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515136 | SUNNYSD7 | 345 | 11.0206 | 11.0282 | 0.00068962
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 514908 | ARCADIA7 | 345 | 30.6072 | 30.6277 | 0.00066978
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 514880 | NORTWST7 | 345 | 33.0413 | 33.063 | 0.00065675
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 514827 | CTNWOOD4 | 138 | 18.1397 | 18.1516 | 0.00065602
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515229 | AGENCY 2 | 69 | 12.9096 | 12.918 | 0.00065068
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515044 | SEMINOL4 | 138 | 40.0654 | 40.091 | 0.00063896
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515227 | 5TRIBES2 | 69 | 12.6248 | 12.6328 | 0.00063367
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 514901 | CIMARON7 | 345 | 34.5896 | 34.6112 | 0.00062447
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 514907 | ARCADIA4 | 138 | 43.807 | 43.8341 | 0.00061862
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 521157 | HUGO 7 | 345 | 11.1023 | 11.1089 | 0.00059447
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515461 | RNDBARN4 | 138 | 41.4854 | 41.5097 | 0.00058575
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 514909 | REDBUD 7 | 345 | 28.9155 | 28.9324 | 0.00058446
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 588043 | G16133_765MP | 765 | 4.0542 | 4.0565 | 0.00056731
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515075 | FRSTHIL4 | 138 | 13.8188 | 13.8266 | 0.00056445
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510921 | DUSTIN-4 | 138 | 9.3147 | 9.3198 | 0.00054752
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 514933 | DRAPER 4 | 138 | 39.3786 | 39.3998 | 0.00053836
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 514808 | JOHNCO 4 | 138 | 14.931 | 14.9389 | 0.0005291
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 587804 | G16-100-TAP | 345 | 21.9166 | 21.9281 | 0.00052472
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 514906 | JNSKAMO4 | 138 | 20.6591 | 20.6695 | 0.00050341
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515894 | THUNDER7 | 345 | 11.3237 | 11.329 | 0.00046804
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 514881 | SPRNGCK7 | 345 | 23.8462 | 23.857 | 0.0004529
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515305 | FTSMITH8 | 500 | 8.3973 | 8.4011 | 0.00045253
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515055 | MAUD 4 | 138 | 19.9584 | 19.9671 | 0.00043591
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515301 | FTSMTHW5 | 161 | 22.898 | 22.9076 | 0.00041925
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515300 | FTSMTHE5 | 161 | 23.0236 | 23.0332 | 0.00041696
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 514879 | NORTWST4 | 138 | 44.3924 | 44.4108 | 0.00041449
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 514946 | MIDWEST4 | 138 | 30.6139 | 30.6262 | 0.00040178
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515135 | SUNNYSD4 | 138 | 18.4585 | 18.4657 | 0.00039006
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 560088 | G16-063-TAP | 345 | 7.8302 | 7.8332 | 0.00038313
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 587430 | GEN-2016-063 | 345 | 7.7314 | 7.7343 | 0.00037509
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510899 | MCALEST2 | 69 | 4.8017 | 4.8035 | 0.00037487
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 589130 | GEN-2017-075 | 345 | 7.8196 | 7.8225 | 0.00037086
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515299 | BEVYTAP5 | 161 | 20.3431 | 20.3504 | 0.00035884
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515465 | LGARBER4 | 138 | 21.4859 | 21.4934 | 0.00034907
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 587800 | GEN-2016-100 | 345 | 14.9185 | 14.9237 | 0.00034856
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 504182 | BEVERLY5 | 161 | 19.5597 | 19.5664 | 0.00034254
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515345 | COLONY 5 | 161 | 18.2162 | 18.2223 | 0.00033487
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 520948 | HUGO PP4 | 138 | 22.1004 | 22.1078 | 0.00033484
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515122 | SXMLCKT4 | 138 | 10.9444 | 10.948 | 0.00032894
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515120 | RUSSET-4 | 138 | 11.1342 | 11.1378 | 0.00032333
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 521122 | HOWE 4 | 138 | 10.8417 | 10.8452 | 0.00032283
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515310 | QUANXTP5 | 161 | 17.5041 | 17.5096 | 0.00031421
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510918 | VALIANT4 | 138 | 14.7574 | 14.762 | 0.00031171
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515474 | QUANEXS5 | 161 | 16.5843 | 16.5893 | 0.00030149
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515178 | PARKLN 4 | 138 | 16.2138 | 16.2186 | 0.00029604
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515117 | ARBUCKL4 | 138 | 15.5845 | 15.5891 | 0.00029517
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515306 | ARKOMA 5 | 161 | 16.0234 | 16.0281 | 0.00029332
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 514898 | CIMARON4 | 138 | 43.3248 | 43.3374 | 0.00029083
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515308 | 3RDST 5 | 161 | 15.4222 | 15.4265 | 0.00027882
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 588670 | GEN-2017-023 | 138 | 18.3072 | 18.3123 | 0.00027858
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515003 | BARNES 4 | 138 | 15.8287 | 15.833 | 0.00027166
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515610 | FSHRTAP7 | 345 | 17.7246 | 17.7292 | 0.00025953
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 588045 | G16133_765CS | 765 | 3.5157 | 3.5166 | 0.00025599
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 508298 | LYDIA 7 | 345 | 12.5635 | 12.5666 | 0.00024675
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 588180 | GEN-2016-126 | 138 | 12.9061 | 12.9092 | 0.0002402
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515174 | VANOSS 4 | 138 | 13.1499 | 13.153 | 0.00023574
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 514961 | GM 4 | 138 | 19.1936 | 19.1981 | 0.00023445
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515531 | VANOSTP4 | 138 | 13.2751 | 13.2782 | 0.00023352
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 514949 | SOONRTP4 | 138 | 20.3707 | 20.3754 | 0.00023072
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 587950 | GEN-2016-119 | 345 | 11.7707 | 11.7734 | 0.00022938
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515150 | CANEYCK4 | 138 | 8.4199 | 8.4218 | 0.00022566
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515318 | SOTHADA4 | 138 | 11.2764 | 11.2789 | 0.0002217
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 511568 | TERRYRD7 | 345 | 9.9356 | 9.9378 | 0.00022143
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510866 | V-WEYCO4 | 138 | 9.6578 | 9.6598 | 0.00020709
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510948 | EARLSBORO 4 | 138 | 8.0011 | 8.0027 | 0.00019997
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 508072 | NWTXARK7 | 345 | 13.0046 | 13.0072 | 0.00019993
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 588080 | ZONE-4 SUB | 345 | 7.8057 | 7.8072 | 0.00019217
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 588046 | G16133_345CS | 345 | 7.9204 | 7.9219 | 0.00018938
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 514801 | MINCO 7 | 345 | 18.2057 | 18.2091 | 0.00018675
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515133 | BLUERIV4 | 138 | 10.4405 | 10.4424 | 0.00018198
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 587955 | GEN2016-119B | 345 | 9.8967 | 9.8985 | 0.00018188
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515444 | MCNOWND7 | 345 | 18.1495 | 18.1528 | 0.00018182
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515605 | CANADN7 | 345 | 12.9556 | 12.9579 | 0.00017753
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 588100 | ZONE-6 SUB | 345 | 7.0415 | 7.0427 | 0.00017042
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 504021 | FARM_1 2 | 69 | 8.0603 | 8.0616 | 0.00016128
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 588050 | ZONE-1 SUB | 345 | 6.3025 | 6.3035 | 0.00015867
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 587820 | GEN-2016-102 | 138 | 9.5679 | 9.5694 | 0.00015677
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 588090 | ZONE-5 SUB | 345 | 6.5065 | 6.5075 | 0.00015369
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 588070 | ZONE-3 SUB | 345 | 6.5318 | 6.5328 | 0.0001531
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515600 | KNGFSHR7 | 345 | 11.8984 | 11.9002 | 0.00015128
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515100 | PAOLI- 4 | 138 | 10.2996 | 10.3011 | 0.00014564
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 588060 | ZONE-2 SUB | 345 | 6.3129 | 6.3138 | 0.00014257
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515054 | MAUD 2 | 69 | 11.755 | 11.7566 | 0.00013611
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515114 | CHIGLEY4 | 138 | 8.0822 | 8.0833 | 0.0001361
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515177 | PARKLN 2 | 69 | 14.1839 | 14.1858 | 0.00013395
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510886 | IDABEL-4 | 138 | 6.7374 | 6.7383 | 0.00013358
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 508071 | NWTXARK4 | 138 | 24.3065 | 24.3096 | 0.00012754
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 511571 | RUSHSPR7 | 345 | 6.3575 | 6.3583 | 0.00012584
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515549 | MNCWND37 | 345 | 12.4665 | 12.468 | 0.00012032
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 563259 | GEN-2015-092 | 345 | 6.1634 | 6.1641 | 0.00011357
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515175 | IDEAL 2 | 69 | 11.8437 | 11.845 | 0.00010976
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 900001 | TRAVERSE1 | 345 | 7.3837 | 7.3845 | 0.00010835
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515097 | WLNUTCK4 | 138 | 9.2421 | 9.2431 | 0.0001082
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 507455 | TURK 7 | 345 | 8.7928 | 8.7937 | 0.00010236
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510901 | HUGO---4 | 138 | 3.4725 | 3.4728 | 8.6393e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 508359 | WELSH 7 | 345 | 20.8377 | 20.8395 | 8.6382e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 337909 | 8ANO% | 500 | 17.5426 | 17.5441 | 8.5506e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515124 | MAYSVIL4 | 138 | 6.2202 | 6.2207 | 8.0383e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 584060 | GEN-2015-057 | 345 | 9.1357 | 9.1364 | 7.6622e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 900002 | TRAVERSE2 | 345 | 5.7164 | 5.7168 | 6.9974e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510910 | VALIANT2 | 69 | 7.2552 | 7.2557 | 6.8916e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510870 | WCITYTP2 | 69 | 6.3166 | 6.317 | 6.3325e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515099 | PALIOGE2 | 69 | 8.0639 | 8.0644 | 6.2005e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515939 | MNCWND47 | 345 | 6.8065 | 6.8069 | 5.8767e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 900003 | TRAVERSE3 | 345 | 5.1972 | 5.1975 | 5.7723e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 337922 | 8P.HILL% | 500 | 15.1307 | 15.1314 | 4.6264e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515053 | PEARSNT2 | 69 | 4.4506 | 4.4508 | 4.4938e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510868 | GA PAC 2 | 69 | 2.4741 | 2.4742 | 4.0419e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515052 | TRIBBEY2 | 69 | 2.6015 | 2.6016 | 3.8439e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515637 | SRVCPLT2 | 69 | 2.6089 | 2.609 | 3.833e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515067 | PEARSON2 | 69 | 2.9482 | 2.9483 | 3.3919e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510867 | KI PMPS2 | 69 | 3.0643 | 3.0644 | 3.2634e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 511508 | BLANCHD4 | 138 | 6.5665 | 6.5667 | 3.0458e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 337912 | 5ANO% | 161 | 17.7035 | 17.704 | 2.8243e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 337811 | 8HAPPYVALY% | 500 | 24.9494 | 24.9501 | 2.8057e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510869 | W CITY 2 | 69 | 3.8276 | 3.8277 | 2.6126e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515095 | SRVCEPL2 | 69 | 2.3711 | 2.3711 | 0
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515636 | TRIBYTP2 | 69 | 2.6045 | 2.6045 | 0
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 509752 | INOLATP4 | 138 | 8.7677 | 9.0163 | 0.028354
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 532793 | NEOSHO 7 | 345 | 16.4472 | 16.8864 | 0.026704
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 509736 | INOLA 4 | 138 | 7.5297 | 7.7124 | 0.024264
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 589110 | GEN-2017-073 | 161 | 13.8689 | 14.1649 | 0.021343
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 588990 | GEN-2017-061 | 161 | 21.0425 | 21.4795 | 0.020767
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512629 | DRYGULCH5 | 161 | 14.9318 | 15.2351 | 0.020312
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512742 | WMAIN ST5 | 161 | 26.1139 | 26.5974 | 0.018515
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512757 | NWMAID5 | 161 | 25.7016 | 26.1342 | 0.016832
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512648 | MAID 5 | 161 | 42.0337 | 42.7216 | 0.016365
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512656 | GRDA1 5 | 161 | 41.696 | 42.3541 | 0.015783
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512760 | GERALDGAY5 | 161 | 26.7603 | 27.1519 | 0.014634
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512635 | KERR GR5 | 161 | 27.3021 | 27.58 | 0.010179
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512770 | KERR BRK1 5 | 161 | 27.3021 | 27.58 | 0.010179
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512771 | KERR BRK4 5 | 161 | 27.3021 | 27.58 | 0.010179
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 509790 | CATOOSA4 | 138 | 34.4428 | 34.7238 | 0.0081585
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512639 | PRY0RC22 | 69 | 9.9798 | 10.06 | 0.0080362
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 300739 | 7BLACKBERRY | 345 | 14.7665 | 14.8807 | 0.0077337
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512654 | PENSA 5 | 161 | 12.632 | 12.729 | 0.0076789
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512671 | HUNT 2 | 69 | 13.2212 | 13.3129 | 0.0069358
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512634 | KERR GR3 | 115 | 16.4433 | 16.551 | 0.0065498
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512650 | GRDA1 7 | 345 | 25.9865 | 26.1539 | 0.0064418
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512638 | CATSAGR5 | 161 | 23.1122 | 23.2493 | 0.0059319
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512805 | SALNCRK5 | 161 | 17.8109 | 17.9164 | 0.0059233
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512865 | GREC TAP5 | 345 | 24.9005 | 25.0478 | 0.0059155
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 510416 | HUNTAP-2 | 69 | 8.9456 | 8.9978 | 0.0058353
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 300740 | 7SPORTSMAN | 345 | 23.6136 | 23.749 | 0.005734
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512812 | ARMIN 2 | 69 | 10.8395 | 10.9011 | 0.0056829
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512686 | SALINA 5 | 161 | 17.2179 | 17.3153 | 0.0056569
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512687 | AIRPROD2 | 69 | 12.5676 | 12.6381 | 0.0056097
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512669 | KETCHUM5 | 161 | 10.2578 | 10.3142 | 0.0054983
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 509804 | LLANETP4 | 138 | 26.3863 | 26.5258 | 0.0052868
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512661 | CPPTAP 2 | 69 | 12.6182 | 12.6789 | 0.0048105
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512681 | AMERCAST S2 | 69 | 12.934 | 12.9919 | 0.0044766
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 300949 | 7JASPER | 345 | 12.0507 | 12.1045 | 0.0044645
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512625 | MAIDTP2 | 69 | 11.6454 | 11.697 | 0.0044309
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 300069 | 5CHOTEAU1 | 161 | 40.4609 | 40.6388 | 0.0043968
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 301348 | 5CHOTEAU2 | 161 | 40.4609 | 40.6388 | 0.0043968
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 509771 | LLAN ET4 | 138 | 23.6336 | 23.7353 | 0.0043032
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 300741 | 5SPORTSMAN | 161 | 38.9761 | 39.1423 | 0.0042642
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512626 | MAID 2 | 69 | 14.1113 | 14.1698 | 0.0041456
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 509892 | 141PINE4 | 138 | 19.8285 | 19.9044 | 0.0038278
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512727 | GRDA1 2 | 69 | 12.0314 | 12.0774 | 0.0038233
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 300274 | 5LOCSTGV | 161 | 13.111 | 13.1594 | 0.0036916
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 509728 | LLANE-E4 | 138 | 19.325 | 19.3929 | 0.0035136
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 509841 | PCATSAT4 | 138 | 17.472 | 17.5299 | 0.0033139
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 510406 | N.E.S.-7 | 345 | 15.8275 | 15.8785 | 0.0032222
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 509852 | T.NO.--7 | 345 | 22.5867 | 22.6594 | 0.0032187
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 509899 | BIRDCREE-4 | 138 | 16.9241 | 16.9784 | 0.0032084
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512698 | REDDEN 2 | 69 | 10.3792 | 10.4108 | 0.0030446
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 300993 | 5ELMCRK | 161 | 12.8554 | 12.8914 | 0.0028004
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512637 | 412SUB 5 | 161 | 11.4637 | 11.4954 | 0.0027653
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 509835 | TERNITP4 | 138 | 15.6551 | 15.6979 | 0.0027339
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512685 | CASTING TAP2 | 69 | 9.091 | 9.1152 | 0.002662
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 509895 | T.NO.2-4 | 138 | 33.6374 | 33.7265 | 0.0026488
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 509755 | WEKIWA-7 | 345 | 18.6818 | 18.7267 | 0.0024034
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512683 | AMERCAST N2 | 69 | 8.1658 | 8.1853 | 0.002388
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 301344 | 5CDRCRST | 161 | 10.4498 | 10.4741 | 0.0023254
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512651 | CLARMR 5 | 161 | 12.51 | 12.5388 | 0.0023022
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 509723 | TER-NIT4 | 138 | 12.9515 | 12.9807 | 0.0022546
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512750 | TONECE7 | 345 | 14.5005 | 14.5329 | 0.0022344
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512627 | COLINS 5 | 161 | 11.7421 | 11.7681 | 0.0022143
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 506935 | FLINTCR7 | 345 | 14.6814 | 14.7134 | 0.0021796
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512628 | PENSA 2 | 69 | 13.0379 | 13.0661 | 0.0021629
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 509725 | PCATOSA4 | 138 | 11.2036 | 11.2273 | 0.0021154
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 509887 | OWAS88_4 | 138 | 16.3829 | 16.4174 | 0.0021059
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 506934 | FLINTCR5 | 161 | 31.8761 | 31.9414 | 0.0020486
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 510396 | N.E.S.-4 | 138 | 35.2821 | 35.3504 | 0.0019358
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 300997 | 5KETONVL | 161 | 10.4336 | 10.4537 | 0.0019265
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512714 | KANSATP5 | 161 | 11.3325 | 11.3539 | 0.0018884
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512700 | WAGNOR 5 | 161 | 9.4446 | 9.4607 | 0.0017047
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512643 | SILMCTY5 | 161 | 19.0667 | 19.0979 | 0.0016364
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 506979 | SHIPERD7 | 345 | 9.9081 | 9.9224 | 0.0014433
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 300795 | 4OOLOGAH | 138 | 20.3525 | 20.3801 | 0.0013561
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512707 | CLARMR 4 | 138 | 13.1884 | 13.2061 | 0.0013421
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 505558 | MUSKTAP5 | 161 | 13.9439 | 13.9626 | 0.0013411
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512694 | CLEVLND7 | 345 | 14.9069 | 14.9267 | 0.0013282
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512640 | OKAYGR 5 | 161 | 9.5822 | 9.5949 | 0.0013254
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512655 | TAHLQH 5 | 161 | 10.1269 | 10.1399 | 0.0012837
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512751 | TONECE5 | 161 | 14.7089 | 14.7264 | 0.0011898
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 505560 | FT GIB 5 | 161 | 10.332 | 10.3442 | 0.0011808
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 301307 | 5PARK | 161 | 9.0106 | 9.0209 | 0.0011431
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512705 | COLLINS4 | 138 | 8.3164 | 8.3258 | 0.0011303
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 509799 | CATOOSA2 | 69 | 10.4127 | 10.4244 | 0.0011236
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512679 | CLARMR 2 | 69 | 12.3636 | 12.3762 | 0.0010191
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512624 | CENTLFT2 | 69 | 11.0777 | 11.0879 | 0.00092077
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 549984 | BROOKLINE 7 | 345 | 11.278 | 11.2881 | 0.00089555
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512870 | COLNSGR2 | 69 | 9.9201 | 9.9272 | 0.00071572
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 300992 | 2COLINS | 69 | 9.92 | 9.927 | 0.00070565
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 301345 | 2CDRCRST | 69 | 8.0233 | 8.0285 | 0.00064811
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 301002 | 2SEQUOYA | 69 | 6.7757 | 6.7799 | 0.00061986
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512646 | OKAYGR 2 | 69 | 9.5995 | 9.6045 | 0.00052086
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512725 | CHELSGR2 | 69 | 4.4584 | 4.4606 | 0.00049345
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512820 | SILMCTY2 | 69 | 13.0474 | 13.0536 | 0.00047519
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512737 | SSSWTP2 | 69 | 12.1751 | 12.1805 | 0.00044353
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512697 | WAGNOR 2 | 69 | 6.773 | 6.7759 | 0.00042817
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 300970 | 2SWAGONR | 69 | 7.0338 | 7.0368 | 0.00042651
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512828 | UNARCO 2 | 69 | 6.8025 | 6.8054 | 0.00042631
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 300956 | 2FTGIBSN | 69 | 7.4162 | 7.4193 | 0.000418
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512690 | WAGNRTP2 | 69 | 6.795 | 6.7978 | 0.00041207
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512730 | SSSWES2 | 69 | 11.1406 | 11.1451 | 0.00040393
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 300973 | 2WHITETP | 69 | 6.427 | 6.4295 | 0.00038898
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512759 | WAGCTY22 | 69 | 6.229 | 6.2314 | 0.00038529
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512801 | WAGCTY12 | 69 | 6.2904 | 6.2928 | 0.00038153
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512744 | SSMOSS2 | 69 | 10.0523 | 10.056 | 0.00036807
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 300972 | 2WAGNERW | 69 | 4.4124 | 4.4136 | 0.00027196
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 301464 | 2PYRCRNR | 69 | 0.9905 | 0.9907 | 0.00020192
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 300905 | 2MUSK-SW | 69 | 5.8004 | 5.8015 | 0.00018964
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 300974 | 2WHITHRN | 69 | 3.1751 | 3.1757 | 0.00018897
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512765 | PYRCRNRTP2 | 69 | 1.6063 | 1.6066 | 0.00018676
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 300955 | 2COWETA | 69 | 2.3983 | 2.3987 | 0.00016678
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512753 | TONNEC2 | 69 | 4.7099 | 4.7106 | 0.00014862
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 300991 | 2CHILDRS | 69 | 1.38 | 1.3802 | 0.00014493
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512723 | CHILDRS2 | 69 | 1.3802 | 1.3804 | 0.00014491
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512728 | ARKLIN2 | 69 | 3.6464 | 3.6469 | 0.00013712
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512756 | TONECESTR2 | 69 | 3.7544 | 3.7549 | 0.00013318
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512745 | SSLINC2 | 69 | 2.7443 | 2.7446 | 0.00010932
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 300958 | 2HIGHLND | 69 | 1.8441 | 1.8443 | 0.00010845
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 301001 | 2SCOFEYV | 69 | 0.9648 | 0.9649 | 0.00010365
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512747 | SSNEWN2 | 69 | 3.034 | 3.0343 | 9.8879e-05
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512746 | SSNORT2 | 69 | 2.7976 | 2.7978 | 7.149e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 589240 | GEN-2017-086 | 345 | 9.9635 | 10.5552 | 0.059387 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 588540 | GEN-2017-009 | 345 | 9.9978 | 10.5633 | 0.056562 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 588544 | G17-009-TAP | 345 | 10.8451 | 11.4101 | 0.052097 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532798 | VIOLA 7 | 345 | 13.8783 | 14.4624 | 0.042087 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532793 | NEOSHO 7 | 345 | 16.4472 | 16.8864 | 0.026704 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533075 | VIOLA 4 | 138 | 24.0364 | 24.4751 | 0.018251 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 588364 | G16-153-TAP | 345 | 7.4618 | 7.5924 | 0.017502 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 588360 | GEN-2016-153 | 345 | 7.1436 | 7.2624 | 0.01663 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532792 | FR2EAST7 | 345 | 6.7405 | 6.843 | 0.015207 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515543 | RENFROW7 | 345 | 12.3872 | 12.5431 | 0.012586 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532795 | FR2WEST7 | 345 | 5.3886 | 5.4506 | 0.011506 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532780 | CANEYRV7 | 345 | 9.847 | 9.9559 | 0.011059 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515646 | GRNTWD 7 | 345 | 10.8855 | 11.0042 | 0.010904 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532781 | CANEYWF7 | 345 | 9.5894 | 9.692 | 0.010699 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 578530 | FR3HV | 345 | 4.9398 | 4.9915 | 0.010466 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532796 | WICHITA7 | 345 | 24.1532 | 24.3835 | 0.009535 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532800 | LATHAMS7 | 345 | 10.4136 | 10.5083 | 0.0090939 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539009 | CONWAY | 138 | 12.6276 | 12.7355 | 0.0085448 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539008 | MILAN_GOAB | 138 | 11.8476 | 11.9472 | 0.0084068 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532801 | ELKRVR17 | 345 | 9.1912 | 9.2645 | 0.007975 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 589060 | GEN-2017-068 | 345 | 20.1103 | 20.2698 | 0.0079313 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539676 | MILAN 4 | 138 | 10.4656 | 10.5429 | 0.0073861 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532782 | BUFFALO7 | 345 | 20.5614 | 20.7023 | 0.0068526 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539675 | MILANTP4 | 138 | 9.8621 | 9.9226 | 0.0061346 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515476 | HUNTERS7 | 345 | 13.4924 | 13.573 | 0.0059737 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515477 | CHSHLMV7 | 345 | 13.4742 | 13.5546 | 0.005967 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533044 | GILL E 4 | 138 | 21.9045 | 22.0344 | 0.0059303 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533045 | GILL W 4 | 138 | 21.9045 | 22.0344 | 0.0059303 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533046 | GILL S 4 | 138 | 21.9045 | 22.0344 | 0.0059303 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533047 | GILL 4 | 138 | 21.9045 | 22.0344 | 0.0059303 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532794 | ROSEHIL7 | 345 | 18.9572 | 19.0665 | 0.0057656 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532791 | BENTON 7 | 345 | 19.6359 | 19.7468 | 0.0056478 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533036 | CLEARWT4 | 138 | 14.0937 | 14.1705 | 0.0054492 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533071 | WACO S 4 | 138 | 19.1512 | 19.2466 | 0.0049814 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 587500 | GEN-2016-073 | 345 | 15.119 | 15.1939 | 0.004954 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533040 | EVANS N4 | 138 | 33.3755 | 33.5322 | 0.0046951 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533041 | EVANS S4 | 138 | 33.3755 | 33.5322 | 0.0046951 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533062 | ROSEHIL4 | 138 | 30.8868 | 31.0133 | 0.0040956 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533039 | ELPASO 4 | 138 | 24.1926 | 24.2863 | 0.0038731 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533059 | ELPASOE4 | 138 | 24.1926 | 24.2863 | 0.0038731 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515544 | RENFROW4 | 138 | 14.3714 | 14.4241 | 0.003667 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533074 | 45TH ST4 | 138 | 24.1728 | 24.2608 | 0.0036405 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533029 | 59TH ST4 | 138 | 17.0897 | 17.1516 | 0.0036221 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532986 | BENTON 4 | 138 | 27.8896 | 27.9879 | 0.0035246 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533795 | GILL E 2 | 69 | 29.2006 | 29.301 | 0.0034383 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533796 | GILL W 2 | 69 | 29.2006 | 29.301 | 0.0034383 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533049 | HOOVERN4 | 138 | 17.1453 | 17.2018 | 0.0032954 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533050 | HOOVERS4 | 138 | 17.1453 | 17.2018 | 0.0032954 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539003 | CLDWELL4 | 138 | 5.5937 | 5.6121 | 0.0032894 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533038 | COWSKIN4 | 138 | 17.5293 | 17.5823 | 0.0030235 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532991 | WEAVER 4 | 138 | 21.7367 | 21.8021 | 0.0030087 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533035 | CHISHLM4 | 138 | 21.2936 | 21.3567 | 0.0029633 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533053 | LAKERDG4 | 138 | 17.2997 | 17.3508 | 0.0029538 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533054 | MAIZE 4 | 138 | 21.0644 | 21.1262 | 0.0029339 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533068 | STEARMN4 | 138 | 19.1751 | 19.2296 | 0.0028422 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533034 | CENTENN4 | 138 | 14.7464 | 14.7883 | 0.0028414 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 514715 | WOODRNG7 | 345 | 19.0903 | 19.1426 | 0.0027396 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533052 | PARKCTY4 | 138 | 20.1019 | 20.1569 | 0.0027361 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533805 | HOOVERN2 | 69 | 30.449 | 30.5323 | 0.0027357 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533060 | NOEASTE4 | 138 | 20.2888 | 20.3433 | 0.0026862 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533061 | NOEASTW4 | 138 | 20.2888 | 20.3433 | 0.0026862 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533065 | SG12COL4 | 138 | 19.7318 | 19.7841 | 0.0026505 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533042 | FARBER 4 | 138 | 15.7644 | 15.806 | 0.0026389 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515569 | MDFRDTP4 | 138 | 11.4762 | 11.5063 | 0.0026228 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533001 | ALTOONA4 | 138 | 8.0292 | 8.0501 | 0.002603 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533064 | 17TH 4 | 138 | 17.2325 | 17.2761 | 0.0025301 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 588320 | GEN-2016-162 | 345 | 9.7523 | 9.7768 | 0.0025122 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533024 | 29TH 4 | 138 | 19.377 | 19.4255 | 0.002503 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533030 | BOEINGE4 | 138 | 16.6198 | 16.661 | 0.002479 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 520409 | WFEC_RNFRO4 | 138 | 10.6021 | 10.628 | 0.0024429 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532988 | BELAIRE4 | 138 | 18.7482 | 18.7936 | 0.0024216 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533037 | COMOTAR4 | 138 | 18.4588 | 18.5033 | 0.0024108 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533026 | ANDOVER4 | 138 | 17.5952 | 17.6373 | 0.0023927 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533043 | FOWLER 4 | 138 | 15.8625 | 15.9002 | 0.0023767 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539668 | HARPER 4 | 138 | 7.2078 | 7.2244 | 0.0023031 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539002 | BLF-CRK4 | 138 | 4.6999 | 4.7107 | 0.0022979 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532984 | SUMNER 4 | 138 | 10.2243 | 10.2477 | 0.0022887 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533850 | VULCAN 2 | 69 | 18.7158 | 18.757 | 0.0022013 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 588330 | GEN-2016-163 | 345 | 8.6195 | 8.6384 | 0.0021927 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 560053 | G15-052T | 345 | 13.1034 | 13.1318 | 0.0021674 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533032 | BU11PON4 | 138 | 14.8177 | 14.8496 | 0.0021528 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 584900 | GEN-2015-052 | 345 | 13.0534 | 13.0815 | 0.0021527 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533840 | 17TH 2 | 69 | 26.6243 | 26.6814 | 0.0021447 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 588630 | GEN-2017-018 | 345 | 16.3709 | 16.4054 | 0.0021074 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539801 | THISTLE7 | 345 | 16.3709 | 16.4054 | 0.0021074 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533067 | SPRNGDL4 | 138 | 14.2305 | 14.2594 | 0.0020308 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532982 | OXFORD 4 | 138 | 9.3635 | 9.3817 | 0.0019437 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 562476 | G14-001-TAP | 345 | 10.6079 | 10.6282 | 0.0019137 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533063 | SC10BEL4 | 138 | 9.6835 | 9.702 | 0.0019105 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532797 | WOLFCRK7 | 345 | 18.0814 | 18.1154 | 0.0018804 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533823 | NOEASTE2 | 69 | 25.1631 | 25.2079 | 0.0017804 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532783 | KINGMAN7 | 345 | 6.821 | 6.8327 | 0.0017153 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 522397 | MEDFORD4 | 138 | 7.4872 | 7.5 | 0.0017096 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 542981 | LACYGNE7 | 345 | 24.761 | 24.8029 | 0.0016922 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533859 | RIPLEYE2 | 69 | 22.2574 | 22.2948 | 0.0016803 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532771 | RENO 7 | 345 | 12.6248 | 12.6459 | 0.0016713 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 543629 | LACYGNE11_7 | 345 | 24.1469 | 24.1868 | 0.0016524 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 543632 | LACYGNE22_7 | 345 | 24.1469 | 24.1868 | 0.0016524 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532799 | WAVERLY7 | 345 | 16.0356 | 16.0608 | 0.0015715 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515546 | GRANTCO4 | 138 | 6.4548 | 6.4642 | 0.0014563 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533786 | CHISHLM2 | 69 | 19.7124 | 19.7409 | 0.0014458 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533788 | COWSKIN2 | 69 | 15.8589 | 15.8814 | 0.0014188 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 560084 | G16-061-TAP | 345 | 16.1024 | 16.125 | 0.0014035 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 587410 | GEN-2016-061 | 345 | 16.1024 | 16.125 | 0.0014035 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533874 | SG9STMK2 | 69 | 15.5648 | 15.5864 | 0.0013877 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532990 | MIDIAN 4 | 138 | 10.5446 | 10.5589 | 0.0013561 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532784 | NINN1WF7 | 345 | 5.6816 | 5.6893 | 0.0013553 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532993 | TALLGRS4 | 138 | 10.1282 | 10.1418 | 0.0013428 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532987 | BUTLER 4 | 138 | 10.362 | 10.3759 | 0.0013414 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532989 | BUTLERS4 | 138 | 10.362 | 10.3759 | 0.0013414 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532802 | WAVERTX7 | 345 | 13.4196 | 13.437 | 0.0012966 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533015 | BENTLEY4 | 138 | 10.8046 | 10.8186 | 0.0012957 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539000 | RAGO 4 | 138 | 3.9456 | 3.9506 | 0.0012672 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539804 | THISTLE4 | 138 | 17.4802 | 17.502 | 0.0012471 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 583850 | GEN-2014-001 | 345 | 7.0819 | 7.0906 | 0.0012285 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532992 | TIMBJCT4 | 138 | 5.8655 | 5.8727 | 0.0012275 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539638 | FLATRDG4 | 138 | 15.5121 | 15.5308 | 0.0012055 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 585250 | GEN-2015-090 | 345 | 5.0769 | 5.0829 | 0.0011818 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 514825 | KAYWIND7 | 345 | 12.6052 | 12.6199 | 0.0011662 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515621 | OPENSKY7 | 345 | 12.64 | 12.6547 | 0.001163 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 522398 | PONDCRK4 | 138 | 5.091 | 5.0969 | 0.0011589 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515877 | REDDIRT7 | 345 | 18.0507 | 18.0716 | 0.0011578 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515875 | REDNGTN7 | 345 | 18.0549 | 18.0758 | 0.0011576 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515426 | RDRUNNR4 | 138 | 8.4138 | 8.4234 | 0.001141 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532985 | TCROCK 4 | 138 | 5.4745 | 5.4807 | 0.0011325 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 588190 | GEN-2016-128 | 345 | 7.9459 | 7.9545 | 0.0010823 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533016 | WWUPLNT4 | 138 | 8.1516 | 8.1596 | 0.0009814 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 529200 | OMCDLEC7 | 345 | 13.8474 | 13.8608 | 0.00096769 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515576 | RANCHRD7 | 345 | 13.8732 | 13.8866 | 0.00096589 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532981 | CRESWLN4 | 138 | 9.1264 | 9.1352 | 0.00096424 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533597 | MIDIANW2 | 69 | 13.8298 | 13.8422 | 0.00089661 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533610 | MIDIANE2 | 69 | 13.8298 | 13.8422 | 0.00089661 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 587884 | G16-111-TAP | 345 | 11.3773 | 11.3875 | 0.00089652 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533011 | HALSTD 4 | 138 | 8.3248 | 8.3322 | 0.00088891 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533799 | GRANT 2 | 69 | 12.2628 | 12.2736 | 0.00088071 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 520434 | WAKTASW4 | 138 | 6.3232 | 6.3287 | 0.00086981 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515852 | DGRASSE7 | 345 | 14.5452 | 14.5578 | 0.00086627 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533583 | BUTLERN2 | 69 | 13.54 | 13.5517 | 0.00086411 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 587460 | GEN-2016-068 | 345 | 6.5264 | 6.5319 | 0.00084273 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533604 | WEAVER 2 | 69 | 11.6633 | 11.6729 | 0.00082309 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 584770 | GEN-2015-034 | 345 | 11.7376 | 11.747 | 0.00080085 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 587160 | GEN-2016-022 | 345 | 11.7376 | 11.747 | 0.00080085 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 587910 | GEN-2016-114 | 345 | 10.1469 | 10.155 | 0.00079827 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539631 | FLATRWD4 | 138 | 10.3583 | 10.3664 | 0.00078198 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533416 | RENO 3 | 115 | 26.7821 | 26.8023 | 0.00075424 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515688 | FRNTWND7 | 345 | 11.1998 | 11.2082 | 0.00075001 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 584570 | GEN-2015-015 | 138 | 5.8242 | 5.8284 | 0.00072113 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533558 | TIMBJCT2 | 69 | 8.1517 | 8.1575 | 0.00071151 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 542968 | STILWEL7 | 345 | 23.1239 | 23.1391 | 0.00065733 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515547 | GRANTCO2 | 69 | 7.4693 | 7.4742 | 0.00065602 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 514714 | WOODRNG4 | 138 | 20.0668 | 20.0796 | 0.00063787 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 587894 | G16-112-TAP | 345 | 11.1782 | 11.1849 | 0.00059938 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533541 | AKRON 2 | 69 | 6.7266 | 6.7306 | 0.00059465 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533589 | CHESNEY2 | 69 | 8.9552 | 8.9604 | 0.00058067 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 542965 | W.GRDNR7 | 345 | 24.8262 | 24.8406 | 0.00058003 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533013 | MOUND 4 | 138 | 6.9434 | 6.9474 | 0.00057609 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533070 | SLATECRK4 | 138 | 6.7318 | 6.7356 | 0.00056448 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533603 | THUNBRD2 | 69 | 8.1334 | 8.1378 | 0.00054098 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 587880 | GEN-2016-111 | 345 | 7.1243 | 7.1281 | 0.00053339 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539674 | BARBER 4 | 138 | 8.2188 | 8.2231 | 0.00052319 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533413 | CIRCLE 3 | 115 | 23.6123 | 23.6235 | 0.00047433 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533674 | ALTOO W2 | 69 | 2.9702 | 2.9716 | 0.00047135 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533421 | HEC GT 3 | 115 | 22.9426 | 22.953 | 0.00045331 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539800 | CLARKCOUNTY7 | 345 | 13.2594 | 13.2652 | 0.00043743 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533419 | HEC 3 | 115 | 21.8737 | 21.8832 | 0.00043431 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533630 | CC3WEST2 | 69 | 4.4272 | 4.4291 | 0.00042917 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533429 | MOUNDRG3 | 115 | 8.6474 | 8.6511 | 0.00042787 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532768 | EMPEC 7 | 345 | 17.5987 | 17.6059 | 0.00040912 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532769 | LANG 7 | 345 | 17.3797 | 17.3867 | 0.00040277 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533736 | HALSTED2 | 69 | 7.2751 | 7.278 | 0.00039862 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532773 | SUMMIT 7 | 345 | 12.1324 | 12.1372 | 0.00039563 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515375 | WWRDEHV7 | 345 | 19.8126 | 19.8204 | 0.00039369 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533626 | BURLJCT2 | 69 | 4.8155 | 4.8173 | 0.00037379 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 583370 | GEN-2012-024 | 345 | 11.3107 | 11.3148 | 0.00036249 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515853 | DGRASSE4 | 138 | 15.3869 | 15.3923 | 0.00035095 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539852 | P1 MPT PRI | 345 | 10.7671 | 10.7708 | 0.00034364 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533653 | WOLFCRK2 | 69 | 5.8582 | 5.8601 | 0.00032433 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 582008 | GEN-2011-008 | 345 | 10.514 | 10.5174 | 0.00032338 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 542977 | CRAIG 7 | 345 | 21.4243 | 21.4312 | 0.00032206 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533742 | MOUND 2 | 69 | 7.0573 | 7.0595 | 0.00031173 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 542966 | WGARDNR5 | 161 | 23.42 | 23.4273 | 0.0003117 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 588494 | G17-004-TAP | 345 | 10.1178 | 10.1209 | 0.00030639 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 585100 | GEN-2015-073 | 345 | 13.3961 | 13.4002 | 0.00030606 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 520529 | RSVLYSW4 | 138 | 13.6729 | 13.677 | 0.00029986 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 543105 | BULLCRK5 | 161 | 22.4616 | 22.4683 | 0.00029829 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533440 | 43LORAN | 115 | 14.4364 | 14.4407 | 0.00029786 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 560080 | G16-046-TAP | 345 | 11.4289 | 11.4323 | 0.00029749 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 514795 | KNOBHIL4 | 138 | 11.3899 | 11.3932 | 0.00028973 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539857 | P2 MPT PRI | 345 | 9.1297 | 9.1323 | 0.00028478 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 585300 | GEN-2015-095 | 138 | 11.3108 | 11.314 | 0.00028292 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533705 | STUDBKR2 | 69 | 1.7767 | 1.7772 | 0.00028142 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515407 | TATONGA7 | 345 | 16.7215 | 16.7261 | 0.00027509 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533551 | SC1KING2 | 69 | 3.2879 | 3.2888 | 0.00027373 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533628 | CC1BURL2 | 69 | 3.3205 | 3.3214 | 0.00027104 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533624 | BURLING2 | 69 | 3.3336 | 3.3345 | 0.00026998 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 582908 | G-2011-008-2 | 345 | 8.4349 | 8.4371 | 0.00026082 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 582708 | G-2011-008-1 | 345 | 8.5619 | 8.564 | 0.00024527 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 587310 | GEN-2016-046 | 345 | 9.8417 | 9.8441 | 0.00024386 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533629 | CC2SHAR2 | 69 | 4.545 | 4.5461 | 0.00024202 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532774 | SWISVAL7 | 345 | 16.163 | 16.1669 | 0.00024129 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 531469 | SPERVIL7 | 345 | 13.7357 | 13.739 | 0.00024025 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 588490 | GEN-2017-004 | 345 | 8.0601 | 8.062 | 0.00023573 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533625 | BURLIND2 | 69 | 2.9763 | 2.977 | 0.00023519 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 587980 | GEN-2016-122 | 345 | 5.2087 | 5.2099 | 0.00023038 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532871 | CIRCLE 6 | 230 | 10.0555 | 10.0578 | 0.00022873 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 579480 | GEN-2008-124 | 345 | 12.6868 | 12.6897 | 0.00022858 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539803 | IRONWOOD7 | 345 | 13.1375 | 13.1405 | 0.00022835 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515599 | G07621119-20 | 345 | 13.2006 | 13.2036 | 0.00022726 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533601 | POTWIN 2 | 69 | 3.528 | 3.5288 | 0.00022676 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533546 | FLORALJ2 | 69 | 2.7316 | 2.7322 | 0.00021965 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515585 | MAMTHPW7 | 345 | 13.2772 | 13.2801 | 0.00021842 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533692 | YELLOWJ2 | 69 | 1.3845 | 1.3848 | 0.00021668 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532873 | SUMMIT 6 | 230 | 14.5337 | 14.5368 | 0.0002133 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533412 | ARKVALJ3 | 115 | 10.8426 | 10.8449 | 0.00021213 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 560071 | G16-003-TAP | 345 | 15.2376 | 15.2408 | 0.00021001 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 587020 | GEN-2016-003 | 345 | 15.2376 | 15.2408 | 0.00021001 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533411 | ARKVAL 3 | 115 | 10.6123 | 10.6145 | 0.00020731 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 585430 | PRSIMN_CRK1 | 345 | 11.6164 | 11.6188 | 0.0002066 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533415 | DAVIS 3 | 115 | 8.7128 | 8.7146 | 0.00020659 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533557 | TIMBER 2 | 69 | 2.4233 | 2.4238 | 0.00020633 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533701 | NEW ALB2 | 69 | 1.4684 | 1.4687 | 0.0002043 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533434 | SALTCRK3 | 115 | 9.0473 | 9.0491 | 0.00019895 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 587890 | GEN-2016-112 | 345 | 4.6684 | 4.6693 | 0.00019279 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515448 | CRSRDSW7 | 345 | 11.741 | 11.7432 | 0.00018738 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532770 | MORRIS 7 | 345 | 12.8665 | 12.8689 | 0.00018653 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533414 | CITIES 3 | 115 | 8.5877 | 8.5893 | 0.00018631 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 585440 | PRSIMN_CRK2 | 345 | 10.6077 | 10.6096 | 0.00017912 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533732 | BURRTON2 | 69 | 3.4761 | 3.4767 | 0.00017261 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 588560 | GEN-2017-011 | 345 | 12.2618 | 12.2639 | 0.00017126 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532872 | EMCPHER6 | 230 | 9.3745 | 9.3761 | 0.00017068 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533545 | FLORAL 2 | 69 | 2.4109 | 2.4113 | 0.00016591 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 585410 | GREAT_WESTRN | 345 | 9.9457 | 9.9473 | 0.00016087 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533584 | BU6DEGR2 | 69 | 2.4872 | 2.4876 | 0.00016082 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532856 | SWISVAL6 | 230 | 20.9983 | 21.0016 | 0.00015716 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515376 | WWRDEHV4 | 138 | 24.1729 | 24.1765 | 0.00014893 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532767 | GEARY 7 | 345 | 10.3222 | 10.3237 | 0.00014532 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533380 | SPRGCRK3 | 115 | 3.8099 | 3.8104 | 0.00013124 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532863 | MORRIS 6 | 230 | 13.9585 | 13.9603 | 0.00012895 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 588654 | G17-021-TAP | 345 | 10.1299 | 10.1312 | 0.00012833 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539695 | SPEARVL6 | 230 | 12.4713 | 12.4729 | 0.00012829 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539117 | SPRVILL-EHVB | 230 | 12.1436 | 12.1451 | 0.00012352 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 543054 | CEDARNL5 | 161 | 8.9661 | 8.9672 | 0.00012268 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 543659 | LACYGNE2 | 69 | 8.4733 | 8.4743 | 0.00011802 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533369 | HILSBOR3 | 115 | 2.5456 | 2.5459 | 0.00011785 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 585420 | COWBOY_RIDGE | 345 | 7.6718 | 7.6727 | 0.00011731 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533438 | WMCPHER3 | 115 | 15.7555 | 15.7573 | 0.00011425 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 589370 | GEN-2017-099 | 345 | 9.6557 | 9.6568 | 0.00011392 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 588650 | GEN-2017-021 | 345 | 9.6638 | 9.6649 | 0.00011383 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533417 | EMCPHER3 | 115 | 15.2137 | 15.2154 | 0.00011174 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533304 | LANG 3 | 115 | 14.5028 | 14.5044 | 0.00011032 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515582 | SLNGWND7 | 345 | 7.3455 | 7.3463 | 0.00010891 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533428 | MCPHER 3 | 115 | 15.7273 | 15.729 | 0.00010809 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533506 | DAVIS 2 | 69 | 7.4951 | 7.4959 | 0.00010674 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533427 | REFINRY3 | 115 | 14.6512 | 14.6527 | 0.00010238 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532766 | JEC N 7 | 345 | 23.7584 | 23.7608 | 0.00010102 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533520 | 2ND ELM2 | 69 | 6.1435 | 6.1441 | 9.7664e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533516 | MAPLE J2 | 69 | 7.1953 | 7.196 | 9.7286e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533372 | PHILIPS3 | 115 | 12.8586 | 12.8598 | 9.3323e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533529 | MWIRNJ22 | 69 | 6.5493 | 6.5499 | 9.1613e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533366 | FLORENC3 | 115 | 3.3362 | 3.3365 | 8.9923e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 531501 | BUCKNER7 | 345 | 9.0367 | 9.0375 | 8.8528e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 588310 | GEN-2016-158 | 345 | 4.6245 | 4.6249 | 8.6496e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 588300 | GEN-2016-157 | 345 | 4.8983 | 4.8987 | 8.1661e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533519 | MWIRONJ2 | 69 | 6.1417 | 6.1422 | 8.1411e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533513 | HEC 2 | 69 | 11.1813 | 11.1822 | 8.0492e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533518 | MWIRON 2 | 69 | 6.3596 | 6.3601 | 7.8621e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532874 | UNIONRG6 | 230 | 8.9642 | 8.9649 | 7.8088e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533426 | MANVILE3 | 115 | 11.7012 | 11.7021 | 7.6915e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533505 | NCTYSVC2 | 69 | 3.9782 | 3.9785 | 7.5411e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533307 | PRAIRIE3 | 115 | 9.2854 | 9.2861 | 7.5387e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532862 | MCDOWEL6 | 230 | 7.005 | 7.0055 | 7.1378e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539679 | GRTBEND6 | 230 | 8.5124 | 8.513 | 7.0485e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 531502 | CIMRRN 7 | 345 | 7.1715 | 7.172 | 6.972e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 531504 | CIMWD2 7 | 345 | 7.1715 | 7.172 | 6.972e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532765 | HOYT 7 | 345 | 15.8447 | 15.8458 | 6.9424e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532851 | AUBURN 6 | 230 | 13.1378 | 13.1387 | 6.8505e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532857 | TECHILL6 | 230 | 10.7002 | 10.7009 | 6.5419e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533301 | EAST ST3 | 115 | 9.236 | 9.2366 | 6.4963e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532852 | JEC 6 | 230 | 24.7674 | 24.769 | 6.4601e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533305 | MORRIS 3 | 115 | 12.4747 | 12.4755 | 6.413e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 530686 | RICE 6 | 230 | 4.9179 | 4.9182 | 6.1002e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539759 | SPRVL 3 | 115 | 11.5608 | 11.5615 | 6.0549e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533599 | PEABODY2 | 69 | 1.7306 | 1.7307 | 5.7783e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533522 | 17HUXMN2 | 69 | 7.0441 | 7.0445 | 5.6785e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533509 | 11HALST2 | 69 | 7.3924 | 7.3928 | 5.411e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515398 | OUSPRT 4 | 138 | 9.4837 | 9.4842 | 5.2722e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533394 | CORONAD3 | 115 | 7.6677 | 7.6681 | 5.2167e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533504 | CITYSVC2 | 69 | 3.9513 | 3.9515 | 5.0616e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533439 | WHEATLD3 | 115 | 7.9438 | 7.9442 | 5.0354e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533503 | CESSNAJ2 | 69 | 5.9718 | 5.9721 | 5.0236e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533521 | 17HALST2 | 69 | 8.1271 | 8.1275 | 4.9218e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 530618 | HUNTSVL3 | 115 | 4.0986 | 4.0988 | 4.8797e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533523 | 17 PLUM2 | 69 | 6.2554 | 6.2557 | 4.7959e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533306 | READING3 | 115 | 6.3868 | 6.3871 | 4.6972e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532854 | LEC U5 6 | 230 | 12.9986 | 12.9992 | 4.6159e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532875 | GEN-2015-069 | 230 | 6.5502 | 6.5505 | 4.58e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532853 | LAWHILL6 | 230 | 13.1179 | 13.1185 | 4.5739e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515394 | KEENAN 4 | 138 | 8.912 | 8.9124 | 4.4883e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515458 | BORDER 7 | 345 | 4.4958 | 4.496 | 4.4486e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533511 | 14LORAN2 | 69 | 6.7624 | 6.7627 | 4.4363e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 530620 | LYONS 3 | 115 | 5.6298 | 5.63 | 3.5525e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533502 | CESSNA 2 | 69 | 5.8605 | 5.8607 | 3.4127e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533507 | 18&PLUM2 | 69 | 6.166 | 6.1662 | 3.2436e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 530688 | BUFLOCRK6 | 230 | 3.6481 | 3.6482 | 2.7412e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533359 | UNIONRG3 | 115 | 3.8029 | 3.803 | 2.6296e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 530711 | SAXMAN 3 | 115 | 4.3857 | 4.3858 | 2.2801e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533183 | WM BROS3 | 115 | 11.0007 | 11.0009 | 1.8181e-05 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 543669 | LAC8_STAR7 | 345 | 0.6133 | 0.6133 | 0 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533360 | TCHOPE 3 | 115 | 3.3791 | 3.3791 | 0 |  |  | X
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 543667 | LAC3_STAR7 | 345 | 0.6403 | 0.6403 | 0 |  |  | X
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 589090 | GEN-2017-071 | 138 | 7.5805 | 8.2795 | 0.09221
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515417 | GRNWOOD4 | 138 | 7.845 | 8.5572 | 0.090784
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 589100 | GEN-2017-072 | 138 | 7.5805 | 8.2587 | 0.089466
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515033 | CUSHING4 | 138 | 7.0346 | 7.4039 | 0.052498
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515043 | GRTPLNS4 | 138 | 6.779 | 7.133 | 0.05222
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515453 | LNWOODT4 | 138 | 6.7539 | 7.0913 | 0.049956
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515401 | LINWOOD4 | 138 | 6.7099 | 7.0428 | 0.049613
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515416 | GRNWOOD2 | 69 | 8.1669 | 8.4418 | 0.03366
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515032 | CUSHING2 | 69 | 8.1882 | 8.433 | 0.029897
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515019 | HY99TAP2 | 69 | 7.048 | 7.2515 | 0.028873
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515021 | OAKGROV2 | 69 | 7.2682 | 7.4632 | 0.026829
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515035 | BRISTOW4 | 138 | 9.8092 | 10.0533 | 0.024885
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515026 | DRMRITE2 | 69 | 7.2387 | 7.4166 | 0.024576
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515675 | TRYON 4 | 138 | 9.1552 | 9.3776 | 0.024292
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515413 | CUSHOIL2 | 69 | 6.0365 | 6.1823 | 0.024153
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515039 | PAYNESB4 | 138 | 8.8061 | 9.0107 | 0.023234
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515020 | PLCNTRT2 | 69 | 5.7889 | 5.9212 | 0.022854
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515508 | SHLCSHT2 | 69 | 5.901 | 6.0358 | 0.022844
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515119 | SEAWAYS2 | 69 | 5.7749 | 5.906 | 0.022702
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515018 | ARCO PL2 | 69 | 5.7757 | 5.9066 | 0.022664
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515022 | PIPELIN2 | 69 | 5.7827 | 5.9136 | 0.022636
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515023 | SHELCSH2 | 69 | 5.8499 | 5.9823 | 0.022633
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515025 | EUCHEE 2 | 69 | 6.436 | 6.5805 | 0.022452
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515470 | SKPLCSH2 | 69 | 5.6759 | 5.8031 | 0.022411
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515027 | TIGERCK2 | 69 | 6.5632 | 6.6966 | 0.020325
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515574 | SPGVLLY4 | 138 | 10.491 | 10.7029 | 0.020198
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515028 | SVCPLTP2 | 69 | 6.4951 | 6.624 | 0.019846
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515016 | CHDRTAP2 | 69 | 4.6561 | 4.7452 | 0.019136
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515514 | KNIPE 4 | 138 | 7.9445 | 8.0833 | 0.017471
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515031 | SVCPLDR2 | 69 | 5.5167 | 5.6102 | 0.016949
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515047 | WARWICK4 | 138 | 10.3846 | 10.5483 | 0.015764
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515015 | SINDRUM2 | 69 | 3.5173 | 3.5684 | 0.014528
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515048 | KEYWEST4 | 138 | 5.7324 | 5.8006 | 0.011897
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515414 | ANTIOCH2 | 69 | 3.3865 | 3.4258 | 0.011605
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515369 | BELLCOW4 | 138 | 6.5038 | 6.5768 | 0.011224
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515011 | STILWTR4 | 138 | 13.9315 | 14.0722 | 0.010099
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515037 | PRNCVLT2 | 69 | 6.5286 | 6.5866 | 0.008884
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515030 | PRINCEV2 | 69 | 6.4068 | 6.4627 | 0.0087251
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515366 | WFROSST4 | 138 | 12.2847 | 12.3868 | 0.0083112
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 521107 | RSSVILE4 | 138 | 12.2847 | 12.3868 | 0.0083112
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515009 | MCELROY4 | 138 | 13.6114 | 13.7211 | 0.0080594
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515249 | BEGGS 4 | 138 | 5.4729 | 5.5141 | 0.007528
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515034 | BRISTOW2 | 69 | 5.7114 | 5.7533 | 0.0073362
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515235 | PECANCK7 | 345 | 21.3829 | 21.5268 | 0.0067297
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515242 | BLUEBEL4 | 138 | 16.6445 | 16.7529 | 0.0065127
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515200 | KELLYVL4 | 138 | 13.2901 | 13.3446 | 0.0041008
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515241 | BLUEBEL2 | 69 | 11.2247 | 11.2673 | 0.0037952
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515447 | MORISNT4 | 138 | 13.8859 | 13.9311 | 0.0032551
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515245 | LONESTR4 | 138 | 13.0189 | 13.0567 | 0.0029035
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 509758 | PRATTV-4 | 138 | 19.8477 | 19.9027 | 0.0027711
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515234 | PECANCK5 | 161 | 20.9267 | 20.9845 | 0.002762
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515247 | BEELINE4 | 138 | 21.592 | 21.6509 | 0.0027279
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515243 | BOWDEN 4 | 138 | 11.9167 | 11.9484 | 0.0026601
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 509815 | S.S.---4 | 138 | 27.7211 | 27.7896 | 0.002471
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515244 | HICKORY4 | 138 | 12.9855 | 13.0171 | 0.0024335
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 509896 | DENV_WTAP4 | 138 | 27.0461 | 27.1109 | 0.0023959
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515218 | POLECTP4 | 138 | 14.9557 | 14.9915 | 0.0023937
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 509812 | SHEFFD-4 | 138 | 25.0803 | 25.1346 | 0.002165
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515219 | POLECAT4 | 138 | 12.3767 | 12.4012 | 0.0019795
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515233 | PECANCK4 | 138 | 9.5555 | 9.5735 | 0.0018837
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515228 | 5TRIBES5 | 161 | 15.4215 | 15.4503 | 0.0018675
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 509739 | CARSN-T4 | 138 | 31.4964 | 31.5511 | 0.0017367
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515230 | AGENCY 5 | 161 | 14.0106 | 14.0335 | 0.0016345
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 509823 | WED-TAP4 | 138 | 18.6485 | 18.6767 | 0.0015122
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515236 | SAPULPA2 | 69 | 7.7468 | 7.7575 | 0.0013812
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515246 | BEELINE2 | 69 | 11.7156 | 11.729 | 0.0011438
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 509740 | UNIONAV4 | 138 | 20.4392 | 20.4622 | 0.0011253
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 509865 | CARSONT4 | 138 | 11.7252 | 11.7363 | 0.00094668
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 509749 | CARSN-C4 | 138 | 16.7592 | 16.7746 | 0.0009189
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 509832 | W.ED.-W4 | 138 | 11.3239 | 11.3342 | 0.00090958
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 509748 | DENVR-W4 | 138 | 9.4088 | 9.4166 | 0.00082901
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 509741 | CARSN-N4 | 138 | 9.1335 | 9.1403 | 0.00074451
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 509754 | WHORSE-4 | 138 | 3.8711 | 3.8724 | 0.00033582
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 509897 | WILDCT_TP4 | 138 | 3.8719 | 3.8732 | 0.00033575
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 509821 | HWY20-T4 | 138 | 3.8796 | 3.8809 | 0.00033509
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 509898 | WILDCAT_4 | 138 | 3.866 | 3.8672 | 0.0003104
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 509816 | S.S.---2 | 69 | 6.2283 | 6.23 | 0.00027295
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 509798 | HWY20--4 | 138 | 2.9668 | 2.9676 | 0.00026965
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 529306 | OMHOMNY4 | 138 | 2.49 | 2.4906 | 0.00024096
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 514927 | HSLEAST2 | 69 | 11.1732 | 11.175 | 0.0001611
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 509796 | DX----W2 | 69 | 3.745 | 3.7456 | 0.00016021
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515017 | CHANDLR2 | 69 | 1.7237 | 1.7237 | 0
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 589090 | GEN-2017-071 | 138 | 7.5805 | 8.2795 | 0.09221
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515417 | GRNWOOD4 | 138 | 7.845 | 8.5572 | 0.090784
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 589100 | GEN-2017-072 | 138 | 7.5805 | 8.2587 | 0.089466
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515033 | CUSHING4 | 138 | 7.0346 | 7.4039 | 0.052498
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515043 | GRTPLNS4 | 138 | 6.779 | 7.133 | 0.05222
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515453 | LNWOODT4 | 138 | 6.7539 | 7.0913 | 0.049956
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515401 | LINWOOD4 | 138 | 6.7099 | 7.0428 | 0.049613
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515416 | GRNWOOD2 | 69 | 8.1669 | 8.4418 | 0.03366
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515032 | CUSHING2 | 69 | 8.1882 | 8.433 | 0.029897
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515019 | HY99TAP2 | 69 | 7.048 | 7.2515 | 0.028873
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515021 | OAKGROV2 | 69 | 7.2682 | 7.4632 | 0.026829
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515035 | BRISTOW4 | 138 | 9.8092 | 10.0533 | 0.024885
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515026 | DRMRITE2 | 69 | 7.2387 | 7.4166 | 0.024576
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515675 | TRYON 4 | 138 | 9.1552 | 9.3776 | 0.024292
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515413 | CUSHOIL2 | 69 | 6.0365 | 6.1823 | 0.024153
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515039 | PAYNESB4 | 138 | 8.8061 | 9.0107 | 0.023234
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515020 | PLCNTRT2 | 69 | 5.7889 | 5.9212 | 0.022854
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515508 | SHLCSHT2 | 69 | 5.901 | 6.0358 | 0.022844
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515119 | SEAWAYS2 | 69 | 5.7749 | 5.906 | 0.022702
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515018 | ARCO PL2 | 69 | 5.7757 | 5.9066 | 0.022664
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515022 | PIPELIN2 | 69 | 5.7827 | 5.9136 | 0.022636
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515023 | SHELCSH2 | 69 | 5.8499 | 5.9823 | 0.022633
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515025 | EUCHEE 2 | 69 | 6.436 | 6.5805 | 0.022452
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515470 | SKPLCSH2 | 69 | 5.6759 | 5.8031 | 0.022411
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515027 | TIGERCK2 | 69 | 6.5632 | 6.6966 | 0.020325
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515574 | SPGVLLY4 | 138 | 10.491 | 10.7029 | 0.020198
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515028 | SVCPLTP2 | 69 | 6.4951 | 6.624 | 0.019846
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515016 | CHDRTAP2 | 69 | 4.6561 | 4.7452 | 0.019136
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515514 | KNIPE 4 | 138 | 7.9445 | 8.0833 | 0.017471
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515031 | SVCPLDR2 | 69 | 5.5167 | 5.6102 | 0.016949
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515047 | WARWICK4 | 138 | 10.3846 | 10.5483 | 0.015764
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515015 | SINDRUM2 | 69 | 3.5173 | 3.5684 | 0.014528
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515048 | KEYWEST4 | 138 | 5.7324 | 5.8006 | 0.011897
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515414 | ANTIOCH2 | 69 | 3.3865 | 3.4258 | 0.011605
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515369 | BELLCOW4 | 138 | 6.5038 | 6.5768 | 0.011224
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515011 | STILWTR4 | 138 | 13.9315 | 14.0722 | 0.010099
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515037 | PRNCVLT2 | 69 | 6.5286 | 6.5866 | 0.008884
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515030 | PRINCEV2 | 69 | 6.4068 | 6.4627 | 0.0087251
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515366 | WFROSST4 | 138 | 12.2847 | 12.3868 | 0.0083112
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 521107 | RSSVILE4 | 138 | 12.2847 | 12.3868 | 0.0083112
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515009 | MCELROY4 | 138 | 13.6114 | 13.7211 | 0.0080594
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515249 | BEGGS 4 | 138 | 5.4729 | 5.5141 | 0.007528
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515034 | BRISTOW2 | 69 | 5.7114 | 5.7533 | 0.0073362
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515235 | PECANCK7 | 345 | 21.3829 | 21.5268 | 0.0067297
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515242 | BLUEBEL4 | 138 | 16.6445 | 16.7529 | 0.0065127
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515200 | KELLYVL4 | 138 | 13.2901 | 13.3446 | 0.0041008
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515241 | BLUEBEL2 | 69 | 11.2247 | 11.2673 | 0.0037952
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515447 | MORISNT4 | 138 | 13.8859 | 13.9311 | 0.0032551
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515245 | LONESTR4 | 138 | 13.0189 | 13.0567 | 0.0029035
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 509758 | PRATTV-4 | 138 | 19.8477 | 19.9027 | 0.0027711
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515234 | PECANCK5 | 161 | 20.9267 | 20.9845 | 0.002762
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515247 | BEELINE4 | 138 | 21.592 | 21.6509 | 0.0027279
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515243 | BOWDEN 4 | 138 | 11.9167 | 11.9484 | 0.0026601
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 509815 | S.S.---4 | 138 | 27.7211 | 27.7896 | 0.002471
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515244 | HICKORY4 | 138 | 12.9855 | 13.0171 | 0.0024335
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 509896 | DENV_WTAP4 | 138 | 27.0461 | 27.1109 | 0.0023959
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515218 | POLECTP4 | 138 | 14.9557 | 14.9915 | 0.0023937
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 509812 | SHEFFD-4 | 138 | 25.0803 | 25.1346 | 0.002165
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515219 | POLECAT4 | 138 | 12.3767 | 12.4012 | 0.0019795
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515233 | PECANCK4 | 138 | 9.5555 | 9.5735 | 0.0018837
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515228 | 5TRIBES5 | 161 | 15.4215 | 15.4503 | 0.0018675
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 509739 | CARSN-T4 | 138 | 31.4964 | 31.5511 | 0.0017367
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515230 | AGENCY 5 | 161 | 14.0106 | 14.0335 | 0.0016345
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 509823 | WED-TAP4 | 138 | 18.6485 | 18.6767 | 0.0015122
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515236 | SAPULPA2 | 69 | 7.7468 | 7.7575 | 0.0013812
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515246 | BEELINE2 | 69 | 11.7156 | 11.729 | 0.0011438
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 509740 | UNIONAV4 | 138 | 20.4392 | 20.4622 | 0.0011253
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 509865 | CARSONT4 | 138 | 11.7252 | 11.7363 | 0.00094668
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 509749 | CARSN-C4 | 138 | 16.7592 | 16.7746 | 0.0009189
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 509832 | W.ED.-W4 | 138 | 11.3239 | 11.3342 | 0.00090958
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 509748 | DENVR-W4 | 138 | 9.4088 | 9.4166 | 0.00082901
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 509741 | CARSN-N4 | 138 | 9.1335 | 9.1403 | 0.00074451
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 509754 | WHORSE-4 | 138 | 3.8711 | 3.8724 | 0.00033582
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 509897 | WILDCT_TP4 | 138 | 3.8719 | 3.8732 | 0.00033575
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 509821 | HWY20-T4 | 138 | 3.8796 | 3.8809 | 0.00033509
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 509898 | WILDCAT_4 | 138 | 3.866 | 3.8672 | 0.0003104
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 509816 | S.S.---2 | 69 | 6.2283 | 6.23 | 0.00027295
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 509798 | HWY20--4 | 138 | 2.9668 | 2.9676 | 0.00026965
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 529306 | OMHOMNY4 | 138 | 2.49 | 2.4906 | 0.00024096
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 514927 | HSLEAST2 | 69 | 11.1732 | 11.175 | 0.0001611
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 509796 | DX----W2 | 69 | 3.745 | 3.7456 | 0.00016021
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515017 | CHANDLR2 | 69 | 1.7237 | 1.7237 | 0
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 510437 | ROCKPT-4 | 138 | 6.5227 | 6.8527 | 0.050593
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509752 | INOLATP4 | 138 | 8.7677 | 9.0163 | 0.028354
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509736 | INOLA 4 | 138 | 7.5297 | 7.7124 | 0.024264
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 589110 | GEN-2017-073 | 161 | 13.8689 | 14.1649 | 0.021343
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 588990 | GEN-2017-061 | 161 | 21.0425 | 21.4795 | 0.020767
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512629 | DRYGULCH5 | 161 | 14.9318 | 15.2351 | 0.020312
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512742 | WMAIN ST5 | 161 | 26.1139 | 26.5974 | 0.018515
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512757 | NWMAID5 | 161 | 25.7016 | 26.1342 | 0.016832
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512648 | MAID 5 | 161 | 42.0337 | 42.7216 | 0.016365
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512656 | GRDA1 5 | 161 | 41.696 | 42.3541 | 0.015783
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512760 | GERALDGAY5 | 161 | 26.7603 | 27.1519 | 0.014634
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512635 | KERR GR5 | 161 | 27.3021 | 27.58 | 0.010179
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512770 | KERR BRK1 5 | 161 | 27.3021 | 27.58 | 0.010179
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512771 | KERR BRK4 5 | 161 | 27.3021 | 27.58 | 0.010179
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509790 | CATOOSA4 | 138 | 34.4428 | 34.7238 | 0.0081585
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 300739 | 7BLACKBERRY | 345 | 14.7665 | 14.8807 | 0.0077337
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512654 | PENSA 5 | 161 | 12.632 | 12.729 | 0.0076789
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512671 | HUNT 2 | 69 | 13.2212 | 13.3129 | 0.0069358
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512634 | KERR GR3 | 115 | 16.4433 | 16.551 | 0.0065498
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 510423 | L GROVE3 | 115 | 15.3902 | 15.4904 | 0.0065106
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512650 | GRDA1 7 | 345 | 25.9865 | 26.1539 | 0.0064418
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512638 | CATSAGR5 | 161 | 23.1122 | 23.2493 | 0.0059319
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512805 | SALNCRK5 | 161 | 17.8109 | 17.9164 | 0.0059233
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512865 | GREC TAP5 | 345 | 24.9005 | 25.0478 | 0.0059155
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 300740 | 7SPORTSMAN | 345 | 23.6136 | 23.749 | 0.005734
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512812 | ARMIN 2 | 69 | 10.8395 | 10.9011 | 0.0056829
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512686 | SALINA 5 | 161 | 17.2179 | 17.3153 | 0.0056569
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512669 | KETCHUM5 | 161 | 10.2578 | 10.3142 | 0.0054983
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509804 | LLANETP4 | 138 | 26.3863 | 26.5258 | 0.0052868
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512699 | PRYORCHEM2 | 69 | 12.5184 | 12.5832 | 0.0051764
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512661 | CPPTAP 2 | 69 | 12.6182 | 12.6789 | 0.0048105
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509770 | LLAN WT4 | 138 | 23.6891 | 23.8015 | 0.0047448
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512681 | AMERCAST S2 | 69 | 12.934 | 12.9919 | 0.0044766
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512625 | MAIDTP2 | 69 | 11.6454 | 11.697 | 0.0044309
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 300069 | 5CHOTEAU1 | 161 | 40.4609 | 40.6388 | 0.0043968
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 301348 | 5CHOTEAU2 | 161 | 40.4609 | 40.6388 | 0.0043968
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509771 | LLAN ET4 | 138 | 23.6336 | 23.7353 | 0.0043032
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 300741 | 5SPORTSMAN | 161 | 38.9761 | 39.1423 | 0.0042642
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512626 | MAID 2 | 69 | 14.1113 | 14.1698 | 0.0041456
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509720 | LLANE-W4 | 138 | 19.2616 | 19.3358 | 0.0038522
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509892 | 141PINE4 | 138 | 19.8285 | 19.9044 | 0.0038278
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512727 | GRDA1 2 | 69 | 12.0314 | 12.0774 | 0.0038233
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 300274 | 5LOCSTGV | 161 | 13.111 | 13.1594 | 0.0036916
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509728 | LLANE-E4 | 138 | 19.325 | 19.3929 | 0.0035136
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509841 | PCATSAT4 | 138 | 17.472 | 17.5299 | 0.0033139
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509852 | T.NO.--7 | 345 | 22.5867 | 22.6594 | 0.0032187
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509899 | BIRDCREE-4 | 138 | 16.9241 | 16.9784 | 0.0032084
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512698 | REDDEN 2 | 69 | 10.3792 | 10.4108 | 0.0030446
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509787 | DAWSN-N4 | 138 | 17.2228 | 17.2727 | 0.0028973
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 300993 | 5ELMCRK | 161 | 12.8554 | 12.8914 | 0.0028004
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512637 | 412SUB 5 | 161 | 11.4637 | 11.4954 | 0.0027653
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512632 | AFTON 5 | 161 | 8.1359 | 8.1583 | 0.0027532
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509835 | TERNITP4 | 138 | 15.6551 | 15.6979 | 0.0027339
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509886 | E41ST_W4 | 138 | 20.9176 | 20.9735 | 0.0026724
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512685 | CASTING TAP2 | 69 | 9.091 | 9.1152 | 0.002662
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512683 | AMERCAST N2 | 69 | 8.1658 | 8.1853 | 0.002388
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 301344 | 5CDRCRST | 161 | 10.4498 | 10.4741 | 0.0023254
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512651 | CLARMR 5 | 161 | 12.51 | 12.5388 | 0.0023022
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509723 | TER-NIT4 | 138 | 12.9515 | 12.9807 | 0.0022546
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512750 | TONECE7 | 345 | 14.5005 | 14.5329 | 0.0022344
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512627 | COLINS 5 | 161 | 11.7421 | 11.7681 | 0.0022143
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 506935 | FLINTCR7 | 345 | 14.6814 | 14.7134 | 0.0021796
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 547487 | HOC404 5 | 161 | 12.8473 | 12.8753 | 0.0021794
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512628 | PENSA 2 | 69 | 13.0379 | 13.0661 | 0.0021629
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509786 | BA.N-ST4 | 138 | 23.2255 | 23.2754 | 0.0021485
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509725 | PCATOSA4 | 138 | 11.2036 | 11.2273 | 0.0021154
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509887 | OWAS88_4 | 138 | 16.3829 | 16.4174 | 0.0021059
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512631 | MIAMI 5 | 161 | 9.1774 | 9.196 | 0.0020267
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509843 | OWASO2_4 | 138 | 13.8307 | 13.8582 | 0.0019883
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509839 | CDC-ET 4 | 138 | 18.3658 | 18.4023 | 0.0019874
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 300997 | 5KETONVL | 161 | 10.4336 | 10.4537 | 0.0019265
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512714 | KANSATP5 | 161 | 11.3325 | 11.3539 | 0.0018884
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512716 | KANSAS 5 | 161 | 10.7727 | 10.7921 | 0.0018008
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509854 | VERDIGS4 | 138 | 13.5268 | 13.5511 | 0.0017964
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512700 | WAGNOR 5 | 161 | 9.4446 | 9.4607 | 0.0017047
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512642 | SILSPWW5 | 161 | 14.2884 | 14.3105 | 0.0015467
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512633 | AFTON 2 | 69 | 10.147 | 10.1618 | 0.0014586
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509715 | CDC 4 | 138 | 13.2464 | 13.2654 | 0.0014344
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509714 | CIP 4 | 138 | 13.2554 | 13.2744 | 0.0014334
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 515252 | ROSSLAK5 | 161 | 13.2325 | 13.251 | 0.0013981
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512708 | FAIRTAP2 | 69 | 9.8061 | 9.8195 | 0.0013665
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 300795 | 4OOLOGAH | 138 | 20.3525 | 20.3801 | 0.0013561
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512707 | CLARMR 4 | 138 | 13.1884 | 13.2061 | 0.0013421
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512672 | EXPL TP2 | 69 | 8.2196 | 8.2305 | 0.0013261
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512640 | OKAYGR 5 | 161 | 9.5822 | 9.5949 | 0.0013254
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512655 | TAHLQH 5 | 161 | 10.1269 | 10.1399 | 0.0012837
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512751 | TONECE5 | 161 | 14.7089 | 14.7264 | 0.0011898
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 505560 | FT GIB 5 | 161 | 10.332 | 10.3442 | 0.0011808
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512630 | MIAMI 2 | 69 | 11.8766 | 11.8906 | 0.0011788
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 301455 | 2JAY (AECI) | 69 | 5.8661 | 5.873 | 0.0011762
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 301307 | 5PARK | 161 | 9.0106 | 9.0209 | 0.0011431
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512705 | COLLINS4 | 138 | 8.3164 | 8.3258 | 0.0011303
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509799 | CATOOSA2 | 69 | 10.4127 | 10.4244 | 0.0011236
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512692 | CLEORTP2 | 69 | 7.3058 | 7.314 | 0.0011224
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 301451 | 2GRAY TP | 69 | 6.8768 | 6.8845 | 0.0011197
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509721 | BA.NO-S4 | 138 | 12.0065 | 12.0198 | 0.0011077
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 300766 | 5BRIGGSTP | 161 | 8.2541 | 8.2627 | 0.0010419
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 510415 | AFTONTP2 | 69 | 6.4472 | 6.4539 | 0.0010392
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512679 | CLARMR 2 | 69 | 12.3636 | 12.3762 | 0.0010191
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509794 | BCIRCLE2 | 69 | 9.147 | 9.1557 | 0.00095113
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 301453 | 2ZENA TP | 69 | 5.4709 | 5.476 | 0.0009322
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 301452 | 2GRAY | 69 | 5.7002 | 5.7055 | 0.00092979
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512624 | CENTLFT2 | 69 | 11.0777 | 11.0879 | 0.00092077
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 300767 | 5BRIGGS | 161 | 7.1793 | 7.1858 | 0.00090538
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 510427 | A-CONT 2 | 69 | 5.5085 | 5.5133 | 0.00087138
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 301462 | 2COMMNEO | 69 | 8.2757 | 8.2825 | 0.00082168
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 510428 | AFTN-EX2 | 69 | 5.1862 | 5.1904 | 0.00080984
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512870 | COLNSGR2 | 69 | 9.9201 | 9.9272 | 0.00071572
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 300992 | 2COLINS | 69 | 9.92 | 9.927 | 0.00070565
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 301345 | 2CDRCRST | 69 | 8.0233 | 8.0285 | 0.00064811
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 301454 | 2ZENA | 69 | 3.7395 | 3.7419 | 0.0006418
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 301002 | 2SEQUOYA | 69 | 6.7757 | 6.7799 | 0.00061986
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512695 | ADARNEO2 | 69 | 4.7363 | 4.7392 | 0.00061229
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512647 | TAHLQH 2 | 69 | 10.9979 | 11.0046 | 0.00060921
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 301460 | 2CLEORA | 69 | 3.8107 | 3.8129 | 0.00057732
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512696 | PARKER 2 | 69 | 4.4129 | 4.4152 | 0.0005212
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512646 | OKAYGR 2 | 69 | 9.5995 | 9.6045 | 0.00052086
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512725 | CHELSGR2 | 69 | 4.4584 | 4.4606 | 0.00049345
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512804 | RDFRNTP2 | 69 | 8.6747 | 8.6789 | 0.00048417
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 510409 | SAILBOA2 | 69 | 3.5802 | 3.5819 | 0.00047483
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 515014 | REDFERN2 | 69 | 8.3502 | 8.3541 | 0.00046705
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 300962 | 2PEGGS | 69 | 6.1001 | 6.1029 | 0.00045901
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 301472 | 2PARK | 69 | 8.171 | 8.1747 | 0.00045282
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512697 | WAGNOR 2 | 69 | 6.773 | 6.7759 | 0.00042817
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512690 | WAGNRTP2 | 69 | 6.795 | 6.7978 | 0.00041207
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512759 | WAGCTY22 | 69 | 6.229 | 6.2314 | 0.00038529
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512823 | TAH33CT2 | 69 | 7.0182 | 7.0209 | 0.00038471
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 301467 | 2NEWPORT | 69 | 2.6209 | 2.6219 | 0.00038155
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 301465 | 2MONKEY | 69 | 2.3385 | 2.3393 | 0.0003421
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 300960 | 2LOWERY | 69 | 4.7054 | 4.707 | 0.00034003
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 515527 | HWY59TP5 | 161 | 15.6992 | 15.7041 | 0.00031212
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 504191 | HWY59 5 | 161 | 15.5028 | 15.5075 | 0.00030317
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 300972 | 2WAGNERW | 69 | 4.4124 | 4.4136 | 0.00027196
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 301464 | 2PYRCRNR | 69 | 0.9905 | 0.9907 | 0.00020192
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512765 | PYRCRNRTP2 | 69 | 1.6063 | 1.6066 | 0.00018676
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 300955 | 2COWETA | 69 | 2.3983 | 2.3987 | 0.00016678
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512753 | TONNEC2 | 69 | 4.7099 | 4.7106 | 0.00014862
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 300991 | 2CHILDRS | 69 | 1.38 | 1.3802 | 0.00014493
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512723 | CHILDRS2 | 69 | 1.3802 | 1.3804 | 0.00014491
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512728 | ARKLIN2 | 69 | 3.6464 | 3.6469 | 0.00013712
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512756 | TONECESTR2 | 69 | 3.7544 | 3.7549 | 0.00013318
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512745 | SSLINC2 | 69 | 2.7443 | 2.7446 | 0.00010932
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 300958 | 2HIGHLND | 69 | 1.8441 | 1.8443 | 0.00010845
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 301001 | 2SCOFEYV | 69 | 0.9648 | 0.9649 | 0.00010365
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512747 | SSNEWN2 | 69 | 3.034 | 3.0343 | 9.8879e-05
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512746 | SSNORT2 | 69 | 2.7976 | 2.7978 | 7.149e-05
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 589150 | GEN-2017-077 | 138 | 5.192 | 5.8373 | 0.12429
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 589154 | G17-077-TAP | 138 | 5.5749 | 6.2387 | 0.11907
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510431 | PRY_CRK4 | 138 | 5.5867 | 6.2236 | 0.114
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510366 | MCARBDE4 | 138 | 5.7078 | 6.3044 | 0.10452
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510401 | EXCLART4 | 138 | 5.5966 | 6.1696 | 0.10238
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510419 | PRY-JCT4 | 138 | 6.0208 | 6.6262 | 0.10055
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 589120 | GEN-2017-074 | 138 | 5.9969 | 6.5998 | 0.10054
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510373 | CHOUTEA4 | 138 | 5.7192 | 6.1945 | 0.083106
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510405 | EXPCLAR4 | 138 | 4.221 | 4.5404 | 0.075669
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510398 | BIRDHOL4 | 138 | 4.2813 | 4.4412 | 0.037348
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510400 | PRY-JCT2 | 69 | 13.2696 | 13.7242 | 0.034259
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510421 | JAY 4 | 138 | 4.2956 | 4.3849 | 0.020789
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 512810 | PRYORC12 | 69 | 10.4784 | 10.6227 | 0.013771
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510402 | GROVE 4 | 138 | 5.0487 | 5.1106 | 0.012261
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510387 | ADAIR--2 | 69 | 6.1071 | 6.1706 | 0.010398
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 512719 | COWSKIN 4 | 138 | 4.3016 | 4.3445 | 0.009973
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510407 | PRY-JCT3 | 115 | 7.8619 | 7.9375 | 0.009616
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 512622 | PRYORC32 | 69 | 9.6682 | 9.7576 | 0.0092468
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 512639 | PRY0RC22 | 69 | 9.9798 | 10.06 | 0.0080362
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510408 | PCP-TAP2 | 69 | 8.091 | 8.1527 | 0.0076258
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510399 | LSTAR--3 | 115 | 9.6373 | 9.7099 | 0.0075332
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 512671 | HUNT 2 | 69 | 13.2212 | 13.3129 | 0.0069358
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 512634 | KERR GR3 | 115 | 16.4433 | 16.551 | 0.0065498
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510423 | L GROVE3 | 115 | 15.3902 | 15.4904 | 0.0065106
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510411 | GROVE 5 | 161 | 5.6048 | 5.6409 | 0.0064409
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510416 | HUNTAP-2 | 69 | 8.9456 | 8.9978 | 0.0058353
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 512812 | ARMIN 2 | 69 | 10.8395 | 10.9011 | 0.0056829
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510425 | NEOHOME2 | 69 | 5.7529 | 5.7837 | 0.0053538
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510426 | PCPIPE 2 | 69 | 4.3118 | 4.3289 | 0.0039659
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 547496 | NOL435 5 | 161 | 9.6195 | 9.6542 | 0.0036073
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510393 | CHOUTEA2 | 69 | 5.5605 | 5.5774 | 0.0030393
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510404 | VINITA-2 | 69 | 6.7204 | 6.7351 | 0.0021874
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 512717 | COWSKIN2 | 69 | 3.8702 | 3.8778 | 0.0019637
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 512680 | ESH TP 2 | 69 | 6.4458 | 6.458 | 0.0018927
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 300983 | 2VINITAHQ | 69 | 5.6053 | 5.6146 | 0.0016591
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 301468 | 2ESHOSP | 69 | 5.5826 | 5.5918 | 0.001648
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510418 | VINTAJC2 | 69 | 6.3726 | 6.3831 | 0.0016477
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 512673 | VINEOTP2 | 69 | 6.3038 | 6.3139 | 0.0016022
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 301463 | 2TURKEY | 69 | 3.1541 | 3.1591 | 0.0015852
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 512677 | VIN NEO2 | 69 | 5.6156 | 5.6235 | 0.0014068
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510417 | VINTAJC4 | 138 | 4.9879 | 4.9924 | 0.00090218
GEN-2017-077 | Central | 08 - North Oklahoma/South Central Kansas | 589150 | GEN-2017-077 | 138 | 5.192 | 5.8373 | 0.12429
GEN-2017-077 | Central | 08 - North Oklahoma/South Central Kansas | 589154 | G17-077-TAP | 138 | 5.5749 | 6.2387 | 0.11907
GEN-2017-077 | Central | 08 - North Oklahoma/South Central Kansas | 510431 | PRY_CRK4 | 138 | 5.5867 | 6.2236 | 0.114
GEN-2017-077 | Central | 08 - North Oklahoma/South Central Kansas | 510366 | MCARBDE4 | 138 | 5.7078 | 6.3044 | 0.10452
GEN-2017-077 | Central | 08 - North Oklahoma/South Central Kansas | 510401 | EXCLART4 | 138 | 5.5966 | 6.1696 | 0.10238
GEN-2017-077 | Central | 08 - North Oklahoma/South Central Kansas | 510419 | PRY-JCT4 | 138 | 6.0208 | 6.6262 | 0.10055
GEN-2017-077 | Central | 08 - North Oklahoma/South Central Kansas | 589120 | GEN-2017-074 | 138 | 5.9969 | 6.5998 | 0.10054
GEN-2017-077 | Central | 08 - North Oklahoma/South Central Kansas | 510373 | CHOUTEA4 | 138 | 5.7192 | 6.1945 | 0.083106
GEN-2017-077 | Central | 08 - North Oklahoma/South Central Kansas | 510405 | EXPCLAR4 | 138 | 4.221 | 4.5404 | 0.075669
GEN-2017-077 | Central | 08 - North Oklahoma/South Central Kansas | 510437 | ROCKPT-4 | 138 | 6.5227 | 6.8527 | 0.050593
GEN-2017-077 | Central | 08 - North Oklahoma/South Central Kansas | 510398 | BIRDHOL4 | 138 | 4.2813 | 4.4412 | 0.037348
GEN-2017-077 | Central | 08 - North Oklahoma/South Central Kansas | 510400 | PRY-JCT2 | 69 | 13.2696 | 13.7242 | 0.034259
GEN-2017-077 | Central | 08 - North Oklahoma/South Central Kansas | 509752 | INOLATP4 | 138 | 8.7677 | 9.0163 | 0.028354
GEN-2017-077 | Central | 08 - North Oklahoma/South Central Kansas | 509736 | INOLA 4 | 138 | 7.5297 | 7.7124 | 0.024264
GEN-2017-077 | Central | 08 - North Oklahoma/South Central Kansas | 510421 | JAY 4 | 138 | 4.2956 | 4.3849 | 0.020789
GEN-2017-077 | Central | 08 - North Oklahoma/South Central Kansas | 512810 | PRYORC12 | 69 | 10.4784 | 10.6227 | 0.013771
GEN-2017-077 | Central | 08 - North Oklahoma/South Central Kansas | 510387 | ADAIR--2 | 69 | 6.1071 | 6.1706 | 0.010398
GEN-2017-077 | Central | 08 - North Oklahoma/South Central Kansas | 510407 | PRY-JCT3 | 115 | 7.8619 | 7.9375 | 0.009616
GEN-2017-077 | Central | 08 - North Oklahoma/South Central Kansas | 509790 | CATOOSA4 | 138 | 34.4428 | 34.7238 | 0.0081585
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 589240 | GEN-2017-086 | 345 | 9.9635 | 10.5552 | 0.059387
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532798 | VIOLA 7 | 345 | 13.8783 | 14.4624 | 0.042087
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533075 | VIOLA 4 | 138 | 24.0364 | 24.4751 | 0.018251
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 588364 | G16-153-TAP | 345 | 7.4618 | 7.5924 | 0.017502
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 588360 | GEN-2016-153 | 345 | 7.1436 | 7.2624 | 0.01663
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532792 | FR2EAST7 | 345 | 6.7405 | 6.843 | 0.015207
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 515543 | RENFROW7 | 345 | 12.3872 | 12.5431 | 0.012586
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532795 | FR2WEST7 | 345 | 5.3886 | 5.4506 | 0.011506
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532780 | CANEYRV7 | 345 | 9.847 | 9.9559 | 0.011059
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 515646 | GRNTWD 7 | 345 | 10.8855 | 11.0042 | 0.010904
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532781 | CANEYWF7 | 345 | 9.5894 | 9.692 | 0.010699
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 578530 | FR3HV | 345 | 4.9398 | 4.9915 | 0.010466
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532796 | WICHITA7 | 345 | 24.1532 | 24.3835 | 0.009535
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532800 | LATHAMS7 | 345 | 10.4136 | 10.5083 | 0.0090939
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 539009 | CONWAY | 138 | 12.6276 | 12.7355 | 0.0085448
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 539008 | MILAN_GOAB | 138 | 11.8476 | 11.9472 | 0.0084068
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532801 | ELKRVR17 | 345 | 9.1912 | 9.2645 | 0.007975
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 589060 | GEN-2017-068 | 345 | 20.1103 | 20.2698 | 0.0079313
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 539676 | MILAN 4 | 138 | 10.4656 | 10.5429 | 0.0073861
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532782 | BUFFALO7 | 345 | 20.5614 | 20.7023 | 0.0068526
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 539675 | MILANTP4 | 138 | 9.8621 | 9.9226 | 0.0061346
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 515476 | HUNTERS7 | 345 | 13.4924 | 13.573 | 0.0059737
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 515477 | CHSHLMV7 | 345 | 13.4742 | 13.5546 | 0.005967
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533044 | GILL E 4 | 138 | 21.9045 | 22.0344 | 0.0059303
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533045 | GILL W 4 | 138 | 21.9045 | 22.0344 | 0.0059303
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533046 | GILL S 4 | 138 | 21.9045 | 22.0344 | 0.0059303
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533047 | GILL 4 | 138 | 21.9045 | 22.0344 | 0.0059303
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532794 | ROSEHIL7 | 345 | 18.9572 | 19.0665 | 0.0057656
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532791 | BENTON 7 | 345 | 19.6359 | 19.7468 | 0.0056478
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533036 | CLEARWT4 | 138 | 14.0937 | 14.1705 | 0.0054492
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533071 | WACO S 4 | 138 | 19.1512 | 19.2466 | 0.0049814
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533072 | WACO 4 | 138 | 19.1512 | 19.2466 | 0.0049814
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 587500 | GEN-2016-073 | 345 | 15.119 | 15.1939 | 0.004954
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533040 | EVANS N4 | 138 | 33.3755 | 33.5322 | 0.0046951
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533041 | EVANS S4 | 138 | 33.3755 | 33.5322 | 0.0046951
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533062 | ROSEHIL4 | 138 | 30.8868 | 31.0133 | 0.0040956
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533039 | ELPASO 4 | 138 | 24.1926 | 24.2863 | 0.0038731
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533059 | ELPASOE4 | 138 | 24.1926 | 24.2863 | 0.0038731
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 515544 | RENFROW4 | 138 | 14.3714 | 14.4241 | 0.003667
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533074 | 45TH ST4 | 138 | 24.1728 | 24.2608 | 0.0036405
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533029 | 59TH ST4 | 138 | 17.0897 | 17.1516 | 0.0036221
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532986 | BENTON 4 | 138 | 27.8896 | 27.9879 | 0.0035246
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533795 | GILL E 2 | 69 | 29.2006 | 29.301 | 0.0034383
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533796 | GILL W 2 | 69 | 29.2006 | 29.301 | 0.0034383
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533051 | INTERST4 | 138 | 15.7061 | 15.7592 | 0.0033809
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533049 | HOOVERN4 | 138 | 17.1453 | 17.2018 | 0.0032954
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 539003 | CLDWELL4 | 138 | 5.5937 | 5.6121 | 0.0032894
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533038 | COWSKIN4 | 138 | 17.5293 | 17.5823 | 0.0030235
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532991 | WEAVER 4 | 138 | 21.7367 | 21.8021 | 0.0030087
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533035 | CHISHLM4 | 138 | 21.2936 | 21.3567 | 0.0029633
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533053 | LAKERDG4 | 138 | 17.2997 | 17.3508 | 0.0029538
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533054 | MAIZE 4 | 138 | 21.0644 | 21.1262 | 0.0029339
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533068 | STEARMN4 | 138 | 19.1751 | 19.2296 | 0.0028422
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 514715 | WOODRNG7 | 345 | 19.0903 | 19.1426 | 0.0027396
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533052 | PARKCTY4 | 138 | 20.1019 | 20.1569 | 0.0027361
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533060 | NOEASTE4 | 138 | 20.2888 | 20.3433 | 0.0026862
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533065 | SG12COL4 | 138 | 19.7318 | 19.7841 | 0.0026505
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533042 | FARBER 4 | 138 | 15.7644 | 15.806 | 0.0026389
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 515569 | MDFRDTP4 | 138 | 11.4762 | 11.5063 | 0.0026228
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533851 | VULCTP 2 | 69 | 22.0309 | 22.0878 | 0.0025827
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533064 | 17TH 4 | 138 | 17.2325 | 17.2761 | 0.0025301
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 588320 | GEN-2016-162 | 345 | 9.7523 | 9.7768 | 0.0025122
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533024 | 29TH 4 | 138 | 19.377 | 19.4255 | 0.002503
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 520409 | WFEC_RNFRO4 | 138 | 10.6021 | 10.628 | 0.0024429
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532988 | BELAIRE4 | 138 | 18.7482 | 18.7936 | 0.0024216
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533037 | COMOTAR4 | 138 | 18.4588 | 18.5033 | 0.0024108
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 539668 | HARPER 4 | 138 | 7.2078 | 7.2244 | 0.0023031
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 539002 | BLF-CRK4 | 138 | 4.6999 | 4.7107 | 0.0022979
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532984 | SUMNER 4 | 138 | 10.2243 | 10.2477 | 0.0022887
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533850 | VULCAN 2 | 69 | 18.7158 | 18.757 | 0.0022013
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 588330 | GEN-2016-163 | 345 | 8.6195 | 8.6384 | 0.0021927
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 560053 | G15-052T | 345 | 13.1034 | 13.1318 | 0.0021674
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 584900 | GEN-2015-052 | 345 | 13.0534 | 13.0815 | 0.0021527
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 588630 | GEN-2017-018 | 345 | 16.3709 | 16.4054 | 0.0021074
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 539801 | THISTLE7 | 345 | 16.3709 | 16.4054 | 0.0021074
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533798 | GILLJCT2 | 69 | 20.4559 | 20.4989 | 0.0021021
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533813 | MACARTH2 | 69 | 21.0946 | 21.1389 | 0.0021001
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 539001 | ANTHONY4 | 138 | 5.0166 | 5.0268 | 0.0020332
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532982 | OXFORD 4 | 138 | 9.3635 | 9.3817 | 0.0019437
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 562476 | G14-001-TAP | 345 | 10.6079 | 10.6282 | 0.0019137
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533063 | SC10BEL4 | 138 | 9.6835 | 9.702 | 0.0019105
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532797 | WOLFCRK7 | 345 | 18.0814 | 18.1154 | 0.0018804
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532783 | KINGMAN7 | 345 | 6.821 | 6.8327 | 0.0017153
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 522397 | MEDFORD4 | 138 | 7.4872 | 7.5 | 0.0017096
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 542981 | LACYGNE7 | 345 | 24.761 | 24.8029 | 0.0016922
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532771 | RENO 7 | 345 | 12.6248 | 12.6459 | 0.0016713
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 543629 | LACYGNE11_7 | 345 | 24.1469 | 24.1868 | 0.0016524
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 543632 | LACYGNE22_7 | 345 | 24.1469 | 24.1868 | 0.0016524
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532799 | WAVERLY7 | 345 | 16.0356 | 16.0608 | 0.0015715
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533804 | HAYSVJN2 | 69 | 13.5493 | 13.5691 | 0.0014613
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 515546 | GRANTCO4 | 138 | 6.4548 | 6.4642 | 0.0014563
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533786 | CHISHLM2 | 69 | 19.7124 | 19.7409 | 0.0014458
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 560084 | G16-061-TAP | 345 | 16.1024 | 16.125 | 0.0014035
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 587410 | GEN-2016-061 | 345 | 16.1024 | 16.125 | 0.0014035
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532990 | MIDIAN 4 | 138 | 10.5446 | 10.5589 | 0.0013561
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532784 | NINN1WF7 | 345 | 5.6816 | 5.6893 | 0.0013553
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532987 | BUTLER 4 | 138 | 10.362 | 10.3759 | 0.0013414
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532802 | WAVERTX7 | 345 | 13.4196 | 13.437 | 0.0012966
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533015 | BENTLEY4 | 138 | 10.8046 | 10.8186 | 0.0012957
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 539000 | RAGO 4 | 138 | 3.9456 | 3.9506 | 0.0012672
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 514803 | SOONER 7 | 345 | 27.048 | 27.0822 | 0.0012644
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 539804 | THISTLE4 | 138 | 17.4802 | 17.502 | 0.0012471
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 583850 | GEN-2014-001 | 345 | 7.0819 | 7.0906 | 0.0012285
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532992 | TIMBJCT4 | 138 | 5.8655 | 5.8727 | 0.0012275
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 539638 | FLATRDG4 | 138 | 15.5121 | 15.5308 | 0.0012055
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 585250 | GEN-2015-090 | 345 | 5.0769 | 5.0829 | 0.0011818
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 514825 | KAYWIND7 | 345 | 12.6052 | 12.6199 | 0.0011662
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 515621 | OPENSKY7 | 345 | 12.64 | 12.6547 | 0.001163
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 522398 | PONDCRK4 | 138 | 5.091 | 5.0969 | 0.0011589
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 515877 | REDDIRT7 | 345 | 18.0507 | 18.0716 | 0.0011578
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 515875 | REDNGTN7 | 345 | 18.0549 | 18.0758 | 0.0011576
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 515426 | RDRUNNR4 | 138 | 8.4138 | 8.4234 | 0.001141
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532985 | TCROCK 4 | 138 | 5.4745 | 5.4807 | 0.0011325
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 588190 | GEN-2016-128 | 345 | 7.9459 | 7.9545 | 0.0010823
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533016 | WWUPLNT4 | 138 | 8.1516 | 8.1596 | 0.0009814
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532981 | CRESWLN4 | 138 | 9.1264 | 9.1352 | 0.00096424
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533803 | HAYSV 2 | 69 | 8.5824 | 8.5901 | 0.00089718
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533597 | MIDIANW2 | 69 | 13.8298 | 13.8422 | 0.00089661
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 587884 | G16-111-TAP | 345 | 11.3773 | 11.3875 | 0.00089652
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533011 | HALSTD 4 | 138 | 8.3248 | 8.3322 | 0.00088891
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 515581 | COYOTE 4 | 138 | 8.2619 | 8.2692 | 0.00088357
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 520434 | WAKTASW4 | 138 | 6.3232 | 6.3287 | 0.00086981
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 515852 | DGRASSE7 | 345 | 14.5452 | 14.5578 | 0.00086627
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 520452 | WAKTASB4 | 138 | 6.2893 | 6.2947 | 0.0008586
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533802 | HAYSVJS2 | 69 | 7.9127 | 7.9194 | 0.00084674
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 587460 | GEN-2016-068 | 345 | 6.5264 | 6.5319 | 0.00084273
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 587910 | GEN-2016-114 | 345 | 10.1469 | 10.155 | 0.00079827
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 539631 | FLATRWD4 | 138 | 10.3583 | 10.3664 | 0.00078198
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533416 | RENO 3 | 115 | 26.7821 | 26.8023 | 0.00075424
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533543 | CRESWLN2 | 69 | 12.9226 | 12.9321 | 0.00073515
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533573 | CRESWLS2 | 69 | 12.9226 | 12.9321 | 0.00073515
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533555 | SC7CRES2 | 69 | 12.7271 | 12.7363 | 0.00072287
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 584570 | GEN-2015-015 | 138 | 5.8242 | 5.8284 | 0.00072113
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 515497 | MATHWSN7 | 345 | 33.2303 | 33.254 | 0.0007132
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533558 | TIMBJCT2 | 69 | 8.1517 | 8.1575 | 0.00071151
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 514804 | MIDLTNT4 | 138 | 9.0073 | 9.0136 | 0.00069943
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 515547 | GRANTCO2 | 69 | 7.4693 | 7.4742 | 0.00065602
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 514714 | WOODRNG4 | 138 | 20.0668 | 20.0796 | 0.00063787
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 587894 | G16-112-TAP | 345 | 11.1782 | 11.1849 | 0.00059938
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533559 | UDALL 2 | 69 | 7.0322 | 7.0364 | 0.00059725
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533541 | AKRON 2 | 69 | 6.7266 | 6.7306 | 0.00059465
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 514709 | FRMNTAP4 | 138 | 18.7487 | 18.7597 | 0.00058671
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 542965 | W.GRDNR7 | 345 | 24.8262 | 24.8406 | 0.00058003
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533013 | MOUND 4 | 138 | 6.9434 | 6.9474 | 0.00057609
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533070 | SLATECRK4 | 138 | 6.7318 | 6.7356 | 0.00056448
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 587480 | GEN-2016-071 | 138 | 7.4626 | 7.4667 | 0.00054941
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 587880 | GEN-2016-111 | 345 | 7.1243 | 7.1281 | 0.00053339
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 521198 | CHILOCCO4 | 138 | 6.7544 | 6.758 | 0.00053299
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533413 | CIRCLE 3 | 115 | 23.6123 | 23.6235 | 0.00047433
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 515894 | THUNDER7 | 345 | 11.3237 | 11.329 | 0.00046804
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 514711 | WAUKOTP4 | 138 | 16.069 | 16.0765 | 0.00046674
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533421 | HEC GT 3 | 115 | 22.9426 | 22.953 | 0.00045331
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 539800 | CLARKCOUNTY7 | 345 | 13.2594 | 13.2652 | 0.00043743
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533419 | HEC 3 | 115 | 21.8737 | 21.8832 | 0.00043431
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533429 | MOUNDRG3 | 115 | 8.6474 | 8.6511 | 0.00042787
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533561 | WINFLD 2 | 69 | 6.3557 | 6.3584 | 0.00042482
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 514739 | MEDFORD2 | 69 | 5.4515 | 5.4538 | 0.0004219
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532768 | EMPEC 7 | 345 | 17.5987 | 17.6059 | 0.00040912
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532769 | LANG 7 | 345 | 17.3797 | 17.3867 | 0.00040277
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 520447 | BLUFCRK4 | 138 | 3.7612 | 3.7627 | 0.00039881
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532773 | SUMMIT 7 | 345 | 12.1324 | 12.1372 | 0.00039563
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 515375 | WWRDEHV7 | 345 | 19.8126 | 19.8204 | 0.00039369
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533626 | BURLJCT2 | 69 | 4.8155 | 4.8173 | 0.00037379
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 584170 | GEN-2014-064 | 138 | 9.641 | 9.6446 | 0.00037341
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 583370 | GEN-2012-024 | 345 | 11.3107 | 11.3148 | 0.00036249
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 514708 | OTTER 4 | 138 | 9.7166 | 9.7201 | 0.00036021
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 515853 | DGRASSE4 | 138 | 15.3869 | 15.3923 | 0.00035095
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 539852 | P1 MPT PRI | 345 | 10.7671 | 10.7708 | 0.00034364
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533653 | WOLFCRK2 | 69 | 5.8582 | 5.8601 | 0.00032433
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 582008 | GEN-2011-008 | 345 | 10.514 | 10.5174 | 0.00032338
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 514719 | CLYDE 2 | 69 | 4.4044 | 4.4058 | 0.00031786
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 585100 | GEN-2015-073 | 345 | 13.3961 | 13.4002 | 0.00030606
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 560080 | G16-046-TAP | 345 | 11.4289 | 11.4323 | 0.00029749
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 521085 | WAKITA 2 | 69 | 5.1561 | 5.1576 | 0.00029092
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 539857 | P2 MPT PRI | 345 | 9.1297 | 9.1323 | 0.00028478
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533551 | SC1KING2 | 69 | 3.2879 | 3.2888 | 0.00027373
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533628 | CC1BURL2 | 69 | 3.3205 | 3.3214 | 0.00027104
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533624 | BURLING2 | 69 | 3.3336 | 3.3345 | 0.00026998
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 582908 | G-2011-008-2 | 345 | 8.4349 | 8.4371 | 0.00026082
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 582708 | G-2011-008-1 | 345 | 8.5619 | 8.564 | 0.00024527
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 587310 | GEN-2016-046 | 345 | 9.8417 | 9.8441 | 0.00024386
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533629 | CC2SHAR2 | 69 | 4.545 | 4.5461 | 0.00024202
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532774 | SWISVAL7 | 345 | 16.163 | 16.1669 | 0.00024129
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 531469 | SPERVIL7 | 345 | 13.7357 | 13.739 | 0.00024025
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533625 | BURLIND2 | 69 | 2.9763 | 2.977 | 0.00023519
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 587980 | GEN-2016-122 | 345 | 5.2087 | 5.2099 | 0.00023038
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532871 | CIRCLE 6 | 230 | 10.0555 | 10.0578 | 0.00022873
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 515599 | G07621119-20 | 345 | 13.2006 | 13.2036 | 0.00022726
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533546 | FLORALJ2 | 69 | 2.7316 | 2.7322 | 0.00021965
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 514733 | MARSHL 4 | 138 | 8.4007 | 8.4025 | 0.00021427
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 521006 | MARSHAL4 | 138 | 8.4007 | 8.4025 | 0.00021427
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533412 | ARKVALJ3 | 115 | 10.8426 | 10.8449 | 0.00021213
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533411 | ARKVAL 3 | 115 | 10.6123 | 10.6145 | 0.00020731
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 585430 | PRSIMN_CRK1 | 345 | 11.6164 | 11.6188 | 0.0002066
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533415 | DAVIS 3 | 115 | 8.7128 | 8.7146 | 0.00020659
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533557 | TIMBER 2 | 69 | 2.4233 | 2.4238 | 0.00020633
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 587890 | GEN-2016-112 | 345 | 4.6684 | 4.6693 | 0.00019279
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532770 | MORRIS 7 | 345 | 12.8665 | 12.8689 | 0.00018653
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533414 | CITIES 3 | 115 | 8.5877 | 8.5893 | 0.00018631
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 585440 | PRSIMN_CRK2 | 345 | 10.6077 | 10.6096 | 0.00017912
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533545 | FLORAL 2 | 69 | 2.4109 | 2.4113 | 0.00016591
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 585410 | GREAT_WESTRN | 345 | 9.9457 | 9.9473 | 0.00016087
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532856 | SWISVAL6 | 230 | 20.9983 | 21.0016 | 0.00015716
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533380 | SPRGCRK3 | 115 | 3.8099 | 3.8104 | 0.00013124
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532863 | MORRIS 6 | 230 | 13.9585 | 13.9603 | 0.00012895
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 543659 | LACYGNE2 | 69 | 8.4733 | 8.4743 | 0.00011802
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533369 | HILSBOR3 | 115 | 2.5456 | 2.5459 | 0.00011785
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 585420 | COWBOY_RIDGE | 345 | 7.6718 | 7.6727 | 0.00011731
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533438 | WMCPHER3 | 115 | 15.7555 | 15.7573 | 0.00011425
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533304 | LANG 3 | 115 | 14.5028 | 14.5044 | 0.00011032
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 900001 | TRAVERSE1 | 345 | 7.3837 | 7.3845 | 0.00010835
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533428 | MCPHER 3 | 115 | 15.7273 | 15.729 | 0.00010809
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533506 | DAVIS 2 | 69 | 7.4951 | 7.4959 | 0.00010674
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532766 | JEC N 7 | 345 | 23.7584 | 23.7608 | 0.00010102
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533529 | MWIRNJ22 | 69 | 6.5493 | 6.5499 | 9.1613e-05
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 588310 | GEN-2016-158 | 345 | 4.6245 | 4.6249 | 8.6496e-05
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 588300 | GEN-2016-157 | 345 | 4.8983 | 4.8987 | 8.1661e-05
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533519 | MWIRONJ2 | 69 | 6.1417 | 6.1422 | 8.1411e-05
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533518 | MWIRON 2 | 69 | 6.3596 | 6.3601 | 7.8621e-05
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533426 | MANVILE3 | 115 | 11.7012 | 11.7021 | 7.6915e-05
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533505 | NCTYSVC2 | 69 | 3.9782 | 3.9785 | 7.5411e-05
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 900002 | TRAVERSE2 | 345 | 5.7164 | 5.7168 | 6.9974e-05
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 900003 | TRAVERSE3 | 345 | 5.1972 | 5.1975 | 5.7723e-05
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533394 | CORONAD3 | 115 | 7.6677 | 7.6681 | 5.2167e-05
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533504 | CITYSVC2 | 69 | 3.9513 | 3.9515 | 5.0616e-05
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533439 | WHEATLD3 | 115 | 7.9438 | 7.9442 | 5.0354e-05
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 543669 | LAC8_STAR7 | 345 | 0.6133 | 0.6133 | 0
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 543667 | LAC3_STAR7 | 345 | 0.6403 | 0.6403 | 0
GEN-2017-060 | Central | 12 - Northwest Arkansas | 588980 | GEN-2017-060 | 161 | 5.1425 | 5.7501 | 0.11815
GEN-2017-060 | Central | 12 - Northwest Arkansas | 589200 | GEN-2017-082 | 161 | 6.5984 | 7.2138 | 0.093265
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547476 | ASB349 5 | 161 | 9.8099 | 10.4272 | 0.062926
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547479 | LAR382 5 | 161 | 12.5231 | 13.142 | 0.049421
GEN-2017-060 | Central | 12 - Northwest Arkansas | 532932 | LITCH 5 | 161 | 8.3258 | 8.6426 | 0.03805
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547491 | PUR421 5 | 161 | 8.8 | 9.0825 | 0.032102
GEN-2017-060 | Central | 12 - Northwest Arkansas | 505488 | CARTHAG5 | 161 | 14.9914 | 15.4083 | 0.027809
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547477 | CJ 366 5 | 161 | 11.5152 | 11.8216 | 0.026608
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547485 | CAR395 5 | 161 | 11.2875 | 11.576 | 0.025559
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547490 | FIR417 5 | 161 | 13.2874 | 13.595 | 0.02315
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547467 | ORO110 5 | 161 | 18.1203 | 18.4918 | 0.020502
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547466 | ATL109 5 | 161 | 15.0356 | 15.3285 | 0.01948
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547494 | OAK432 5 | 161 | 16.4794 | 16.8003 | 0.019473
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547480 | MON383 5 | 161 | 10.9918 | 11.1548 | 0.014829
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547470 | JOP145 5 | 161 | 16.8006 | 17.0133 | 0.01266
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547498 | STL439 5 | 161 | 23.602 | 23.8627 | 0.011046
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547469 | RIV4525 | 161 | 22.9986 | 23.2407 | 0.010527
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547503 | RIV452T 5 | 161 | 22.6118 | 22.8433 | 0.010238
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547459 | WWR477 | 161 | 21.5641 | 21.7815 | 0.010082
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547483 | JOP389 5 | 161 | 19.1974 | 19.3878 | 0.009918
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547472 | TIP292 5 | 161 | 16.7605 | 16.9246 | 0.0097909
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547502 | RIV167 5 | 161 | 21.3713 | 21.578 | 0.0096718
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547501 | RIV453 5 | 161 | 21.8449 | 22.056 | 0.0096636
GEN-2017-060 | Central | 12 - Northwest Arkansas | 505486 | NEO SPA5 | 161 | 14.7701 | 14.8979 | 0.0086526
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547500 | RNM393 5 | 161 | 13.7156 | 13.824 | 0.0079034
GEN-2017-060 | Central | 12 - Northwest Arkansas | 505490 | CARTHG 2 | 69 | 13.1587 | 13.2582 | 0.0075615
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547471 | NEO184 5 | 161 | 13.648 | 13.7498 | 0.007459
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547462 | SVRCK469 5 | 161 | 13.7285 | 13.8296 | 0.0073642
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547593 | JOP391 5 | 161 | 12.9002 | 12.9942 | 0.0072867
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547533 | ATL109 2 | 69 | 19.9663 | 20.1099 | 0.0071921
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547607 | JOP422 5 | 161 | 12.75 | 12.8397 | 0.0070353
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547468 | AUR124 5 | 161 | 9.8562 | 9.9248 | 0.0069601
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547534 | ORO110 2 | 69 | 17.3555 | 17.4606 | 0.0060557
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547595 | RNM393 2 | 69 | 18.615 | 18.7164 | 0.0054472
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547556 | OAK280 2 | 69 | 15.3404 | 15.4233 | 0.005404
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547591 | MON383 2 | 69 | 11.8616 | 11.9195 | 0.0048813
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547588 | JOP372 2 | 69 | 14.7519 | 14.8184 | 0.0045079
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547581 | JOP360 2 | 69 | 13.6161 | 13.6768 | 0.004458
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547540 | MON152 2 | 69 | 10.3092 | 10.3513 | 0.0040837
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547608 | JOP430 2 | 69 | 15.2468 | 15.309 | 0.0040795
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547685 | PLB447 2 | 69 | 13.8559 | 13.9104 | 0.0039333
GEN-2017-060 | Central | 12 - Northwest Arkansas | 506934 | FLINTCR5 | 161 | 31.8219 | 31.9414 | 0.0037553
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547592 | JOP389 2 | 69 | 14.7987 | 14.8527 | 0.003649
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547564 | SOL315 2 | 69 | 9.9339 | 9.969 | 0.0035334
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547463 | KOD471 2 | 69 | 11.6008 | 11.6403 | 0.0034049
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547537 | AUR124 2 | 69 | 11.7987 | 11.8376 | 0.003297
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547499 | CPK446 5 | 161 | 8.1479 | 8.1745 | 0.0032646
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547405 | MON352J2 | 69 | 7.4624 | 7.4853 | 0.0030687
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547527 | WEB436 2 | 69 | 9.2188 | 9.246 | 0.0029505
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547406 | MON352 2 | 69 | 7.1717 | 7.1928 | 0.0029421
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300751 | 2REEDS | 69 | 6.2071 | 6.2235 | 0.0026421
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547407 | MON311J2 | 69 | 6.3976 | 6.4143 | 0.0026104
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547559 | TIP292 2 | 69 | 9.5721 | 9.5969 | 0.0025909
GEN-2017-060 | Central | 12 - Northwest Arkansas | 505492 | SPRGFLD5 | 161 | 26.7935 | 26.8628 | 0.0025864
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547401 | MON376 2 | 69 | 6.3182 | 6.3345 | 0.0025798
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547408 | MON311 2 | 69 | 6.3182 | 6.3345 | 0.0025798
GEN-2017-060 | Central | 12 - Northwest Arkansas | 506935 | FLINTCR7 | 345 | 14.6762 | 14.7134 | 0.0025347
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547431 | WEB105 2 | 69 | 7.7177 | 7.7371 | 0.0025137
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547543 | NEO184 2 | 69 | 11.3621 | 11.3903 | 0.0024819
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549959 | BATTLEFIELD5 | 161 | 26.1754 | 26.2398 | 0.0024603
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300745 | 2DMNDTP | 69 | 5.2979 | 5.3106 | 0.0023972
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547578 | AUR355 2 | 69 | 9.0089 | 9.0302 | 0.0023643
GEN-2017-060 | Central | 12 - Northwest Arkansas | 512750 | TONECE7 | 345 | 14.499 | 14.5329 | 0.0023381
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549969 | BROOKLINE 5 | 161 | 27.9605 | 28.0243 | 0.0022818
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547532 | CAR108 2 | 69 | 8.0727 | 8.0903 | 0.0021802
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547563 | LIN314 2 | 69 | 9.6797 | 9.7001 | 0.0021075
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300748 | 2NEOSAC | 69 | 9.6525 | 9.6722 | 0.0020409
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547438 | EXP449T2 | 69 | 8.6558 | 8.6733 | 0.0020218
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549954 | JTEC 5 | 161 | 27.0836 | 27.1381 | 0.0020123
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547496 | NOL435 5 | 161 | 9.635 | 9.6542 | 0.0019927
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547449 | PRC460 2 | 69 | 5.4449 | 5.4557 | 0.0019835
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549960 | SW DISP PLT5 | 161 | 25.2728 | 25.3226 | 0.0019705
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547560 | ROC296 2 | 69 | 8.5408 | 8.5574 | 0.0019436
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547473 | RDS295 5 | 161 | 7.4227 | 7.4368 | 0.0018996
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300680 | 2VERONA | 69 | 6.2314 | 6.2431 | 0.0018776
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547484 | DEC392 5 | 161 | 14.8357 | 14.863 | 0.0018402
GEN-2017-060 | Central | 12 - Northwest Arkansas | 506979 | SHIPERD7 | 345 | 9.9042 | 9.9224 | 0.0018376
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300762 | 2WNTWRT | 69 | 4.5233 | 4.5314 | 0.0017907
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300678 | 5NIXA-1 | 161 | 18.8008 | 18.8338 | 0.0017552
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547492 | RDS424 5 | 161 | 7.9691 | 7.9827 | 0.0017066
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549955 | JUNCTION 5 | 161 | 20.368 | 20.4025 | 0.0016938
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547439 | EXP4492 | 69 | 7.1821 | 7.194 | 0.0016569
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549958 | MAIN STREET5 | 161 | 18.5062 | 18.5366 | 0.0016427
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300750 | 2NEOSHO | 69 | 8.2235 | 8.237 | 0.0016416
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300348 | 5BTLFD | 161 | 21.7694 | 21.805 | 0.0016353
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549956 | NICHOLS 5 | 161 | 18.5381 | 18.5682 | 0.0016237
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549957 | WEST BELT 5 | 161 | 18.2824 | 18.3119 | 0.0016136
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547400 | MON376J2 | 69 | 3.9084 | 3.9146 | 0.0015863
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547618 | CPK446 2 | 69 | 9.9027 | 9.9183 | 0.0015753
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300129 | 5WASHBRN | 161 | 7.7304 | 7.7425 | 0.0015652
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547478 | DAD368 5 | 161 | 16.7205 | 16.7465 | 0.001555
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300101 | 5MORGAN | 161 | 17.7579 | 17.7855 | 0.0015542
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547553 | ALB262 2 | 69 | 8.2888 | 8.301 | 0.0014719
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547544 | WEN205 2 | 69 | 4.3134 | 4.3196 | 0.0014374
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549984 | BROOKLINE 7 | 345 | 11.272 | 11.2881 | 0.0014283
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547606 | MTV420 2 | 69 | 6.7427 | 6.7522 | 0.0014089
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300089 | 5JAMESV | 161 | 15.5561 | 15.5778 | 0.001395
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547402 | MON416J2 | 69 | 3.4446 | 3.4493 | 0.0013645
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300677 | 2MTVRN | 69 | 8.5924 | 8.6041 | 0.0013617
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547582 | SAR362T2 | 69 | 4.1908 | 4.1965 | 0.0013601
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549971 | PIC WEST 5 | 161 | 16.6881 | 16.7106 | 0.0013483
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547403 | MON416 2 | 69 | 3.3555 | 3.36 | 0.0013411
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547488 | BRN412 5 | 161 | 9.4472 | 9.4598 | 0.0013337
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300045 | 7MORGAN | 345 | 12.7077 | 12.7243 | 0.0013063
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300754 | 2SPGCTP | 69 | 5.3641 | 5.371 | 0.0012863
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300659 | 2BOWRML | 69 | 5.8389 | 5.8464 | 0.0012845
GEN-2017-060 | Central | 12 - Northwest Arkansas | 505472 | TABLE R5 | 161 | 13.931 | 13.9484 | 0.001249
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549970 | CLAY 5 | 161 | 17.9079 | 17.9302 | 0.0012453
GEN-2017-060 | Central | 12 - Northwest Arkansas | 505480 | BEAVER 5 | 161 | 10.1705 | 10.1829 | 0.0012192
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547497 | RVS438 5 | 161 | 11.4408 | 11.4546 | 0.0012062
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300679 | 2PRDYTP | 69 | 4.8977 | 4.9035 | 0.0011842
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547489 | BRN413 5 | 161 | 9.9369 | 9.9485 | 0.0011674
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547546 | BIL221 2 | 69 | 9.5492 | 9.5601 | 0.0011415
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549925 | NICHOLS 2 | 69 | 23.032 | 23.0582 | 0.0011375
GEN-2017-060 | Central | 12 - Northwest Arkansas | 505496 | NIXA 5 | 161 | 12.2079 | 12.2217 | 0.0011304
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547611 | MAR437 2 | 69 | 5.7004 | 5.7067 | 0.0011052
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300744 | 2DMNDGR | 69 | 2.474 | 2.4767 | 0.0010914
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300658 | 2BILLNG | 69 | 7.9793 | 7.9876 | 0.0010402
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547626 | HOL478_5 | 161 | 9.6843 | 9.6943 | 0.0010326
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549962 | MILL 5 | 161 | 15.3487 | 15.3644 | 0.0010229
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300726 | 5RIVRDL | 161 | 11.1603 | 11.1716 | 0.0010125
GEN-2017-060 | Central | 12 - Northwest Arkansas | 504000 | AVOCA 5 | 161 | 8.7039 | 8.7126 | 0.00099955
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549963 | MENTOR 5 | 161 | 14.592 | 14.6061 | 0.00096628
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300719 | 5COMPTN | 161 | 10.7659 | 10.7763 | 0.00096601
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300805 | 5RIVERSIDE | 161 | 10.563 | 10.5731 | 0.00095617
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549961 | JAMES RIVER5 | 161 | 15.8807 | 15.8957 | 0.00094454
GEN-2017-060 | Central | 12 - Northwest Arkansas | 510411 | GROVE 5 | 161 | 5.6356 | 5.6409 | 0.00094045
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300718 | 5CLEVCOV | 161 | 11.288 | 11.2986 | 0.00093905
GEN-2017-060 | Central | 12 - Northwest Arkansas | 506932 | EUREKA 5 | 161 | 9.1859 | 9.1945 | 0.00093622
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549966 | SUMMIT 5 | 161 | 12.8209 | 12.8328 | 0.00092817
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300681 | 2BUTRFLD | 69 | 4.901 | 4.9055 | 0.00091818
GEN-2017-060 | Central | 12 - Northwest Arkansas | 301161 | 5LOGAN | 161 | 13.985 | 13.9978 | 0.00091527
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547450 | JAS344T2 | 69 | 4.8546 | 4.859 | 0.00090636
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549921 | MAIN STREET2 | 69 | 24.9345 | 24.957 | 0.00090236
GEN-2017-060 | Central | 12 - Northwest Arkansas | 338682 | 5OSAGE CRK#! | 161 | 8.9865 | 8.9946 | 0.00090135
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300649 | 2JASPER | 69 | 4.6934 | 4.6976 | 0.00089487
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300727 | 5ROARK | 161 | 9.5421 | 9.5503 | 0.00085935
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549968 | MC CARTNEY 5 | 161 | 14.3422 | 14.3543 | 0.00084366
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300670 | 2EPURDY | 69 | 3.4475 | 3.4504 | 0.00084119
GEN-2017-060 | Central | 12 - Northwest Arkansas | 338099 | 5GRANDVIEW% | 161 | 8.4811 | 8.4882 | 0.00083716
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300949 | 7JASPER | 345 | 12.0944 | 12.1045 | 0.0008351
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549979 | BATTLEFIELD2 | 69 | 19.8269 | 19.8425 | 0.00078681
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547451 | JAS344 | 69 | 4.2248 | 4.2281 | 0.0007811
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547610 | NOL435 2 | 69 | 8.1189 | 8.1252 | 0.00077597
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549911 | GOLDEN 2 | 69 | 19.4601 | 19.4752 | 0.00077595
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549924 | LAUREL 2 | 69 | 17.3873 | 17.4007 | 0.00077068
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547566 | AND322 2 | 69 | 5.5033 | 5.5075 | 0.00076318
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300758 | 2SWTWT | 69 | 4.1047 | 4.1078 | 0.00075523
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300763 | 2WASHBRN | 69 | 6.4293 | 6.4341 | 0.00074658
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300764 | 2SPURGNTP | 69 | 3.0369 | 3.0391 | 0.00072442
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549913 | DAYTON 2 | 69 | 18.522 | 18.5353 | 0.00071807
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300824 | 2SELIGM | 69 | 5.8556 | 5.8598 | 0.00071726
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300725 | 2REEDSP | 69 | 9.7864 | 9.7931 | 0.00068462
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549918 | MILL 2 | 69 | 21.5519 | 21.5665 | 0.00067743
GEN-2017-060 | Central | 12 - Northwest Arkansas | 301368 | 5STRAFFORD | 161 | 12.1497 | 12.1579 | 0.00067491
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547424 | RES364 2 | 69 | 3.8646 | 3.8672 | 0.00067277
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549929 | WASHINGTON 2 | 69 | 18.6318 | 18.6443 | 0.0006709
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549922 | GRAND 2 | 69 | 18.4624 | 18.4744 | 0.00064997
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300765 | 2SPURGN | 69 | 2.7775 | 2.7793 | 0.00064806
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547404 | PUR390 2 | 69 | 1.7097 | 1.7108 | 0.00064339
GEN-2017-060 | Central | 12 - Northwest Arkansas | 505494 | SPRGFLD2 | 69 | 15.4971 | 15.507 | 0.00063883
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300667 | 2CRANE | 69 | 3.1765 | 3.1785 | 0.00062962
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549903 | JRPS 69B-2 2 | 69 | 18.8201 | 18.8319 | 0.00062699
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547430 | SAR362 2 | 69 | 1.9304 | 1.9316 | 0.00062163
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300755 | 2SPGCTY | 69 | 2.6225 | 2.6241 | 0.0006101
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549914 | FORT 2 | 69 | 16.916 | 16.9263 | 0.00060889
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300651 | 2LAMR | 69 | 9.5732 | 9.579 | 0.00060586
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549920 | HARGISS 2 | 69 | 17.3849 | 17.3953 | 0.00059822
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300666 | 2CLRKSN | 69 | 2.7085 | 2.7101 | 0.00059073
GEN-2017-060 | Central | 12 - Northwest Arkansas | 301395 | 2ROUNDGRVETP | 69 | 4.2478 | 4.2503 | 0.00058854
GEN-2017-060 | Central | 12 - Northwest Arkansas | 505474 | TABLE R2 | 69 | 12.906 | 12.9135 | 0.00058113
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300660 | 2BRNSPG | 69 | 3.6463 | 3.6484 | 0.00057593
GEN-2017-060 | Central | 12 - Northwest Arkansas | 301393 | 2ROUNDGROVE | 69 | 4.0712 | 4.0735 | 0.00056494
GEN-2017-060 | Central | 12 - Northwest Arkansas | 301360 | 2T.ROCKSW | 69 | 11.9745 | 11.9811 | 0.00055117
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549916 | BLACKMAN 2 | 69 | 17.5578 | 17.5673 | 0.00054107
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547493 | BOL431 5 | 161 | 5.7418 | 5.7449 | 0.0005399
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300735 | 2T.ROCK | 69 | 11.7126 | 11.7188 | 0.00052934
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300656 | 2JACK ST | 69 | 7.1827 | 7.1864 | 0.00051513
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549917 | INGRAM 2 | 69 | 16.3806 | 16.3889 | 0.0005067
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300685 | 2LAMARPT | 69 | 8.0932 | 8.0973 | 0.0005066
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549910 | COX 2 | 69 | 13.4604 | 13.4672 | 0.00050519
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549919 | CHAD 2 | 69 | 15.2669 | 15.2746 | 0.00050436
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549905 | PLAINVIEW 2 | 69 | 13.7275 | 13.7341 | 0.00048079
GEN-2017-060 | Central | 12 - Northwest Arkansas | 505498 | STOCKTN5 | 161 | 9.2958 | 9.3002 | 0.00047333
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547585 | DAD368 2 | 69 | 9.3451 | 9.3495 | 0.00047083
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300794 | 5LAMAR | 161 | 8.3969 | 8.4008 | 0.00046446
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549904 | JAMES RIVER2 | 69 | 15.4348 | 15.4419 | 0.00046
GEN-2017-060 | Central | 12 - Northwest Arkansas | 505501 | NIXA 2 | 69 | 11.9887 | 11.9941 | 0.00045042
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549932 | PACKER 2 | 69 | 13.8029 | 13.809 | 0.00044194
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300118 | 5STKAEC | 161 | 8.642 | 8.6458 | 0.00043971
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300673 | 2JAMESV | 69 | 11.6561 | 11.6612 | 0.00043754
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300042 | 7HUBEN | 345 | 9.9408 | 9.9451 | 0.00043256
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300653 | 2MEDOC | 69 | 2.3693 | 2.3703 | 0.00042207
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547604 | BHJ415 2 | 69 | 10.6802 | 10.6847 | 0.00042134
GEN-2017-060 | Central | 12 - Northwest Arkansas | 505543 | NX ESPY2 | 69 | 10.9342 | 10.9386 | 0.00040241
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300753 | 2SIMS | 69 | 3.5189 | 3.5203 | 0.00039785
GEN-2017-060 | Central | 12 - Northwest Arkansas | 505541 | NIXA DT2 | 69 | 10.5001 | 10.5041 | 0.00038095
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547428 | SWC414 2 | 69 | 3.6366 | 3.6379 | 0.00035748
GEN-2017-060 | Central | 12 - Northwest Arkansas | 505545 | NIX_SLR_U1_2 | 69 | 8.4782 | 8.4809 | 0.00031846
GEN-2017-060 | Central | 12 - Northwest Arkansas | 504001 | AVOCA_1 2 | 69 | 6.3537 | 6.3557 | 0.00031478
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300668 | 2DADEVL | 69 | 5.4435 | 5.4451 | 0.00029393
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300782 | 2MORGAN | 69 | 6.5173 | 6.5192 | 0.00029153
GEN-2017-060 | Central | 12 - Northwest Arkansas | 338120 | 5S.LEAD HILL | 161 | 6.2137 | 6.2154 | 0.00027359
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300774 | 2EUDORA | 69 | 5.4601 | 5.4613 | 0.00021978
GEN-2017-060 | Central | 12 - Northwest Arkansas | 301362 | 2LAMRLNDFL | 69 | 3.2081 | 3.2088 | 0.0002182
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300095 | 5MANSFD | 161 | 8.7665 | 8.7684 | 0.00021673
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300652 | 2LAMRCTS | 69 | 3.7463 | 3.7471 | 0.00021354
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300663 | 2CASSIDY | 69 | 6.6196 | 6.621 | 0.00021149
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300816 | 5COLLINS | 161 | 6.298 | 6.2993 | 0.00020641
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300723 | 2PARDIS | 69 | 4.8498 | 4.8508 | 0.00020619
GEN-2017-060 | Central | 12 - Northwest Arkansas | 338554 | 2OSAGE CRK-1 | 69 | 4.4225 | 4.4234 | 0.0002035
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300800 | 2BONA | 69 | 3.2784 | 3.279 | 0.00018302
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300647 | 2BLLMYTP | 69 | 4.9819 | 4.9828 | 0.00018065
GEN-2017-060 | Central | 12 - Northwest Arkansas | 338556 | 2OSAGE CRK-2 | 69 | 3.9872 | 3.9879 | 0.00017556
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300669 | 2ELWOOD | 69 | 5.1586 | 5.1595 | 0.00017447
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300788 | 2SLAGLE | 69 | 5.7331 | 5.7341 | 0.00017443
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300081 | 5GAINES | 161 | 5.6565 | 5.6572 | 0.00012375
GEN-2017-060 | Central | 12 - Northwest Arkansas | 301057 | 5GRVSPG | 161 | 6.711 | 6.7118 | 0.00011921
GEN-2017-060 | Central | 12 - Northwest Arkansas | 301168 | 2MANSFL | 69 | 9.9617 | 9.9628 | 0.00011042
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300657 | 2ASHGRV | 69 | 3.8347 | 3.8351 | 0.00010431
GEN-2017-060 | Central | 12 - Northwest Arkansas | 301128 | 5MTNGRV | 161 | 5.9308 | 5.9314 | 0.00010117
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300664 | 2CAVESP | 69 | 2.2837 | 2.2839 | 8.7577e-05
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300646 | 2BELLAMY | 69 | 2.5008 | 2.501 | 7.9974e-05
GEN-2017-060 | Central | 12 - Northwest Arkansas | 301058 | 2HARTVL | 69 | 3.2259 | 3.226 | 3.0999e-05
GEN-2017-076 | Central | 12 - Northwest Arkansas | 589140 | GEN-2017-076 | 161 | 19.4844 | 19.67 | 0.0095256
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506944 | CHAMSPR5 | 161 | 21.7701 | 21.9572 | 0.0085944
GEN-2017-076 | Central | 12 - Northwest Arkansas | 547471 | NEO184 5 | 161 | 13.648 | 13.7498 | 0.007459
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506945 | CHAMSPR7 | 345 | 9.5126 | 9.5542 | 0.0043731
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506957 | TONTITN5 | 161 | 19.6004 | 19.6826 | 0.0041938
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506978 | MATTISN5 | 161 | 19.1394 | 19.2178 | 0.0040963
GEN-2017-076 | Central | 12 - Northwest Arkansas | 504202 | SILOAMSP 5 | 161 | 18.7045 | 18.7808 | 0.0040792
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506959 | TONTITN7 | 345 | 8.4699 | 8.5029 | 0.0038961
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506948 | SILOAM 5 | 161 | 20.9588 | 21.039 | 0.0038266
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506934 | FLINTCR5 | 161 | 31.8219 | 31.9414 | 0.0037553
GEN-2017-076 | Central | 12 - Northwest Arkansas | 504010 | ELMSPRGS 5 | 161 | 16.4507 | 16.5089 | 0.0035378
GEN-2017-076 | Central | 12 - Northwest Arkansas | 504020 | FARMNGTN 5 | 161 | 12.143 | 12.1858 | 0.0035247
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506927 | DYESS 5 | 161 | 15.7448 | 15.7987 | 0.0034234
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506956 | FARMING5 | 161 | 11.907 | 11.9461 | 0.0032838
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506947 | SFAYTVL5 | 161 | 12.1293 | 12.1669 | 0.0030999
GEN-2017-076 | Central | 12 - Northwest Arkansas | 504201 | GENTRY 5 | 161 | 25.4989 | 25.5755 | 0.0030041
GEN-2017-076 | Central | 12 - Northwest Arkansas | 512643 | SILMCTY5 | 161 | 19.0409 | 19.0979 | 0.0029936
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506933 | FAYETVL5 | 161 | 11.648 | 11.6817 | 0.0028932
GEN-2017-076 | Central | 12 - Northwest Arkansas | 504274 | CARLEYRD 5 | 161 | 12.3698 | 12.405 | 0.0028456
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506983 | GREGGST5 | 161 | 11.5396 | 11.5718 | 0.0027904
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506939 | VANASCH5 | 161 | 11.819 | 11.8519 | 0.0027837
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506943 | SEFAYTV5 | 161 | 10.878 | 10.9077 | 0.0027303
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506949 | SOSPRDL5 | 161 | 11.8548 | 11.8863 | 0.0026572
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506935 | FLINTCR7 | 345 | 14.6762 | 14.7134 | 0.0025347
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506937 | HYLAND 5 | 161 | 10.1967 | 10.2223 | 0.0025106
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506985 | OSBURN | 161 | 10.4862 | 10.5114 | 0.0024032
GEN-2017-076 | Central | 12 - Northwest Arkansas | 512750 | TONECE7 | 345 | 14.499 | 14.5329 | 0.0023381
GEN-2017-076 | Central | 12 - Northwest Arkansas | 504015 | EFAYETVL 5 | 161 | 9.8403 | 9.8632 | 0.0023272
GEN-2017-076 | Central | 12 - Northwest Arkansas | 549969 | BROOKLINE 5 | 161 | 27.9605 | 28.0243 | 0.0022818
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506991 | BRUSHCRK_5 | 161 | 12.3195 | 12.3474 | 0.0022647
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506931 | EROGERS5 | 161 | 14.2508 | 14.2797 | 0.002028
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506938 | LOWELL 5 | 161 | 11.6918 | 11.7152 | 0.0020014
GEN-2017-076 | Central | 12 - Northwest Arkansas | 547496 | NOL435 5 | 161 | 9.635 | 9.6542 | 0.0019927
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506942 | ROGERS 5 | 161 | 12.0679 | 12.0908 | 0.0018976
GEN-2017-076 | Central | 12 - Northwest Arkansas | 512642 | SILSPWW5 | 161 | 14.2838 | 14.3105 | 0.0018693
GEN-2017-076 | Central | 12 - Northwest Arkansas | 512751 | TONECE5 | 161 | 14.6993 | 14.7264 | 0.0018436
GEN-2017-076 | Central | 12 - Northwest Arkansas | 547484 | DEC392 5 | 161 | 14.8357 | 14.863 | 0.0018402
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506979 | SHIPERD7 | 345 | 9.9042 | 9.9224 | 0.0018376
GEN-2017-076 | Central | 12 - Northwest Arkansas | 504200 | WROGERS 5 | 161 | 13.3408 | 13.3644 | 0.001769
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506955 | BENT ML5 | 161 | 13.4582 | 13.4813 | 0.0017164
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506990 | GREENHOUSE 5 | 161 | 14.4557 | 14.4804 | 0.0017087
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506960 | BEN279_5 | 161 | 12.6447 | 12.6636 | 0.0014947
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506980 | SHIPERD5 | 161 | 14.7688 | 14.7908 | 0.0014896
GEN-2017-076 | Central | 12 - Northwest Arkansas | 549984 | BROOKLINE 7 | 345 | 11.272 | 11.2881 | 0.0014283
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506926 | DYESS 2 | 69 | 14.9756 | 14.9964 | 0.0013889
GEN-2017-076 | Central | 12 - Northwest Arkansas | 300045 | 7MORGAN | 345 | 12.7077 | 12.7243 | 0.0013063
GEN-2017-076 | Central | 12 - Northwest Arkansas | 505480 | BEAVER 5 | 161 | 10.1705 | 10.1829 | 0.0012192
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506950 | SPRDALE2 | 69 | 11.2835 | 11.2954 | 0.0010546
GEN-2017-076 | Central | 12 - Northwest Arkansas | 504000 | AVOCA 5 | 161 | 8.7039 | 8.7126 | 0.00099955
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506951 | SPRDALT2 | 69 | 10.5723 | 10.5827 | 0.0009837
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506946 | SFAYTVL2 | 69 | 10.2696 | 10.2796 | 0.00097375
GEN-2017-076 | Central | 12 - Northwest Arkansas | 512714 | KANSATP5 | 161 | 11.3431 | 11.3539 | 0.00095212
GEN-2017-076 | Central | 12 - Northwest Arkansas | 510411 | GROVE 5 | 161 | 5.6356 | 5.6409 | 0.00094045
GEN-2017-076 | Central | 12 - Northwest Arkansas | 512716 | KANSAS 5 | 161 | 10.7825 | 10.7921 | 0.00089033
GEN-2017-076 | Central | 12 - Northwest Arkansas | 512820 | SILMCTY2 | 69 | 13.0422 | 13.0536 | 0.00087409
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506973 | SILOAM 2 | 69 | 10.8976 | 10.9069 | 0.0008534
GEN-2017-076 | Central | 12 - Northwest Arkansas | 512737 | SSSWTP2 | 69 | 12.1706 | 12.1805 | 0.00081344
GEN-2017-076 | Central | 12 - Northwest Arkansas | 504021 | FARM_1 2 | 69 | 8.0553 | 8.0616 | 0.00078209
GEN-2017-076 | Central | 12 - Northwest Arkansas | 547610 | NOL435 2 | 69 | 8.1189 | 8.1252 | 0.00077597
GEN-2017-076 | Central | 12 - Northwest Arkansas | 512730 | SSSWES2 | 69 | 11.1368 | 11.1451 | 0.00074528
GEN-2017-076 | Central | 12 - Northwest Arkansas | 512650 | GRDA1 7 | 345 | 26.1358 | 26.1539 | 0.00069254
GEN-2017-076 | Central | 12 - Northwest Arkansas | 504013 | ELMSPG_2 2 | 69 | 7.4705 | 7.4755 | 0.0006693
GEN-2017-076 | Central | 12 - Northwest Arkansas | 512744 | SSMOSS2 | 69 | 10.0493 | 10.056 | 0.00066671
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506930 | EROGERS2 | 69 | 11.5581 | 11.5658 | 0.0006662
GEN-2017-076 | Central | 12 - Northwest Arkansas | 504016 | EFAYVL_1 2 | 69 | 6.5263 | 6.5306 | 0.00065887
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506940 | NROGERS2 | 69 | 10.5868 | 10.5932 | 0.00060453
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506936 | GREENLD2 | 69 | 7.1325 | 7.1366 | 0.00057483
GEN-2017-076 | Central | 12 - Northwest Arkansas | 509745 | CLARKSV7 | 345 | 19.6676 | 19.6788 | 0.00056946
GEN-2017-076 | Central | 12 - Northwest Arkansas | 512637 | 412SUB 5 | 161 | 11.4891 | 11.4954 | 0.00054835
GEN-2017-076 | Central | 12 - Northwest Arkansas | 504018 | EFAYTVL2-2 | 69 | 4.9899 | 4.9924 | 0.00050101
GEN-2017-076 | Central | 12 - Northwest Arkansas | 504011 | ELMSPG_1 2 | 69 | 5.3983 | 5.401 | 0.00050016
GEN-2017-076 | Central | 12 - Northwest Arkansas | 547594 | DEC392 2 | 69 | 8.1957 | 8.1996 | 0.00047586
GEN-2017-076 | Central | 12 - Northwest Arkansas | 547569 | DEC467 2 | 69 | 6.963 | 6.9659 | 0.00041649
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506941 | PRGROVE2 | 69 | 4.8692 | 4.8711 | 0.00039021
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506972 | LINCOLN2 | 69 | 4.6958 | 4.6975 | 0.00036203
GEN-2017-076 | Central | 12 - Northwest Arkansas | 547428 | SWC414 2 | 69 | 3.6366 | 3.6379 | 0.00035748
GEN-2017-076 | Central | 12 - Northwest Arkansas | 510380 | DELWARE7 | 345 | 10.9891 | 10.9927 | 0.0003276
GEN-2017-076 | Central | 12 - Northwest Arkansas | 504001 | AVOCA_1 2 | 69 | 6.3537 | 6.3557 | 0.00031478
GEN-2017-076 | Central | 12 - Northwest Arkansas | 509807 | ONETA--7 | 345 | 26.6882 | 26.6954 | 0.00026978
GEN-2017-076 | Central | 12 - Northwest Arkansas | 509836 | OEC 7 | 345 | 26.4323 | 26.4393 | 0.00026483
GEN-2017-076 | Central | 12 - Northwest Arkansas | 512753 | TONNEC2 | 69 | 4.7094 | 4.7106 | 0.00025481
GEN-2017-076 | Central | 12 - Northwest Arkansas | 510406 | N.E.S.-7 | 345 | 15.8748 | 15.8785 | 0.00023307
GEN-2017-076 | Central | 12 - Northwest Arkansas | 509852 | T.NO.--7 | 345 | 22.6544 | 22.6594 | 0.00022071
GEN-2017-076 | Central | 12 - Northwest Arkansas | 512756 | TONECESTR2 | 69 | 3.7541 | 3.7549 | 0.0002131
GEN-2017-076 | Central | 12 - Northwest Arkansas | 512728 | ARKLIN2 | 69 | 3.6462 | 3.6469 | 0.00019198
GEN-2017-076 | Central | 12 - Northwest Arkansas | 515224 | MUSKOGE7 | 345 | 28.963 | 28.9683 | 0.00018299
GEN-2017-076 | Central | 12 - Northwest Arkansas | 509806 | ONETA--4 | 138 | 47.3567 | 47.3648 | 0.00017104
GEN-2017-076 | Central | 12 - Northwest Arkansas | 512747 | SSNEWN2 | 69 | 3.0338 | 3.0343 | 0.00016481
GEN-2017-076 | Central | 12 - Northwest Arkansas | 512745 | SSLINC2 | 69 | 2.7442 | 2.7446 | 0.00014576
GEN-2017-076 | Central | 12 - Northwest Arkansas | 588039 | G16133G16146 | 345 | 28.9046 | 28.9088 | 0.00014531
GEN-2017-076 | Central | 12 - Northwest Arkansas | 509782 | R.S.S.-7 | 345 | 28.9046 | 28.9088 | 0.00014531
GEN-2017-076 | Central | 12 - Northwest Arkansas | 512746 | SSNORT2 | 69 | 2.7974 | 2.7978 | 0.00014299
GEN-2017-076 | Central | 12 - Northwest Arkansas | 509834 | COGENT 7 | 345 | 26.7575 | 26.7611 | 0.00013454
GEN-2017-076 | Central | 12 - Northwest Arkansas | 515235 | PECANCK7 | 345 | 21.524 | 21.5268 | 0.00013009
GEN-2017-076 | Central | 12 - Northwest Arkansas | 509870 | SAPLPRD7 | 345 | 22.2724 | 22.2751 | 0.00012123
GEN-2017-076 | Central | 12 - Northwest Arkansas | 509786 | BA.N-ST4 | 138 | 23.2733 | 23.2754 | 9.0232e-05
GEN-2017-076 | Central | 12 - Northwest Arkansas | 509875 | RSS T2 4 | 138 | 50.3973 | 50.4013 | 7.9369e-05
GEN-2017-076 | Central | 12 - Northwest Arkansas | 509773 | RSS T1 4 | 138 | 49.5212 | 49.5251 | 7.8754e-05
GEN-2017-076 | Central | 12 - Northwest Arkansas | 509891 | BA_71ST4 | 138 | 22.6193 | 22.621 | 7.5157e-05
GEN-2017-076 | Central | 12 - Northwest Arkansas | 509769 | BA101-N4 | 138 | 19.1465 | 19.1477 | 6.2675e-05
GEN-2017-076 | Central | 12 - Northwest Arkansas | 515234 | PECANCK5 | 161 | 20.9832 | 20.9845 | 6.1954e-05
GEN-2017-076 | Central | 12 - Northwest Arkansas | 509869 | 121LYNN4 | 138 | 17.2797 | 17.2807 | 5.7871e-05
GEN-2017-076 | Central | 12 - Northwest Arkansas | 509768 | BA101ST4 | 138 | 18.3213 | 18.3223 | 5.4581e-05
GEN-2017-076 | Central | 12 - Northwest Arkansas | 509737 | BA101 S4 | 138 | 17.6639 | 17.6648 | 5.0951e-05
GEN-2017-076 | Central | 12 - Northwest Arkansas | 509721 | BA.NO-S4 | 138 | 12.0192 | 12.0198 | 4.992e-05
GEN-2017-076 | Central | 12 - Northwest Arkansas | 588810 | GEN-2017-040 | 345 | 11.1324 | 11.1329 | 4.4914e-05
GEN-2017-076 | Central | 12 - Northwest Arkansas | 588838 | G17-092-SWYD | 345 | 11.2884 | 11.2888 | 3.5435e-05
GEN-2017-076 | Central | 12 - Northwest Arkansas | 588839 | FIREWHL-TAP | 345 | 11.2884 | 11.2888 | 3.5435e-05
GEN-2017-076 | Central | 12 - Northwest Arkansas | 588834 | FWL-WND-SWYD | 345 | 11.2884 | 11.2888 | 3.5435e-05
GEN-2017-076 | Central | 12 - Northwest Arkansas | 589300 | GEN-2017-092 | 345 | 9.9029 | 9.9032 | 3.0294e-05
GEN-2017-076 | Central | 12 - Northwest Arkansas | 515302 | FTSMITH7 | 345 | 10.0546 | 10.0548 | 1.9891e-05
GEN-2017-076 | Central | 12 - Northwest Arkansas | 515301 | FTSMTHW5 | 161 | 22.9073 | 22.9076 | 1.3096e-05
GEN-2017-076 | Central | 12 - Northwest Arkansas | 515305 | FTSMITH8 | 500 | 8.401 | 8.4011 | 1.1903e-05
GEN-2017-076 | Central | 12 - Northwest Arkansas | 515422 | C-RIVER7 | 345 | 9.9891 | 9.9892 | 1.0011e-05
GEN-2017-076 | Central | 12 - Northwest Arkansas | 514908 | ARCADIA7 | 345 | 30.6274 | 30.6277 | 9.7952e-06
GEN-2017-076 | Central | 12 - Northwest Arkansas | 515045 | SEMINOL7 | 345 | 26.7436 | 26.7438 | 7.4784e-06
GEN-2017-076 | Central | 12 - Northwest Arkansas | 510925 | KIOWA 7 | 345 | 13.4926 | 13.4927 | 7.4115e-06
GEN-2017-076 | Central | 12 - Northwest Arkansas | 510907 | PITTSB-7 | 345 | 13.7362 | 13.7363 | 7.28e-06
GEN-2017-076 | Central | 12 - Northwest Arkansas | 514909 | REDBUD 7 | 345 | 28.9322 | 28.9324 | 6.9127e-06
GEN-2017-076 | Central | 12 - Northwest Arkansas | 514934 | DRAPER 7 | 345 | 21.0659 | 21.066 | 4.747e-06
GEN-2017-076 | Central | 12 - Northwest Arkansas | 515044 | SEMINOL4 | 138 | 40.0909 | 40.091 | 2.4943e-06
GEN-2017-082 | Central | 12 - Northwest Arkansas | 588980 | GEN-2017-060 | 161 | 5.1425 | 5.7501 | 0.11815
GEN-2017-082 | Central | 12 - Northwest Arkansas | 589200 | GEN-2017-082 | 161 | 6.5984 | 7.2138 | 0.093265
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547476 | ASB349 5 | 161 | 9.8099 | 10.4272 | 0.062926
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547479 | LAR382 5 | 161 | 12.5231 | 13.142 | 0.049421
GEN-2017-082 | Central | 12 - Northwest Arkansas | 532932 | LITCH 5 | 161 | 8.3258 | 8.6426 | 0.03805
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547491 | PUR421 5 | 161 | 8.8 | 9.0825 | 0.032102
GEN-2017-082 | Central | 12 - Northwest Arkansas | 505488 | CARTHAG5 | 161 | 14.9914 | 15.4083 | 0.027809
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547477 | CJ 366 5 | 161 | 11.5152 | 11.8216 | 0.026608
GEN-2017-082 | Central | 12 - Northwest Arkansas | 532938 | FRANKLIN5 | 161 | 7.4171 | 7.6097 | 0.025967
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547485 | CAR395 5 | 161 | 11.2875 | 11.576 | 0.025559
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547490 | FIR417 5 | 161 | 13.2874 | 13.595 | 0.02315
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547467 | ORO110 5 | 161 | 18.1203 | 18.4918 | 0.020502
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547466 | ATL109 5 | 161 | 15.0356 | 15.3285 | 0.01948
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547494 | OAK432 5 | 161 | 16.4794 | 16.8003 | 0.019473
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533765 | LITCH N2 | 69 | 12.206 | 12.4335 | 0.018638
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533766 | LITCH S2 | 69 | 12.206 | 12.4335 | 0.018638
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533769 | PITNAC 2 | 69 | 10.7546 | 10.9282 | 0.016142
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547480 | MON383 5 | 161 | 10.9918 | 11.1548 | 0.014829
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533771 | ROUSE 2 | 69 | 9.1703 | 9.2932 | 0.013402
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533876 | FRANKLIN2 | 69 | 10.8288 | 10.9702 | 0.013058
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533759 | DEPAUL 2 | 69 | 9.0438 | 9.1617 | 0.013037
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547470 | JOP145 5 | 161 | 16.8006 | 17.0133 | 0.01266
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533770 | PITTSBG2 | 69 | 8.2424 | 8.3412 | 0.011987
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533775 | FRONTEN2 | 69 | 8.3192 | 8.4155 | 0.011576
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533764 | HUDSJCT2 | 69 | 7.8627 | 7.9533 | 0.011523
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533756 | AQUARS 2 | 69 | 7.82 | 7.9101 | 0.011522
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547498 | STL439 5 | 161 | 23.602 | 23.8627 | 0.011046
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533767 | MULBERY2 | 69 | 7.9236 | 8.0076 | 0.010601
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547469 | RIV4525 | 161 | 22.9986 | 23.2407 | 0.010527
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547503 | RIV452T 5 | 161 | 22.6118 | 22.8433 | 0.010238
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547459 | WWR477 | 161 | 21.5641 | 21.7815 | 0.010082
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547472 | TIP292 5 | 161 | 16.7605 | 16.9246 | 0.0097909
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547502 | RIV167 5 | 161 | 21.3713 | 21.578 | 0.0096718
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547501 | RIV453 5 | 161 | 21.8449 | 22.056 | 0.0096636
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533763 | HUDSON-2 | 69 | 6.2554 | 6.312 | 0.0090482
GEN-2017-082 | Central | 12 - Northwest Arkansas | 588504 | G17-005-TAP | 161 | 6.7929 | 6.8529 | 0.0088328
GEN-2017-082 | Central | 12 - Northwest Arkansas | 588500 | GEN-2017-005 | 161 | 6.71 | 6.7684 | 0.0087034
GEN-2017-082 | Central | 12 - Northwest Arkansas | 505486 | NEO SPA5 | 161 | 14.7701 | 14.8979 | 0.0086526
GEN-2017-082 | Central | 12 - Northwest Arkansas | 505490 | CARTHG 2 | 69 | 13.1587 | 13.2582 | 0.0075615
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547471 | NEO184 5 | 161 | 13.648 | 13.7498 | 0.007459
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547533 | ATL109 2 | 69 | 19.9663 | 20.1099 | 0.0071921
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547539 | JOP145 2 | 69 | 20.9516 | 21.0841 | 0.0063241
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547534 | ORO110 2 | 69 | 17.3555 | 17.4606 | 0.0060557
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547574 | JOP341 2 | 69 | 17.8753 | 17.9753 | 0.0055943
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547556 | OAK280 2 | 69 | 15.3404 | 15.4233 | 0.005404
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533762 | GIR JCT2 | 69 | 6.3087 | 6.3413 | 0.0051675
GEN-2017-082 | Central | 12 - Northwest Arkansas | 532934 | MARMTNE5 | 161 | 8.3607 | 8.3996 | 0.0046527
GEN-2017-082 | Central | 12 - Northwest Arkansas | 532935 | MARMTNW5 | 161 | 8.3607 | 8.3996 | 0.0046527
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547541 | RIV167 2 | 69 | 18.3903 | 18.47 | 0.0043338
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547487 | HOC404 5 | 161 | 12.821 | 12.8753 | 0.0042352
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533774 | SHEFFLD2 | 69 | 4.4202 | 4.4364 | 0.003665
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533761 | GIRARD 2 | 69 | 4.4138 | 4.4296 | 0.0035797
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547564 | SOL315 2 | 69 | 9.9339 | 9.969 | 0.0035334
GEN-2017-082 | Central | 12 - Northwest Arkansas | 532926 | BAKER 2 | 69 | 4.8588 | 4.8748 | 0.003293
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547527 | WEB436 2 | 69 | 9.2188 | 9.246 | 0.0029505
GEN-2017-082 | Central | 12 - Northwest Arkansas | 300751 | 2REEDS | 69 | 6.2071 | 6.2235 | 0.0026421
GEN-2017-082 | Central | 12 - Northwest Arkansas | 505492 | SPRGFLD5 | 161 | 26.7935 | 26.8628 | 0.0025864
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547431 | WEB105 2 | 69 | 7.7177 | 7.7371 | 0.0025137
GEN-2017-082 | Central | 12 - Northwest Arkansas | 300745 | 2DMNDTP | 69 | 5.2979 | 5.3106 | 0.0023972
GEN-2017-082 | Central | 12 - Northwest Arkansas | 543650 | DAKOTA_5 | 161 | 7.6687 | 7.6868 | 0.0023602
GEN-2017-082 | Central | 12 - Northwest Arkansas | 532937 | NEOSHO 5 | 161 | 21.328 | 21.3739 | 0.0021521
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533652 | WARE 2 | 69 | 3.444 | 3.4512 | 0.0020906
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533772 | SE1GREE2 | 69 | 5.9545 | 5.9667 | 0.0020489
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547690 | GLF339 2 | 69 | 9.0855 | 9.1038 | 0.0020142
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533021 | NEOSHO 4 | 138 | 23.0646 | 23.1093 | 0.001938
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533768 | NEOSHON2 | 69 | 22.3941 | 22.4333 | 0.0017505
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533778 | NEOSHOS2 | 69 | 22.3941 | 22.4333 | 0.0017505
GEN-2017-082 | Central | 12 - Northwest Arkansas | 543651 | PRQN_WIND5 | 161 | 6.5721 | 6.5832 | 0.001689
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533758 | CRAWFOR2 | 69 | 7.1173 | 7.129 | 0.0016439
GEN-2017-082 | Central | 12 - Northwest Arkansas | 300129 | 5WASHBRN | 161 | 7.7304 | 7.7425 | 0.0015652
GEN-2017-082 | Central | 12 - Northwest Arkansas | 300744 | 2DMNDGR | 69 | 2.474 | 2.4767 | 0.0010914
GEN-2017-082 | Central | 12 - Northwest Arkansas | 300649 | 2JASPER | 69 | 4.6934 | 4.6976 | 0.00089487
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533703 | ORDNJCT2 | 69 | 8.2819 | 8.2867 | 0.00057958
GEN-2017-082 | Central | 12 - Northwest Arkansas | 300653 | 2MEDOC | 69 | 2.3693 | 2.3703 | 0.00042207
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533702 | ORDNCE 2 | 69 | 5.9934 | 5.9958 | 0.00040044
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 588730 | GEN-2017-030 | 345 | 1.9361 | 2.3916 | 0.23527
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 588734 | G17-030-SWYD | 345 | 1.946 | 2.4011 | 0.23386
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 588736 | G17-030-TAP | 345 | 17.3162 | 17.6998 | 0.022153
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541400 | EASTOWN7 | 345 | 16.9906 | 17.2416 | 0.014773
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541199 | ST JOE 3 | 345 | 18.3626 | 18.5524 | 0.010336
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 542982 | IATAN 7 | 345 | 26.6621 | 26.9152 | 0.0094929
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 532772 | STRANGR7 | 345 | 24.9171 | 25.0555 | 0.0055544
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541200 | PHILL 7 | 345 | 17.1896 | 17.2807 | 0.0052997
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541401 | EASTOWN5 | 161 | 16.0995 | 16.1838 | 0.0052362
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 542980 | NASHUA 7 | 345 | 20.0559 | 20.1602 | 0.0052005
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541253 | ST JOE 5 | 161 | 18.8312 | 18.9279 | 0.0051351
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541258 | WOODBIN5 | 161 | 15.9201 | 15.9925 | 0.0045477
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541256 | IND PRK5 | 161 | 14.0882 | 14.1517 | 0.0045073
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541254 | EAST 5 | 161 | 14.7652 | 14.8312 | 0.00447
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541257 | COOK 5 | 161 | 13.0246 | 13.0728 | 0.0037007
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 300039 | 7FAIRPT | 345 | 12.0185 | 12.0611 | 0.0035445
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 542972 | HAWTH 7 | 345 | 20.5754 | 20.6473 | 0.0034945
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541255 | LAKE RD5 | 161 | 11.2867 | 11.325 | 0.0033934
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541355 | EDMOND5 | 161 | 11.5722 | 11.6114 | 0.0033874
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 542965 | W.GRDNR7 | 345 | 24.7636 | 24.8406 | 0.0031094
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 542977 | CRAIG 7 | 345 | 21.3649 | 21.4312 | 0.0031032
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541201 | SIBLEY 7 | 345 | 19.4936 | 19.5538 | 0.0030882
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 543665 | HAWTHN5 | 161 | 48.9327 | 49.0822 | 0.0030552
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 542973 | HAWTHS5 | 161 | 48.5017 | 48.6486 | 0.0030288
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 532775 | 87TH 7 | 345 | 20.0172 | 20.0774 | 0.0030074
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541354 | ALABAMA5 | 161 | 9.9879 | 10.0179 | 0.0030036
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 542978 | CRAIG 5 | 161 | 38.3482 | 38.4581 | 0.0028658
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541414 | SIB REA1 | 345 | 17.4648 | 17.5131 | 0.0027656
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 542976 | LEVEE 5 | 161 | 43.6062 | 43.7256 | 0.0027381
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 543028 | NASHUA-5 | 161 | 25.9332 | 25.9939 | 0.0023406
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541203 | NASHUA 5 | 161 | 25.8323 | 25.8924 | 0.0023265
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 543000 | BLUEVLY5 | 161 | 34.4014 | 34.4745 | 0.0021249
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 543011 | CHOUTEU5 | 161 | 31.0216 | 31.0849 | 0.0020405
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541202 | SIBLEY 5 | 161 | 25.3037 | 25.3548 | 0.0020195
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541350 | IATAN5 | 161 | 14.4641 | 14.4929 | 0.0019911
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 533268 | STRANGR3 | 115 | 32.9223 | 32.9872 | 0.0019713
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 543027 | RANDLPH5 | 161 | 29.3518 | 29.4075 | 0.0018977
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541204 | SMTHVL 5 | 161 | 19.7347 | 19.7702 | 0.0017989
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541230 | RNRIDGE5 | 161 | 20.9173 | 20.9528 | 0.0016972
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541351 | WESTON 5 | 161 | 12.5686 | 12.5888 | 0.0016072
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 543026 | TIFFANY5 | 161 | 18.5206 | 18.5477 | 0.0014632
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541221 | PLTCTY 5 | 161 | 15.0998 | 15.1216 | 0.0014437
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541318 | NCONGRS5 | 161 | 17.2377 | 17.2621 | 0.0014155
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 588240 | GEN-2016-149 | 345 | 8.5381 | 8.5494 | 0.0013235
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 543019 | BARRY 5 | 161 | 16.8595 | 16.8817 | 0.0013168
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 300076 | 5FAIRPT | 161 | 16.318 | 16.3393 | 0.0013053
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 543029 | SHOLCRK5 | 161 | 15.9418 | 15.9619 | 0.0012608
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 543016 | GLADSTN5 | 161 | 16.8156 | 16.8364 | 0.0012369
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 533283 | 87TH 3 | 115 | 25.8886 | 25.9192 | 0.001182
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 640139 | COOPER 3 | 345 | 26.0325 | 26.0632 | 0.0011793
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541247 | LBRTYWT5 | 161 | 13.9111 | 13.9275 | 0.0011789
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 533244 | JARBALO3 | 115 | 24.9331 | 24.9624 | 0.0011751
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541212 | KCI 5 | 161 | 12.4135 | 12.4273 | 0.0011117
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541349 | POPE | 161 | 12.0913 | 12.1046 | 0.0011
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 532765 | HOYT 7 | 345 | 15.8298 | 15.8458 | 0.0010108
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 533281 | MNTCLLO3 | 115 | 22.0226 | 22.0441 | 0.00097627
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 533259 | NW LEAV3 | 115 | 15.9564 | 15.9712 | 0.00092753
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541394 | AVENUECTY 5 | 161 | 6.1272 | 6.1327 | 0.00089764
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 533272 | THORNTN3 | 115 | 15.1424 | 15.1555 | 0.00086512
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 533266 | SPRUCE 3 | 115 | 14.4909 | 14.503 | 0.00083501
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 543022 | CLAYCM15 | 161 | 10.4832 | 10.4918 | 0.00082036
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 533274 | FRTLEAV3 | 115 | 14.1202 | 14.1317 | 0.00081444
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 533233 | 166TH 3 | 115 | 15.7773 | 15.7884 | 0.00070354
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 533273 | TIMBRLN3 | 115 | 13.0983 | 13.1072 | 0.00067948
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 533242 | HALLMRK3 | 115 | 12.042 | 12.0501 | 0.00067265
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 301347 | 5WINSLOW | 161 | 8.9923 | 8.9983 | 0.00066724
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 533278 | WAVERLY3 | 115 | 14.1294 | 14.1388 | 0.00066528
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 588250 | GEN-2016-174 | 345 | 5.6405 | 5.6442 | 0.00065597
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 635017 | ATCHSN 3 | 345 | 16.7077 | 16.7171 | 0.00056261
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 533219 | TONGATP3 | 115 | 14.9588 | 14.9669 | 0.00054149
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 533246 | EFAIRMNT3 | 115 | 10.5334 | 10.539 | 0.00053164
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 300073 | 5GENTRY | 161 | 10.041 | 10.0463 | 0.00052784
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 635018 | WESTBORO 3 | 345 | 15.9341 | 15.9422 | 0.00050834
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 637084 | J476 SHENHLL | 345 | 15.8534 | 15.8613 | 0.00049832
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 300249 | 2FAIRPT | 69 | 16.6356 | 16.6437 | 0.00048691
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 300107 | 5OSBORN | 161 | 7.2124 | 7.2159 | 0.00048528
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541500 | KETCHEM7 | 345 | 7.9687 | 7.9725 | 0.00047687
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541392 | EDMOND2 | 69 | 3.4441 | 3.4456 | 0.00043553
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 588300 | GEN-2016-157 | 345 | 4.8966 | 4.8987 | 0.00042887
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541501 | OSBORN7 | 345 | 7.0589 | 7.0619 | 0.000425
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 533249 | LEC U4 3 | 115 | 23.4267 | 23.4365 | 0.00041833
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 588310 | GEN-2016-158 | 345 | 4.623 | 4.6249 | 0.00041099
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541369 | MIDWAY_5 | 161 | 6.1006 | 6.1031 | 0.0004098
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 587730 | GEN-2016-088 | 345 | 6.8982 | 6.901 | 0.0004059
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 533216 | KERFORD3 | 115 | 7.2631 | 7.266 | 0.00039928
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 533163 | HOYT 3 | 115 | 22.8296 | 22.8386 | 0.00039423
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 532766 | JEC N 7 | 345 | 23.7515 | 23.7608 | 0.00039155
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 533211 | ARNOLD 3 | 115 | 7.2397 | 7.2425 | 0.00038676
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 588260 | GEN-2016-176 | 345 | 4.2174 | 4.219 | 0.00037938
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 533215 | AMELIA 3 | 115 | 6.6338 | 6.6361 | 0.00034671
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 300307 | 2PLATCTY | 69 | 8.4195 | 8.4221 | 0.00030881
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 640140 | COOPER 5 | 161 | 17.2241 | 17.2293 | 0.0003019
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 533218 | PARALEL3 | 115 | 5.6524 | 5.6541 | 0.00030076
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 533240 | EUDORA 3 | 115 | 10.9888 | 10.9921 | 0.00030031
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 345408 | 7OVERTON | 345 | 12.3948 | 12.3985 | 0.00029851
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 645458 | S3458 3 | 345 | 28.5379 | 28.5463 | 0.00029435
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 533165 | HTI JCT3 | 115 | 16.6213 | 16.626 | 0.00028277
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 588270 | GEN-2016-150 | 345 | 3.2201 | 3.221 | 0.00027949
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 533156 | 54&MERI3 | 115 | 15.8856 | 15.8894 | 0.00023921
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 533164 | HTI 3 | 115 | 13.4469 | 13.4499 | 0.0002231
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541391 | SAVANAH2 | 69 | 1.803 | 1.8034 | 0.00022185
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 533169 | NTHLAND3 | 115 | 15.8874 | 15.8909 | 0.0002203
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541510 | HOLT 7 | 345 | 9.7395 | 9.7415 | 0.00020535
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 533471 | ARNOLD 2 | 69 | 7.3075 | 7.309 | 0.00020527
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541517 | HOLT_REACT7 | 345 | 9.6829 | 9.6848 | 0.00019622
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 532852 | JEC 6 | 230 | 24.7642 | 24.769 | 0.00019383
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 300087 | 5HICKCK | 161 | 5.1766 | 5.1776 | 0.00019318
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 532770 | MORRIS 7 | 345 | 12.8666 | 12.8689 | 0.00017876
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541260 | RNRDGE 2 | 69 | 4.818 | 4.8187 | 0.00014529
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541511 | ROCKCK7 | 345 | 7.3804 | 7.3814 | 0.00013549
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 587920 | GEN-2016-115 | 345 | 6.944 | 6.9449 | 0.00012961
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541368 | MIDWY1 2 | 69 | 3.8978 | 3.8983 | 0.00012828
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541390 | MIDWY2 2 | 69 | 3.903 | 3.9035 | 0.00012811
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 640590 | MONOLITH 3 | 345 | 22.0965 | 22.0991 | 0.00011767
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 640277 | MOORE 3 | 345 | 22.5709 | 22.5735 | 0.00011519
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541389 | MDWYTP 2 | 69 | 3.7322 | 3.7326 | 0.00010718
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541376 | AMOILTP2 | 69 | 3.7684 | 3.7688 | 0.00010615
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 650189 | 103&ROKEBY3 | 345 | 20.1555 | 20.1576 | 0.00010419
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 646280 | S1280 5 | 161 | 9.7037 | 9.7047 | 0.00010305
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541358 | AMOIL 2 | 69 | 3.8848 | 3.8852 | 0.00010297
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 532767 | GEARY 7 | 345 | 10.3227 | 10.3237 | 9.6874e-05
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 645456 | S3456 3 | 345 | 30.6166 | 30.619 | 7.8389e-05
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541377 | KELLOG 2 | 69 | 2.5568 | 2.557 | 7.8223e-05
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541366 | MNDCITY2 | 69 | 1.3024 | 1.3025 | 7.6781e-05
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 645740 | S3740 3 | 345 | 17.2834 | 17.2846 | 6.9431e-05
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 541367 | BRWNCRV2 | 69 | 1.605 | 1.6051 | 6.2305e-05
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 640591 | MONOLITH 7 | 115 | 42.3932 | 42.3953 | 4.9536e-05
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 560746 | GEN-2013-002 | 115 | 42.3932 | 42.3953 | 4.9536e-05
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 583700 | GEN-2013-019 | 115 | 42.3932 | 42.3953 | 4.9536e-05
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 640141 | COOPER_ESST8 | 69 | 4.4581 | 4.4583 | 4.4862e-05
GEN-2017-030 | Central | 13 - Northeast Kansas/Northwest Missouri | 640446 | COOPER 8 | 69 | 4.5511 | 4.5513 | 4.3945e-05
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 589280 | GEN-2017-090 | 161 | 5.0958 | 6.4026 | 0.25645
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541240 | ADRIAN 5 | 161 | 7.5635 | 8.771 | 0.15965
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 301342 | 5BUTLER | 161 | 6.278 | 6.8228 | 0.086779
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541207 | ARCHIE 5 | 161 | 13.3178 | 14.1155 | 0.059897
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541239 | HSNVL 5 | 161 | 13.4501 | 13.9403 | 0.036446
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541208 | NEVADA 5 | 161 | 5.6495 | 5.7821 | 0.023471
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541341 | S.HARP 5 | 161 | 18.9418 | 19.2777 | 0.017733
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300689 | 2BUTLER | 69 | 5.7195 | 5.8125 | 0.01626
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541344 | PECULRS5 | 161 | 19.6527 | 19.9154 | 0.013367
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300707 | 2PL GAP | 69 | 4.6323 | 4.6891 | 0.012262
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300070 | 5CLARK | 161 | 7.5209 | 7.6077 | 0.011541
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300690 | 2BUTLERE | 69 | 4.5861 | 4.639 | 0.011535
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541342 | PECULR 5 | 161 | 21.0636 | 21.3042 | 0.011423
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541225 | PHILL 5 | 161 | 30.7679 | 31.0587 | 0.0094514
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541340 | BELTONS5 | 161 | 17.945 | 18.0896 | 0.008058
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300697 | 2CRESTH | 69 | 3.1272 | 3.1498 | 0.0072269
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541243 | LKWINGB5 | 161 | 23.3724 | 23.524 | 0.0064863
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300709 | 2SHARSNV | 69 | 6.1058 | 6.1445 | 0.0063382
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541313 | HARRIS | 161 | 23.0849 | 23.2294 | 0.0062595
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541308 | NEVADA 2 | 69 | 4.3826 | 4.4099 | 0.0062292
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541198 | PECULR 7 | 345 | 18.7576 | 18.8701 | 0.0059976
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300699 | 2ELYNTP | 69 | 5.8335 | 5.8684 | 0.0059827
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541307 | NEVPLT 2 | 69 | 4.1244 | 4.1486 | 0.0058675
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 542969 | STILWEL5 | 161 | 36.5596 | 36.773 | 0.005837
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300708 | 2RICHHIL | 69 | 3.0706 | 3.0878 | 0.0056015
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541249 | HOOKRD 5 | 161 | 21.6409 | 21.7609 | 0.0055451
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541218 | GRNWD 5 | 161 | 21.0848 | 21.1972 | 0.0053309
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541200 | PHILL 7 | 345 | 17.1896 | 17.2807 | 0.0052997
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541295 | HSNVL 2 | 69 | 7.9986 | 8.0406 | 0.0052509
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 542968 | STILWEL7 | 345 | 23.0198 | 23.1391 | 0.0051825
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300704 | 2METZ | 69 | 2.9821 | 2.9965 | 0.0048288
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541309 | METZ 2 | 69 | 3.3616 | 3.3778 | 0.0048191
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300700 | 2FREEMN | 69 | 2.7946 | 2.808 | 0.004795
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541311 | NEVJCT 2 | 69 | 3.314 | 3.3298 | 0.0047677
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 543002 | MARTCIT5 | 161 | 22.8469 | 22.952 | 0.0046002
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300705 | 2PECULR | 69 | 3.2162 | 3.2306 | 0.0044773
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541296 | HSNVLSW2 | 69 | 7.3327 | 7.3652 | 0.0044322
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541310 | 3M 2 | 69 | 3.0569 | 3.0703 | 0.0043835
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541294 | HSNVLS 2 | 69 | 6.8003 | 6.8301 | 0.0043822
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 543053 | REDEL 5 | 161 | 22.8591 | 22.9535 | 0.0041296
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300794 | 5LAMAR | 161 | 8.3677 | 8.4008 | 0.0039557
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541293 | HSNVLW 2 | 69 | 6.1627 | 6.1868 | 0.0039106
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541292 | ANCONDA2 | 69 | 6.0642 | 6.0874 | 0.0038257
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300793 | 5HYDERHL | 161 | 7.9953 | 8.0249 | 0.0037022
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 542993 | STHTOWN5 | 161 | 32.8241 | 32.9439 | 0.0036498
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541297 | HSNVLN 2 | 69 | 6.733 | 6.7568 | 0.0035348
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300802 | 2CLARK | 69 | 6.1639 | 6.1844 | 0.0033258
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300698 | 2ELYNNE | 69 | 3.1551 | 3.1654 | 0.0032646
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541316 | LONEJACK | 161 | 12.4467 | 12.4857 | 0.0031334
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 542965 | W.GRDNR7 | 345 | 24.7636 | 24.8406 | 0.0031094
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541201 | SIBLEY 7 | 345 | 19.4936 | 19.5538 | 0.0030882
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300118 | 5STKAEC | 161 | 8.6192 | 8.6458 | 0.0030861
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300814 | 2WALKER | 69 | 4.5979 | 4.612 | 0.0030666
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300688 | 2AUSTIN | 69 | 4.1597 | 4.1719 | 0.0029329
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300706 | 2PIPER | 69 | 3.5543 | 3.5643 | 0.0028135
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 543050 | ANTIOCH5 | 161 | 21.2006 | 21.2597 | 0.0027877
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541414 | SIB REA1 | 345 | 17.4648 | 17.5131 | 0.0027656
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 543057 | BUCYRUS5 | 161 | 19.4208 | 19.4734 | 0.0027084
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541298 | GRDNCTY2 | 69 | 3.9319 | 3.9413 | 0.0023907
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541291 | FREEMAN2 | 69 | 4.2856 | 4.2957 | 0.0023567
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541299 | GUNNPS2 | 69 | 3.7633 | 3.7719 | 0.0022852
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541343 | S.HARP 2 | 69 | 4.3341 | 4.3439 | 0.0022611
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 542994 | HICKMAN5 | 161 | 18.2777 | 18.3189 | 0.0022541
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541499 | SHELDON_69 | 69 | 1.5534 | 1.5569 | 0.0022531
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541280 | PHILL 2 | 69 | 9.9311 | 9.9532 | 0.0022253
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541279 | RGREEN 2 | 69 | 9.2094 | 9.2298 | 0.0022151
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300654 | 2MILO | 69 | 5.0888 | 5.0999 | 0.0021813
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 543046 | OXFORD 5 | 161 | 19.3743 | 19.4145 | 0.0020749
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 543126 | LACKMAN5 | 161 | 12.947 | 12.9708 | 0.0018383
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300950 | 5JASPER | 161 | 12.2914 | 12.3134 | 0.0017899
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300071 | 5CLINTN | 161 | 11.4578 | 11.478 | 0.001763
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541242 | CLINTON5 | 161 | 11.4194 | 11.4394 | 0.0017514
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300692 | 2CLINTN | 69 | 12.7012 | 12.7219 | 0.0016298
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300651 | 2LAMR | 69 | 9.5635 | 9.579 | 0.0016207
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 543068 | WAGSTAF5 | 161 | 13.5774 | 13.5991 | 0.0015982
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 542981 | LACYGNE7 | 345 | 24.7651 | 24.8029 | 0.0015263
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 543629 | LACYGNE11_7 | 345 | 24.1508 | 24.1868 | 0.0014906
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 543632 | LACYGNE22_7 | 345 | 24.1508 | 24.1868 | 0.0014906
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300798 | 2HYDERHL | 69 | 7.9428 | 7.9546 | 0.0014856
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541347 | RAYMORE | 69 | 7.926 | 7.9377 | 0.0014762
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 532914 | SPRGHL 5 | 161 | 10.4977 | 10.5125 | 0.0014098
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541312 | LAMAR 2 | 69 | 0.9984 | 0.9998 | 0.0014022
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300685 | 2LAMARPT | 69 | 8.0862 | 8.0973 | 0.0013727
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541306 | APCITY 2 | 69 | 2.3412 | 2.3443 | 0.0013241
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 301477 | 5OSCEOKC | 161 | 6.1508 | 6.1587 | 0.0012844
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 543058 | NLOUISB5 | 161 | 8.7654 | 8.7761 | 0.0012207
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300645 | 2BRONA | 69 | 2.1295 | 2.1314 | 0.00089223
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541304 | URICHTP2 | 69 | 3.0174 | 3.02 | 0.00086167
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541217 | WINDSR 5 | 161 | 7.094 | 7.0996 | 0.0007894
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300652 | 2LAMRCTS | 69 | 3.7447 | 3.7471 | 0.00064091
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541305 | URICH 2 | 69 | 2.1742 | 2.1755 | 0.00059792
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300124 | 5HOLDEN | 161 | 10.5015 | 10.5067 | 0.00049517
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 588300 | GEN-2016-157 | 345 | 4.8966 | 4.8987 | 0.00042887
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 588310 | GEN-2016-158 | 345 | 4.623 | 4.6249 | 0.00041099
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 505502 | TRUMAN 5 | 161 | 7.0374 | 7.0401 | 0.00038366
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 543659 | LACYGNE2 | 69 | 8.4734 | 8.4743 | 0.00010621
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 543669 | LAC8_STAR7 | 345 | 0.6133 | 0.6133 | 0
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 543667 | LAC3_STAR7 | 345 | 0.6403 | 0.6403 | 0