## Executive Summary
Executive Summary: DISIS-2017-001 Phase Two Power Flow
Pursuant to the Southwest Power Pool (SPP) Open Access Transmission Tariff (OATT), SPP has conducted this Definitive Interconnection System Impact Study (DISIS) for generation interconnection requests received during the DISIS Queue Cluster Window which closed on March 31, 2017. The primary objective of this DISIS is to identify the system constraints, transient instabilities, and over-dutied equipment associated with connecting the generation to the area transmission system. The Impact Study and other subsequent Interconnection Studies are designed to identify required Transmission Owner Interconnection Facilities, Network Upgrades and other Direct Assignment Facilities needed to inject power into the grid at each specific point of interconnection. The study analysis for the generation interconnection requests included in this DISIS are displayed in this workbook. This workbook provides a convenient method to sort and analyze required study data. The DISIS Manual Version 1.3 posted on http://opsportal.spp.org/Studies/Gen contains details about the DISIS process, methodology, definitions, and useful links. Please review the DISIS Manual or contact gistudies@spp.org for more information about the study process. DISIS-2017-001 Phase 2 includes study requests in the following cluster groups: 01 - Woodward, 02 - Hitchland, 03 - Spearville, 04 - Northwest Kansas, 06 - South Texas Panhandle/New Mexico, 07 - Southwestern Oklahoma, 08 - North Oklahoma/South Central Kansas, 09 - Nebraska, 10 - Southeast Oklahoma/Northeast Texas, 12 - Northwest Arkansas, 13 - Northeast Kansas/Northwest Missouri, 14 - South Central Oklahoma, 15 - Eastern South Dakota, 16 - Western North Dakota, 17 - Western South Dakota NOTE: per SPP Tariff Attachment V; section 8.4.2 DISIS Phase Two will consist of a power flow analysis, a stability analysis and a short-circuit analysis.
DISIS Manual Version 1.3
https://opsportal.spp.org/documents/studies/DISIS%20Manual.pdf
This DISIS analyzes the impact of interconnecting new generation for total of:
10398 MW
The minimum cost, including both power flow and stability, of interconnecting all requests included in this DISIS is estimated at:
4818214558.78
Models Used in Study
2019 ITP Series
Winter: 2019, 2024
Summer: 2020, 2024, 2029
Light: 2024 & Spring: 2020
By: SPP Generator Interconnection Department
Published: April 7, 2021

## Revision History
Revision History
Date | Author | Change Description
2020-10-29 | SPP | Phase 1 Posting
2020-11-18 | SPP | Phase One Report Workbook has been updated to adjust 3.7% of assigned upgrade costs. Updates include Interconnection Upgrades cost adjustment totaling $10,681,245.00 and reallocation of Network Upgrade cost assignments totaling $315,101,329.37. Details regarding all report updates are included in the "Revision Details" tab for tracking.
2021-04-07 | SPP | Phase 2 Posting

## Revision Details
Revision Date | Update Type | Tab Order | Results Data Tab | Update Details

## Requests
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | LOIS Amount | Service | Area | POI | Status
GEN-2016-037 | 07 - Southwestern Oklahoma | 18 | DIS-17-1 | Wind | 300 | 300 | ER | AEPW | Chisholm-Gracemont 345kV | DISIS STAGE
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 112 | 61.2 | ER | SPS | Swisher 115kV | DISIS STAGE
GEN-2016-103 | 15 - Eastern South Dakota | 18 | DIS-17-1 | Wind | 240 | 0 | ER | WAPA | Fort Thompson-Leland Olds 345kV | DISIS STAGE
GEN-2016-159 | 09 - Nebraska | 18 | DIS-17-1 | Wind | 427.8 | 257.7 | ER | NPPD | Turtle Creek 345kV | DISIS STAGE
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 231 | 201.1 | ER | SPS | Newhart 115kV | DISIS STAGE
GEN-2017-004 | 04 - Northwest Kansas | 18 | DIS-17-1 | Wind | 201.6 | 201.6 | ER | SUNC | Elm Creek - Summit 345kV | DISIS STAGE
GEN-2017-005 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Wind | 190 | 188 | ER | WERE | Marmaton - Litchfield 161kV | DISIS STAGE
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 297.5 | 270.9 | ER | SPS | Pleasant Hill 230kV sub | DISIS STAGE
GEN-2017-008 | 09 - Nebraska | 18 | DIS-17-1 | Solar | 305 | 158.6 | ER | NPPD | Pauline 345kV Substation | DISIS STAGE
GEN-2017-009 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Wind | 302 | 0 | ER | WERE | Neosho - Caney River 345kV | DISIS STAGE
GEN-2017-010 | 16 - Western North Dakota | 18 | DIS-17-1 | Wind | 200.1 | 0 | ER | WAPA | Rhame 230kV Sub | DISIS STAGE
GEN-2017-011 | 01 - Woodward | 18 | DIS-17-1 | Solar | 151.8 | 151.8 | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | DISIS STAGE
GEN-2017-013 | 04 - Northwest Kansas | 18 | DIS-17-1 | Wind | 200 | 200 | ER/NR | SUNC | Mingo 345kV | DISIS STAGE
GEN-2017-014 | 17 - Western South Dakota | 18 | DIS-17-1 | Wind | 300 | 293.8 | ER/NR | WAPA | Underwood - Philip Tap 230kV | DISIS STAGE
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 33 | 6.3 | ER/NR | SPS | Norton 115kV Switching Station | DISIS STAGE
GEN-2017-018 | 03 - Spearville | 18 | DIS-17-1 | Solar | 189 | 189.9 | ER/NR | SUNC | Thistle 345kV sub | DISIS STAGE
GEN-2017-021 | 03 - Spearville | 18 | DIS-17-1 | Wind | 200 | 197.5 | ER/NR | SUNC | Post Rock - Spearville 345kV | DISIS STAGE
GEN-2017-022 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 65 | 18.3 | ER/NR | WERE | Altoona- NE Parson 138kV | DISIS STAGE
GEN-2017-023 | 14 - South Central Oklahoma | 18 | DIS-17-1 | Solar | 85 | 84.5 | ER/NR | WFEC | Hugo Power Plant 138kV Sub | DISIS STAGE
GEN-2017-024 | 14 - South Central Oklahoma | 18 | DIS-17-1 | Solar | 50 | 49.4 | ER/NR | WFEC | Frogville 138kV sub | DISIS STAGE
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 235 | 210.3 | ER/NR | SPS | Tolk 230kV | DISIS STAGE
GEN-2017-027 | 14 - South Central Oklahoma | 18 | DIS-17-1 | Wind | 140 | 137.1 | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV | DISIS STAGE
GEN-2017-028 | 01 - Woodward | 18 | DIS-17-1 | Solar | 50 | 50 | ER/NR | OKGE | El Reno SW 138kV switch station | DISIS STAGE
GEN-2017-030 | 13 - Northeast Kansas/Northwest Missouri | 18 | DIS-17-1 | Wind | 200 | 194.1 | ER | KCPL | Eastown - Iatan 345kV | DISIS STAGE
GEN-2017-031 | 09 - Nebraska | 18 | DIS-17-1 | Wind | 100 | 0 | ER | NPPD | Wildhorse - Covalt 115kV | DISIS STAGE
GEN-2017-032 | 03 - Spearville | 18 | DIS-17-1 | Wind | 200 | 196.2 | ER | SPS | Finney - Lamar 345kV | DISIS STAGE
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 200 | 200 | ER/NR | AEPW | Oklaunion 345kV sub | DISIS STAGE
GEN-2017-036 | 07 - Southwestern Oklahoma | 18 | DIS-17-1 | Solar | 100 | 100 | ER | WFEC | Snyder - Cache 138kV | DISIS STAGE
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 200.1 | 173.7 | ER | SPS | Needmore 230kV sub | DISIS STAGE
GEN-2017-040 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Wind | 200.1 | 163 | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | DISIS STAGE
GEN-2017-047 | 02 - Hitchland | 18 | DIS-17-1 | Wind | 102 | 102 | ER/NR | SPS | Cole 115kV | DISIS STAGE
GEN-2017-048 | 16 - Western North Dakota | 18 | DIS-17-1 | Wind | 300 | 292.7 | ER | WAPA | Neset 230kV | DISIS STAGE
GEN-2017-051 | 07 - Southwestern Oklahoma | 18 | DIS-17-1 | Solar | 30 | 30 | ER | OMPA | Tap Lake Creek SW - Russell SW 69kV | DISIS STAGE
GEN-2017-052 | 03 - Spearville | 18 | DIS-17-1 | Solar | 25 | 21 | ER | SUNC | Tap Bear Creek-Johnson Corner 115kV | DISIS STAGE
GEN-2017-055 | 09 - Nebraska | 18 | DIS-17-1 | Solar | 228.25 | 119.2 | ER/NR | LES | Wagener 115kV Sub | DISIS STAGE
GEN-2017-057 | 10 - Southeast Oklahoma/Northeast Texas | 18 | DIS-17-1 | Solar | 72.5 | 72.5 | ER | AEPW | Hosston 69kV | DISIS STAGE
GEN-2017-058 | 02 - Hitchland | 18 | DIS-17-1 | Solar | 135 | 135 | ER | SPS | Hereford Northeast 115kV | DISIS STAGE
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 90 | 19.3 | ER/NR | SPS | TUCO 230kV | DISIS STAGE
GEN-2017-060 | 12 - Northwest Arkansas | 18 | DIS-17-1 | Wind | 149.4 | 149.4 | ER | EMDE | LaRussell Energy Center 161kV | DISIS STAGE
GEN-2017-061 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 101.5 | 2.4 | ER/NR | GRDA | GRDA1 to CLARMR 5 161kV line | DISIS STAGE
GEN-2017-064 | 17 - Western South Dakota | 18 | DIS-17-1 | Solar | 110 | 107.1 | ER/NR | WAPA | Underwood - Wayside 230kV | DISIS STAGE
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 200.25 | 200.3 | ER/NR | AEPW | Oklaunion 345kV sub | DISIS STAGE
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 103.5 | 0 | ER/NR | WERE | Wichita 345kV | DISIS STAGE
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 1.8 | 0.1 | ER/NR | SPS | Norton 115kV Switching Station | DISIS STAGE
GEN-2017-071 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 124.7 | 0 | ER | OKGE | Greenwood 138kV sub | DISIS STAGE
GEN-2017-072 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 52.2 | 0 | ER | OKGE | Greenwood 138kV sub | DISIS STAGE
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 72.5 | 0 | ER | GRDA | Dry Gulch 161kV sub | DISIS STAGE
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 72.5 | 0 | ER | AEPW | Pryor Junction 138kV sub | DISIS STAGE
GEN-2017-075 | 14 - South Central Oklahoma | 18 | DIS-17-1 | Solar | 200 | 198.8 | ER | OKGE | Hugo-Sunnyside 345kV | DISIS STAGE
GEN-2017-076 | 12 - Northwest Arkansas | 18 | DIS-17-1 | Solar | 52.2 | 52.2 | ER | AEPW | Chamber Springs 161kV sub | DISIS STAGE
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 124.7 | 44.5 | ER | AEPW | Explorer Claremore Tap EXCLART4 | DISIS STAGE
GEN-2017-078 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 220 | 200.9 | ER/NR | SPS | Eddy County-Tolk (Crossroads) 345kV | DISIS STAGE
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 525 | 500.3 | ER | SPS | Tolk 230kV | DISIS STAGE
GEN-2017-082 | 12 - Northwest Arkansas | 18 | DIS-17-1 | Wind | 149.4 | 149.4 | ER | EMDE | Asbury Plant 161kV | DISIS STAGE
GEN-2017-085 | 09 - Nebraska | 18 | DIS-17-1 | Wind | 0.6 | 0 | ER/NR | NPPD | Friend 115kV | DISIS STAGE
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Wind | 150 | 0 | ER | WERE | Viola 345kV | DISIS STAGE
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 128 | 101.3 | ER | SPS | Clovis Interchange 115kV | DISIS STAGE
GEN-2017-090 | 13 - Northeast Kansas/Northwest Missouri | 18 | DIS-17-1 | Solar | 150 | 150 | ER | KCPL | Adrian 161kV sub | DISIS STAGE
GEN-2017-092 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 200 | 162.9 | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | DISIS STAGE
GEN-2017-094 | 15 - Eastern South Dakota | 18 | DIS-17-1 | Wind | 200 | 189.6 | ER/NR | WAPA | Fort Thompson-Huron 230kV | DISIS STAGE
GEN-2017-097 | 17 - Western South Dakota | 18 | DIS-17-1 | Solar | 128 | 123.6 | ER | WAPA | Underwood 115kV Sub | DISIS STAGE
GEN-2017-099 | 03 - Spearville | 18 | DIS-17-1 | Wind | 150 | 147.5 | ER/NR | SUNC | Post Rock - Spearville 345kV | DISIS STAGE
GEN-2017-100 | 02 - Hitchland | 18 | DIS-17-1 | Solar | 102.6 | 102.6 | ER/NR | SPS | Texas County 115kV | DISIS STAGE
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 240 | 160.4 | ER/NR | SPS | Hobbs 230kV | DISIS STAGE
ASGI-2018-001GIA-61 | 13 - Northeast Kansas/Northwest Missouri | 17.5 | DIS-17-1-PQ | Wind | 242 |  | ER/NR | AECI | Maryville 161kV
BEPCAyrshire | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Wind | 21 |  | ER | BEPC-SPP | Ayershire 69kV
BEPCGerled | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Wind | 10.5 |  | ER | BEPC-SPP | Gerled Tap 69kV
BEPCHummel | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Wind | 10.5 |  | ER | BEPC-SPP | Hummel 69kV
BEPCNDPW0 | 16 - Western North Dakota | 17.5 | DIS-17-1-PQ | Wind | 7.5 |  | ER | BEPC-SPP | SW Minot 115kV
BEPCNDPW1 | 16 - Western North Dakota | 17.5 | DIS-17-1-PQ | Wind | 5 |  | ER | BEPC-SPP | ND Prairie Wind 115kV
J718 | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Solar | 49.98 |  | ER/NR | XEL
J748 | 09 - Nebraska | 17.5 | DIS-17-1-PQ | Wind | 200 |  | ER/NR | MEC
NPPDSpringview | 09 - Nebraska | 17.5 | DIS-17-1-PQ | Wind | 3 |  | ER | NPPD
SPSChanning | 06 - South Texas Panhandle/New Mexico | 17.5 | DIS-17-1-PQ | Wind | 4.2 |  | ER | SPS
SPSLeaCounty | 06 - South Texas Panhandle/New Mexico | 17.5 | DIS-17-1-PQ | Solar | 5.5 |  | ER | SPS
SWPANixaSolar | 12 - Northwest Arkansas | 17.5 | DIS-17-1-PQ | Solar | 7.9 |  | ER | SWPA
WAPAMPSWind | 18 - Eastern North Dakota | 17.5 | DIS-17-1-PQ | Wind | 1.5 |  | ER | WAPA
WAPATitanWind | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Wind | 25 |  | ER | WAPA
ASGI-2016-010 | 02 - Hitchland | 17 | DIS-16-2 | Wind | 90 |  | ER | SPS | Powell Corner 115kV
GEN-2016-036 | 15 - Eastern South Dakota | 17 | DIS-16-2 | Wind | 44.6 |  | ER | WAPA | Granite Falls 115kV | FACILITY STUDY STAGE
GEN-2016-074 | 09 - Nebraska | 17 | DIS-16-2 | Wind | 200 |  | ER | NPPD | Sweetwater 345kV | FACILITY STUDY STAGE
GEN-2016-087 | 15 - Eastern South Dakota | 17 | DIS-16-2 | Wind | 98.9 |  | ER | WAPA | Bismark-Glenham 230kV line | FACILITY STUDY STAGE
GEN-2016-088 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 151.2 |  | ER/NR | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-091 | 07 - Southwestern Oklahoma | 17 | DIS-16-2 | Wind | 303.6 |  | ER | AEPW | Gracemont-Lawton East Side 345kV | IA PENDING
GEN-2016-092 | 15 - Eastern South Dakota | 17 | DIS-16-2 | Wind | 175 |  | ER | WAPA | Fort Thompson-Leland Olds 345kV | FACILITY STUDY STAGE
GEN-2016-094 | 17 - Western South Dakota | 17 | DIS-16-2 | Wind | 200 |  | ER | WAPA | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | FACILITY STUDY STAGE
GEN-2016-095 | 07 - Southwestern Oklahoma | 17 | DIS-16-2 | Wind | 200 |  | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | FACILITY STUDY STAGE
GEN-2016-097 | 07 - Southwestern Oklahoma | 17 | DIS-16-2 | Wind | 100 |  | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | FACILITY STUDY STAGE
GEN-2016-100 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 100 |  | ER | OKGE | Spring Creek-Sooner 345kV | FACILITY STUDY STAGE
GEN-2016-101 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 195 |  | ER | OKGE | Spring Creek-Sooner 345kV | FACILITY STUDY STAGE
GEN-2016-102 | 14 - South Central Oklahoma | 17 | DIS-16-2 | Wind | 150.9 |  | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-106 | 09 - Nebraska | 17 | DIS-16-2 | Wind | 400 |  | ER | NPPD | Gerald Gentleman Station 345kV | FACILITY STUDY STAGE
GEN-2016-110 | 09 - Nebraska | 17 | DIS-16-2 | Wind | 152 |  | ER | WAPA | Laramie River-Stegall 345kV Line | FACILITY STUDY STAGE
GEN-2016-111 | 04 - Northwest Kansas | 17 | DIS-16-2 | Wind | 302 |  | ER | WERE | Reno-(GEN-2016-112 Tap) Summit 345kV | FACILITY STUDY STAGE
GEN-2016-112 | 04 - Northwest Kansas | 17 | DIS-16-2 | Wind | 220 |  | ER | WERE | Reno (GEN-2016-111 Tap)-Summit 345kV | FACILITY STUDY STAGE
GEN-2016-114 | 04 - Northwest Kansas | 17 | DIS-16-2 | Wind | 310 |  | ER/NR | WERE | Reno-(GEN-2016-112 Tap) Summit 345kV | FACILITY STUDY STAGE
GEN-2016-115 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 300 |  | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-118 | 01 - Woodward | 17 | DIS-16-2 | Wind | 288 |  | ER | WFEC | Dover Switchyard 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-119 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 600 |  | ER | OKGE | Spring Creek-Sooner 345kV | FACILITY STUDY STAGE
GEN-2016-121 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Solar | 110 |  | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-122 | 04 - Northwest Kansas | 17 | DIS-16-2 | Wind | 225 |  | ER | WERE | Reno (GEN-2016-111 Tap)-Summit 345kV | FACILITY STUDY STAGE
GEN-2016-123 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Wind | 298 |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-124 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Wind | 150 |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-125 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Wind | 74 |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-126 | 14 - South Central Oklahoma | 17 | DIS-16-2 | Wind | 172.5 |  | ER/NR | OKGE | Arbuckle 138kV | IA PENDING
GEN-2016-128 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 176 |  | ER | OKGE | Woodring 345kV | FACILITY STUDY STAGE
GEN-2016-130 | 16 - Western North Dakota | 17 | DIS-16-2 | Wind | 202 |  | ER | WAPA | Leland Olds 345kV | FACILITY STUDY STAGE
GEN-2016-131 | 01 - Woodward | 17 | DIS-16-2 | Wind | 2.5 |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-132 | 07 - Southwestern Oklahoma | 17 | DIS-16-2 | Wind | 6.12 |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-133 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 187.5 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-134 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 187.5 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-137 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 187.5 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-138 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 187.5 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-139 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 100 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-141 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 350 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-142 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 350 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-145 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 175 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-146 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 175 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-147 | 09 - Nebraska | 17 | DIS-16-2 | Solar | 40 |  | ER | NPPD | Sidney 115kV Sub | FACILITY STUDY STAGE
GEN-2016-149 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 302 |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-150 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 302 |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-151 | 16 - Western North Dakota | 17 | DIS-16-2 | Wind | 202 |  | ER | BEPC-SPP | Tande 345kV | IA PENDING
GEN-2016-153 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 134 |  | ER | WERE | Viola 345kV | FACILITY STUDY STAGE
GEN-2016-157 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 252 |  | ER | KCPL | West Gardner 345kV | IA PENDING
GEN-2016-158 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 252 |  | ER | KCPL | West Gardner 345kV | IA PENDING
GEN-2016-160 | 04 - Northwest Kansas | 17 | DIS-16-2 | Battery | 20 |  | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-161 | 02 - Hitchland | 17 | DIS-16-2 | Wind | 3.02 |  | ER | SPS | Martin 115kV | FACILITY STUDY STAGE
GEN-2016-162 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 252 |  | ER | WERE | Benton 345kV | FACILITY STUDY STAGE
GEN-2016-163 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 252 |  | ER | WERE | Benton 345kV | FACILITY STUDY STAGE
GEN-2016-167 | 10 - Southeast Oklahoma/Northeast Texas | 17 | DIS-16-2 | Solar | 73.5 |  | ER/NR | AEPW | Lieberman - North Benton 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-174 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 302 |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-176 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 302 |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-177 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Gas Turbine | 17 |  | ER | SPS | XTO-Cornell 115kV station | IA PENDING
ASGI-2016-011 | 14 - South Central Oklahoma | 16.5 | DIS-16-2-PQ | Thermal | 7.4 |  | ER | SWPA | Allen 138kV
ASGI-2016-012 | 14 - South Central Oklahoma | 16.5 | DIS-16-2-PQ | Thermal | 61.73 |  | ER | SWPA | Tupelo 138kV
ASGI-2016-013 | 14 - South Central Oklahoma | 16.5 | DIS-16-2-PQ | Thermal | 4.92 |  | ER | WFEC | Ashland 138kV
ASGI-2017-006GIA-53 | 13 - Northeast Kansas/Northwest Missouri | 16.5 | Dis-16-2-PQ | Wind | 242 |  | ER/NR | AECI | Maryville 161kV
J302 | 18 - Eastern North Dakota | 16.5 | DIS-16-2-PQ | Wind | 101.2 |  | ER/NR | MDU | 230kV Heskett-Wishek
J476 | 13 - Northeast Kansas/Northwest Missouri | 16.5 | DIS-16-2-PQ | Wind | 246 |  | ER/NR | AMMO | Atchison County to Booneville 345kV Line Tap
J503 | 18 - Eastern North Dakota | 16.5 | DIS-16-2-PQ | Wind | 98.8 |  | ER/NR | MDU | 230kV Heskett-Wishek, 20 miles NW of Wishek
J512 | 15 - Eastern South Dakota | 16.5 | DIS-16-2-PQ | Wind | 250 |  | ER/NR | MP | Nobles - Fenton 115kV line
J541 | 13 - Northeast Kansas/Northwest Missouri | 16.5 | DIS-16-2-PQ | Wind | 400 |  | ER/NR | AMMO | Zachary-Ottumwa 345kV line
J555 | 09 - Nebraska | 16.5 | DIS-16-2-PQ | Wind | 140 |  | ER/NR | MEC
J569 | 15 - Eastern South Dakota | 16.5 | DIS-16-2-PQ | Wind | 100 |  | ER/NR | XEL | NSP Rock County
J583 | 09 - Nebraska | 16.5 | DIS-16-2-PQ | Wind | 200 |  | ER/NR | MEC | Fallow Avenue 345kV . Zip Code 50002
J587 | 15 - Eastern South Dakota | 16.5 | DIS-16-2-PQ | Wind | 200 |  | ER/NR | XEL | J460 on the Brookings-H081 345kV line
J590 | 15 - Eastern South Dakota | 16.5 | DIS-16-2-PQ | Wind | 90 |  | ER/NR | MEC | Obrien - Kossuth 345kV line
J611 | 13 - Northeast Kansas/Northwest Missouri | 16.5 | DIS-16-2-PQ | Wind | 110 |  | ER/NR | MEC | Clarinda - Merryville 161kV tap
ASGI-2016-003 | 13 - Northeast Kansas/Northwest Missouri | 16 | DIS-16-1 | Diesel | 12 |  | ER | KCPL | Paola 161kV
ASGI-2016-004 | 06 - South Texas Panhandle/New Mexico | 16 | DIS-16-1 | Wind | 10 |  | ER | SPS | Palo Duro 115kV
GEN-2015-036 | 14 - South Central Oklahoma | 16 | DIS-16-1 | Wind | 303.6 |  | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-041 | 06 - South Texas Panhandle/New Mexico | 16 | DIS-16-1 | CT | 5 |  | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-082 | 02 - Hitchland | 16 | DIS-16-1 | Wind | 200 |  | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-089 | 09 - Nebraska | 16 | DIS-16-1 | Wind | 200 |  | ER | WAPA | Utica 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-095 | 01 - Woodward | 16 | DIS-16-1 | Wind | 176 |  | ER | WFEC | Tap Mooreland - Knob Hill 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-003 | 01 - Woodward | 16 | DIS-16-1 | Wind | 248.4 |  | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-004 | 16 - Western North Dakota | 16 | DIS-16-1 | Wind | 202 |  | ER/NR | WAPA | Basin Electric 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-007 | 18 - Eastern North Dakota | 16 | DIS-16-1 | Wind | 100.05 |  | ER | WAPA | Valley City 115kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-009 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Steam Turbine | 29 |  | ER | OKGE | Osage 69kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-013 | 12 - Northwest Arkansas | 16 | DIS-16-1 | CT | 10 |  | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-014 | 12 - Northwest Arkansas | 16 | DIS-16-1 | CT | 10 |  | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-016 | 03 - Spearville | 16 | DIS-16-1 | Wind | 78.2 |  | ER | MIDW | North Kinsley 115kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-017 | 15 - Eastern South Dakota | 16 | DIS-16-1 | Wind | 250.24 |  | ER | WAPA | Fort Thompson-Leland Olds 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-020 | 01 - Woodward | 16 | DIS-16-1 | Wind | 150 |  | ER | WFEC | Moreland 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-021 | 09 - Nebraska | 16 | DIS-16-1 | WIND | 300 |  | ER | NPPD | Turtle Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-022 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 151.8 |  | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA PENDING
GEN-2016-028 | 14 - South Central Oklahoma | 16 | DIS-16-1 | Wind | 100 |  | ER | AEPW | Clayton 138kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-030 | 14 - South Central Oklahoma | 16 | DIS-16-1 | Solar | 100 |  | ER/NR | OKGE | Brown 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-031 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 1.5 |  | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 200 |  | ER/NR | OKGE | Crescent 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-043 | 09 - Nebraska | 16 | DIS-16-1 | Wind | 230 |  | ER | NPPD | Turtle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-045 | 01 - Woodward | 16 | DIS-16-1 | Wind | 499.1 |  | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-046 | 03 - Spearville | 16 | DIS-16-1 | Wind | 299 |  | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-047 | 01 - Woodward | 16 | DIS-16-1 | CT | 24 |  | ER | OKGE | Mustang 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | 09 - Nebraska | 16 | DIS-16-1 | Wind | 250.7 |  | ER | NPPD | Axtell â€“ Post Rock 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-051 | 07 - Southwestern Oklahoma | 16 | DIS-16-1 | Wind | 9.8 |  | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-057 | 01 - Woodward | 16 | DIS-16-1 | Wind | 499.1 |  | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-061 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 250.7 |  | ER | OKGE | Sooner-Woodring 345kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-063 | 14 - South Central Oklahoma | 16 | DIS-16-1 | Wind | 200 |  | ER/NR | OKGE | Hugo-Sunnyside 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-067 | 04 - Northwest Kansas | 16 | DIS-16-1 | Wind | 73.6 |  | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-068 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 250 |  | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-070 | 02 - Hitchland | 16 | DIS-16-1 | Wind | 5.3 |  | ER | SPS | Martin 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-071 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 200.1 |  | ER | OKGE | Middleton Tap 138kV | IA PENDING
GEN-2016-073 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | WIND | 220 |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA PENDING
GEN-2016-075 | 09 - Nebraska | 16 | DIS-16-1 | Wind | 50 |  | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA PENDING
PQOKGEMustang | 01 - Woodward | 16 | DIS-16-1 | CT | 444.1 |  | ER | OKGE
G359R | 18 - Eastern North Dakota | 15.5 | DIS-16-1-PQ | Wind | 150 |  | ER/NR | MDU | Merricourt
J432 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 98 |  | ER/NR | XEL | Brookings 345kV
J460 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 200 |  | ER/NR | XEL | on Brookings - H081 345kV line approx. 10 miles west of proposed
J475 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 200 |  | ER/NR | MEC
J488 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 151.8 |  | ER | OTP | 345kV at new Tap on proposed MVP Big Stone to Ellendale line
J493 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 150 |  | ER/NR | OTP | Big Stone - Brookings 345kV
J495 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 200 |  | ER/NR | ALTW | Ledyard-Colby 345kV line
J498 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 340 |  | ER/NR | MEC | MEC 345kV Grimes-Lehigh line (18 miles south of Leigh )
J499 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 340 |  | ER/NR | MEC | MEC 345kV Fallow-Grimes line (18 miles east of Fallow )
J500 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 500 |  | ER/NR | MEC | New at intersection of MEC 345kV Boone-Atchison and MEC 345kV Rolling Hills-Madison County
J506 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 200 |  | ER/NR | MEC | Raun-Lakefield Jct 345kV line tap (T-19N, R-43W)
J510 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Gas | 284.5 |  | ER/NR | OTP | Scandinavia Township 113N, Range 48W
J524 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Solar | 100 |  | ER/NR | MEC | Webster 161kV bus
J526 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 300 |  | ER/NR | OTP | Brooking County to Big Stone South 345kV line
J527 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 250 |  | ER/NR | MEC | Booneville Cooper 345kV line
J529 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 250 |  | ER/NR | MEC | Obrien - Kossuth 345kV line
J530 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 250 |  | ER/NR | MEC | Montezuma - Hills 345kV Line
J534 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 250 |  | ER/NR | ALTW | Kossuth â€“ Webster 345kV Line
J535 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 210 |  | ER/NR | ALTW | J411 â€“ Lehigh 345kV Line
GEN-2015-034 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 200 |  | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-045 | 14 - South Central Oklahoma | 15 | DIS-15-2 | Battery | 20 |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-046 | 16 - Western North Dakota | 15 | DIS-15-2 | Wind | 300 |  | ER | WAPA | Tande 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-047 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 300 |  | ER | OKGE | Sooner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 01 - Woodward | 15 | DIS-15-2 | Wind | 200 |  | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-052 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 300 |  | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-055 | 07 - Southwestern Oklahoma | 15 | DIS-15-2 | Solar | 40 |  | ER | WFEC | Erick 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-057 | 01 - Woodward | 15 | DIS-15-2 | Wind | 100 |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-062 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 4.5 |  | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-063 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 300 |  | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-064 | 04 - Northwest Kansas | 15 | DIS-15-2 | Wind | 197.8 |  | ER | SUNC | Mingo 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-065 | 04 - Northwest Kansas | 15 | DIS-15-2 | Wind | 202.4 |  | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-066 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 248.4 |  | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-069 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 300 |  | ER | WERE | Union Ridge 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-073 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 200.1 |  | ER/NR | WERE | Emporia 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-088 | 09 - Nebraska | 15 | DIS-15-2 | Wind | 300 |  | ER/NR | NPPD | Moore-Pauline 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-090 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 219.99 |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-092 | 14 - South Central Oklahoma | 15 | DIS-15-2 | Wind | 250 |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-093 | 01 - Woodward | 15 | DIS-15-2 | Wind | 250 |  | ER | OKGE | Gracemont 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-096 | 16 - Western North Dakota | 15 | DIS-15-2 | Wind | 150 |  | ER | BEPC-SPP | Brady 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-008IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 40.5 |  | ER/NR | BEPC-SPP | Edgeley 115kV [Pomona 115kV]
GEN-2002-009IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 40.5 |  | ER/NR | BEPC-SPP | Ft Thompson 69kV [Hyde 69kV]
GEN-2005-003IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | BEPC-SPP | Nelson 115kV
GEN-2005-008IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 50 |  | ER/NR | BEPC-SPP | Hilken 230kV [Ecklund 230kV]
GEN-2006-002IS | 17 - Western South Dakota | 14.5 | DIS-15-2-PQ | Wind | 53 |  | ER/NR | WAPA | Wessington Springs 230kV
GEN-2006-006IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 10 |  | ER/NR | XEL | Marshall 115kV
GEN-2006-015IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 50 |  | ER/NR | BEPC-SPP | Hilken 230kV [Ecklund 230kV]
GEN-2007-013IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 50 |  | ER/NR | BEPC-SPP | Wessington Springs 230kV
GEN-2007-014IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | BEPC-SPP | Wessington Springs 230kV
GEN-2007-015IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | BEPC-SPP | Hilken 230kV [Ecklund 230kV]
GEN-2007-020IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 16 |  | ER/NR | BEPC-SPP | Nelson 115kV
GEN-2008-008IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 5 |  | ER/NR | WAPA | Nelson 115kV
GEN-2009-001IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | BEPC-SPP | Groton-Watertown 345kV
GEN-2009-018IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 |  | ER | BEPC-SPP | Groton 115kV
GEN-2009-020AIS | 17 - Western South Dakota | 14.5 | DIS-15-2-PQ | Wind | 80 |  | ER/NR | WAPA | Tripp Junction 115kV
GEN-2009-026IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 110 |  | ER/NR | BEPC-SPP | Dickenson-Heskett 230kV
GEN-2010-001IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 99 |  | ER/NR | BEPC-SPP | Bismarck-Glenham 230kV
GEN-2010-003IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 34 |  | ER/NR | BEPC-SPP | Wessington Springs 230kV
GEN-2013-009IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 19.5 |  | ER | WAPA | Redfield NW 115kV
GEN-2014-001IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 103.24 |  | ER | WAPA | Sulphur 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-006IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Gas | 125 |  | ER/NR | BEPC-SPP | Williston 115kV
GEN-2014-010IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 150 |  | ER/NR | BEPC-SPP | Neset 115kV
GEN-2014-014IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 150 |  | ER/NR | BEPC-SPP | Belfield-Rhame 230kV
J412 | 09 - Nebraska | 14.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | MEC | LeHigh - Raun 345kV line
J436 | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 150 |  | ER | OTP | Big Stone South - Ellendale 345kV line
J437 | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 150 |  | ER | OTP | Big Stone South - Ellendale 345kV line
J442 | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | OTP | Big Stone via a radial 230kV line
J455 | 09 - Nebraska | 14.5 | DIS-15-2-PQ | Wind | 300 |  | ER | ALTW | Kossuth â€“ Obrien 345kV line
MPC00100 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 99 |  | ER | OTP | Langdon 115kV
MPC00200 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 60 |  | ER | OTP | Langdon 115kV
MPC00300 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 40.5 |  | ER | OTP | Langdon 115kV
MPC00500 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 327.8 |  | ER/NR | OTP | Maple River 230kV
MPC01200 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 49.6 |  | ER | OTP | Maple River 230kV
MPC01300 | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Coal | 493 |  | ER/NR | OTP | Square Butte 230kV
MPC02100 | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 |  | ER | OTP | Center - Mandan 230kV
ASGI-2015-001 | 03 - Spearville | 14 | DIS-15-1 | Thermal | 6.13 |  | ER | SUNC | Ninnescah 115kV
ASGI-2015-002 | 06 - South Texas Panhandle/New Mexico | 14 | DIS-15-1 | Wind | 2 |  | ER | SPS | SP-Yuma 69kV
ASGI-2015-004 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Thermal | 54 |  | ER | GRDA | Coffeyville City 69kV
GEN-2015-001 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 200 |  | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | 13 - Northeast Kansas/Northwest Missouri | 14 | DIS-15-1 | Wind | 200.11 |  | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-007 | 09 - Nebraska | 14 | DIS-15-1 | Wind | 160 |  | ER | NPPD | Turtle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 07 - Southwestern Oklahoma | 14 | DIS-15-1 | Solar | 120 |  | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-014 | 06 - South Texas Panhandle/New Mexico | 14 | DIS-15-1 | Wind | 150 |  | ER | SPS | Tap Cochran - Lehman 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-015 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 154.58 |  | ER/NR | OKGE | Tap Medford Tap â€“ Coyote 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-016 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 200 |  | ER/NR | KCPL | Tap Marmaton - Centerville 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-021 | 03 - Spearville | 14 | DIS-15-1 | Solar | 20 |  | ER/NR | SUNC | Johnson Corner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-023 | 09 - Nebraska | 14 | DIS-15-1 | Wind | 300.72 |  | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-024 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 220 |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 219.98 |  | ER | WERE | Tap Thistle â€“ Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
G736 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | OTP | Big Stone South 230kV
GEN-2007-017IS | 09 - Nebraska | 13.5 | DIS-15-2-PQ | Wind | 166 |  | ER/NR | OPPD | Ft Thompson-Grand Island 345kV
GEN-2007-018IS | 09 - Nebraska | 13.5 | DIS-15-2-PQ | Wind | 234 |  | ER/NR | OPPD | Ft Thompson-Grand Island 345kV
J299 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Combined Cycle | 73 |  | ER | XEL | Wilmarth
J385 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Solar | 100 |  | ER/NR | XEL | Chisago 115kV
J400 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Solar | 62.5 |  | ER/NR | XEL | Lyon County 115kV
J405 | 16 - Western North Dakota | 13.5 | DIS-15-2-PQ | Gas | 40 |  | ER/NR | MDU | MDUs existing Lewis & Clark Jct
J407 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | XEL | Glenworth 161kV
J411 | 09 - Nebraska | 13.5 | DIS-15-2-PQ | Wind | 300 |  | ER/NR | MEC | LeHigh - Raun 345kV Line
J426 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | XEL | Chanarambie 35.4kV
ASGI-2014-014 | 08 - North Oklahoma/South Central Kansas | 13 | DIS-14-2 | Thermal | 56.4 |  | ER | GRDA | Ferguson 69kV
GEN-2004-017 | 08 - North Oklahoma/South Central Kansas | 13 | DIS-14-2 | CT/ST | 260 |  | ER/NR | EMDE | Riverton 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-027 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Wind | 148.35 |  | ER/NR | SPS | Tolk - Yoakum 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-020 | 01 - Woodward | 13 | DIS-14-2 | Wind | 100 |  | ER/NR | AEPW | Tuttle 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-021 | 13 - Northeast Kansas/Northwest Missouri | 13 | DIS-14-2 | Wind | 300 |  | ER/NR | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-025 | 04 - Northwest Kansas | 13 | DIS-14-2 | Wind | 2.42 |  | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-028 | 08 - North Oklahoma/South Central Kansas | 13 | DIS-14-2 | CC | 50 |  | ER | EMDE | Riverton 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-031 | 09 - Nebraska | 13 | DIS-14-2 | Wind | 35.8 |  | ER/NR | GRIS | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | 09 - Nebraska | 13 | DIS-14-2 | Wind | 10.22 |  | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-033 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Solar | 70 |  | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-034 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Solar | 70 |  | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-035 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Solar | 30 |  | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-039 | 09 - Nebraska | 13 | DIS-14-2 | Wind | 73.4 |  | ER/NR | NPPD | Friend 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-040 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Wind | 320 |  | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-056 | 01 - Woodward | 13 | DIS-14-2 | Wind | 250 |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-057 | 14 - South Central Oklahoma | 13 | DIS-14-2 | Wind | 249.9 |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-064 | 08 - North Oklahoma/South Central Kansas | 13 | DIS-14-2 | Wind | 248.4 |  | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
G237 | 18 - Eastern North Dakota | 12.5 | DIS-15-2-PQ | Gas | 579.04 |  | ER | XEL | Highbridge
J285 | 09 - Nebraska | 12.5 | DIS-15-2-PQ | Wind | 250 |  | ER/NR | MEC | Proposed O'Brien County 345kV
J316 | 16 - Western North Dakota | 12.5 | DIS-15-2-PQ | Wind | 150 |  | ER/NR | MDU | MDU 230kV Tatanka-Ellendale line
J320 | 18 - Eastern North Dakota | 12.5 | DIS-15-2-PQ | Wind | 55 |  | ER | XEL | Xcel's existing High Bridge 115kV
J343 | 09 - Nebraska | 12.5 | DIS-15-2-PQ | Wind | 150 |  | ER/NR | MEC | 161kV on Creston-Clarinda line
GEN-2014-001 | 08 - North Oklahoma/South Central Kansas | 12 | DIS-14-1 | Wind | 200.6 |  | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-002 | 01 - Woodward | 12 | DIS-14-1 | Wind | 10.53 |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-004 | 09 - Nebraska | 12 | DIS-14-1 | Wind | 3.96 |  | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 01 - Woodward | 12 | DIS-14-1 | Wind | 5.67 |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-013 | 09 - Nebraska | 12 | DIS-14-1 | Wind | 73.5 |  | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-004 | 04 - Northwest Kansas | 11 | DIS-13-2 | Gas | 36.6 |  | ER | SUNC | Garden City 115kV
ASGI-2013-005 | 06 - South Texas Panhandle/New Mexico | 11 | DIS-13-2 | Wind | 1.65 |  | ER | SPS | Clovis Intg. 115kV
GEN-2006-031 | 04 - Northwest Kansas | 11 | DIS-13-2 | Gas | 75.6 |  | ER | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-019 | 09 - Nebraska | 11 | DIS-13-2 | Wind | 73.6 |  | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-022 | 06 - South Texas Panhandle/New Mexico | 11 | DIS-13-2 | Solar | 25 |  | ER/NR | SPS | Norton 115kV Switching Station | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-028 | 08 - North Oklahoma/South Central Kansas | 11 | DIS-13-2 | Gas | 559.4 |  | ER | GRDA | Tap N Tulsa - GRDA 1 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-029 | 08 - North Oklahoma/South Central Kansas | 11 | DIS-13-2 | Wind | 299 |  | ER | OKGE | Renfrow 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-032 | 09 - Nebraska | 11 | DIS-13-2 | Wind | 202.5 |  | ER | NPPD | Antelope 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-033 | 04 - Northwest Kansas | 11 | DIS-13-2 | Gas | 28.02 |  | ER/NR | MIDW | Goodman Energy Center 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
J274 | 09 - Nebraska | 10.5 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | MEC | Winterset. - Creston 161kV
J278 | 15 - Eastern South Dakota | 10.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | XEL | 161kV bus at the Pleasant Valley Station
J279 | 09 - Nebraska | 10.5 | DIS-15-2-PQ | Coal | 30 |  | ER/NR | MEC | Raun 345kV
J289 | 09 - Nebraska | 10.5 | DIS-15-2-PQ | Wind | 20 |  | ER/NR | MEC | 161kV sybstation on Winterset Junction to Creston 161kV Line
J290 | 16 - Western North Dakota | 10.5 | DIS-15-2-PQ | Wind | 150 |  | ER/NR | XEL | 230kV Rugby to Glenboro
ASGI-2013-001 | 02 - Hitchland | 10 | DIS-13-1 | Wind | 11.5 |  | ER | SPS | PanTex South 115kV
ASGI-2013-002 | 06 - South Texas Panhandle/New Mexico | 10 | DIS-13-1 | Wind | 18.4 |  | ER | SPS | FE Tucumcari 115kV
ASGI-2013-003 | 06 - South Texas Panhandle/New Mexico | 10 | DIS-13-1 | Wind | 18.4 |  | ER | SPS | Clovis Intg. 115kV
GEN-2006-010 | 12 - Northwest Arkansas | 10 | DIS-13-1 | Coal | 651 |  | ER | AEPW | Turk 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-002 | 09 - Nebraska | 10 | DIS-13-1 | Wind | 50.6 |  | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-007 | 14 - South Central Oklahoma | 10 | DIS-13-1 | Wind | 100 |  | ER/NR | OKGE | Tap Prices Falls - Carter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-008 | 09 - Nebraska | 10 | DIS-13-1 | Wind | 1.2 |  | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-011 | 12 - Northwest Arkansas | 10 | DIS-13-1 | Coal | 40 |  | ER | AEPW | Turk 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-012 | 08 - North Oklahoma/South Central Kansas | 10 | DIS-13-1 | Gas | 147 |  | ER | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-012PQ | 08 - North Oklahoma/South Central Kansas | 10 | DIS-13-1 | Gas | 1299 |  | ER | OKGE | Redbud 345kV
GEN-2013-016 | 06 - South Texas Panhandle/New Mexico | 10 | DIS-13-1 | CT | 203 |  | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
J262 | 16 - Western North Dakota | 9.5 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | OTP | OTP Jamestown 345/115kV
J263 | 16 - Western North Dakota | 9.5 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | OTP | OTP Jamestown 345/115kV
ASGI-2012-002 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | Wind | 18.15 |  | ER | SPS | FE-Clovis Interchange 115kV
GEN-2012-020 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | Wind | 478 |  | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-021 | 09 - Nebraska | 9 | DIS-12-2 | Gas | 4.8 |  | ER | LES | Terry Bundy Generating Station 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-024 | 03 - Spearville | 9 | DIS-12-2 | Wind | 180 |  | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-028 | 07 - Southwestern Oklahoma | 9 | DIS-12-2 | Wind | 74 |  | ER | WFEC | Gotebo 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-032 | 08 - North Oklahoma/South Central Kansas | 9 | DIS-12-2 | Wind | 299 |  | ER | OKGE | Rose Hill-(Ranch Road) Sooner (Open Sky) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-033 | 08 - North Oklahoma/South Central Kansas | 9 | DIS-12-2 | Wind | 98.82 |  | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-034 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | CT | 7 |  | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-035 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | CT | 7 |  | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-036 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | CT | 7 |  | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-037 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | CT | 203 |  | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-041 | 08 - North Oklahoma/South Central Kansas | 9 | DIS-12-2 | CT | 121.5 |  | ER | OMPA | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
H081 | 15 - Eastern South Dakota | 8.5 | DIS-15-2-PQ | Wind | 201 |  | ER | XEL | Brookings County - Lyon County 345kV
J171 | 18 - Eastern North Dakota | 8.5 | DIS-15-2-PQ | Biomass | 7 |  | ER/NR | XEL | Benson 115kV
J183 | 15 - Eastern South Dakota | 8.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | XEL | Split Rock
J191 | 09 - Nebraska | 8.5 | DIS-15-2-PQ | Wind | 101.2 |  | ER/NR | MEC | Rolling Hills 345kV
J200 | 18 - Eastern North Dakota | 8.5 | DIS-15-2-PQ | Gas | 99 |  | ER/NR | MDU | RM Heskett Station 115kV & 41.6kV
J249 | 18 - Eastern North Dakota | 8.5 | DIS-15-2-PQ | Wind | 90 |  | ER/NR | MDU | MDU Tatanka
ASGI-2012-006 | 03 - Spearville | 8 | DIS-12-1 | Steam | 22.5 |  | ER | SUNC | ABBK 2 69kV
ASGI-2012-008 | 13 - Northeast Kansas/Northwest Missouri | 8 | PQ | Gas | 3.55 |  | ER | WERE | Sheffield 69kV
GEN-2012-001 | 06 - South Texas Panhandle/New Mexico | 8 | DIS-12-1 | Wind | 61.2 |  | ER | SPS | Tap Grassland Â- Borden County 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-004 | 14 - South Central Oklahoma | 8 | DIS-12-1 | Wind | 40.8 |  | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-007 | 03 - Spearville | 8 | DIS-12-1 | Gas | 120 |  | ER/NR | SUNC | Rubart 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
G735 | 15 - Eastern South Dakota | 7.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | ALTW | Lime Creek
G826 | 15 - Eastern South Dakota | 7.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | XEL | Xcel Lakefield Generation SW - Lakefield Junction 345kV
G830 | 16 - Western North Dakota | 7.5 | DIS-15-2-PQ | Wind | 99 |  | ER/NR | GRE | GRE McHenry
G870 | 15 - Eastern South Dakota | 7.5 | DIS-15-2-PQ | Wind | 201 |  | ER/NR | ALTW | Hayward - Winnebago 161kV
H096 | 09 - Nebraska | 7.5 | DIS-15-2-PQ | Wind | 50 |  | ER/NR | ALTW | Grand Junction - Perry 161kV
ASGI-2011-004 | 06 - South Texas Panhandle/New Mexico | 7 | DIS-11-2 | Wind | 19.8 |  | ER | SPS | Pleasant Hill 69kV
GEN-2011-037 | 07 - Southwestern Oklahoma | 7 | DIS-11-2 | Wind | 6.6 |  | ER | WFEC | Blue Canyon 5 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-040 | 14 - South Central Oklahoma | 7 | DIS-11-2 | Wind | 111 |  | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-045 | 06 - South Texas Panhandle/New Mexico | 7 | DIS-11-2 | NG CT | 205 |  | ER | SPS | Jones 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-046 | 06 - South Texas Panhandle/New Mexico | 7 | DIS-11-2 | Diesel CT | 23 |  | ER | SPS | Tucumcari 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-048 | 06 - South Texas Panhandle/New Mexico | 7 | DIS-11-2 | CT | 175 |  | ER/NR | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-050 | 14 - South Central Oklahoma | 7 | DIS-11-2 | Wind | 108 |  | ER | AEPW | Tap Rush Springs Â- Marlow 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-054 | 01 - Woodward | 7 | DIS-11-2 | Wind | 300 |  | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056 | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 3.6 |  | ER | NPPD | Jeffrey 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056A | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 3.6 |  | ER | NPPD | John 1 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056APQ | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 18 |  | ER | NPPD | John 1 115kV
GEN-2011-056B | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 4.5 |  | ER | NPPD | John 2 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056BPQ | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 18 |  | ER | NPPD | John 2 115kV
GEN-2011-056PQ | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 18 |  | ER | NPPD | Jeffrey 115kV
GEN-2011-057 | 08 - North Oklahoma/South Central Kansas | 7 | DIS-11-2 | Wind | 150 |  | ER | WERE | Creswell 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2011-002 | 02 - Hitchland | 6 | DIS-11-1 | Wind | 20 |  | ER | SPS | Herring 115kV
ASGI-2011-003 | 06 - South Texas Panhandle/New Mexico | 6 | DIS-11-1 | Wind | 10 |  | ER | SPS | Hendricks 69kV
GEN-2004-008 | 13 - Northeast Kansas/Northwest Missouri | 6 | DIS-11-1 | Coal | 904.5 |  | ER | KCPL | Iatan 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-055 | 08 - North Oklahoma/South Central Kansas | 6 | DIS-11-1 | Gas | 4.5 |  | ER | AEPW | Wekiwa 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-057 | 04 - Northwest Kansas | 6 | DIS-11-1 | Wind | 201 |  | ER/NR | MIDW | Rice County 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-008 | 03 - Spearville | 6 | DIS-11-1 | Wind | 600 |  | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-010 | 01 - Woodward | 6 | DIS-11-1 | Wind | 100.8 |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-011 | 13 - Northeast Kansas/Northwest Missouri | 6 | DIS-11-1 | Coal | 50 |  | ER | KCPL | Iatan 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-014 | 02 - Hitchland | 6 | DIS-11-1 | Wind | 198 |  | ER | OKGE | Beaver CountyÂ-Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-018 | 09 - Nebraska | 6 | DIS-11-1 | Wind | 73.6 |  | ER/NR | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | 01 - Woodward | 6 | DIS-11-1 | Wind | 175 |  | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 01 - Woodward | 6 | DIS-11-1 | Wind | 165.6 |  | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-022 | 02 - Hitchland | 6 | DIS-11-1 | Wind | 299 |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-025 | 06 - South Texas Panhandle/New Mexico | 6 | DIS-11-1 | Wind | 79.96 |  | ER | SPS | Tap Floyd County - Crosby County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-027 | 09 - Nebraska | 6 | DIS-11-1 | Wind | 120 |  | ER/NR | NPPD | Hoskins-Twin Church 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-020 | 06 - South Texas Panhandle/New Mexico | 5 | DIS-10-2 | Wind | 30 |  | ER | SPS | Tap LE-Tatum - LE-Crossroads 69kV
ASGI-2010-021 | 06 - South Texas Panhandle/New Mexico | 5 | DIS-10-2 | Wind | 15 |  | ER | SPS | Tap LE-Saunders Tap - LE-Anderson 69kV
ASGI-2011-001 | 06 - South Texas Panhandle/New Mexico | 5 | DIS-10-2 | Wind | 27.3 |  | ER | SPS | Lovington 115kV
GEN-2010-001 | 02 - Hitchland | 5 | DIS-10-2 | Wind | 300 |  | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036 | 13 - Northeast Kansas/Northwest Missouri | 5 | DIS-10-2 | Hydro | 4.6 |  | ER | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036PQ | 13 - Northeast Kansas/Northwest Missouri | 5 | DIS-10-2 | Hydro | 1.17 |  | ER | WERE | Westar 6th Street 115kV
GEN-2010-040 | 01 - Woodward | 5 | DIS-10-2 | Wind | 300 |  | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-051 | 09 - Nebraska | 5 | DIS-10-2 | Wind | 200 |  | ER | NPPD | Hoskins-Twin Church 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-010 | 06 - South Texas Panhandle/New Mexico | 4 | DIS-10-1 | Gas | 46.5 |  | ER | SPS | Lovington 115kV
GEN-2008-022 | 06 - South Texas Panhandle/New Mexico | 4 | DIS-10-1 | Wind | 299.65 |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-037 | 07 - Southwestern Oklahoma | 4 | DIS-10-1 | Wind | 99 |  | ER | WFEC | Tap Washita - Blue Canyon Wind 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-044 | 01 - Woodward | 4 | DIS-10-1 | Wind | 197.8 |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-047 | 02 - Hitchland | 4 | DIS-10-1 | Wind | 263.13 |  | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-098 | 08 - North Oklahoma/South Central Kansas | 4 | DIS-10-1 | Wind | 99.5 |  | ER | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-123N | 09 - Nebraska | 4 | DIS-10-1 | Wind | 89.66 |  | ER | NPPD | Tap Pauline - Hildreth (Rosemont) 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-008 | 04 - Northwest Kansas | 4 | DIS-10-1 | Wind | 198.69 |  | ER | MIDW | South Hays 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-020 | 04 - Northwest Kansas | 4 | DIS-10-1 | Wind | 48.3 |  | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-040 | 09 - Nebraska | 4 | DIS-10-1 | Wind | 72 |  | ER | WERE | Tap Smittyville - Knob Hill 115KV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-003 | 08 - North Oklahoma/South Central Kansas | 4 | DIS-10-1 | Wind | 99.5 |  | ER | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-005 | 08 - North Oklahoma/South Central Kansas | 4 | DIS-10-1 | Wind | 299.2 |  | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-006 | 06 - South Texas Panhandle/New Mexico | 4 | DIS-10-1 | Gas | 205 |  | ER | SPS | Jones 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-009 | 03 - Spearville | 4 | DIS-10-1 | Wind | 165.6 |  | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-011 | 01 - Woodward | 4 | DIS-10-1 | Wind | 29.7 |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-014 | 02 - Hitchland | 4 | DIS-10-1 | Wind | 358.8 |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2006-037N1 | 09 - Nebraska | 3 | DIS-09-1 | Wind | 75 |  | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044N | 09 - Nebraska | 3 | DIS-09-1 | Wind | 40.5 |  | ER | NPPD | North Petersburg 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-040 | 03 - Spearville | 3 | DIS-09-1 | Wind | 131.1 |  | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-023 | 07 - Southwestern Oklahoma | 3 | DIS-09-1 | Wind | 150 |  | ER | AEPW | Hobart Junction 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-051 | 02 - Hitchland | 3 | DIS-09-1 | Wind | 161 |  | ER | SPS | Potter County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-079 | 03 - Spearville | 3 | DIS-09-1 | Wind | 98.9 |  | ER | SUNC | Crooked Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 09 - Nebraska | 3 | DIS-09-1 | Wind | 201 |  | ER | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-092 | 04 - Northwest Kansas | 3 | DIS-09-1 | Wind | 200.48 |  | ER | MIDW | Post Rock 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-124 | 03 - Spearville | 3 | DIS-09-1 | Wind | 200.1 |  | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-129 | 13 - Northeast Kansas/Northwest Missouri | 3 | DIS-09-1 | CT | 687.1 |  | ER | KCPL | Pleasant Hill 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-025 | 08 - North Oklahoma/South Central Kansas | 3 | DIS-09-1 | Wind | 59.8 |  | ER | OKGE | TAP Deer Creek â€“ Sinclair 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-021 | 01 - Woodward | 2 | ICS1 | Wind | 198.9 |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-025 | 08 - North Oklahoma/South Central Kansas | 2 | ICS1 | Wind | 299.2 |  | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-043 | 01 - Woodward | 2 | ICS1 | Wind | 200 |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-044 | 01 - Woodward | 2 | ICS1 | Wind | 299.2 |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-046 | 02 - Hitchland | 2 | ICS1 | Wind | 200 |  | ER | SPS | Hitchland 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-050 | 01 - Woodward | 2 | ICS1 | Wind | 151.8 |  | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-052 | 07 - Southwestern Oklahoma | 2 | ICS1 | Gas | 150 |  | ER | WFEC | Anadarko 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-062 | 01 - Woodward | 2 | ICS1 | Wind | 424 |  | ER | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-003 | 01 - Woodward | 2 | ICS1 | Wind | 101.2 |  | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-013 | 08 - North Oklahoma/South Central Kansas | 2 | ICS1 | Wind | 300 |  | ER | OKGE | Hunter 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-018 | 03 - Spearville | 2 | ICS1 | Wind | 250 |  | ER | SPS | Finney 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-006 | 08 - North Oklahoma/South Central Kansas | 1 | PQ | Wind | 150 |  | ER | AECI | Remington 138kV
ASGI-2016-005NWE205 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 |  | ER | WAPA | Tap White Lake - Stickeny 69kV
ASGI-2016-007NWE208 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 |  | ER | WAPA | Kimball 69kV
Coyote | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 452 |  | ER | OTP | Coyote 345kV
G034 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Biomass | 55 |  | ER/NR | XEL
G132 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Wind | 90 |  | ER/NR | MDU | Ellendale Sub 230kV
G255 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | XEL | Yankee
G261 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Combined Cycle | 677.1 |  | ER | XEL
G287 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | XEL | Nobles County
G349 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 200 |  | ER | XEL | Brookings County
G362 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | GRE | Pleasant Valley
G370 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Gas | 205 |  | ER | XEL | Anson 4
G380 | 16 - Western North Dakota | 1 | DIS-15-2-PQ | Wind | 150 |  | ER | OTP | Rugby 115kV
G389 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Gas | 200 |  | ER/NR | GRE | Elk River 230kV
G514 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 150 |  | ER | XEL | Lakefield Station via Trimont G263 Interconnect
G540 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 80 |  | ER/NR | ALTW | Adams - Lime Creek 161kV
G548 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 80 |  | ER/NR | ALTW | Barton 161kV
G586 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 30 |  | ER/NR | XEL | Xcel New Yankee Sub 34.5kV
G595 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 150 |  | ER | ALTW | Lime Creek 161kV
G602 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 32 |  | ER/NR | XEL | Nobles County 115kV
G604 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 44 |  | ER/NR | ALTW | Owatonna - County Line 69kV
G612 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 150 |  | ER | ALTW | ITC Midwest Fernald 115kV
G619 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Wind | 50 |  | ER/NR | OTP | GRE Tamarac 41kV
G621 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 |  | ER/NR | XEL | Golf - Wookstock 34.5kV
G645 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 50 |  | ER/NR | GRE
G685 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 |  | ER | XEL | Lake Lillian - Atwater 69kV
G741 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Waste Heat Recovery | 8 |  | ER/NR | ALTW | Near Alliant 69kV line
G752 | 16 - Western North Dakota | 1 | DIS-15-2-PQ | Wind | 150 |  | ER/NR | MDU | Bison - Hettinger 230kV
G788 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 49 |  | ER/NR | GRE | Ladish 115kV
G930 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Coal | 60 |  | ER/NR | XEL | Sherco
G930SHERCO | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Coal | 2491.5 |  | ER/NR | XEL
G971 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 |  | ER | XEL | 69kV line in SE 1/4 of Sec 17 in Cosmos Twp
GEN-2001-014 | 01 - Woodward | 1 | PQ | Wind | 94.5 |  | ER | WFEC | Ft Supply 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-026 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 74.25 |  | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-030 | 12 - Northwest Arkansas | 1 | PQ | CT | 50 |  | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-033 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Wind | 180 |  | ER | SPS | San Juan Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-036 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Wind | 80 |  | ER | SPS | Norton 115kV Switching Station | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-037 | 01 - Woodward | 1 | PQ | Wind | 102 |  | ER | OKGE | FPL Moreland Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-039A | 03 - Spearville | 1 | PQ | Wind | 104 |  | ER | SUNC | Shooting Star Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-039M | 04 - Northwest Kansas | 1 | PQ | Wind | 100 |  | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-040 | 12 - Northwest Arkansas | 1 | PQ | CT | 50 |  | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-004 | 08 - North Oklahoma/South Central Kansas | 1 | PQ | Wind | 153 |  | ER | WERE | Latham 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-005 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 123 |  | ER | WFEC | Red Hills Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-008 | 02 - Hitchland | 1 | PQ | Wind | 240 |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-009 | 02 - Hitchland | 1 | PQ | Wind | 79.8 |  | ER | SPS | Hansford 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-022 | 02 - Hitchland | 1 | PQ | Wind | 239.2 |  | ER | SPS | Bushland 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-025A | 03 - Spearville | 1 | PQ | Wind | 100.5 |  | ER | SUNC | Spearville 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-004 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 100 |  | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-005 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 99 |  | ER | WFEC | Anadarko - Paradise (Blue Canyon) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 04 - Northwest Kansas | 1 | PQ | Wind | 201 |  | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-019 | 04 - Northwest Kansas | 1 | PQ | Wind | 249.3 |  | ER | MIDW | Smoky Hills Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-020 | 02 - Hitchland | 1 | PQ | Wind | 159.1 |  | ER | SPS | Martin 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-021N | 09 - Nebraska | 1 | PQ | Wind | 75 |  | ER | NPPD | Ainsworth Wind Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-022 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 120 |  | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-014 | 03 - Spearville | 1 | PQ | Wind | 152 |  | ER | SUNC | Spearville 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-015 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | CT | 150 |  | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-020 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 27 |  | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-023 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 20.6 |  | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-023N | 09 - Nebraska | 1 | PQ | Coal | 75 |  | ER | NPPD | Columbus Co 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-003 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 30.6 |  | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-008 | 01 - Woodward | 1 | PQ | Wind | 120 |  | ER | OKGE | Woodward 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-012 | 03 - Spearville | 1 | PQ | Wind | 248.4 |  | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-013 | 08 - North Oklahoma/South Central Kansas | 1 | PQ | Wind | 199.8 |  | ER | WERE | Caney River 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-001IS | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Wind | 10 |  | ER/NR | XEL
GEN-2006-002 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 100.8 |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-015 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Gas | 150 |  | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-018 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | CT | 168.12 |  | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020N | 09 - Nebraska | 1 | PQ | Wind | 42 |  | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020S | 02 - Hitchland | 1 | PQ | Wind | 20 |  | ER | SPS | DWS Frisco 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-021 | 03 - Spearville | 1 | PQ | Wind | 94 |  | ER | SUNC | Flat Ridge Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-024S | 01 - Woodward | 1 | PQ | Wind | 18.9 |  | ER | WFEC | Buffalo Bear Tap 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-026 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Gas | 604 |  | ER | SPS | Hobbs 230kV & Hobbs 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-035 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 132 |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-038N005 | 09 - Nebraska | 1 | PQ | Wind | 80 |  | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-038N019 | 09 - Nebraska | 1 | PQ | Wind | 80 |  | ER | NPPD | Petersburg North 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-043 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 99 |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | 02 - Hitchland | 1 | PQ | Wind | 370 |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-046 | 01 - Woodward | 1 | PQ | Wind | 129.6 |  | ER | OKGE | Dewey 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-011N08 | 09 - Nebraska | 1 | PQ | Wind | 81 |  | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-119O | 09 - Nebraska | 1 | PQ | Wind | 60 |  | ER | OPPD | S1399 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GrayCountyWindMontezuma | 03 - Spearville | 1 | PQ | Wind | 110 |  | ER | SUNC | Gray County Tap 115kV
H092 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 60 |  | ER/NR | MP | MP Boswell
H092BOSWELL | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 585 |  | ER/NR | MP | MP Boswell
J091 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 66 |  | ER/NR | ALTW
J279NEAL | 09 - Nebraska | 1 | DIS-15-2-PQ | Coal | 680 |  | ER/NR | MEC
J416 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | ALTW
LlanoEstacadoWhiteDeer | 02 - Hitchland | 1 | PQ | Wind | 80 |  | ER | SPS | Llano Wind 115kV
MPC00500GRE | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Wind | 51 |  | ER/NR | GRE
NPPDBrokenBow | 09 - Nebraska | 1 | PQ | Heat | 7.3 |  | ER | NPPD | Broken Bow 115kV
NPPDBuffaloCountySolar | 09 - Nebraska | 1 | PQ | Solar | 10 |  | ER | NPPD | Kearney Northeast
NPPDBurtCountyWind | 09 - Nebraska | 1 | PQ | Wind | 20 |  | ER | NPPD | Tekamah & Oakland 115kV
NPPDBurwell | 09 - Nebraska | 1 | PQ | Heat | 3.3 |  | ER | NPPD | Ord 115kV
NPPDColumbusHydro | 09 - Nebraska | 1 | PQ | Hydro | 45 |  | ER | NPPD | Columbus 115kV
NPPDOrd | 09 - Nebraska | 1 | PQ | Heat | 10.8 |  | ER | NPPD | Ord 115kV
NPPDStuart | 09 - Nebraska | 1 | PQ | Heat | 1.8 |  | ER | NPPD | Ainsworth 115kV
R15 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 80 |  | ER/NR | MEC | Pomeroy 161kV
R22 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | MEC
R23 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | MEC | Monona - Carroll 161kV
R26 | 13 - Northeast Kansas/Northwest Missouri | 1 | DIS-15-2-PQ | Wind | 400 |  | ER | MEC | MEC Cooper - Booneville 345kV
R34 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 250 |  | ER/NR | MEC | Council Bluffs - Madison County 345kV
R35 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 80 |  | ER/NR | MEC | Pomeroy Wind Farm site
R39 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 499.98 |  | ER/NR | MEC | Raun - Lakefield Junction
R42 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 250 |  | ER/NR | MEC
R49 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 12 |  | ER/NR | MEC | Pomeroy Generating station
R65 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 92 |  | ER/NR | MEC | R34 Expansion
SPSCarson | 02 - Hitchland | 1 | PQ | Wind | 10 |  | ER | SPS | Martin 115kV
SPSDumas19thSt | 02 - Hitchland | 1 | PQ | Wind | 20 |  | ER | SPS | Dumas 19th Street 115kV
SPSEtter | 02 - Hitchland | 1 | PQ | Wind | 20 |  | ER | SPS | Etter 115kV
SPSHopi | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 |  | ER | SPS | Hopi 115kV
SPSJal | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 |  | ER | SPS | S Jal 115kV
SPSLeaRoad | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 |  | ER | SPS | Lea Road 115kV
SPSMonument | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 |  | ER | SPS | Monument 115kV
SPSMooreE | 02 - Hitchland | 1 | PQ | Wind | 17.5 |  | ER | SPS | Moore East 115kV
SPSOcotillo | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 |  | ER | SPS | S_Jal 115kV
SPSSherman | 02 - Hitchland | 1 | PQ | Wind | 20 |  | ER | SPS | Sherman 115kV
Sunray | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Wind | 34.5 |  | ER | SPS | Valero 115kV
WAPASEAMSFtRandleHydro | 09 - Nebraska | 1 | PQ | Hydro | 351.2 |  | ER | WAPA | Ft Randle (WAPA) 230kV & 115kV
WAPASEAMSGavinsPtHydro | 09 - Nebraska | 1 | PQ | Hydro | 102 |  | ER | WAPA | Gavins Point (WAPA) 115kV
WAPASEAMSSpiritMoundHeat | 09 - Nebraska | 1 | PQ | Heat | 120 |  | ER | BEPC-SPP | Spirit Mound (WAPA) 115kV
Young1 | 16 - Western North Dakota | 1 | DIS-15-2-PQ | Coal | 274 |  | ER | OTP

## Constraints Summary
Group | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name | Detail
01ALL | ERIS | Non-Converge | None |  | None | [7 empty] | None | N/A
01ALL | ERIS | Thermal | None |  | None | [7 empty] | None | N/A
02ALL | ERIS | Non-Converge | Non-Converge | 24L | P23:345:SUNC:HLC_BRK188 | [7 empty] | Beaver County to Clark County 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 55 miles of new 345kV line from Beaver County to Clark County
02ALL | ERIS | Non-Converge | Non-Converge | 24L | P23:345:SUNC:HLC_BRK188 | [7 empty] | Beaver County to Clark County 345kV New Line (DISIS-2017-001) (OKGE) | Build approximately 70 miles of new 345kV line from Beaver County to Clark County
02ALL | ERIS | Non-Converge | Non-Converge | 24L | P23:345:SUNC:HLC_BRK188 | [7 empty] | Beaver County to Grapeveine 345kV New Line (DISIS-2017-001) (OKGE) | Build approximately 45 miles of new 345kV line from Beaver County to Grapevine
02ALL | ERIS | Non-Converge | Non-Converge | 24L | P23:345:SUNC:HLC_BRK188 | [7 empty] | Beaver County to Grapeveine 345kV New Line (DISIS-2017-001) (SWPS) | Build approximately 45 miles of new 345kV line from Beaver County to Grapevine
02ALL | ERIS | Non-Converge | Non-Converge | 24L | P23:345:SUNC:HLC_BRK188 | [7 empty] | Grapevine 345kV New Substation (DISIS-2017-001) | Build a new 345kV substation at Grapevine
02ALL | ERIS | Non-Converge | Non-Converge | 24L | P23:345:SUNC:HLC_BRK188 | [7 empty] | Grapevine to Chisholm 345kV New Line (DISIS-2017-001) (AEPW) | Build approximately 35 miles of new 345kV line from Grapevine to Chisholm
02ALL | ERIS | Non-Converge | Non-Converge | 24L | P23:345:SUNC:HLC_BRK188 | [7 empty] | Grapevine to Chisholm 345kV New Line (DISIS-2017-001) (SWPS) | Build approximately 40 miles of new 345kV line from Grapevine to Chisholm
02ALL | ERIS | Non-Converge | Non-Converge | 24L | P23:345:SUNC:HLC_BRK188 | [7 empty] | Potter County to Grapevine 345kV New Line (DISIS-2017-001) | Build approximately 65 miles of new 345kV line from Potter County to Grapevine
02ALL | ERIS | Non-Converge | Non-Converge | 24L | P23:345:SUNC:HLC_BRK282 | [7 empty] | Beaver County to Clark County 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 55 miles of new 345kV line from Beaver County to Clark County
02ALL | ERIS | Non-Converge | Non-Converge | 24L | P23:345:SUNC:HLC_BRK282 | [7 empty] | Beaver County to Clark County 345kV New Line (DISIS-2017-001) (OKGE) | Build approximately 70 miles of new 345kV line from Beaver County to Clark County
02ALL | ERIS | Non-Converge | Non-Converge | 24L | P23:345:SUNC:HLC_BRK282 | [7 empty] | Beaver County to Grapeveine 345kV New Line (DISIS-2017-001) (OKGE) | Build approximately 45 miles of new 345kV line from Beaver County to Grapevine
02ALL | ERIS | Non-Converge | Non-Converge | 24L | P23:345:SUNC:HLC_BRK282 | [7 empty] | Beaver County to Grapeveine 345kV New Line (DISIS-2017-001) (SWPS) | Build approximately 45 miles of new 345kV line from Beaver County to Grapevine
02ALL | ERIS | Non-Converge | Non-Converge | 24L | P23:345:SUNC:HLC_BRK282 | [7 empty] | Grapevine 345kV New Substation (DISIS-2017-001) | Build a new 345kV substation at Grapevine
02ALL | ERIS | Non-Converge | Non-Converge | 24L | P23:345:SUNC:HLC_BRK282 | [7 empty] | Grapevine to Chisholm 345kV New Line (DISIS-2017-001) (AEPW) | Build approximately 35 miles of new 345kV line from Grapevine to Chisholm
02ALL | ERIS | Non-Converge | Non-Converge | 24L | P23:345:SUNC:HLC_BRK282 | [7 empty] | Grapevine to Chisholm 345kV New Line (DISIS-2017-001) (SWPS) | Build approximately 40 miles of new 345kV line from Grapevine to Chisholm
02ALL | ERIS | Non-Converge | Non-Converge | 24L | P23:345:SUNC:HLC_BRK282 | [7 empty] | Potter County to Grapevine 345kV New Line (DISIS-2017-001) | Build approximately 65 miles of new 345kV line from Potter County to Grapevine
02ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24WP, 29SP | P42:345:OKGE:SB_BAER7314 | [7 empty] | Beaver County to Clark County 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 55 miles of new 345kV line from Beaver County to Clark County
02ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24WP, 29SP | P42:345:OKGE:SB_BAER7314 | [7 empty] | Beaver County to Clark County 345kV New Line (DISIS-2017-001) (OKGE) | Build approximately 70 miles of new 345kV line from Beaver County to Clark County
02ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24WP, 29SP | P42:345:OKGE:SB_BAER7314 | [7 empty] | Beaver County to Grapeveine 345kV New Line (DISIS-2017-001) (OKGE) | Build approximately 45 miles of new 345kV line from Beaver County to Grapevine
02ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24WP, 29SP | P42:345:OKGE:SB_BAER7314 | [7 empty] | Beaver County to Grapeveine 345kV New Line (DISIS-2017-001) (SWPS) | Build approximately 45 miles of new 345kV line from Beaver County to Grapevine
02ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24WP, 29SP | P42:345:OKGE:SB_BAER7314 | [7 empty] | Grapevine 345kV New Substation (DISIS-2017-001) | Build a new 345kV substation at Grapevine
02ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24WP, 29SP | P42:345:OKGE:SB_BAER7314 | [7 empty] | Grapevine to Chisholm 345kV New Line (DISIS-2017-001) (AEPW) | Build approximately 35 miles of new 345kV line from Grapevine to Chisholm
02ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24WP, 29SP | P42:345:OKGE:SB_BAER7314 | [7 empty] | Grapevine to Chisholm 345kV New Line (DISIS-2017-001) (SWPS) | Build approximately 40 miles of new 345kV line from Grapevine to Chisholm
02ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24WP, 29SP | P42:345:OKGE:SB_BAER7314 | [7 empty] | Potter County to Grapevine 345kV New Line (DISIS-2017-001) | Build approximately 65 miles of new 345kV line from Potter County to Grapevine
02ALL | ERIS | Thermal | None |  | None | [7 empty] | None | N/A
03ALL | ERIS | Non-Converge | None |  | None | [7 empty] | None | N/A
03ALL | ERIS | Non-Converge | Non-Converge | 29SP | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) | [7 empty] | Finney 345kV Reactive Support (DISIS-2017-001) | Install +250 MVAR Capacitor Bank(s) at Finney 345kV
03ALL | ERIS | Non-Converge | Non-Converge | 29SP | P23:345:SUNC:HLC_BRK188 | [7 empty] | Finney 345kV Reactive Support (DISIS-2017-001) | Install +250 MVAR Capacitor Bank(s) at Finney 345kV
03ALL | ERIS | Non-Converge | Non-Converge | 29SP | P23:345:SUNC:HLC_BRK282 | [7 empty] | Finney 345kV Reactive Support (DISIS-2017-001) | Install +250 MVAR Capacitor Bank(s) at Finney 345kV
03ALL | ERIS | Thermal | 515853 DGRASSE4 138 520436 ROSEVLY4 138 1 | 20G | System Intact | 160 |  |  | 100.26 |  |  |  | Degrassee 138kV Terminal Upgrades (DISIS-2017-001) (OKGE) | Upgrade terminal equipment at Degrasse 138kV to achieve a minimum Spring/Emergency rating of 175 MVA
03ALL | ERIS | Thermal | 515853 DGRASSE4 138 520436 ROSEVLY4 138 1 | 20G | System Intact | 160 |  |  | 100.26 |  |  |  | Rose Valley to Degrasse 138kV Rebuild (DISIS-2017-001) (WFEC) | Rebuild the existing Rose Valley to Degrasse 138kV 3.2 mile line to achieve a minimum Spring/Emergency rating of 175 MVA
03ALL | ERIS | Thermal | 523853 FINNEY 7 345 588754 G17-032-TAP 345 1 | 29S | System Intact | 380 |  |  | 111.75 |  |  |  | Finney to G17-032 Tap 345kV Rebuild (DISIS-2017-001) | Rebuild the existing Finney to G17-032 Tap 345kV 78.75 mile line to achieve a minimum Summer/Emergency rating of 425 MVA
03ALL | ERIS | Thermal | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 24L | System Intact | 319 |  |  | 104.17 |  |  |  | Smokey Hils to Summit 230kV Rebuild (DISIS-2017-001) (MIDW) | Rebuild the existing Smokey Hills to Summit 230kV 16.1 mile line to achieve a minimum Light/Emergency rating of 375 MVA
03ALL | ERIS | Thermal | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 24L | System Intact | 319 |  |  | 104.17 |  |  |  | Smokey Hils to Summit 230kV Rebuild (DISIS-2017-001) (WERE) | Rebuild the existing Smokey Hills to Summit 230kV 22.5 mile line to achieve a minimum Light/Emergency rating of 375 MVA
04ALL | ERIS | Non-Converge | None |  | None | [7 empty] | None | N/A
04ALL | ERIS | Thermal | None |  | None | [7 empty] | None | N/A
06ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | System Intact | [7 empty] | Crawfish Draw 765/345kV New Substation (DISIS-2017-001) | Build a new Crawfish Draw 765/345kV Substation tapping the Tuco to Border 345kV Ckt 1 and Tuco to OKU 345kV Ckt 1. In addition, install a new 1000 MVar SVC for Dynamic Reactive Support at Crawfish Draw 765kV. Both the 765kV and the 345kV Crawfish Draw switchyards shall be constructed with breaker and a half bus schemes. Furthermore, interconnected double circuit lines connected to these switchyards or transformers connecting these switchyards shall not share adjacent breakers in the switchyard(s).
06ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | System Intact | [7 empty] | Crawfish Draw 765/345kV New Transformer (DISIS-2017-001) | Install two new 765/345kV Transformers at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | System Intact | [7 empty] | Crawfish Draw Tap to Tuco to Border 345kV Ckt 1 (DISIS-2017-001) (OKGE) | Tap Tuco to Border 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation
06ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | System Intact | [7 empty] | Crawfish Draw Tap to Tuco to Border 345kV Ckt 1 (DISIS-2017-001) (SWPS) | Tap Tuco to Border 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation
06ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | System Intact | [7 empty] | Crawfish Draw Tap to Tuco to OKU 345kV Ckt 1 (DISIS-2017-001) (AEPW) | Tap Tuco to OKU 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation
06ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | System Intact | [7 empty] | Crawfish Draw Tap to Tuco to OKU 345kV Ckt 1 (DISIS-2017-001) (SWPS) | Tap Tuco to OKU 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation
06ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | System Intact | [7 empty] | Crawfish Draw to Seminole 765kV New Line Double Circuit (DISIS-2017-001) (OKGE) | Build approximately 80 miles of new double circuit 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | System Intact | [7 empty] | Crawfish Draw to Seminole 765kV New Line Double Circuit (DISIS-2017-001) (SWPS) | Build approximately 265 miles of new double circuit 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | System Intact | [7 empty] | Crossroads 765/345kV New Transformer (DISIS-2017-001) | Expand Crossroads 765kV Substation and install a new 765/345 transformer
06ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | System Intact | [7 empty] | Crossroads to Crawfish Draw 765kV New Line (DISIS-2017-001) | Build approximately 85 miles of new 765kV line from Crossroads to Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | System Intact | [7 empty] | Seminole 765/345 New Transformer (DISIS-2017-001) | Expand Seminole 345kV substation to include a new 765kV switchyard connected by a new 765/345kV transformer. In addition, install a new 600 MVar SVC for Dynamic Reactive Support at Seminole 765kV.
06ALL | ERIS | Thermal | 524502 NORTON 3 115 524768 PLSNT_HILL 3 115 1 | 20G, 20SP, 24L, 24SP, 29SP | P12:115:SPS:W59.1.LOPEZ.CMPBLL |  | 128.1 | 87.64 | 114.39 |  |  |  | Norton to Pleasant Hills 115kV Rebuild (DISIS-2017-001) | Rebuild the existing Norton to Pleasant Hills 115kV 54.54 mile line to achieve a minimum Light/Emergency rating of 150 MVA
06ALL | ERIS | Thermal | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 | 20G | P12:345:SPS:J15.1.XRDS.TOLK |  | 643 | 47.11 | 133.54 |  |  |  | Crawfish Draw 345/230kV Transformer Ckt 1 (DISIS-2017-001) | Install a new 345/230kV Transformer at Crawfish Draw
06ALL | ERIS | Thermal | 525830 TUCO_INT 6 230 998078 SIEM 8743066 230 2 | 20G | P12:345:SPS:J15.1.XRDS.TOLK |  | 643 | 40.6 | 116.5 |  |  |  | Crawfish Draw 345/230kV Transformer Ckt 1 (DISIS-2017-001) | Install a new 345/230kV Transformer at Crawfish Draw
06ALL | ERIS | Thermal | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 20G | P12:345:SPS:J15.1.XRDS.TOLK |  | 997.3 | N/A | 109.65 |  |  |  | Crawfish Draw 345/230kV Transformer Ckt 1 (DISIS-2017-001) | Install a new 345/230kV Transformer at Crawfish Draw
06ALL | ERIS | Thermal | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 | 20G | P12:345:SPS:J15.1.XRDS.TOLK |  | 643 | 45.77 | 133.6 |  |  |  | Crawfish Draw 345/230kV Transformer Ckt 1 (DISIS-2017-001) | Install a new 345/230kV Transformer at Crawfish Draw
06ALL | ERIS | Thermal | 525832 TUCO_INT 7 345 998078 SIEM 8743066 230 2 | 20G | P12:345:SPS:J15.1.XRDS.TOLK |  | 643 | 40.13 | 118.47 |  |  |  | Crawfish Draw 345/230kV Transformer Ckt 1 (DISIS-2017-001) | Install a new 345/230kV Transformer at Crawfish Draw
06ALL | ERIS | Thermal | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 19WP, 24L, 24SP, 24WP, 29SP | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT |  | 553 | 71.21 | 204.34 |  |  |  | Tolk 345/230 kV CKT 2 Transformer (DISIS-2016-002) | Build new 345/230 kV Transformer Ckt 2 at Tolk to achieve a minimum emergency rating of 921 MVA on the Crossroads - Tolk 345 kV Ckt 1 line.
06ALL | ERIS | Thermal | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 | 20SP | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT |  | 553 | 61.87 | 175.5 |  |  |  | Tolk 345/230 kV CKT 2 Transformer (DISIS-2016-002) | Build new 345/230 kV Transformer Ckt 2 at Tolk to achieve a minimum emergency rating of 921 MVA on the Crossroads - Tolk 345 kV Ckt 1 line.
06ALL | ERIS | Thermal | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | 20SP, 24L, 24SP, 24WP | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT |  | 956 | 40.57 | 117.64 |  |  |  | Tolk to Tuco 345kV New Line (DISIS-2017-001) | Build approximately 54 miles of new 345kV line from Tolk to Tuco
06ALL | ERIS | Thermal | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 19WP, 24L, 24SP, 24WP, 29SP | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT |  | 553 | 69.86 | 194 |  |  |  | Tolk 345/230 kV CKT 2 Transformer (DISIS-2016-002) | Build new 345/230 kV Transformer Ckt 2 at Tolk to achieve a minimum emergency rating of 921 MVA on the Crossroads - Tolk 345 kV Ckt 1 line.
06ALL | ERIS | Thermal | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 | 20SP | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT |  | 553 | 61.02 | 171.96 |  |  |  | Tolk 345/230 kV CKT 2 Transformer (DISIS-2016-002) | Build new 345/230 kV Transformer Ckt 2 at Tolk to achieve a minimum emergency rating of 921 MVA on the Crossroads - Tolk 345 kV Ckt 1 line.
06ALL | ERIS | Thermal | 525531 TOLK 6 230 998088 TOLK2 230 2 | 20G | P42:345:OKGE:SB_BAER7314 |  | 553 | 33.16 | 100.51 |  |  |  | Tolk 345/230kV Transformer Ckt 3 (DISIS-2017-001) | Install a new 345/230kV Transformer at Tolk
06ALL | ERIS | Thermal | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 | 20G | P42:345:OKGE:SB_BAER7314 |  | 553 | 62.43 | 125.63 |  |  |  | Tolk 345/230 kV CKT 2 Transformer (DISIS-2016-002) | Build new 345/230 kV Transformer Ckt 2 at Tolk to achieve a minimum emergency rating of 921 MVA on the Crossroads - Tolk 345 kV Ckt 1 line.
06ALL | ERIS | Thermal | 525549 TOLK 7 345 998088 TOLK2 230 2 | 20G | P42:345:OKGE:SB_BAER7314 |  | 553 | 33.61 | 100.66 |  |  |  | Tolk 345/230kV Transformer Ckt 3 (DISIS-2017-001) | Install a new 345/230kV Transformer at Tolk
06ALL | ERIS | Thermal | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 | 20G | P42:345:OKGE:SB_BAER7314 |  | 553 | 61.59 | 125.5 |  |  |  | Tolk 345/230 kV CKT 2 Transformer (DISIS-2016-002) | Build new 345/230 kV Transformer Ckt 2 at Tolk to achieve a minimum emergency rating of 921 MVA on the Crossroads - Tolk 345 kV Ckt 1 line.
06ALL | ERIS | Thermal | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 20G | P42:345:SPS:CROSSROADS_6R30_19L |  | 997.3 | N/A | 136.64 |  |  |  | Tuco to Crawfish Draw 345kV Rebuild (DISIS-2017-001) | Rebuild the existing Tuco to Crawfish Draw 345kV 1.54 mile line to achieve a minimum light/emergency rating of 1094 MVA
06ALL | ERIS | Thermal | 524502 NORTON 3 115 524768 PLSNT_HILL 3 115 1 | 20G, 20SP, 24L | System Intact | 128.1 |  | 84.51 | 111.11 |  |  |  | Norton to Pleasant Hills 115kV Rebuild (DISIS-2017-001) | Rebuild the existing Norton to Pleasant Hills 115kV 54.54 mile line to achieve a minimum Light/Emergency rating of 150 MVA
06ALL | ERIS | Thermal | 525454 HALE_CNTY 3 115 525828 TUCO_INT 3 115 1 | 20G | System Intact | 80 |  | 25.91 | 114.43 |  |  |  | Model Correction | 2021 ITP models show the Rate A for this line is 96 MVA, no mitigation is required
06ALL | ERIS | Thermal | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 | 20SP | System Intact | 478 |  | 67.48 | 148.08 |  |  |  | Tolk 345/230 kV CKT 2 Transformer (DISIS-2016-002) | Build new 345/230 kV Transformer Ckt 2 at Tolk to achieve a minimum emergency rating of 921 MVA on the Crossroads - Tolk 345 kV Ckt 1 line.
06ALL | ERIS | Thermal | 525531 TOLK 6 230 998088 TOLK2 230 2 | 20G | System Intact | 478 |  | 31.32 | 101.35 |  |  |  | Tolk 345/230kV Transformer Ckt 3 (DISIS-2017-001) | Install a new 345/230kV Transformer at Tolk
06ALL | ERIS | Thermal | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 | 20G | System Intact | 478 |  | 75.98 | 123.2 |  |  |  | Tolk 345/230 kV CKT 2 Transformer (DISIS-2016-002) | Build new 345/230 kV Transformer Ckt 2 at Tolk to achieve a minimum emergency rating of 921 MVA on the Crossroads - Tolk 345 kV Ckt 1 line.
06ALL | ERIS | Thermal | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 19WP, 24L, 24SP, 24WP, 29SP | System Intact | 478 |  | 76.13 | 179.04 |  |  |  | Tolk 345/230 kV CKT 2 Transformer (DISIS-2016-002) | Build new 345/230 kV Transformer Ckt 2 at Tolk to achieve a minimum emergency rating of 921 MVA on the Crossroads - Tolk 345 kV Ckt 1 line.
06ALL | ERIS | Thermal | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 | 20SP | System Intact | 478 |  | 66.59 | 147.21 |  |  |  | Tolk 345/230 kV CKT 2 Transformer (DISIS-2016-002) | Build new 345/230 kV Transformer Ckt 2 at Tolk to achieve a minimum emergency rating of 921 MVA on the Crossroads - Tolk 345 kV Ckt 1 line.
06ALL | ERIS | Thermal | 525549 TOLK 7 345 998088 TOLK2 230 2 | 20G | System Intact | 478 |  | 31.75 | 101.74 |  |  |  | Tolk 345/230kV Transformer Ckt 3 (DISIS-2017-001) | Install a new 345/230kV Transformer at Tolk
06ALL | ERIS | Thermal | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 | 20G | System Intact | 478 |  | 74.93 | 123.37 |  |  |  | Tolk 345/230 kV CKT 2 Transformer (DISIS-2016-002) | Build new 345/230 kV Transformer Ckt 2 at Tolk to achieve a minimum emergency rating of 921 MVA on the Crossroads - Tolk 345 kV Ckt 1 line.
06ALL | ERIS | Thermal | 525830 TUCO_INT 6 230 998078 SIEM 8743066 230 2 | 20G | System Intact | 559 |  | 52.06 | 107.96 |  |  |  | Crawfish Draw 345/230kV Transformer Ckt 1 (DISIS-2017-001) | Install a new 345/230kV Transformer at Crawfish Draw
06ALL | ERIS | Thermal | 525832 TUCO_INT 7 345 998078 SIEM 8743066 230 2 | 20G | System Intact | 559 |  | 51.58 | 108.9 |  |  |  | Crawfish Draw 345/230kV Transformer Ckt 1 (DISIS-2017-001) | Install a new 345/230kV Transformer at Crawfish Draw
07ALL | ERIS | Non-Converge | None |  | None | [7 empty] | None | N/A
07ALL | ERIS | Thermal | None |  | None | [7 empty] | None | N/A
08ALL | ERIS | Non-Converge | Non-Converge | 19WP | P23:345:AEPW:RIVERSIDE CB 3413A NBTB | [7 empty] | Invalid Contingency | Contingency not valid - unit at PRWINDG1 (530690) removed with area interchange disabled.
08ALL | ERIS | Non-Converge | Non-Converge | 20SP, 24SP, 29SP | P23:345:WERE:JEC_345-16:: | [7 empty] | Invalid Contingency | Contingency not valid - large unit at JEC U2 (532652) removed with area interchange disabled.
08ALL | ERIS | Non-Converge | Non-Converge | 19WP, 24WP | P23:345:WERE:WOLF_345-50:: | [7 empty] | Invalid Contingency | Contingency not valid - large unit at WCGS U1 (532751) removed with area interchange disabled.
08ALL | ERIS | Non-Converge | Non-Converge | 19WP | P43:345:GRDA:GRDA CB9580 | [7 empty] | Solved manually | Lock Shunt at NEO184B1 (547709)
08ALL | ERIS | Thermal | 547476 ASB349 5 161 547477 CJ 366 5 161 1 | 24WP | P12:161:EMDE:SCHD_REMOVE_2019::ASB349_CAR(SPA) |  | 223 | 67.19 | 100.28 |  |  |  | Model Correction | 2021 ITP models show the Rate B for this line is 322 MVA, no mitigation is required
08ALL | ERIS | Thermal | 532938 FRANKLIN5 161 997850 FRAN TX-1 69.0 1 | 29SP | P12:161:WERE:FRAN-LITC_161:: |  | 110 | 76.58 | 130.73 |  |  |  | Franklin 161/69kV Transformer Ckt 2 (DISIS-2017-001) | Install a new 161/69kV Transformer at Franklin
08ALL | ERIS | Thermal | 532938 FRANKLIN5 161 997851 FRAN TX-1 69.0 1 | 24SP, 24WP | P12:161:WERE:FRAN-LITC_161:: |  | 110 | 72.63 | 114.8 |  |  |  | Franklin 161/69kV Transformer Ckt 2 (DISIS-2017-001) | Install a new 161/69kV Transformer at Franklin
08ALL | ERIS | Thermal | 532938 FRANKLIN5 161 997852 FRAN TX-1 69.0 1 | 19WP | P12:161:WERE:FRAN-LITC_161:: |  | 110 | 71.16 | 111.76 |  |  |  | Franklin 161/69kV Transformer Ckt 2 (DISIS-2017-001) | Install a new 161/69kV Transformer at Franklin
08ALL | ERIS | Thermal | 532938 FRANKLIN5 161 997855 FRAN TX-1 69.0 1 | 20SP | P12:161:WERE:FRAN-LITC_161:: |  | 110 | 70.61 | 109.64 |  |  |  | Franklin 161/69kV Transformer Ckt 2 (DISIS-2017-001) | Install a new 161/69kV Transformer at Franklin
08ALL | ERIS | Thermal | 532938 FRANKLIN5 161 997861 FRAN TX-1 69.0 1 | 20G | P12:161:WERE:FRAN-LITC_161:: |  | 110 | 64.77 | 108.74 |  |  |  | Franklin 161/69kV Transformer Ckt 2 (DISIS-2017-001) | Install a new 161/69kV Transformer at Franklin
08ALL | ERIS | Thermal | 533876 FRANKLIN2 69.0 997850 FRAN TX-1 69.0 1 | 29SP | P12:161:WERE:FRAN-LITC_161:: |  | 110 | 74.55 | 115.26 |  |  |  | Franklin 161/69kV Transformer Ckt 2 (DISIS-2017-001) | Install a new 161/69kV Transformer at Franklin
08ALL | ERIS | Thermal | 533876 FRANKLIN2 69.0 997851 FRAN TX-1 69.0 1 | 24SP, 24WP | P12:161:WERE:FRAN-LITC_161:: |  | 110 | 75.41 | 114.98 |  |  |  | Franklin 161/69kV Transformer Ckt 2 (DISIS-2017-001) | Install a new 161/69kV Transformer at Franklin
08ALL | ERIS | Thermal | 533876 FRANKLIN2 69.0 997852 FRAN TX-1 69.0 1 | 19WP | P12:161:WERE:FRAN-LITC_161:: |  | 110 | 69.68 | 109.22 |  |  |  | Franklin 161/69kV Transformer Ckt 2 (DISIS-2017-001) | Install a new 161/69kV Transformer at Franklin
08ALL | ERIS | Thermal | 533876 FRANKLIN2 69.0 997855 FRAN TX-1 69.0 1 | 20SP | P12:161:WERE:FRAN-LITC_161:: |  | 110 | 69.07 | 108.24 |  |  |  | Franklin 161/69kV Transformer Ckt 2 (DISIS-2017-001) | Install a new 161/69kV Transformer at Franklin
08ALL | ERIS | Thermal | 533876 FRANKLIN2 69.0 997861 FRAN TX-1 69.0 1 | 20G | P12:161:WERE:FRAN-LITC_161:: |  | 110 | 63.88 | 107.6 |  |  |  | Franklin 161/69kV Transformer Ckt 2 (DISIS-2017-001) | Install a new 161/69kV Transformer at Franklin
08ALL | ERIS | Thermal | 532932 LITCH 5 161 532938 FRANKLIN5 161 1 | 19WP, 24WP | P12:161:WERE:NSES-EMDE_161:: |  | 251 | 88.72 | 113.39 |  |  |  | Litchfield to Franklin 161kV Rebuild (DISIS-2017-001) | Rebuild the existing Litchfield to Franklin 161kV 6.22 mile line to achieve a minimum Winter/Emergency rating of 300 MVA
08ALL | ERIS | Thermal | 532932 LITCH 5 161 547476 ASB349 5 161 1 | 19WP, 20G, 24WP | P12:161:WERE:NSES-EMDE_161:: |  | 251 | 105.64 | 129.13 |  |  |  | Litchfield to Asbury Plant 161kV Rebuild (DISIS-2017-001) (EMDE) | Rebuild the existing Litchfield to Asbury Plant 161kV 5 mile line to achieve a minimum Winter/Emergency rating of 325 MVA
08ALL | ERIS | Thermal | 532932 LITCH 5 161 547476 ASB349 5 161 1 | 19WP, 20G, 24WP | P12:161:WERE:NSES-EMDE_161:: |  | 251 | 105.64 | 129.13 |  |  |  | Litchfield to Asbury Plant 161kV Rebuild (DISIS-2017-001) (WERE) | Rebuild the existing Litchfield to Asbury Plant 161kV 1.6 mile line to achieve a minimum Winter/Emergency rating of 325 MVA
08ALL | ERIS | Thermal | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 | 19WP, 20G, 20SP, 24SP, 24WP, 29SP | P12:161:WERE:NSES-EMDE_161:: |  | 223 | 94.91 | 128.35 |  |  |  | Franklin to G17-005 Tap 161kV Rebuild (DISIS-2017-001) | Rebuild the existing Franklin to G17-005 Tap 161kV 20.56 mile line to achieve a minimum Winter/Emergency rating of 300 MVA
08ALL | ERIS | Thermal | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 | 19WP, 20G, 20SP, 24SP, 24WP, 29SP | P12:345:WERE:WAVS-LACY_345:: |  | 956 | 104.26 | 131.72 |  |  |  | Neosho to G17-009 Tap Rebuild (DISIS-2017-001) | Rebuild the existing Neosho to G17-009 345kV 18.17 mile line to achieve a minimum Winter/Emergency rating of 1260 MVA
08ALL | ERIS | Thermal | 532798 VIOLA 7 345 997930 VIOLA TX-1 138 1 | 29SP | P23:345:WERE:WICH_345-116:: |  | 440 | 94.15 | 104.06 |  |  |  | Viola 345/138kV Transformer CKT 2 (DISIS-2016-002-2) | Build second 345/138/13.8kV transformer at Viola.
08ALL | ERIS | Thermal | 532798 VIOLA 7 345 997931 VIOLA TX-1 138 1 | 24SP | P23:345:WERE:WICH_345-116:: |  | 440 | 94.02 | 104.22 |  |  |  | Viola 345/138kV Transformer CKT 2 (DISIS-2016-002-2) | Build second 345/138/13.8kV transformer at Viola.
08ALL | ERIS | Thermal | 532798 VIOLA 7 345 997935 VIOLA TX-1 138 1 | 20SP | P23:345:WERE:WICH_345-116:: |  | 440 | 94.65 | 104.81 |  |  |  | Viola 345/138kV Transformer CKT 2 (DISIS-2016-002-2) | Build second 345/138/13.8kV transformer at Viola.
08ALL | ERIS | Thermal | 533075 VIOLA 4 138 997930 VIOLA TX-1 138 1 | 29SP | P23:345:WERE:WICH_345-116:: |  | 440 | 93.01 | 102.4 |  |  |  | Viola 345/138kV Transformer CKT 2 (DISIS-2016-002-2) | Build second 345/138/13.8kV transformer at Viola.
08ALL | ERIS | Thermal | 533075 VIOLA 4 138 997931 VIOLA TX-1 138 1 | 24SP | P23:345:WERE:WICH_345-116:: |  | 440 | 92.94 | 102.61 |  |  |  | Viola 345/138kV Transformer CKT 2 (DISIS-2016-002-2) | Build second 345/138/13.8kV transformer at Viola.
08ALL | ERIS | Thermal | 533075 VIOLA 4 138 997935 VIOLA TX-1 138 1 | 20SP | P23:345:WERE:WICH_345-116:: |  | 440 | 93.26 | 102.86 |  |  |  | Viola 345/138kV Transformer CKT 2 (DISIS-2016-002-2) | Build second 345/138/13.8kV transformer at Viola.
08ALL | ERIS | Thermal | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 20SP, 24SP, 29SP | System Intact | 194 |  | 103.45 | 105.47 |  |  |  | Afton to Ketchum 161kV Rebuild (DISIS-2017-001) | Rebuild the existing Afton to Ketchum 161kV 12.8 mile line to achieve a minimum Summer/Emergency rating of 225 MVA
08ALL | ERIS | Thermal | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 20SP, 24SP, 29SP | System Intact | 194 |  | 106.71 | 108.72 |  |  |  | Pensacola to Ketchum 161kV Rebuild (DISIS-2017-001) | Rebuild the existing Pensacole to Ketchum 161kV 4.8 mile line to achieve a minimum Summer/Emergency rating of 225 MVA
08ALL | ERIS | Thermal | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 | 19WP, 20G, 24WP | System Intact | 956 |  | 80.21 | 103.87 |  |  |  | Neosho to G17-009 Tap Rebuild (DISIS-2017-001) | Rebuild the existing Neosho to G17-009 345kV 18.17 mile line to achieve a minimum Winter/Emergency rating of 1260 MVA
08ALL | ERIS | Thermal | 532799 WAVERLY7 345 542981 LACYGNE7 345 1 | 20G, 20SP, 24SP | System Intact | 1141 |  | 99.47 | 108.39 |  |  |  | Wolf Creek to Blackberry 345kV | Build a new 86 mile 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA
08ALL | ERIS | Thermal | 532937 NEOSHO 5 161 547469 RIV4525 161 1 | 19WP, 20G, 20SP, 24SP, 24WP, 29SP | System Intact | 205 |  |  | 174.51 |  |  |  | Model Correction | 2021 ITP models show the Rate A for this line is 754 MVA, no mitigation is required
08ALL | ERIS | Thermal | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 | 19WP, 24WP, 29SP | System Intact | 220 |  | 74.69 | 108.15 |  |  |  | Franklin to G17-005 Tap 161kV Rebuild (DISIS-2017-001) | Rebuild the existing Franklin to G17-005 Tap 161kV 20.56 mile line to achieve a minimum Winter/Emergency rating of 300 MVA
08ALL | ERIS | Thermal | 589305 G17-092XFMR2 34.5 589300 GEN-2017-092 345 1 | 19WP, 20G, 20SP, 24SP, 24WP, 29SP | System Intact | 125 |  |  | 103.15 |  |  |  | Interconnection Facilities | Project Equipment will be built to enure no thermal overloads on collector system, no mitigation required
08ALL | ERIS | Thermal | 505480 BEAVER 5 161 506932 EUREKA 5 161 1 | 24L | System Intact | 247 |  | 99.75 | 100.41 |  |  |  | Beaver to Eureka 161kV Rebuild (DISIS-2017-001) (SWPA) | Rebuild the existing Beaver to Eureka 161kV 6 mile line section to achieve a minimum light/emergency rating of 258 MVA
08ALL | ERIS | Thermal | 505480 BEAVER 5 161 506932 EUREKA 5 161 1 | 24L | System Intact | 247 |  | 99.75 | 100.41 |  |  |  | Beaver to Eureka 161kV Rebuild (DISIS-2017-001) (AEP) | Rebuild the existing Beaver to Eureka 161kV 1.22 mile line section to achieve a minimum light/emergency rating of 258 MVA
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT | [7 empty] | Cooper Joe 345kV New Substation (DISIS-2017-001) | Build a new 345 kV substation at Cooper Joe. Tap the Cooper to St. Joe 345kV line 20 miles from St. Joe 345kV
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 6 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 60 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT | [7 empty] | Holt 345kV Terminal Upgrades (DISIS-2017-001) (TMO) | Upgrade terminal equipment at Holt 345kV to accept Holt to Holt new line
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 100 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 26 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS | [7 empty] | Cooper Joe 345kV New Substation (DISIS-2017-001) | Build a new 345 kV substation at Cooper Joe. Tap the Cooper to St. Joe 345kV line 20 miles from St. Joe 345kV
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 6 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 60 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS | [7 empty] | Holt 345kV Terminal Upgrades (DISIS-2017-001) (TMO) | Upgrade terminal equipment at Holt 345kV to accept Holt to Holt new line
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 100 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 26 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR | [7 empty] | Cooper Joe 345kV New Substation (DISIS-2017-001) | Build a new 345 kV substation at Cooper Joe. Tap the Cooper to St. Joe 345kV line 20 miles from St. Joe 345kV
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 6 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 60 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR | [7 empty] | Holt 345kV Terminal Upgrades (DISIS-2017-001) (TMO) | Upgrade terminal equipment at Holt 345kV to accept Holt to Holt new line
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 100 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 26 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:SUNC:MINGO-SETAB::531451-531465(1) | [7 empty] | Holt 345kV Terminal Upgrades (DISIS-2017-001) (TMO) | Upgrade terminal equipment at Holt 345kV to accept Holt to Holt new line
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:SUNC:MINGO-SETAB::531451-531465(1) | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 100 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:SUNC:MINGO-SETAB::531451-531465(1) | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 26 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1) | [7 empty] | Cooper Joe 345kV New Substation (DISIS-2017-001) | Build a new 345 kV substation at Cooper Joe. Tap the Cooper to St. Joe 345kV line 20 miles from St. Joe 345kV
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1) | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 6 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1) | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 60 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1) | [7 empty] | Holt 345kV Terminal Upgrades (DISIS-2017-001) (TMO) | Upgrade terminal equipment at Holt 345kV to accept Holt to Holt new line
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1) | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 100 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1) | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 26 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P14:345:GMO-OPPD:S3458 REACTOR | [7 empty] | Holt 345kV Terminal Upgrades (DISIS-2017-001) (TMO) | Upgrade terminal equipment at Holt 345kV to accept Holt to Holt new line
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P14:345:GMO-OPPD:S3458 REACTOR | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 100 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P14:345:GMO-OPPD:S3458 REACTOR | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 26 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:161-345:GMO-NPPD:STJOE_R5-33::STJOE-COOPER-STJOET22 | [7 empty] | Holt 345kV Terminal Upgrades (DISIS-2017-001) (TMO) | Upgrade terminal equipment at Holt 345kV to accept Holt to Holt new line
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:161-345:GMO-NPPD:STJOE_R5-33::STJOE-COOPER-STJOET22 | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 100 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:161-345:GMO-NPPD:STJOE_R5-33::STJOE-COOPER-STJOET22 | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 26 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | [7 empty] | Cooper Joe 345kV New Substation (DISIS-2017-001) | Build a new 345 kV substation at Cooper Joe. Tap the Cooper to St. Joe 345kV line 20 miles from St. Joe 345kV
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 6 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 60 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | [7 empty] | Holt 345kV Terminal Upgrades (DISIS-2017-001) (TMO) | Upgrade terminal equipment at Holt 345kV to accept Holt to Holt new line
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 100 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 26 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT | [7 empty] | Cooper Joe 345kV New Substation (DISIS-2017-001) | Build a new 345 kV substation at Cooper Joe. Tap the Cooper to St. Joe 345kV line 20 miles from St. Joe 345kV
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 6 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 60 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT | [7 empty] | Holt 345kV Terminal Upgrades (DISIS-2017-001) (TMO) | Upgrade terminal equipment at Holt 345kV to accept Holt to Holt new line
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 100 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 26 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER | [7 empty] | Cooper Joe 345kV New Substation (DISIS-2017-001) | Build a new 345 kV substation at Cooper Joe. Tap the Cooper to St. Joe 345kV line 20 miles from St. Joe 345kV
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 6 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 60 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:KCPL-GMO:NASHUA_R2-11::NASHUA-HAWTHORN-STJOE | [7 empty] | Cooper Joe 345kV New Substation (DISIS-2017-001) | Build a new 345 kV substation at Cooper Joe. Tap the Cooper to St. Joe 345kV line 20 miles from St. Joe 345kV
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:KCPL-GMO:NASHUA_R2-11::NASHUA-HAWTHORN-STJOE | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 6 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:KCPL-GMO:NASHUA_R2-11::NASHUA-HAWTHORN-STJOE | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 60 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:SUNC:HLC_BRK282 | [7 empty] | Cooper Joe 345kV New Substation (DISIS-2017-001) | Build a new 345 kV substation at Cooper Joe. Tap the Cooper to St. Joe 345kV line 20 miles from St. Joe 345kV
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:SUNC:HLC_BRK282 | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 6 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:SUNC:HLC_BRK282 | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 60 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:SUNC:HLC_BRK282 | [7 empty] | Holt 345kV Terminal Upgrades (DISIS-2017-001) (TMO) | Upgrade terminal equipment at Holt 345kV to accept Holt to Holt new line
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:SUNC:HLC_BRK282 | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 100 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:SUNC:HLC_BRK282 | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 26 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P42:345:NPPD:BKR-CPR-3304 | [7 empty] | Cooper Joe 345kV New Substation (DISIS-2017-001) | Build a new 345 kV substation at Cooper Joe. Tap the Cooper to St. Joe 345kV line 20 miles from St. Joe 345kV
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P42:345:NPPD:BKR-CPR-3304 | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 6 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P42:345:NPPD:BKR-CPR-3304 | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 60 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P42:345:NPPD:BKR-CPR-3304 | [7 empty] | Holt 345kV Terminal Upgrades (DISIS-2017-001) (TMO) | Upgrade terminal equipment at Holt 345kV to accept Holt to Holt new line
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P42:345:NPPD:BKR-CPR-3304 | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 100 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P42:345:NPPD:BKR-CPR-3304 | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 26 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P42:345:NPPD:BKR-RW-3302 | [7 empty] | Cooper Joe 345kV New Substation (DISIS-2017-001) | Build a new 345 kV substation at Cooper Joe. Tap the Cooper to St. Joe 345kV line 20 miles from St. Joe 345kV
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P42:345:NPPD:BKR-RW-3302 | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 6 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P42:345:NPPD:BKR-RW-3302 | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 60 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P42:345:NPPD:BKR-RW-3302 | [7 empty] | Holt 345kV Terminal Upgrades (DISIS-2017-001) (TMO) | Upgrade terminal equipment at Holt 345kV to accept Holt to Holt new line
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P42:345:NPPD:BKR-RW-3302 | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 100 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P42:345:NPPD:BKR-RW-3302 | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 26 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Thermal | 640068 B.SPRGS7 115 640091 BRULE 7 115 1 | 19WP, 20G, 20SP, 24SP, 24WP, 29SP | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z |  | 109 | 92.28 | 141.82 |  |  |  | Keystone to Sidney 345kV Ckt 2 (DISIS-2017-001) (NPPD) | Build approximately 80 miles of new 345kV line from Keystone to Sidney
09ALL | ERIS | Thermal | 640068 B.SPRGS7 115 640091 BRULE 7 115 1 | 19WP, 20G, 20SP, 24SP, 24WP, 29SP | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z |  | 109 | 92.28 | 141.82 |  |  |  | Keystone to Sidney 345kV Ckt 2 (DISIS-2017-001) (TSGT) | Review for potential impacts to TSGT facilities from Keystone to Sidney Ckt 2
09ALL | ERIS | Thermal | 640068 B.SPRGS7 115 640091 BRULE 7 115 1 | 19WP, 20G, 20SP, 24SP, 24WP, 29SP | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z |  | 109 | 92.28 | 141.82 |  |  |  | Sidney 345kV Terminal Upgrades (DISIS-2017-001) (BEPC) | Upgrade terminal equipment at Sidney 345kV to accept Keystone to Sidney Ckt 2
09ALL | ERIS | Thermal | 640091 BRULE 7 115 659801 OGALALA_-TS7 115 1 | 19WP, 20G, 20SP, 24SP, 24WP, 29SP | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z |  | 120 | 82.44 | 127.45 |  |  |  | Keystone to Sidney 345kV Ckt 2 (DISIS-2017-001) (NPPD) | Build approximately 80 miles of new 345kV line from Keystone to Sidney
09ALL | ERIS | Thermal | 640091 BRULE 7 115 659801 OGALALA_-TS7 115 1 | 19WP, 20G, 20SP, 24SP, 24WP, 29SP | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z |  | 120 | 82.44 | 127.45 |  |  |  | Keystone to Sidney 345kV Ckt 2 (DISIS-2017-001) (TSGT) | Review for potential impacts to TSGT facilities from Keystone to Sidney Ckt 2
09ALL | ERIS | Thermal | 640091 BRULE 7 115 659801 OGALALA_-TS7 115 1 | 19WP, 20G, 20SP, 24SP, 24WP, 29SP | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z |  | 120 | 82.44 | 127.45 |  |  |  | Sidney 345kV Terminal Upgrades (DISIS-2017-001) (BEPC) | Upgrade terminal equipment at Sidney 345kV to accept Keystone to Sidney Ckt 2
09ALL | ERIS | Thermal | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 | 19WP, 20G, 20SP, 24SP, 24WP, 29SP | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z |  | 320 | 116.14 | 129.8 |  |  |  | Keystone to Sidney 345kV Ckt 2 (DISIS-2017-001) (NPPD) | Build approximately 80 miles of new 345kV line from Keystone to Sidney
09ALL | ERIS | Thermal | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 | 19WP, 20G, 20SP, 24SP, 24WP, 29SP | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z |  | 320 | 116.14 | 129.8 |  |  |  | Keystone to Sidney 345kV Ckt 2 (DISIS-2017-001) (TSGT) | Review for potential impacts to TSGT facilities from Keystone to Sidney Ckt 2
09ALL | ERIS | Thermal | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 | 19WP, 20G, 20SP, 24SP, 24WP, 29SP | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z |  | 320 | 116.14 | 129.8 |  |  |  | Sidney 345kV Terminal Upgrades (DISIS-2017-001) (BEPC) | Upgrade terminal equipment at Sidney 345kV to accept Keystone to Sidney Ckt 2
09ALL | ERIS | Thermal | 640226 HOSKINS3 345 997393 HOSKN T4 115 1 | 19WP | P42:345:NPPD:BKR-HOS-3310 |  | 336 | 89.17 | 119.61 |  |  |  | Hoskins 345/230kV Transformer T4 Replacement (DISIS-2017-001) | Replace the existing Hoskins 345/230kV Transformer to achieve a minimum emergency rating of 406 MVA
09ALL | ERIS | Thermal | 640226 HOSKINS3 345 997396 HOSKN T4 115 1 | 20SP | P42:345:NPPD:BKR-HOS-3310 |  | 336 | 90.41 | 120.56 |  |  |  | Hoskins 345/230kV Transformer T4 Replacement (DISIS-2017-001) | Replace the existing Hoskins 345/230kV Transformer to achieve a minimum emergency rating of 406 MVA
09ALL | ERIS | Thermal | 640228 HOSKINS7 115 997393 HOSKN T4 115 1 | 19WP | P42:345:NPPD:BKR-HOS-3310 |  | 336 | 87.62 | 117.63 |  |  |  | Hoskins 345/230kV Transformer T4 Replacement (DISIS-2017-001) | Replace the existing Hoskins 345/230kV Transformer to achieve a minimum emergency rating of 406 MVA
09ALL | ERIS | Thermal | 640228 HOSKINS7 115 997396 HOSKN T4 115 1 | 20SP | P42:345:NPPD:BKR-HOS-3310 |  | 336 | 89.3 | 119 |  |  |  | Hoskins 345/230kV Transformer T4 Replacement (DISIS-2017-001) | Replace the existing Hoskins 345/230kV Transformer to achieve a minimum emergency rating of 406 MVA
09ALL | ERIS | Thermal | 640184 GENTLMN4 230 640302 OGALALA4 230 1 | 19WP, 20G | P42:345:NPPD:BKR-KEY-3310 |  | 320 | 86.14 | 104.72 |  |  |  | Keystone to Sidney 345kV Ckt 2 (DISIS-2017-001) (NPPD) | Build approximately 80 miles of new 345kV line from Keystone to Sidney
09ALL | ERIS | Thermal | 640184 GENTLMN4 230 640302 OGALALA4 230 1 | 19WP, 20G | P42:345:NPPD:BKR-KEY-3310 |  | 320 | 86.14 | 104.72 |  |  |  | Keystone to Sidney 345kV Ckt 2 (DISIS-2017-001) (TSGT) | Review for potential impacts to TSGT facilities from Keystone to Sidney Ckt 2
09ALL | ERIS | Thermal | 640184 GENTLMN4 230 640302 OGALALA4 230 1 | 19WP, 20G | P42:345:NPPD:BKR-KEY-3310 |  | 320 | 86.14 | 104.72 |  |  |  | Sidney 345kV Terminal Upgrades (DISIS-2017-001) (BEPC) | Upgrade terminal equipment at Sidney 345kV to accept Keystone to Sidney Ckt 2
09ALL | ERIS | Thermal | 523959 POTTER_CO 6 230 998123 WAUK 90343-A 230 1 | 24L | System Intact | 516 |  | 90.25 | 101.18 |  |  |  | Potter County 345/230kV Transformer Ckt 2 (DISIS-2017-001) | Install a new 345/230kV Transformer at Potter County
09ALL | ERIS | Thermal | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 20G, 24L | System Intact | 319 |  | 108.36 | 115.53 |  |  |  | Smokey Hils to Summit 230kV Rebuild (DISIS-2017-001) (MIDW) | Rebuild the existing Smokey Hills to Summit 230kV 16.1 mile line to achieve a minimum Light/Emergency rating of 375 MVA
09ALL | ERIS | Thermal | 560347 DIXONCO 230 640386 TWIN CH4 230 1 | 24L | System Intact | 320 |  | 84.79 | 100.16 |  |  |  | Dixon County to Twin Church 230kV Rebuild (DISIS-2017-001) | Rebuild the existing Dixon County to Twin Church 230kV 27.7 mile line to achieve a minimum light/emergency rating of 325 MVA
09ALL | ERIS | Thermal | 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1 | 24L | System Intact | 478 |  | 99.02 | 106.42 |  |  |  | Model Correction | 2021 ITP models show the Rate A for this line is 956 MVA, no mitigation is required
09ALL | ERIS | Thermal | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 20G | System Intact | 956 |  | 98.55 | 103.98 |  |  |  | MISO Facilities | Facilities are not under SPP tariff
09ALL | ERIS | Thermal | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 19WP, 20G, 20SP, 24L, 24WP, 29SP | System Intact | 926 |  | 135.06 | 144.9 |  |  |  | MISO Facilities | Facilities are not under SPP tariff
09ALL | ERIS | Thermal | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 20G | System Intact | 956 |  | 111.46 | 115.24 |  |  |  | MISO Facilities | Facilities are not under SPP tariff
09ALL | ERIS | Thermal | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | System Intact | 956 |  | 137.9 | 142.35 |  |  |  | MISO Facilities | Facilities are not under SPP tariff
09ALL | ERIS | Thermal | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | System Intact | 956 |  | 137.65 | 142.09 |  |  |  | MISO Facilities | Facilities are not under SPP tariff
09ALL | ERIS | Thermal | 640138 COOPER JOE 345 640139 COOPER 3 345 1 | 20G, 20SP | System Intact | 1195 |  | 95.78 | 108.34 |  |  |  | Cooper 345kV Terminal Upgrades (DISIS-2017-001) (NPPD) | Upgrade terminal equipment at Cooper 345 kV line to achieve a minimum Spring/Emergency rating of 1295 MVA
09ALL | ERIS | Thermal | 640138 COOPER JOE 345 640139 COOPER 3 345 1 | 20G, 20SP | System Intact | 1195 |  | 95.78 | 108.34 |  |  |  | Cooper Joe to Cooper 345kV Rebuild (DISIS-2017-001) (KCPL) | Rebuild Cooper Joe to Cooper 345 kV 22.2 miles line to achieve a minimum Spring/Emergency rating of 1295 MVA
09ALL | ERIS | Thermal | 640138 COOPER JOE 345 640139 COOPER 3 345 1 | 20G, 20SP | System Intact | 1195 |  | 95.78 | 108.34 |  |  |  | Cooper Joe to Cooper 345kV Rebuild (DISIS-2017-001) (OPPD) | Rebuild Cooper Joe to Cooper 345 kV 26.6 miles line to achieve a minimum Spring/Emergency rating of 1295 MVA
10ALL | ERIS | Non-Converge | None |  | None | [7 empty] | None | N/A
10ALL | ERIS | Thermal | None |  | None | [7 empty] | None | N/A
12ALL | ERIS | Non-Converge | None |  | None | [7 empty] | None | N/A
12ALL | ERIS | Thermal | None |  | None | [7 empty] | None | N/A
13ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P12:345:GMO-OPPD:S3458-HOLT | [7 empty] | Holt 345kV Terminal Upgrades (DISIS-2017-001) (TMO) | Upgrade terminal equipment at Holt 345kV to accept Holt to Holt new line
13ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P12:345:GMO-OPPD:S3458-HOLT | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 100 miles of new 345kV line from Holt to Hoyt
13ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P12:345:GMO-OPPD:S3458-HOLT | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 26 miles of new 345kV line from Holt to Hoyt
13ALL | ERIS | Thermal | 532772 STRANGR7 345 532775 87TH 7 345 1 | 19WP, 20G, 24WP | P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN |  | 1195 | 109 | 110.75 |  |  |  | Model Correction | With the Soldier Creek WF project to convert the Stranger Creek 345kV substation to Breaker and Half configuration, the new ratings on the Stranger Creek-87th Street 345kV line for winter will be: Rate A (MVA) = 1388 and Rate B (MVA) = 1515
14ALL | ERIS | Non-Converge | None |  | None | [7 empty] | None | N/A
14ALL | ERIS | Thermal | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 19WP, 24WP | P12:345:AEPW-WFEC:VALIANT7:HUGO7 |  | 287 | 75.98 | 105.87 |  |  |  | Valiant 138kV Terminal Upgrades (DISIS-2017-001) (AEPW) | Upgrade terminal equipment at Valiant to Hugo PP4 138kV to achieve a minimum winter/emergency rating of 305 MVA
14ALL | ERIS | Thermal | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 19WP, 24WP | P12:345:AEPW-WFEC:VALIANT7:HUGO7 |  | 287 | 75.98 | 105.87 |  |  |  | Valiant 138kV Terminal Upgrades (DISIS-2017-001) (WFEC) | Upgrade terminal equipment at Valiant to Hugo PP4 138kV to achieve a minimum winter/emergency rating of 305 MVA
15ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON | [7 empty] | Ft. Thompson 345kV Terminal Upgrades (DISIS-2017-001) (WAPA) | Upgrade terminal equipment at Ft. Thompson 345kV to accept G16-017 Tap to Ft. Thompson Ckt 2
15ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON | [7 empty] | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC) | Build approximately 30 miles of new 345kV line from G16-017 Tap to Ft. Thompson
15ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON | [7 empty] | Modify Contingency | Update contingency to remove line outage out of 659424
15ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992) | [7 empty] | Ft. Thompson 345kV Terminal Upgrades (DISIS-2017-001) (WAPA) | Upgrade terminal equipment at Ft. Thompson 345kV to accept G16-017 Tap to Ft. Thompson Ckt 2
15ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992) | [7 empty] | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC) | Build approximately 30 miles of new 345kV line from G16-017 Tap to Ft. Thompson
15ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992) | [7 empty] | Modify Contingency | Update contingency to remove line outage out of 659424
15ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996) | [7 empty] | Ft. Thompson 345kV Terminal Upgrades (DISIS-2017-001) (WAPA) | Upgrade terminal equipment at Ft. Thompson 345kV to accept G16-017 Tap to Ft. Thompson Ckt 2
15ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996) | [7 empty] | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC) | Build approximately 30 miles of new 345kV line from G16-017 Tap to Ft. Thompson
15ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996) | [7 empty] | Modify Contingency | Update contingency to remove line outage out of 659424
15ALL | ERIS | Thermal | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 20G, 20SP, 24L, 24SP, 29SP | P23:345:XEL:396 BKR SPK |  | 720 | 107.88 | 125.43 |  |  |  | Model Correction | 2021 ITP models show the Rate A for this line is 956 MVA, no mitigation is required
15ALL | ERIS | Thermal | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 20G, 20SP, 24L, 24SP, 29SP | P23:345:XEL:396 BKR SPK |  | 720 | 107.71 | 125.22 |  |  |  | Model Correction | 2021 ITP models show the Rate A for this line is 956 MVA, no mitigation is required
15ALL | ERIS | Thermal | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 20G | System Intact | 926 |  | 100.49 | 103.44 |  |  |  | Model Correction | 2021 ITP models show the Rate A for this line is 1083 MVA, no mitigation is required
16ALL | ERIS | Non-Converge | None |  | None | [7 empty] | None | N/A
16ALL | ERIS | Thermal | 652468 HEBRON 4 230 661053 MANDAN 4 230 1 | 20SP, 24SP, 29SP | P12:230:UMZ:# 5569 #: IN . PROPER N-1 (LINE) FOR 659351-652497-1 |  | 264 | 84.53 | 113.27 |  |  |  | Model Correction | 2021 ITP models show the Rate A for this line is 352 MVA, no mitigation is required
16ALL | ERIS | Thermal | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P23:345:UMZB:# 3708 #: JDM IN ND. BREAKER FAULT JUDSON (696) |  | 506 | 86.68 | 140.65 |  |  |  | Neset to Tioga 230kV Rebuild (DISIS-2017-001) (BEPC) | Rebuild the existing Neset to Tioga 230kV 1.0 mile line to achieve a minimum Summer/Emergency rating of 725 MVA
16ALL | ERIS | Thermal | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P23:345:UMZB:# 3708 #: JDM IN ND. BREAKER FAULT JUDSON (696) |  | 506 | 86.68 | 140.65 |  |  |  | Tioga 230kV Terminal Upgrades (DISIS-2017-001) (MDU) | Upgrade terminal equipment at Tioga 230kV to achieve a minimum Summer/Emergency rating of 725 MVA
16ALL | ERIS | Thermal | 659120 BROADLND-BE3 345 997093 BD KU2A 230 1 | 29SP | System Intact | 400 |  | 98.18 | 108.83 |  |  |  | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | Replace the existing Broadland 345/230kV Transformer to achieve a minimum Summer/Normal rating of 471 MVA
16ALL | ERIS | Thermal | 659120 BROADLND-BE3 345 997094 BD KU2A 230 1 | 24SP | System Intact | 400 |  | 102.33 | 112.41 |  |  |  | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | Replace the existing Broadland 345/230kV Transformer to achieve a minimum Summer/Normal rating of 471 MVA
16ALL | ERIS | Thermal | 659120 BROADLND-BE3 345 997103 BD KU2A 230 1 | 20SP | System Intact | 400 |  | 99.51 | 109.59 |  |  |  | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | Replace the existing Broadland 345/230kV Transformer to achieve a minimum Summer/Normal rating of 471 MVA
16ALL | ERIS | Thermal | 659205 BROADLND-BE4 230 997093 BD KU2A 230 1 | 29SP | System Intact | 400 |  | 101.01 | 113.27 |  |  |  | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | Replace the existing Broadland 345/230kV Transformer to achieve a minimum Summer/Normal rating of 471 MVA
16ALL | ERIS | Thermal | 659205 BROADLND-BE4 230 997094 BD KU2A 230 1 | 24SP | System Intact | 400 |  | 105.68 | 117.6 |  |  |  | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | Replace the existing Broadland 345/230kV Transformer to achieve a minimum Summer/Normal rating of 471 MVA
16ALL | ERIS | Thermal | 659205 BROADLND-BE4 230 997103 BD KU2A 230 1 | 20SP | System Intact | 400 |  | 102.51 | 114.17 |  |  |  | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | Replace the existing Broadland 345/230kV Transformer to achieve a minimum Summer/Normal rating of 471 MVA
16ALL | ERIS | Thermal | 659205 BROADLND-BE4 230 997109 BD KU2A 230 1 | 20G | System Intact | 400 |  | 87.36 | 100.16 |  |  |  | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | Replace the existing Broadland 345/230kV Transformer to achieve a minimum Summer/Normal rating of 471 MVA
16ALL | ERIS | Thermal | 661091 NAPOLEON SW4 230 661094 WISHEK 4 230 1 | 20SP, 24SP, 29SP | System Intact | 343 |  | 99.24 | 118.58 |  |  |  | Napoleon SW to Wishek 230kV Rebuild (DISIS-2017-001) | Rebuild the existing Napoleon SW to Wishek 230kV 24.89 mile line to achieve a minimum Summer/Normal rating of 407 MVA
16ALL | ERIS | Thermal | 661093 MERRCRT4 230 661094 WISHEK 4 230 1 | 20SP, 24SP, 29SP | System Intact | 343 |  | 97.47 | 116.79 |  |  |  | MERRCRT4 to Wishek 230kV Rebuild (DISIS-2017-001) | Rebuild the existing MERRCRT4 to Wishek 230kV 29.3 mile line to achieve a minimum Summer/Normal rating of 401 MVA
17ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP) | [7 empty] | G17-014 Tap to Philip Tap 230kV New Line (DISIS-2017-001) | Convert existing Philip Tap to a ring bus substation and build approximately 6 miles of new 230kV from new substation to G17-014 Tap creating a double circuit 230kV line.
17ALL | ERIS | Thermal | 588594 G17-014-TAP 230 659188 PHILIP_T-BE4 230 1 | 19WP, 20G, 24WP | P12:230:UMZ:# 5569 #: IN . PROPER N-1 (LINE) FOR 659351-652497-1 |  | 342 | 70.75 | 111.86 |  |  |  | Model Correction | 2021 ITP models show the Rate A for this line is 461 MVA, no mitigation is required
17ALL | ERIS | Thermal | 588594 G17-014-TAP 230 659188 PHILIP_T-BE4 230 1 | 20SP, 24SP | P12:230:UMZ:# 5569 #: IN . PROPER N-1 (LINE) FOR 659351-652497-1 |  | 342 | 70.75 | 111.86 |  |  |  | G17-014 Tap to Philip Tap 230kV New Line (DISIS-2017-001) | 2021 ITP models show the Rate A for this line is 461 MVA, no mitigation is required
17ALL | ERIS | Thermal | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 | 19WP, 20G, 20SP, 24SP, 24WP, 29SP | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z |  | 320 | 93.39 | 121.79 |  |  |  | Keystone to Sidney 345kV Ckt 2 (DISIS-2017-001) (NPPD) | Build approximately 80 miles of new 345kV line from Keystone to Sidney
17ALL | ERIS | Thermal | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 | 19WP, 20G, 20SP, 24SP, 24WP, 29SP | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z |  | 320 | 93.39 | 121.79 |  |  |  | Keystone to Sidney 345kV Ckt 2 (DISIS-2017-001) (TSGT) | Review for potential impacts to TSGT facilities from Keystone to Sidney Ckt 2
17ALL | ERIS | Thermal | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 | 19WP, 20G, 20SP, 24SP, 24WP, 29SP | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z |  | 320 | 93.39 | 121.79 |  |  |  | Sidney 345kV Terminal Upgrades (DISIS-2017-001) (BEPC) | Upgrade terminal equipment at Sidney 345kV to accept Keystone to Sidney Ckt 2
17ALL | ERIS | Thermal | 640184 GENTLMN4 230 640302 OGALALA4 230 1 | 20G | P42:345:NPPD:BKR-KEY-3310 |  | 320 | 73.49 | 102.46 |  |  |  | Keystone to Sidney 345kV Ckt 2 (DISIS-2017-001) (NPPD) | Build approximately 80 miles of new 345kV line from Keystone to Sidney
17ALL | ERIS | Thermal | 640184 GENTLMN4 230 640302 OGALALA4 230 1 | 20G | P42:345:NPPD:BKR-KEY-3310 |  | 320 | 73.49 | 102.46 |  |  |  | Keystone to Sidney 345kV Ckt 2 (DISIS-2017-001) (TSGT) | Review for potential impacts to TSGT facilities from Keystone to Sidney Ckt 2
17ALL | ERIS | Thermal | 640184 GENTLMN4 230 640302 OGALALA4 230 1 | 20G | P42:345:NPPD:BKR-KEY-3310 |  | 320 | 73.49 | 102.46 |  |  |  | Sidney 345kV Terminal Upgrades (DISIS-2017-001) (BEPC) | Upgrade terminal equipment at Sidney 345kV to accept Keystone to Sidney Ckt 2
17ALL | ERIS | Thermal | 588595 G17-014XFMR2 34.5 588590 GEN-2017-014 230 1 | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | System Intact | 160 |  |  | 102.18 |  |  |  | Interconnection Facilities | Project Equipment will be built to enure no thermal overloads on collector system, no mitigation required
17ALL | ERIS | Thermal | 588595 G17-014XFMR2 34.5 588590 GEN-2017-014 230 1 | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | System Intact | 160 |  |  | 102.18 |  |  |  | Interconnection Facilities | Project Equipment will be built to enure no thermal overloads on collector system, no mitigation required
17ALL | ERIS | Thermal | 588595 G17-014XFMR2 34.5 588590 GEN-2017-014 230 1 | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | System Intact | 160 |  |  | 102.18 |  |  |  | Interconnection Facilities | Project Equipment will be built to enure no thermal overloads on collector system, no mitigation required
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P12:345:AEPW:LYDIA7:VALIANT7 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P12:345:AEPW:LYDIA7:VALIANT7 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P12:345:AEPW:PITTSB-7:VALIANT7 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P12:345:AEPW:PITTSB-7:VALIANT7 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P12:345:GMO-OPPD:S3458-HOLT | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P12:345:GMO-OPPD:S3458-HOLT | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P12:345:GRDA:GRDA1 -TONECE | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P12:345:GRDA:GRDA1 -TONECE | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P12:345:OKGE:BKRBKR295 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P12:345:OKGE:BKRBKR295 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P12:345:OPPD:S3458-COOPER | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P12:345:OPPD:S3458-COOPER | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P12:345:SUNC:MINGO-SETAB::531451-531465(1) | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P12:345:SUNC:MINGO-SETAB::531451-531465(1) | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1) | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1) | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 20SP, 24WP | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1) | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 20SP, 24WP | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1) | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P12:345:WERE:BENT-WICH_345:: | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P12:345:WERE:BENT-WICH_345:: | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 20SP | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 20SP | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P13:230-345:MIDW:POST ROCK | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P13:230-345:MIDW:POST ROCK | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P14:345:GMO-OPPD:S3458 REACTOR | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P14:345:GMO-OPPD:S3458 REACTOR | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 20SP | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 20SP | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P22:345:GMO-OPPD:S3458-HOLT | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P22:345:GMO-OPPD:S3458-HOLT | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:AEPW:NW TEXARKANA CB 11810 NBTB | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:AEPW:NW TEXARKANA CB 11810 NBTB | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:AEPW:NW TEXARKANA CB 11820 NBTB | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:AEPW:NW TEXARKANA CB 11820 NBTB | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:AEPW:PITTSBURG CB 3425A NBTB | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:AEPW:PITTSBURG CB 3425A NBTB | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:AEPW:PITTSBURG CB 3429A NBTB | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:AEPW:PITTSBURG CB 3429A NBTB | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:AEPW:VALLIANT CB 3409A NBTB | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:AEPW:VALLIANT CB 3409A NBTB | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:AEPW:VALLIANT CB 3417A NBTB | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:AEPW:VALLIANT CB 3417A NBTB | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:AEPW:VALLIANT CB 3421A NBTB | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:AEPW:VALLIANT CB 3421A NBTB | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:AEPW:WELSH CB 11590 NBTB | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:AEPW:WELSH CB 11590 NBTB | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:AEPW:WELSH CB 11990 NBTB | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:AEPW:WELSH CB 11990 NBTB | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:GRDA:GRDA CB9580 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:GRDA:GRDA CB9580 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:GRDA:TONNECE CB90 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:GRDA:TONNECE CB90 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:GRDA:TONNECE CB9580 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:GRDA:TONNECE CB9580 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:KCPL-GMO:STILWELL_R2-5::STILWELL-PECULIAR-LACYGNE | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:KCPL-GMO:STILWELL_R2-5::STILWELL-PECULIAR-LACYGNE | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 20SP, 24WP | P23:345:MEC:ATCHISON CO 903 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 20SP, 24WP | P23:345:MEC:ATCHISON CO 903 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:OPPD:S3456-S3458&CB | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:OPPD:S3456-S3458&CB | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:OPPD:S3458-COOPER | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:OPPD:S3458-COOPER | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:OPPD:S3458-HOLT | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:OPPD:S3458-HOLT | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:SUNC:HLC_BRK188 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:SUNC:HLC_BRK188 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:SUNC:HLC_BRK282 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:SUNC:HLC_BRK282 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:SUNC:HLC_BRK382 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:SUNC:HLC_BRK382 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:SUNC:MO_BRK182 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:SUNC:MO_BRK182 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 20SP, 24WP | P23:345:SUNC:MO_BRK188 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 20SP, 24WP | P23:345:SUNC:MO_BRK188 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:SUNC:MO_BRK382 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:SUNC:MO_BRK382 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 20SP, 24WP | P23:345:SUNC:MO_BRK388 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 20SP, 24WP | P23:345:SUNC:MO_BRK388 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:SUNC:SB_BRK482 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:SUNC:SB_BRK482 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:SUNC:SB_BRK488 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:SUNC:SB_BRK488 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:SUNC:SB_BRK582 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:SUNC:SB_BRK582 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 20SP, 24WP | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 20SP, 24WP | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 20SP, 24WP | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 20SP, 24WP | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:WERE:BENT_345-110:: | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:WERE:BENT_345-110:: | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:WERE:BENT_345-50:: | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:WERE:BENT_345-50:: | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 20SP, 24WP | P23:345:WERE:HOYT_345_BKRS:: | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 20SP, 24WP | P23:345:WERE:HOYT_345_BKRS:: | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:WERE:LATH_BKRS:: | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:WERE:LATH_BKRS:: | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:WERE:STRA_345-99:: | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:WERE:STRA_345-99:: | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:WERE:WICH_345-50:: | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P23:345:WERE:WICH_345-50:: | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P24:345:GRDA:GRDA CB400T | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P24:345:GRDA:GRDA CB400T | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P41:345:OKGE:SB_MUGE7385 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P41:345:OKGE:SB_MUGE7385 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P42:345:GRDA:TONNECE CB9580 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P42:345:GRDA:TONNECE CB9580 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P42:345:MEC-OPPD:S3456-S3458&CBL | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P42:345:MEC-OPPD:S3456-S3458&CBL | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P42:345:MIDW:SPEARVILLE-POSTROCK-SBF7 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P42:345:MIDW:SPEARVILLE-POSTROCK-SBF7 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P42:345:MIDW:SPEARVILLE-POSTROCK-SBH9 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P42:345:MIDW:SPEARVILLE-POSTROCK-SBH9 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P42:345:NPPD:BKR-AXT-3308 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P42:345:NPPD:BKR-AXT-3308 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P42:345:NPPD:BKR-CPR-3304 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P42:345:NPPD:BKR-CPR-3304 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P42:345:NPPD:BKR-GGS-3322 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P42:345:NPPD:BKR-GGS-3322 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 20SP, 24WP | P42:345:NPPD:BKR-RW-3302 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 20SP, 24WP | P42:345:NPPD:BKR-RW-3302 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P42:345:OKGE:SB_FTTH7385 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P42:345:OKGE:SB_FTTH7385 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P42:345:OKGE:SB_FTTH7386 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P42:345:OKGE:SB_FTTH7386 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P43:345:AEPW:NW TEXARKANA CB 11810 NBTB+FAULT | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P43:345:AEPW:NW TEXARKANA CB 11810 NBTB+FAULT | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P43:345:AEPW:NW TEXARKANA CB 11820 NBTB+FAULT | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P43:345:AEPW:NW TEXARKANA CB 11820 NBTB+FAULT | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P43:345:GRDA:GRDA CB9580 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P43:345:GRDA:GRDA CB9580 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P43:345:GRDA:TONNECE CB90 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P43:345:GRDA:TONNECE CB90 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P44:345:OPPD:S3458-HOL&R1 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P44:345:OPPD:S3458-HOL&R1 | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P45:345:OPPD:S3456-S3458&CBL | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P45:345:OPPD:S3456-S3458&CBL | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 20SP, 24WP | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 20SP, 24WP | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 20SP, 24WP | P45:345:UMZW:# 1328 #: GI IN NE. | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 20SP, 24WP | P45:345:UMZW:# 1328 #: GI IN NE. | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P46:345:GRDA:GRDA CB400T | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P46:345:GRDA:GRDA CB400T | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P55:161-345:KCPL:STILWELL_BUS_22_345:: | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge | 24WP | P55:161-345:KCPL:STILWELL_BUS_22_345:: | [7 empty] | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek
00NR | NRIS | Thermal | 589024 G17-064-TAP 230 640404 WAYSIDE4 230 1 | 24SP, 29SP | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1 |  | 341 | 80.77 | 110.77 |  |  |  | G17-064 Tap to Wayside 230kV Rebuild (DISIS-2017-001) (WAPA) | Rebuild the existing G17-064 Tap to Wayside 230kV 38.05 mile line to achieve a minimum summer/emergency rating of 377 MVA
00NR | NRIS | Thermal | 589024 G17-064-TAP 230 640404 WAYSIDE4 230 1 | 24SP, 29SP | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1 |  | 341 | 80.77 | 110.77 |  |  |  | Wayside 230kV Terminal Upgrades (DISIS-2017-001) (NPPD) | Upgrade terminal equipment at Wayside 230kV to accept Wayside to Shannon new line
00NR | NRIS | Thermal | 589024 G17-064-TAP 230 640404 WAYSIDE4 230 1 | 24SP, 29SP | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1 |  | 341 | 80.77 | 110.77 |  |  |  | G17-064 Tap to Wayside 230kV Rebuild (DISIS-2017-001) (WAPA) | Rebuild the existing G17-064 Tap to Wayside 230kV 38.05 mile line to achieve a minimum summer/emergency rating of 377 MVA
00NR | NRIS | Thermal | 589024 G17-064-TAP 230 640404 WAYSIDE4 230 1 | 24SP, 29SP | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1 |  | 341 | 80.77 | 110.77 |  |  |  | Wayside to Shannon 230kV New Line (DISIS-2017-001) (BEPC) | Build approximately 54 miles of new 345kV line from Wayside to Shannon and install a 230/115kV transformer
00NR | NRIS | Thermal | 640405 WAYSIDE7 115 997300 WAYSIDE T1 115 1 | 20SP | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z |  | 187 | 73.24 | 101.82 |  |  |  | Wayside 230kV Terminal Upgrades (DISIS-2017-001) (NPPD) | Upgrade terminal equipment at Wayside 230kV to accept Wayside to Shannon new line
00NR | NRIS | Thermal | 640404 WAYSIDE4 230 997300 WAYSIDE T1 115 1 | 20SP | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z |  | 187 | 73.2 | 103.59 |  |  |  | Wayside 230kV Terminal Upgrades (DISIS-2017-001) (NPPD) | Upgrade terminal equipment at Wayside 230kV to accept Wayside to Shannon new line
00NR | NRIS | Thermal | 640109 CHADRON7 115 640405 WAYSIDE7 115 1 | 20SP, 24SP, 29SP | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z |  | 160 | 82.5 | 115.47 |  |  |  | Wayside 230kV Terminal Upgrades (DISIS-2017-001) (NPPD) | Upgrade terminal equipment at Wayside 230kV to accept Wayside to Shannon new line
00NR | NRIS | Thermal | 640405 WAYSIDE7 115 997300 WAYSIDE T1 115 1 | 20SP | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z |  | 187 | 73.24 | 101.82 |  |  |  | Wayside to Shannon 230kV New Line (DISIS-2017-001) (BEPC) | Build approximately 54 miles of new 345kV line from Wayside to Shannon and install a 230/115kV transformer
00NR | NRIS | Thermal | 640404 WAYSIDE4 230 997300 WAYSIDE T1 115 1 | 20SP | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z |  | 187 | 73.2 | 103.59 |  |  |  | Wayside to Shannon 230kV New Line (DISIS-2017-001) (BEPC) | Build approximately 54 miles of new 345kV line from Wayside to Shannon and install a 230/115kV transformer
00NR | NRIS | Thermal | 640109 CHADRON7 115 640405 WAYSIDE7 115 1 | 20SP, 24SP, 29SP | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z |  | 160 | 82.5 | 115.47 |  |  |  | Wayside to Shannon 230kV New Line (DISIS-2017-001) (BEPC) | Build approximately 54 miles of new 345kV line from Wayside to Shannon and install a 230/115kV transformer
00NR | NRIS | Thermal | 652530 WATERTN4 230 652582 APPLEDORN 4 230 1 | 20SP, 29SP | P12:230:UMZW:# 137 #: GF IN MN. GF-FB LINE FAULT |  | 352 | 100.06 | 103.14 |  |  |  | Appledorn to Watertown 230kV Rebuild (DISIS-2017-001) | Rebuild the existing Watertown to Appledorn 230kV 55.3 mile line to achieve a minimum summer/emergency rating of 363 MVA
00NR | NRIS | Thermal | 635000 CBLUFFS3 345 645456 S3456 3 345 1 | 19WP, 24WP | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 |  | 956 | 106.23 | 108.2 |  |  |  | Sarpy Co. S3456 to Council Bluffs 345kV Rebuild (DISIS-2017-001) (OPPD) | Rebuild the existing Sarpy Co S3456 to Council Bluffs 345kV 5.63 mile line section to achieve a minimum winter/emergency rating of 1022 MVA
00NR | NRIS | Thermal | 635000 CBLUFFS3 345 645456 S3456 3 345 1 | 19WP, 24WP | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 |  | 956 | 106.23 | 108.2 |  |  |  | Sarpy Co. S3456 to Council Bluffs 345kV Rebuild (DISIS-2017-001) (MEC) | Rebuild the existing Sarpy Co S3456 to Council Bluffs 345kV 3.34 mile line to achieve a minimum winter/emergency rating of 1022 MVA
00NR | NRIS | Thermal | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 | 19WP, 24WP | P12:345:OPPD:S3458-COOPER |  | 956 | 107.81 | 115.84 |  |  |  | Mark Moore to Monolith 345kV Rebuild (DISIS-2017-001) | Rebuild the existing Mark Moore to Monolith 345kV .75 mile line to achieve a minimum winter/normal rating of 1108 MVA
00NR | NRIS | Thermal | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 24SP | P12:345:UMZ:# 6230 #: OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 OR 652832-652532-Z |  | 320 | 94.92 | 104.44 |  |  |  | Fort Randall to Lake Platte 230kV Rebuild (DISIS-2017-001) (WAPA) | Rebuild the existing Fort Randall to Lake Platte 43.34 mile line to achieve a minimum summer/emergency rating of 335 MVA
00NR | NRIS | Thermal | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 24SP, 29SP | P12:345:UMZ:# 6230 #: OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 OR 652832-652532-Z |  | 320 | 98.74 | 108.4 |  |  |  | Fort Thompson to Fort Randall 230kV Rebuild (DISIS-2017-001) | Rebuild the existing Fort Thompson to Fort Randall 87.32 mile line to achieve a minimum summer/emergency rating of 348 MVA
00NR | NRIS | Thermal | 532796 WICHITA7 345 997931 WICH TX-12 138 1 | 20SP | P12:345:WERE:BENT-WICH_345:: |  | 430 | 98.22 | 109.58 |  |  |  | Wichita 345/138kV Tansformer Ckt 3 (DISIS-2017-001) | Install a new 345/138kV Transformer at Wichita
00NR | NRIS | Thermal | 533673 ALTOO E2 69.0 533700 NEODJCT2 69.0 1 | 19WP, 20SP, 24SP, 24WP, 29SP | P13:069-138:WERE:MONT_TX-1_138-69:: |  | 36 | 96.68 | 113.17 |  |  |  | Altoona 69kV Terminal Upgrades (DISIS-2017-001) | Upgrade terminal equipment at Altoona to Neodesha Jct. to achieve a minimum summer/emergency rating of 41 MVA
00NR | NRIS | Thermal | 533673 ALTOO E2 69.0 533700 NEODJCT2 69.0 1 | 19WP, 20SP, 24SP, 24WP, 29SP | P13:069-138:WERE:MONT_TX-1_138-69:: |  | 36 | 96.68 | 113.17 |  |  |  | Neodesha Jct. 69kV Terminal Upgrades (DISIS-2017-001) | Upgrade terminal equipment at Neodesha Jct. to achieve a minimum summer/emergency rating of 41 MVA
00NR | NRIS | Thermal | 652479 MARTIN 7 115 652579 WANBLEE 7 115 1 | 20SP, 24SP, 29SP | P13:115-230:NPPD:WAYSIDE4:T1 |  | 120 | 88.4 | 107.39 |  |  |  | Martin to Wanblee 115kV Rebuild (DISIS-2017-001) | Rebuild the existing Martin to Wanblee 115kV 20.86 mile line to achieve a minimum summer/emergency rating of 129 MVA
00NR | NRIS | Thermal | 652482 MISSION7 115 659153 VETAL_TP-RM7 115 1 | 20SP | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F). |  | 88 | 84.4 | 103.95 |  |  |  | Mission to Vetal Tap 115kV Rebuild (DISIS-2017-001) (WAPA) | Rebuild the existing Mission to Vetal Tap 115kV 37.87 mile line to achieve a minimum summer/normal rating of 92 MVA
00NR | NRIS | Thermal | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 | 20SP | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F). |  | 88 | 88.06 | 102.93 |  |  |  | Martin to Vetal Tap 115kV Rebuild (DISIS-2017-001) (WAPA) | Rebuild the existing Martin to Vetal Tap 115kV 16.67 mile line to achieve a minimum summer/emergency rating of 95 MVA
00NR | NRIS | Thermal | 652482 MISSION7 115 659153 VETAL_TP-RM7 115 1 | 20SP | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F). |  | 88 | 84.4 | 103.95 |  |  |  | Vetal Tap Terminal Upgrades for Mission Rebuild (DISIS-2017-001) (BEPC) | Upgrade terminal equipment at Vetal Tap 115kV 37.87 mile line to achieve a minimum summer/normal rating of 92 MVA
00NR | NRIS | Thermal | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 | 20SP | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F). |  | 88 | 88.06 | 102.93 |  |  |  | Vetal Tap Terminal Upgrades for Martin Rebuild (DISIS-2017-001) (BEPC) | Upgrade terminal equipment at Vetal Tap 115kV to achieve a minimum summer/emergency rating of 95 MVA
00NR | NRIS | Thermal | 640338 SCOTBLF7 115 640397 VICTRYH7 115 1 | 20SP, 24SP | P13:230-345:NPPD:STEGALL3:KV3A |  | 155 | 82.55 | 114.21 |  |  |  | Scottsbluff to Victory Hill 115kV Rebuild (DISIS-2017-001) | Rebuild the existing Scottsbluff to Victory Hill 115kV 8.09 mile line to achieve a minimum summer/emergency rating of 177 MVA
00NR | NRIS | Thermal | 659300 STANTN.T-BE7 115 661008 BEULAH 7 115 1 | 19WP, 24SP, 24WP, 29SP | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 |  | 132 | 118.58 | 128.88 |  |  |  | Stanton to Beulah 115kV Rebuild (DISIS-2017-001) (WAPA) | Rebuild the existing Stanton to Beulah 115kV 13.41 mile line to achieve a minimum winter/emergency rating of 171 MVA
00NR | NRIS | Thermal | 659300 STANTN.T-BE7 115 661008 BEULAH 7 115 1 | 19WP, 24SP, 24WP, 29SP | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 |  | 132 | 118.58 | 128.88 |  |  |  | Stanton 115kV Terminal Upgrades (DISIS-2017-001) (BEPC) | Upgrade terminal equipment at Stanton 115kV to achieve a minimum winter/emergency rating of 171 MVA
00NR | NRIS | Thermal | 659300 STANTN.T-BE7 115 661008 BEULAH 7 115 1 | 19WP, 24SP, 24WP, 29SP | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 |  | 132 | 118.58 | 128.88 |  |  |  | Beulah 115kV Terminal Upgrades (DISIS-2017-001) (MDU) | Upgrade terminal equipment at Beulah 115kV to achieve a minimum winter/emergency rating of 171 MVA
00NR | NRIS | Thermal | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 24SP | P23:345:AEPW:WELSH CB 11990 NBTB |  | 970 | 92.46 | 100.14 |  |  |  | Welsh to Wilkes 345kV Rebuild (DISIS-2017-001) | Rebuild the existing Welsh to Wilkes 345kV 23.74 mile line to achieve a minimum summer/emergency rating of 972 MVA
00NR | NRIS | Thermal | 533040 EVANS N4 138 997931 WICH TX-12 138 1 | 20SP | P23:345:WERE:BENT_345-110:: |  | 430 | 96.9 | 107.89 |  |  |  | Wichita 345/138kV Tansformer Ckt 3 (DISIS-2017-001) | Install a new 345/138kV Transformer at Wichita
00NR | NRIS | Thermal | 533040 EVANS N4 138 997926 WICH TX-12 138 1 | 29SP | P23:345:WERE:BENT_345-110:: |  | 430 | 90.54 | 103.94 |  |  |  | Wichita 345/138kV Tansformer Ckt 3 (DISIS-2017-001) | Install a new 345/138kV Transformer at Wichita
00NR | NRIS | Thermal | 533040 EVANS N4 138 533054 MAIZE 4 138 1 | 29SP | P23:345:WERE:BENT_345-110:: |  | 382 | 88.32 | 103.63 |  |  |  | Gordon Evans to Maize 138kV Rebuild (DISIS-2017-001) | Rebuild the existing Gordon Evans to Maize 138kV 4.9 mile line to achieve a minimum summer/emergency rating of 387 MVA
00NR | NRIS | Thermal | 532796 WICHITA7 345 997927 WICH TX-12 138 1 | 24SP | P23:345:WERE:BENT_345-110:: |  | 430 | 88.46 | 101.69 |  |  |  | Wichita 345/138kV Tansformer Ckt 3 (DISIS-2017-001) | Install a new 345/138kV Transformer at Wichita
00NR | NRIS | Thermal | 532796 WICHITA7 345 997926 WICH TX-12 138 1 | 29SP | P23:345:WERE:BENT_345-110:: |  | 430 | 90.98 | 104.61 |  |  |  | Wichita 345/138kV Tansformer Ckt 3 (DISIS-2017-001) | Install a new 345/138kV Transformer at Wichita
00NR | NRIS | Thermal | 532986 BENTON 4 138 997902 BENT TX-2 138 1 | 20SP | P23:345:WERE:BENT_345-50:: |  | 440 | 110.61 | 110.63 |  |  |  | Benton 345/138kV Transformer Ckt 3 (DISIS-2017-001) | Install a new 345/138kV Transformer at Benton
00NR | NRIS | Thermal | 532986 BENTON 4 138 997898 BENT TX-2 138 1 | 24SP | P23:345:WERE:BENT_345-50:: |  | 440 | 108.41 | 110.93 |  |  |  | Benton 345/138kV Transformer Ckt 3 (DISIS-2017-001) | Install a new 345/138kV Transformer at Benton
00NR | NRIS | Thermal | 532986 BENTON 4 138 997897 BENT TX-2 138 1 | 29SP | P23:345:WERE:BENT_345-50:: |  | 440 | 116.82 | 119.63 |  |  |  | Benton 345/138kV Transformer Ckt 3 (DISIS-2017-001) | Install a new 345/138kV Transformer at Benton
00NR | NRIS | Thermal | 532791 BENTON 7 345 997902 BENT TX-2 138 1 | 20SP | P23:345:WERE:BENT_345-50:: |  | 440 | 115.54 | 115.34 |  |  |  | Benton 345/138kV Transformer Ckt 3 (DISIS-2017-001) | Install a new 345/138kV Transformer at Benton
00NR | NRIS | Thermal | 532791 BENTON 7 345 997898 BENT TX-2 138 1 | 24SP | P23:345:WERE:BENT_345-50:: |  | 440 | 111.05 | 113.66 |  |  |  | Benton 345/138kV Transformer Ckt 3 (DISIS-2017-001) | Install a new 345/138kV Transformer at Benton
00NR | NRIS | Thermal | 532791 BENTON 7 345 997897 BENT TX-2 138 1 | 29SP | P23:345:WERE:BENT_345-50:: |  | 440 | 115.68 | 118.52 |  |  |  | Benton 345/138kV Transformer Ckt 3 (DISIS-2017-001) | Install a new 345/138kV Transformer at Benton
00NR | NRIS | Thermal | 533040 EVANS N4 138 997932 WICH TX-11 138 1 | 20SP | P23:345:WERE:WICH_345-80:: |  | 430 | 96.61 | 102.35 |  |  |  | Wichita 345/138kV Tansformer Ckt 3 (DISIS-2017-001) | Install a new 345/138kV Transformer at Wichita
00NR | NRIS | Thermal | 532796 WICHITA7 345 997932 WICH TX-11 138 1 | 20SP | P23:345:WERE:WICH_345-80:: |  | 430 | 98.35 | 104.44 |  |  |  | Wichita 345/138kV Tansformer Ckt 3 (DISIS-2017-001) | Install a new 345/138kV Transformer at Wichita

## Assigned Upgrade Costs
Gen Number | Group | Upgrade ID | Service Type | Upgrade Name | Upgrade Type | Upgrade Details | Allocated Cost | % Allocated | Total Upgrade Cost
GEN-2016-037 | 07 - Southwestern Oklahoma | 132903 | ERIS | Chisholm - Gracemont 345 kV GEN-2016-037 Interconnection (Non-Shared NU) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-037 (300 MW/Wind), into the Point of Interconnection (POI) at Chisholm - Gracemont 345 kV. | 20639740 | 100% | 20639740
GEN-2016-037 | 07 - Southwestern Oklahoma | 143127 | ERIS | Chisholm - Gracemont 345 kV GEN-2016-037 Interconnection (Non-Shared NU) (OKGE) | Interconnection | Potential interconnection impacts from the following generating facility, GEN-2016-037 (300 MW/Wind), into the Point of Interconnection (POI) at Chisholm - Gracemont 345 kV. | 15000 | 100% | 15000
GEN-2016-037 | 07 - Southwestern Oklahoma | 132902 | ERIS | Chisholm - Gracemont 345 kV GEN-2016-037 Interconnection (TOIF) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-037 (300 MW/Wind), into the Point of Interconnection (POI) at Chisholm - Gracemont 345 kV. | 1146800 | 100% | 1146800
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico | 143198 | ERIS | Crawfish Draw 345/230kV Transformer Ckt 1 (DISIS-2017-001) | Current Study | Install a new 345/230kV Transformer at Crawfish Draw | 1366694.4538 | 11.96% | 11430070
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico | 143204 | ERIS | Crawfish Draw 765/345kV New Substation (DISIS-2017-001) | Current Study | Build a new Crawfish Draw 765/345kV Substation tapping the Tuco to Border 345kV Ckt 1 and Tuco to OKU 345kV Ckt 1. In addition, install a new 1000 MVar SVC for Dynamic Reactive Support at Crawfish Draw 765kV. Both the 765kV and the 345kV Crawfish Draw switchyards shall be constructed with breaker and a half bus schemes. Furthermore, interconnected double circuit lines connected to these switchyards or transformers connecting these switchyards shall not share adjacent breakers in the switchyard(s). | 6230212.025 | 2.176% | 286282000
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico | 143207 | ERIS | Crawfish Draw 765/345kV New Transformer (DISIS-2017-001) | Current Study | Install two new 765/345kV Transformers at Crawfish Draw | 2081067.0656 | 5.203% | 40000000
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico | 143219 | ERIS | Crawfish Draw Tap to Tuco to Border 345kV Ckt 1 (DISIS-2017-001) (OKGE) | Current Study | Tap Tuco to Border 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 1692.9688 | 3.386% | 50000
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico | 143194 | ERIS | Crawfish Draw Tap to Tuco to Border 345kV Ckt 1 (DISIS-2017-001) (SWPS) | Current Study | Tap Tuco to Border 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 270875 | 3.386% | 8000000
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico | 143195 | ERIS | Crawfish Draw Tap to Tuco to OKU 345kV Ckt 1 (DISIS-2017-001) (AEPW) | Current Study | Tap Tuco to OKU 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 28291.4125 | 2.176% | 1300000
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico | 143220 | ERIS | Crawfish Draw Tap to Tuco to OKU 345kV Ckt 1 (DISIS-2017-001) (SWPS) | Current Study | Tap Tuco to OKU 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 174101 | 2.176% | 8000000
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico | 143211 | ERIS | Crawfish Draw to Seminole 765kV New Line Double Circuit (DISIS-2017-001) (OKGE) | Current Study | Build approximately 80 miles of new double circuit 765kV line from Crawfish Draw to Seminole | 24938426.4155 | 3.776% | 660408000
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico | 143221 | ERIS | Crawfish Draw to Seminole 765kV New Line Double Circuit (DISIS-2017-001) (SWPS) | Current Study | Build approximately 265 miles of new double circuit 765kV line from Crawfish Draw to Seminole | 24998543.7594 | 3.776% | 662000000
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico | 143209 | ERIS | Crossroads 765/345kV New Transformer (DISIS-2017-001) | Current Study | Expand Crossroads 765kV Substation and install a new 765/345 transformer | 290473.278 | 1.452% | 20000000
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico | 143210 | ERIS | Crossroads to Crawfish Draw 765kV New Line (DISIS-2017-001) | Current Study | Build approximately 85 miles of new 765kV line from Crossroads to Crawfish Draw | 5519014.2972 | 1.452% | 380000000
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico | 143208 | ERIS | Seminole 765/345 New Transformer (DISIS-2017-001) | Current Study | Expand Seminole 345kV substation to include a new 765kV switchyard connected by a new 765/345kV transformer. In addition, install a new 600 MVar SVC for Dynamic Reactive Support at Seminole 765kV. | 6038876.8264 | 3.776% | 159919200
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico | 132905 | ERIS | Swisher 115 kV Substation GEN-2016-039 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-039 (112 MW/Solar), into the Point of Interconnection (POI) at Swisher 115 kV Substation. | 5147608 | 100% | 5147608
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico | 132904 | ERIS | Swisher 115 kV Substation GEN-2016-039 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-039 (112 MW/Solar), into the Point of Interconnection (POI) at Swisher 115 kV Substation. | 587191 | 100% | 587191
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico | 122568 | ERIS | Tolk 345/230 kV CKT 2 Transformer (DISIS-2016-002) | Contingent | Build new 345/230 kV Transformer Ckt 2 at Tolk to achieve a minimum emergency rating of 921 MVA on the Crossroads - Tolk 345 kV Ckt 1 line. | 0 | 0% | 14055360
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico | 143248 | ERIS | Tolk 345/230kV Transformer Ckt 3 (DISIS-2017-001) | Current Study | Install a new 345/230kV Transformer at Tolk | 328904.6487 | 2.34% | 14055360
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico | 143250 | ERIS | Tolk to Tuco 345kV New Line (DISIS-2017-001) | Current Study | Build approximately 54 miles of new 345kV line from Tolk to Tuco | 1171066.8523 | 1.895% | 61799976
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico | 143251 | ERIS | Tuco to Crawfish Draw 345kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Tuco to Crawfish Draw 345kV 1.54 mile line to achieve a minimum light/emergency rating of 1094 MVA | 74265.9297 | 4.214% | 1762443
GEN-2016-103 | 15 - Eastern South Dakota | 132919 | ERIS | Fort Thompson - Leland Olds 345 kV GEN-2016-103 Interconnection (Non-Shared NU) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-103 (250.7 MW/Wind), into the Point of Interconnection (POI) at Fort Thompson - Leland Olds 345 kV. | 2005466 | 100% | 2005466
GEN-2016-103 | 15 - Eastern South Dakota | 132918 | ERIS | Fort Thompson - Leland Olds 345 kV GEN-2016-103 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-103 (250.7 MW/Wind), into the Point of Interconnection (POI) at Fort Thompson - Leland Olds 345 kV. | 1212933 | 100% | 1212933
GEN-2016-103 | 15 - Eastern South Dakota | 143202 | ERIS | Ft. Thompson 345kV Terminal Upgrades (DISIS-2017-001) (WAPA) | Current Study | Upgrade terminal equipment at Ft. Thompson 345kV to accept G16-017 Tap to Ft. Thompson Ckt 2 | 7546339 | 100% | 7546339
GEN-2016-103 | 15 - Eastern South Dakota | 143201 | ERIS | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC) | Current Study | Build approximately 30 miles of new 345kV line from G16-017 Tap to Ft. Thompson | 65900000 | 100% | 65900000
GEN-2016-159 | 09 - Nebraska | 143215 | ERIS | Cooper 345kV Terminal Upgrades (DISIS-2017-001) (NPPD) | Current Study | Upgrade terminal equipment at Cooper 345 kV line to achieve a minimum Spring/Emergency rating of 1295 MVA | 1294709.5832 | 43.16% | 3000000
GEN-2016-159 | 09 - Nebraska | 143227 | ERIS | Cooper Joe 345kV New Substation (DISIS-2017-001) | Current Study | Build a new 345 kV substation at Cooper Joe. Tap the Cooper to St. Joe 345kV line 20 miles from St. Joe 345kV | 7010364.2354 | 43.16% | 16243869
GEN-2016-159 | 09 - Nebraska | 143212 | ERIS | Cooper Joe to Cooper 345kV Rebuild (DISIS-2017-001) (KCPL) | Current Study | Rebuild Cooper Joe to Cooper 345 kV 22.2 miles line to achieve a minimum Spring/Emergency rating of 1295 MVA | 17451754.1426 | 43.16% | 40437842.97
GEN-2016-159 | 09 - Nebraska | 143214 | ERIS | Cooper Joe to Cooper 345kV Rebuild (DISIS-2017-001) (OPPD) | Current Study | Rebuild Cooper Joe to Cooper 345 kV 26.6 miles line to achieve a minimum Spring/Emergency rating of 1295 MVA | 12791730.5868 | 43.16% | 29640000
GEN-2016-159 | 09 - Nebraska | 143217 | ERIS | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Current Study | Build approximately 6 miles of new 345kV line from Cooper Joe to Hoyt | 6003403.4329 | 43.16% | 13910618
GEN-2016-159 | 09 - Nebraska | 143218 | ERIS | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Current Study | Build approximately 60 miles of new 345kV line from Cooper Joe to Hoyt | 57064287.34 | 43.16% | 132224914
GEN-2016-159 | 09 - Nebraska | 143258 | ERIS | Dixon County to Twin Church 230kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Dixon County to Twin Church 230kV 27.7 mile line to achieve a minimum light/emergency rating of 325 MVA | 24473199 | 100% | 24473199
GEN-2016-159 | 09 - Nebraska | 143259 | ERIS | Holt to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Current Study | Build approximately 26 miles of new 345kV line from Holt to Hoyt | 23869611.7675 | 40.75% | 58576716
GEN-2016-159 | 09 - Nebraska | 143225 | ERIS | Holt 345kV Terminal Upgrades (DISIS-2017-001) (TMO) | Current Study | Upgrade terminal equipment at Holt 345kV to accept Holt to Holt new line | 532554.4556 | 40.75% | 1306904
GEN-2016-159 | 09 - Nebraska | 143213 | ERIS | Holt to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Current Study | Build approximately 100 miles of new 345kV line from Holt to Hoyt | 66526412.2172 | 40.75% | 163257734
GEN-2016-159 | 09 - Nebraska | 143200 | ERIS | Hoskins 345/230kV Transformer T4 Replacement (DISIS-2017-001) | Current Study | Replace the existing Hoskins 345/230kV Transformer to achieve a minimum emergency rating of 406 MVA | 15200000 | 100% | 15200000
GEN-2016-159 | 09 - Nebraska | 143252 | ERIS | Potter County 345/230kV Transformer Ckt 2 (DISIS-2017-001) | Current Study | Install a new 345/230kV Transformer at Potter County | 4695708.2552 | 37.32% | 12583652
GEN-2016-159 | 09 - Nebraska | 132927 | ERIS | Turtle Creek 345 kV Substation GEN-2016-159 Interconnection (Non-Shared NU) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-159 (427.8 MW/Wind), into the Point of Interconnection (POI) at Hoskins 345 kV Substation. | 2900000 | 100% | 2900000
GEN-2016-159 | 09 - Nebraska | 132926 | ERIS | Turtle Creek 345 kV Substation GEN-2016-159 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-159 (427.8 MW/Wind), into the Point of Interconnection (POI) at Hoskins 345 kV Substation. | 2900000 | 100% | 2900000
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico | 143198 | ERIS | Crawfish Draw 345/230kV Transformer Ckt 1 (DISIS-2017-001) | Current Study | Install a new 345/230kV Transformer at Crawfish Draw | 2260571.963 | 19.78% | 11430070
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico | 143204 | ERIS | Crawfish Draw 765/345kV New Substation (DISIS-2017-001) | Current Study | Build a new Crawfish Draw 765/345kV Substation tapping the Tuco to Border 345kV Ckt 1 and Tuco to OKU 345kV Ckt 1. In addition, install a new 1000 MVar SVC for Dynamic Reactive Support at Crawfish Draw 765kV. Both the 765kV and the 345kV Crawfish Draw switchyards shall be constructed with breaker and a half bus schemes. Furthermore, interconnected double circuit lines connected to these switchyards or transformers connecting these switchyards shall not share adjacent breakers in the switchyard(s). | 12667596.7907 | 4.425% | 286282000
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico | 143207 | ERIS | Crawfish Draw 765/345kV New Transformer (DISIS-2017-001) | Current Study | Install two new 765/345kV Transformers at Crawfish Draw | 3917058.9292 | 9.793% | 40000000
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico | 143219 | ERIS | Crawfish Draw Tap to Tuco to Border 345kV Ckt 1 (DISIS-2017-001) (OKGE) | Current Study | Tap Tuco to Border 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 3414.25 | 6.829% | 50000
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico | 143194 | ERIS | Crawfish Draw Tap to Tuco to Border 345kV Ckt 1 (DISIS-2017-001) (SWPS) | Current Study | Tap Tuco to Border 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 546280 | 6.829% | 8000000
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico | 143195 | ERIS | Crawfish Draw Tap to Tuco to OKU 345kV Ckt 1 (DISIS-2017-001) (AEPW) | Current Study | Tap Tuco to OKU 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 57523.2125 | 4.425% | 1300000
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico | 143220 | ERIS | Crawfish Draw Tap to Tuco to OKU 345kV Ckt 1 (DISIS-2017-001) (SWPS) | Current Study | Tap Tuco to OKU 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 353989 | 4.425% | 8000000
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico | 143211 | ERIS | Crawfish Draw to Seminole 765kV New Line Double Circuit (DISIS-2017-001) (OKGE) | Current Study | Build approximately 80 miles of new double circuit 765kV line from Crawfish Draw to Seminole | 51125542.2075 | 7.742% | 660408000
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico | 143221 | ERIS | Crawfish Draw to Seminole 765kV New Line Double Circuit (DISIS-2017-001) (SWPS) | Current Study | Build approximately 265 miles of new double circuit 765kV line from Crawfish Draw to Seminole | 51248787.0246 | 7.742% | 662000000
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico | 143209 | ERIS | Crossroads 765/345kV New Transformer (DISIS-2017-001) | Current Study | Expand Crossroads 765kV Substation and install a new 765/345 transformer | 787896.0329 | 3.939% | 20000000
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico | 143325 | ERIS | Crossroads 765kV Reactive Support (DISIS-2017-001) | Current Study | Stability identified need to install 600 MVar SVC for Dynamic Reactive Support at Crossroads 765kV | 5348112.6465 | 3.939% | 135769200
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico | 143210 | ERIS | Crossroads to Crawfish Draw 765kV New Line (DISIS-2017-001) | Current Study | Build approximately 85 miles of new 765kV line from Crossroads to Crawfish Draw | 14968658.6182 | 3.939% | 380000000
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico | 132931 | ERIS | Newhart 115 kV Substation GEN-2016-172 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-172 (231 MW/Wind), into the Point of Interconnection (POI) at Newhart 115 kV Substation. | 705336 | 100% | 705336
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico | 132930 | ERIS | Newhart 115 kV Substation GEN-2016-172 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-172 (231 MW/Wind), into the Point of Interconnection (POI) at Newhart 115 kV Substation. | 627807 | 100% | 627807
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico | 143208 | ERIS | Seminole 765/345 New Transformer (DISIS-2017-001) | Current Study | Expand Seminole 345kV substation to include a new 765kV switchyard connected by a new 765/345kV transformer. In addition, install a new 600 MVar SVC for Dynamic Reactive Support at Seminole 765kV. | 12380160.8599 | 7.742% | 159919200
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico | 122568 | ERIS | Tolk 345/230 kV CKT 2 Transformer (DISIS-2016-002) | Contingent | Build new 345/230 kV Transformer Ckt 2 at Tolk to achieve a minimum emergency rating of 921 MVA on the Crossroads - Tolk 345 kV Ckt 1 line. | 0 | 0% | 14055360
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico | 143248 | ERIS | Tolk 345/230kV Transformer Ckt 3 (DISIS-2017-001) | Current Study | Install a new 345/230kV Transformer at Tolk | 942497.2796 | 6.706% | 14055360
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico | 143250 | ERIS | Tolk to Tuco 345kV New Line (DISIS-2017-001) | Current Study | Build approximately 54 miles of new 345kV line from Tolk to Tuco | 3618487.038 | 5.855% | 61799976
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico | 143251 | ERIS | Tuco to Crawfish Draw 345kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Tuco to Crawfish Draw 345kV 1.54 mile line to achieve a minimum light/emergency rating of 1094 MVA | 149773.8526 | 8.498% | 1762443
GEN-2017-004 | 04 - Northwest Kansas | 132937 | ERIS | Elm Creek - Summit 345 kV GEN-2017-004 Interconnection (Non-Shared NU) (ITCGP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-004 (201.6 MW/Wind), into the Point of Interconnection (POI) at Elm Creek - Summit 345 kV. | 15081109 | 100% | 15081109
GEN-2017-004 | 04 - Northwest Kansas | 132936 | ERIS | Elm Creek - Summit 345 kV GEN-2017-004 Interconnection (TOIF) (ITCGP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-004 (201.6 MW/Wind), into the Point of Interconnection (POI) at Elm Creek - Summit 345 kV. | 1054767 | 100% | 1054767
GEN-2017-005 | 08 - North Oklahoma/South Central Kansas | 143230 | ERIS | Franklin 161/69kV Transformer Ckt 2 (DISIS-2017-001) | Current Study | Install a new 161/69kV Transformer at Franklin | 5320916 | 100% | 5320916
GEN-2017-005 | 08 - North Oklahoma/South Central Kansas | 143199 | ERIS | Franklin to G17-005 Tap 161kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Franklin to G17-005 Tap 161kV 20.56 mile line to achieve a minimum Winter/Emergency rating of 300 MVA | 37570337 | 100% | 37570337
GEN-2017-005 | 08 - North Oklahoma/South Central Kansas | 143232 | ERIS | Litchfield to Asbury Plant 161kV Rebuild (DISIS-2017-001) (EMDE) | Current Study | Rebuild the existing Litchfield to Asbury Plant 161kV 5 mile line to achieve a minimum Winter/Emergency rating of 325 MVA | 8610000 | 100% | 8610000
GEN-2017-005 | 08 - North Oklahoma/South Central Kansas | 143235 | ERIS | Litchfield to Asbury Plant 161kV Rebuild (DISIS-2017-001) (WERE) | Current Study | Rebuild the existing Litchfield to Asbury Plant 161kV 1.6 mile line to achieve a minimum Winter/Emergency rating of 325 MVA | 2332649 | 100% | 2332649
GEN-2017-005 | 08 - North Oklahoma/South Central Kansas | 143223 | ERIS | Litchfield to Franklin 161kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Litchfield to Franklin 161kV 6.22 mile line to achieve a minimum Winter/Emergency rating of 300 MVA | 10661540 | 100% | 10661540
GEN-2017-005 | 08 - North Oklahoma/South Central Kansas | 132939 | ERIS | Marmaton - Litchfield 161 kV GEN-2017-005 Interconnection (Non-Shared NU) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-005 (195 MW/Wind), into the Point of Interconnection (POI) at Marmaton - Litchfield 161 kV. | 9467883 | 100% | 9467883
GEN-2017-005 | 08 - North Oklahoma/South Central Kansas | 132938 | ERIS | Marmaton - Litchfield 161 kV GEN-2017-005 Interconnection (TOIF) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-005 (195 MW/Wind), into the Point of Interconnection (POI) at Marmaton - Litchfield 161 kV. | 833096 | 100% | 833096
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico | 143198 | ERIS | Crawfish Draw 345/230kV Transformer Ckt 1 (DISIS-2017-001) | Current Study | Install a new 345/230kV Transformer at Crawfish Draw | 1364504.9033 | 11.94% | 11430070
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico | 143204 | ERIS | Crawfish Draw 765/345kV New Substation (DISIS-2017-001) | Current Study | Build a new Crawfish Draw 765/345kV Substation tapping the Tuco to Border 345kV Ckt 1 and Tuco to OKU 345kV Ckt 1. In addition, install a new 1000 MVar SVC for Dynamic Reactive Support at Crawfish Draw 765kV. Both the 765kV and the 345kV Crawfish Draw switchyards shall be constructed with breaker and a half bus schemes. Furthermore, interconnected double circuit lines connected to these switchyards or transformers connecting these switchyards shall not share adjacent breakers in the switchyard(s). | 19799015.0089 | 6.916% | 286282000
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico | 143207 | ERIS | Crawfish Draw 765/345kV New Transformer (DISIS-2017-001) | Current Study | Install two new 765/345kV Transformers at Crawfish Draw | 4364024.3846 | 10.91% | 40000000
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico | 143219 | ERIS | Crawfish Draw Tap to Tuco to Border 345kV Ckt 1 (DISIS-2017-001) (OKGE) | Current Study | Tap Tuco to Border 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 5741.9438 | 11.48% | 50000
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico | 143194 | ERIS | Crawfish Draw Tap to Tuco to Border 345kV Ckt 1 (DISIS-2017-001) (SWPS) | Current Study | Tap Tuco to Border 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 918711 | 11.48% | 8000000
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico | 143195 | ERIS | Crawfish Draw Tap to Tuco to OKU 345kV Ckt 1 (DISIS-2017-001) (AEPW) | Current Study | Tap Tuco to OKU 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 89906.8625 | 6.916% | 1300000
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico | 143220 | ERIS | Crawfish Draw Tap to Tuco to OKU 345kV Ckt 1 (DISIS-2017-001) (SWPS) | Current Study | Tap Tuco to OKU 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 553273 | 6.916% | 8000000
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico | 143211 | ERIS | Crawfish Draw to Seminole 765kV New Line Double Circuit (DISIS-2017-001) (OKGE) | Current Study | Build approximately 80 miles of new double circuit 765kV line from Crawfish Draw to Seminole | 77792479.916 | 11.78% | 660408000
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico | 143221 | ERIS | Crawfish Draw to Seminole 765kV New Line Double Circuit (DISIS-2017-001) (SWPS) | Current Study | Build approximately 265 miles of new double circuit 765kV line from Crawfish Draw to Seminole | 77980008.88 | 11.78% | 662000000
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico | 143209 | ERIS | Crossroads 765/345kV New Transformer (DISIS-2017-001) | Current Study | Expand Crossroads 765kV Substation and install a new 765/345 transformer | 2078135.4758 | 10.39% | 20000000
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico | 143325 | ERIS | Crossroads 765kV Reactive Support (DISIS-2017-001) | Current Study | Stability identified need to install 600 MVar SVC for Dynamic Reactive Support at Crossroads 765kV | 14107395.8266 | 10.39% | 135769200
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico | 143210 | ERIS | Crossroads to Crawfish Draw 765kV New Line (DISIS-2017-001) | Current Study | Build approximately 85 miles of new 765kV line from Crossroads to Crawfish Draw | 39484731.5453 | 10.39% | 380000000
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico | 132943 | ERIS | Pleasant Hill 230 kV Substation GEN-2017-007 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-007 (297.5 MW/Wind), into the Point of Interconnection (POI) at Pleasant Hill 230 kV Substation. | 1865013 | 100% | 1865013
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico | 132942 | ERIS | Pleasant Hill 230 kV Substation GEN-2017-007 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-007 (297.5 MW/Wind), into the Point of Interconnection (POI) at Pleasant Hill 230 kV Substation. | 1074589 | 100% | 1074589
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico | 143208 | ERIS | Seminole 765/345 New Transformer (DISIS-2017-001) | Current Study | Expand Seminole 345kV substation to include a new 765kV switchyard connected by a new 765/345kV transformer. In addition, install a new 600 MVar SVC for Dynamic Reactive Support at Seminole 765kV. | 18837618.1963 | 11.78% | 159919200
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico | 122568 | ERIS | Tolk 345/230 kV CKT 2 Transformer (DISIS-2016-002) | Contingent | Build new 345/230 kV Transformer Ckt 2 at Tolk to achieve a minimum emergency rating of 921 MVA on the Crossroads - Tolk 345 kV Ckt 1 line. | 0 | 0% | 14055360
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico | 143248 | ERIS | Tolk 345/230kV Transformer Ckt 3 (DISIS-2017-001) | Current Study | Install a new 345/230kV Transformer at Tolk | 2232550.0382 | 15.88% | 14055360
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico | 143250 | ERIS | Tolk to Tuco 345kV New Line (DISIS-2017-001) | Current Study | Build approximately 54 miles of new 345kV line from Tolk to Tuco | 9492019.546 | 15.36% | 61799976
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico | 143251 | ERIS | Tuco to Crawfish Draw 345kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Tuco to Crawfish Draw 345kV 1.54 mile line to achieve a minimum light/emergency rating of 1094 MVA | 251883.4405 | 14.29% | 1762443
GEN-2017-008 | 09 - Nebraska | 143215 | ERIS | Cooper 345kV Terminal Upgrades (DISIS-2017-001) (NPPD) | Current Study | Upgrade terminal equipment at Cooper 345 kV line to achieve a minimum Spring/Emergency rating of 1295 MVA | 767795.6123 | 25.59% | 3000000
GEN-2017-008 | 09 - Nebraska | 143227 | ERIS | Cooper Joe 345kV New Substation (DISIS-2017-001) | Current Study | Build a new 345 kV substation at Cooper Joe. Tap the Cooper to St. Joe 345kV line 20 miles from St. Joe 345kV | 4157323.6903 | 25.59% | 16243869
GEN-2017-008 | 09 - Nebraska | 143212 | ERIS | Cooper Joe to Cooper 345kV Rebuild (DISIS-2017-001) (KCPL) | Current Study | Rebuild Cooper Joe to Cooper 345 kV 22.2 miles line to achieve a minimum Spring/Emergency rating of 1295 MVA | 10349332.5737 | 25.59% | 40437842.97
GEN-2017-008 | 09 - Nebraska | 143214 | ERIS | Cooper Joe to Cooper 345kV Rebuild (DISIS-2017-001) (OPPD) | Current Study | Rebuild Cooper Joe to Cooper 345 kV 26.6 miles line to achieve a minimum Spring/Emergency rating of 1295 MVA | 7585820.4828 | 25.59% | 29640000
GEN-2017-008 | 09 - Nebraska | 143217 | ERIS | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Current Study | Build approximately 6 miles of new 345kV line from Cooper Joe to Hoyt | 3560170.41 | 25.59% | 13910618
GEN-2017-008 | 09 - Nebraska | 143218 | ERIS | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Current Study | Build approximately 60 miles of new 345kV line from Cooper Joe to Hoyt | 33840568.8584 | 25.59% | 132224914
GEN-2017-008 | 09 - Nebraska | 143259 | ERIS | Holt to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Current Study | Build approximately 26 miles of new 345kV line from Holt to Hoyt | 13849318.0821 | 23.64% | 58576716
GEN-2017-008 | 09 - Nebraska | 143225 | ERIS | Holt 345kV Terminal Upgrades (DISIS-2017-001) (TMO) | Current Study | Upgrade terminal equipment at Holt 345kV to accept Holt to Holt new line | 308991.8731 | 23.64% | 1306904
GEN-2017-008 | 09 - Nebraska | 143213 | ERIS | Holt to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Current Study | Build approximately 100 miles of new 345kV line from Holt to Hoyt | 38599096.0395 | 23.64% | 163257734
GEN-2017-008 | 09 - Nebraska | 132945 | ERIS | Moore - Pauline 345 kV GEN-2017-008 Interconnection (Non-Shared NU) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-008 (305 MW/Solar), into the Point of Interconnection (POI) at Moore - Pauline 345 kV Substation. | 1200000 | 100% | 1200000
GEN-2017-008 | 09 - Nebraska | 132944 | ERIS | Moore - Pauline 345 kV GEN-2017-008 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-008 (305 MW/Solar), into the Point of Interconnection (POI) at Moore - Pauline 345 kV Substation. | 1200000 | 100% | 1200000
GEN-2017-008 | 09 - Nebraska | 143252 | ERIS | Potter County 345/230kV Transformer Ckt 2 (DISIS-2017-001) | Current Study | Install a new 345/230kV Transformer at Potter County | 3875737.9633 | 30.8% | 12583652
GEN-2017-008 | 09 - Nebraska | 143240 | ERIS | Smokey Hils to Summit 230kV Rebuild (DISIS-2017-001) (MIDW) | Current Study | Rebuild the existing Smokey Hills to Summit 230kV 16.1 mile line to achieve a minimum Light/Emergency rating of 375 MVA | 3342112.6416 | 20.26% | 16500000
GEN-2017-009 | 08 - North Oklahoma/South Central Kansas | 132947 | ERIS | Neosho - Caney River 345 kV GEN-2017-009 Interconnection (Non-Shared NU) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-009 (302.5 MW/Wind), into the Point of Interconnection (POI) at Neosho - Caney River 345 kV. | 15017048 | 100% | 15017048
GEN-2017-009 | 08 - North Oklahoma/South Central Kansas | 132946 | ERIS | Neosho - Caney River 345 kV GEN-2017-009 Interconnection (TOIF) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-009 (302.5 MW/Wind), into the Point of Interconnection (POI) at Neosho - Caney River 345 kV. | 1311181 | 100% | 1311181
GEN-2017-009 | 08 - North Oklahoma/South Central Kansas | 143246 | ERIS | Neosho to G17-009 Tap Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Neosho to G17-009 345kV 18.17 mile line to achieve a minimum Winter/Emergency rating of 1260 MVA | 30446720.4944 | 92.59% | 32884027
GEN-2017-010 | 16 - Western North Dakota | 143226 | ERIS | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | Current Study | Replace the existing Broadland 345/230kV Transformer to achieve a minimum Summer/Normal rating of 471 MVA | 2019128.2858 | 34.19% | 5906325
GEN-2017-010 | 16 - Western North Dakota | 143324 | ERIS | G17-010 Tap 230kV Reactive Support (DISIS-2017-001) | Current Study | Stability identified need to Install 135 MVar SVC for Dynamic Reactive Support at G17-010 Tap 230kV | 30548070 | 100% | 30548070
GEN-2017-010 | 16 - Western North Dakota | 143222 | ERIS | MERRCRT4 to Wishek 230kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing MERRCRT4 to Wishek 230kV 29.3 mile line to achieve a minimum Summer/Normal rating of 401 MVA | 3585072.8163 | 39.83% | 9000000
GEN-2017-010 | 16 - Western North Dakota | 143229 | ERIS | Napoleon SW to Wishek 230kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Napoleon SW to Wishek 230kV 24.89 mile line to achieve a minimum Summer/Normal rating of 407 MVA | 2987560.6803 | 39.83% | 7500000
GEN-2017-010 | 16 - Western North Dakota | 132949 | ERIS | Rhame 230 kV Substation GEN-2017-010 Interconnection (Non-Shared NU) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-010 (200.1 MW/Wind), into the Point of Interconnection (POI) at Rhame 230 kV Substation. | 1189064 | 100% | 1189064
GEN-2017-010 | 16 - Western North Dakota | 132948 | ERIS | Rhame 230 kV Substation GEN-2017-010 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-010 (200.1 MW/Wind), into the Point of Interconnection (POI) at Rhame 230 kV Substation. | 1608232 | 100% | 1608232
GEN-2017-011 | 01 - Woodward | 132951 | ERIS | Badger - Woodward 345 kV GEN-2017-011 Interconnection (Non-Shared NU) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-011 (151.8 MW/Solar), into the Point of Interconnection (POI) at Badger - Woodward 345 kV. | 15000 | 100% | 15000
GEN-2017-011 | 01 - Woodward | 132950 | ERIS | Badger - Woodward 345 kV GEN-2017-011 Interconnection (TOIF) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-011 (151.8 MW/Solar), into the Point of Interconnection (POI) at Badger - Woodward 345 kV. | 0 | 100% | 0
GEN-2017-013 | 04 - Northwest Kansas | 132955 | ERIS | Mingo 345 kV Substation GEN-2017-013 Interconnection (Non-Shared NU) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-013 (200 MW/Wind), into the Point of Interconnection (POI) at Mingo 345 kV Substation. | 3269931 | 100% | 3269931
GEN-2017-013 | 04 - Northwest Kansas | 132954 | ERIS | Mingo 345 kV Substation GEN-2017-013 Interconnection (TOIF) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-013 (200 MW/Wind), into the Point of Interconnection (POI) at Mingo 345 kV Substation. | 2447857 | 100% | 2447857
GEN-2017-013 | 04 - Northwest Kansas | 143317 | NRIS | Mark Moore to Monolith 345kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Mark Moore to Monolith 345kV .75 mile line to achieve a minimum winter/normal rating of 1108 MVA | 1085505.6268 | 24.67% | 4400000
GEN-2017-013 | 04 - Northwest Kansas | 143320 | NRIS | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Current Study | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek | 874597.1132 | 1.244% | 70295174
GEN-2017-013 | 04 - Northwest Kansas | 143319 | NRIS | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Current Study | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek | 1741849.2463 | 1.244% | 140000000
GEN-2017-014 | 17 - Western South Dakota | 143224 | ERIS | G17-014 Tap to Philip Tap 230kV New Line (DISIS-2017-001) | Current Study | Convert existing Philip Tap to a ring bus substation and build approximately 6 miles of new 230kV from new substation to G17-014 Tap creating a double circuit 230kV line. | 10624880.4958 | 37% | 28715520
GEN-2017-014 | 17 - Western South Dakota | 132957 | ERIS | Underwood - Philip 230 kV GEN-2017-014 Interconnection (Non-Shared NU) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-014 (300 MW/Wind), into the Point of Interconnection (POI) at Underwood - Philip 230 kV. | 4604916.81 | 100% | 4604916.81
GEN-2017-014 | 17 - Western South Dakota | 132956 | ERIS | Underwood - Philip 230 kV GEN-2017-014 Interconnection (TOIF) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-014 (300 MW/Wind), into the Point of Interconnection (POI) at Underwood - Philip 230 kV. | 1000000 | 100% | 1000000
GEN-2017-014 | 17 - Western South Dakota | 143312 | NRIS | Beulah 115kV Terminal Upgrades (DISIS-2017-001) (MDU) | Current Study | Upgrade terminal equipment at Beulah 115kV to achieve a minimum winter/emergency rating of 171 MVA | 169456.0669 | 67.78% | 250000
GEN-2017-014 | 17 - Western South Dakota | 143299 | NRIS | G17-064 Tap to Wayside 230kV Rebuild (DISIS-2017-001) (WAPA) | Current Study | Rebuild the existing G17-064 Tap to Wayside 230kV 38.05 mile line to achieve a minimum summer/emergency rating of 377 MVA | 0 | 52.03% | 0
GEN-2017-014 | 17 - Western South Dakota | 143304 | NRIS | Martin to Vetal Tap 115kV Rebuild (DISIS-2017-001) (WAPA) | Current Study | Rebuild the existing Martin to Vetal Tap 115kV 16.67 mile line to achieve a minimum summer/emergency rating of 95 MVA | 119781.8317 | 68.8% | 174097
GEN-2017-014 | 17 - Western South Dakota | 143303 | NRIS | Martin to Wanblee 115kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Martin to Wanblee 115kV 20.86 mile line to achieve a minimum summer/emergency rating of 129 MVA | 0 | 100% | 0
GEN-2017-014 | 17 - Western South Dakota | 143316 | NRIS | Mission to Vetal Tap 115kV Rebuild (DISIS-2017-001) (WAPA) | Current Study | Rebuild the existing Mission to Vetal Tap 115kV 37.87 mile line to achieve a minimum summer/normal rating of 92 MVA | 405930.491 | 68.8% | 590000
GEN-2017-014 | 17 - Western South Dakota | 143302 | NRIS | Scottsbluff to Victory Hill 115kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Scottsbluff to Victory Hill 115kV 8.09 mile line to achieve a minimum summer/emergency rating of 177 MVA | 1914810.075 | 58.02% | 3300000
GEN-2017-014 | 17 - Western South Dakota | 143311 | NRIS | Stanton 115kV Terminal Upgrades (DISIS-2017-001) (BEPC) | Current Study | Upgrade terminal equipment at Stanton 115kV to achieve a minimum winter/emergency rating of 171 MVA | 18707.9498 | 67.78% | 27600
GEN-2017-014 | 17 - Western South Dakota | 143310 | NRIS | Stanton to Beulah 115kV Rebuild (DISIS-2017-001) (WAPA) | Current Study | Rebuild the existing Stanton to Beulah 115kV 13.41 mile line to achieve a minimum winter/emergency rating of 171 MVA | 4012719.6653 | 67.78% | 5920000
GEN-2017-014 | 17 - Western South Dakota | 143315 | NRIS | Vetal Tap Terminal Upgrades for Martin Rebuild (DISIS-2017-001) (BEPC) | Current Study | Upgrade terminal equipment at Vetal Tap 115kV to achieve a minimum summer/emergency rating of 95 MVA | 0 | 68.8% | 0
GEN-2017-014 | 17 - Western South Dakota | 143305 | NRIS | Vetal Tap Terminal Upgrades for Mission Rebuild (DISIS-2017-001) (BEPC) | Current Study | Upgrade terminal equipment at Vetal Tap 115kV 37.87 mile line to achieve a minimum summer/normal rating of 92 MVA | 0 | 68.8% | 0
GEN-2017-014 | 17 - Western South Dakota | 143298 | NRIS | Wayside 230kV Terminal Upgrades (DISIS-2017-001) (NPPD) | Current Study | Upgrade terminal equipment at Wayside 230kV to accept Wayside to Shannon new line | 3496706.7353 | 52.03% | 6721188
GEN-2017-014 | 17 - Western South Dakota | 143322 | NRIS | Wayside to Shannon 230kV New Line (DISIS-2017-001) (BEPC) | Current Study | Build approximately 54 miles of new 345kV line from Wayside to Shannon and install a 230/115kV transformer | 3264073.295 | 4.827% | 67621351
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico | 143198 | ERIS | Crawfish Draw 345/230kV Transformer Ckt 1 (DISIS-2017-001) | Current Study | Install a new 345/230kV Transformer at Crawfish Draw | 157714.323 | 1.38% | 11430070
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico | 143204 | ERIS | Crawfish Draw 765/345kV New Substation (DISIS-2017-001) | Current Study | Build a new Crawfish Draw 765/345kV Substation tapping the Tuco to Border 345kV Ckt 1 and Tuco to OKU 345kV Ckt 1. In addition, install a new 1000 MVar SVC for Dynamic Reactive Support at Crawfish Draw 765kV. Both the 765kV and the 345kV Crawfish Draw switchyards shall be constructed with breaker and a half bus schemes. Furthermore, interconnected double circuit lines connected to these switchyards or transformers connecting these switchyards shall not share adjacent breakers in the switchyard(s). | 2167011.599 | 0.757% | 286282000
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico | 143207 | ERIS | Crawfish Draw 765/345kV New Transformer (DISIS-2017-001) | Current Study | Install two new 765/345kV Transformers at Crawfish Draw | 485516.6638 | 1.214% | 40000000
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico | 143219 | ERIS | Crawfish Draw Tap to Tuco to Border 345kV Ckt 1 (DISIS-2017-001) (OKGE) | Current Study | Tap Tuco to Border 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 625.675 | 1.251% | 50000
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico | 143194 | ERIS | Crawfish Draw Tap to Tuco to Border 345kV Ckt 1 (DISIS-2017-001) (SWPS) | Current Study | Tap Tuco to Border 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 100108 | 1.251% | 8000000
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico | 143195 | ERIS | Crawfish Draw Tap to Tuco to OKU 345kV Ckt 1 (DISIS-2017-001) (AEPW) | Current Study | Tap Tuco to OKU 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 9840.35 | 0.757% | 1300000
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico | 143220 | ERIS | Crawfish Draw Tap to Tuco to OKU 345kV Ckt 1 (DISIS-2017-001) (SWPS) | Current Study | Tap Tuco to OKU 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 60556 | 0.757% | 8000000
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico | 143211 | ERIS | Crawfish Draw to Seminole 765kV New Line Double Circuit (DISIS-2017-001) (OKGE) | Current Study | Build approximately 80 miles of new double circuit 765kV line from Crawfish Draw to Seminole | 8532334.8774 | 1.292% | 660408000
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico | 143221 | ERIS | Crawfish Draw to Seminole 765kV New Line Double Circuit (DISIS-2017-001) (SWPS) | Current Study | Build approximately 265 miles of new double circuit 765kV line from Crawfish Draw to Seminole | 8552903.1884 | 1.292% | 662000000
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico | 143209 | ERIS | Crossroads 765/345kV New Transformer (DISIS-2017-001) | Current Study | Expand Crossroads 765kV Substation and install a new 765/345 transformer | 224148.3816 | 1.121% | 20000000
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico | 143325 | ERIS | Crossroads 765kV Reactive Support (DISIS-2017-001) | Current Study | Stability identified need to install 600 MVar SVC for Dynamic Reactive Support at Crossroads 765kV | 1521555.622 | 1.121% | 135769200
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico | 143210 | ERIS | Crossroads to Crawfish Draw 765kV New Line (DISIS-2017-001) | Current Study | Build approximately 85 miles of new 765kV line from Crossroads to Crawfish Draw | 4258632.5643 | 1.121% | 380000000
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico | 132959 | ERIS | Norton 115 kV Switching Station GEN-2017-016 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-016 (33 MW/Solar), into the Point of Interconnection (POI) at Norton 115 kV Switching Station. | 1069895 | 100% | 1069895
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico | 132958 | ERIS | Norton 115 kV Switching Station GEN-2017-016 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-016 (33 MW/Solar), into the Point of Interconnection (POI) at Norton 115 kV Switching Station. | 617431 | 100% | 617431
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico | 143241 | ERIS | Norton to Pleasant Hills 115kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Norton to Pleasant Hills 115kV 54.54 mile line to achieve a minimum Light/Emergency rating of 150 MVA | 135245.9016 | 90.16% | 150000
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico | 143208 | ERIS | Seminole 765/345 New Transformer (DISIS-2017-001) | Current Study | Expand Seminole 345kV substation to include a new 765kV switchyard connected by a new 765/345kV transformer. In addition, install a new 600 MVar SVC for Dynamic Reactive Support at Seminole 765kV. | 2066124.0802 | 1.292% | 159919200
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico | 122568 | ERIS | Tolk 345/230 kV CKT 2 Transformer (DISIS-2016-002) | Contingent | Build new 345/230 kV Transformer Ckt 2 at Tolk to achieve a minimum emergency rating of 921 MVA on the Crossroads - Tolk 345 kV Ckt 1 line. | 0 | 0% | 14055360
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico | 143248 | ERIS | Tolk 345/230kV Transformer Ckt 3 (DISIS-2017-001) | Current Study | Install a new 345/230kV Transformer at Tolk | 242056.3164 | 1.722% | 14055360
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico | 143250 | ERIS | Tolk to Tuco 345kV New Line (DISIS-2017-001) | Current Study | Build approximately 54 miles of new 345kV line from Tolk to Tuco | 1026186.839 | 1.66% | 61799976
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico | 143251 | ERIS | Tuco to Crawfish Draw 345kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Tuco to Crawfish Draw 345kV 1.54 mile line to achieve a minimum light/emergency rating of 1094 MVA | 27446.6589 | 1.557% | 1762443
GEN-2017-018 | 03 - Spearville | 143239 | ERIS | Degrassee 138kV Terminal Upgrades (DISIS-2017-001) (OKGE) | Current Study | Upgrade terminal equipment at Degrasse 138kV to achieve a minimum Spring/Emergency rating of 175 MVA | 0 | 100% | 0
GEN-2017-018 | 03 - Spearville | 143263 | ERIS | Finney 345kV Reactive Support (DISIS-2017-001) | Current Study | Install +250 MVAR Capacitor Bank(s) at Finney 345kV | 27510.6547 | 0.4432% | 6207750
GEN-2017-018 | 03 - Spearville | 143238 | ERIS | Rose Valley to Degrasse 138kV Rebuild (DISIS-2017-001) (WFEC) | Current Study | Rebuild the existing Rose Valley to Degrasse 138kV 3.2 mile line to achieve a minimum Spring/Emergency rating of 175 MVA | 2080000 | 100% | 2080000
GEN-2017-018 | 03 - Spearville | 132961 | ERIS | Thistle 345 kV Substation GEN-2017-018 Interconnection (Non-Shared NU) (ITCGP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-018 (190 MW/Solar), into the Point of Interconnection (POI) at Thistle 345 kV Substation. | 1412092 | 100% | 1412092
GEN-2017-018 | 03 - Spearville | 143117 | ERIS | Thistle 345 kV Substation GEN-2017-018 Interconnection (Non-Shared NU) (OKGE) | Interconnection | Potential interconnection impacts from the following generating facility, GEN-2017-018 (190 MW/Solar), into the Point of Interconnection (POI) at Thistle 345 kV Substation. | 30000 | 100% | 30000
GEN-2017-018 | 03 - Spearville | 143118 | ERIS | Thistle 345 kV Substation GEN-2017-018 Interconnection (Non-Shared NU) (WERE) | Interconnection | Potential interconnection impacts from the following generating facility, GEN-2017-018 (190 MW/Solar), into the Point of Interconnection (POI) at Thistle 345 kV Substation. | 13299 | 100% | 13299
GEN-2017-018 | 03 - Spearville | 132960 | ERIS | Thistle 345 kV Substation GEN-2017-018 Interconnection (TOIF) (ITCGP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-018 (190 MW/Solar), into the Point of Interconnection (POI) at Thistle 345 kV Substation. | 918132 | 100% | 918132
GEN-2017-018 | 03 - Spearville | 143320 | NRIS | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Current Study | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek | 5769984.6633 | 8.208% | 70295174
GEN-2017-018 | 03 - Spearville | 143319 | NRIS | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Current Study | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek | 11491512.246 | 8.208% | 140000000
GEN-2017-021 | 03 - Spearville | 143263 | ERIS | Finney 345kV Reactive Support (DISIS-2017-001) | Current Study | Install +250 MVAR Capacitor Bank(s) at Finney 345kV | 28958.5839 | 0.4665% | 6207750
GEN-2017-021 | 03 - Spearville | 132963 | ERIS | Post Rock - Spearville 345 kV GEN-2017-021 Interconnection (Non-Shared NU) (ITCGP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-021 (200 MW/Wind), into the Point of Interconnection (POI) at Post Rock - Spearville 345 kV. | 15081109 | 100% | 15081109
GEN-2017-021 | 03 - Spearville | 132962 | ERIS | Post Rock - Spearville 345 kV GEN-2017-021 Interconnection (TOIF) (ITCGP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-021 (200 MW/Wind), into the Point of Interconnection (POI) at Post Rock - Spearville 345 kV. | 1054767 | 100% | 1054767
GEN-2017-021 | 03 - Spearville | 143240 | ERIS | Smokey Hils to Summit 230kV Rebuild (DISIS-2017-001) (MIDW) | Current Study | Rebuild the existing Smokey Hills to Summit 230kV 16.1 mile line to achieve a minimum Light/Emergency rating of 375 MVA | 4150461.2291 | 25.15% | 16500000
GEN-2017-021 | 03 - Spearville | 143242 | ERIS | Smokey Hils to Summit 230kV Rebuild (DISIS-2017-001) (WERE) | Current Study | Rebuild the existing Smokey Hills to Summit 230kV 22.5 mile line to achieve a minimum Light/Emergency rating of 375 MVA | 9735744.5038 | 35.63% | 27323646
GEN-2017-021 | 03 - Spearville | 143320 | NRIS | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Current Study | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek | 3210090.1968 | 4.567% | 70295174
GEN-2017-021 | 03 - Spearville | 143319 | NRIS | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Current Study | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek | 6393221.6392 | 4.567% | 140000000
GEN-2017-022 | 08 - North Oklahoma/South Central Kansas | 132965 | ERIS | Altoona - Parson 138 kV GEN-2017-022 Interconnection (Non-Shared NU) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-022 (65 MW/Solar), into the Point of Interconnection (POI) at Altoona - Parson 138 kV. | 4790295 | 100% | 4790295
GEN-2017-022 | 08 - North Oklahoma/South Central Kansas | 132964 | ERIS | Altoona - Parson 138 kV GEN-2017-022 Interconnection (TOIF) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-022 (65 MW/Solar), into the Point of Interconnection (POI) at Altoona - Parson 138 kV. | 696118 | 100% | 696118
GEN-2017-022 | 08 - North Oklahoma/South Central Kansas | 143295 | NRIS | Altoona 69kV Terminal Upgrades (DISIS-2017-001) | Current Study | Upgrade terminal equipment at Altoona to Neodesha Jct. to achieve a minimum summer/emergency rating of 41 MVA | 3325 | 100% | 3325
GEN-2017-022 | 08 - North Oklahoma/South Central Kansas | 143317 | NRIS | Mark Moore to Monolith 345kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Mark Moore to Monolith 345kV .75 mile line to achieve a minimum winter/normal rating of 1108 MVA | 159589.3141 | 3.627% | 4400000
GEN-2017-022 | 08 - North Oklahoma/South Central Kansas | 143320 | NRIS | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Current Study | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek | 1165355.6067 | 1.658% | 70295174
GEN-2017-022 | 08 - North Oklahoma/South Central Kansas | 143319 | NRIS | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Current Study | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek | 2320924.4057 | 1.658% | 140000000
GEN-2017-022 | 08 - North Oklahoma/South Central Kansas | 143296 | NRIS | Neodesha Jct. 69kV Terminal Upgrades (DISIS-2017-001) | Current Study | Upgrade terminal equipment at Neodesha Jct. to achieve a minimum summer/emergency rating of 41 MVA | 0 | 100% | 0
GEN-2017-022 | 08 - North Oklahoma/South Central Kansas | 143301 | NRIS | Sarpy Co. S3456 to Council Bluffs 345kV Rebuild (DISIS-2017-001) (MEC) | Current Study | Rebuild the existing Sarpy Co S3456 to Council Bluffs 345kV 3.34 mile line to achieve a minimum winter/emergency rating of 1022 MVA | 5158606 | 100% | 5158606
GEN-2017-022 | 08 - North Oklahoma/South Central Kansas | 143300 | NRIS | Sarpy Co. S3456 to Council Bluffs 345kV Rebuild (DISIS-2017-001) (OPPD) | Current Study | Rebuild the existing Sarpy Co S3456 to Council Bluffs 345kV 5.63 mile line section to achieve a minimum winter/emergency rating of 1022 MVA | 216000 | 100% | 216000
GEN-2017-023 | 14 - South Central Oklahoma | 132967 | ERIS | Hugo 138 kV Substation GEN-2017-023 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-023 (85 MW/Solar), into the Point of Interconnection (POI) at Hugo 138 kV Substaion. | 0 | 100% | 0
GEN-2017-023 | 14 - South Central Oklahoma | 132966 | ERIS | Hugo 138 kV Substation GEN-2017-023 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-023 (85 MW/Solar), into the Point of Interconnection (POI) at Hugo 138 kV Substaion. | 750000 | 100% | 750000
GEN-2017-023 | 14 - South Central Oklahoma | 143244 | ERIS | Valiant 138kV Terminal Upgrades (DISIS-2017-001) (AEPW) | Current Study | Upgrade terminal equipment at Valiant to Hugo PP4 138kV to achieve a minimum winter/emergency rating of 305 MVA | 0 | 64.62% | 0
GEN-2017-023 | 14 - South Central Oklahoma | 143243 | ERIS | Valiant 138kV Terminal Upgrades (DISIS-2017-001) (WFEC) | Current Study | Upgrade terminal equipment at Valiant to Hugo PP4 138kV to achieve a minimum winter/emergency rating of 305 MVA | 962770.1942 | 64.62% | 1490000
GEN-2017-023 | 14 - South Central Oklahoma | 143320 | NRIS | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Current Study | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek | 936622.8197 | 1.332% | 70295174
GEN-2017-023 | 14 - South Central Oklahoma | 143319 | NRIS | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Current Study | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek | 1865379.7594 | 1.332% | 140000000
GEN-2017-023 | 14 - South Central Oklahoma | 143323 | NRIS | Welsh to Wilkes 345kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Welsh to Wilkes 345kV 23.74 mile line to achieve a minimum summer/emergency rating of 972 MVA | 13697521.4607 | 34.07% | 40202865
GEN-2017-024 | 14 - South Central Oklahoma | 132969 | ERIS | Frogville 138 kV Substation GEN-2017-024 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-024 (50 MW/Solar), into the Point of Interconnection (POI) at Frogville 138 kV Substation. | 4750000 | 100% | 4750000
GEN-2017-024 | 14 - South Central Oklahoma | 132968 | ERIS | Frogville 138 kV Substation GEN-2017-024 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-024 (50 MW/Solar), into the Point of Interconnection (POI) at Frogville 138 kV Substation. | 400000 | 100% | 400000
GEN-2017-024 | 14 - South Central Oklahoma | 143244 | ERIS | Valiant 138kV Terminal Upgrades (DISIS-2017-001) (AEPW) | Current Study | Upgrade terminal equipment at Valiant to Hugo PP4 138kV to achieve a minimum winter/emergency rating of 305 MVA | 0 | 35.38% | 0
GEN-2017-024 | 14 - South Central Oklahoma | 143243 | ERIS | Valiant 138kV Terminal Upgrades (DISIS-2017-001) (WFEC) | Current Study | Upgrade terminal equipment at Valiant to Hugo PP4 138kV to achieve a minimum winter/emergency rating of 305 MVA | 527229.8058 | 35.38% | 1490000
GEN-2017-024 | 14 - South Central Oklahoma | 143320 | NRIS | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Current Study | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek | 568626.7285 | 0.8089% | 70295174
GEN-2017-024 | 14 - South Central Oklahoma | 143319 | NRIS | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Current Study | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek | 1132478.0559 | 0.8089% | 140000000
GEN-2017-024 | 14 - South Central Oklahoma | 143323 | NRIS | Welsh to Wilkes 345kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Welsh to Wilkes 345kV 23.74 mile line to achieve a minimum summer/emergency rating of 972 MVA | 7718946.2579 | 19.2% | 40202865
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico | 143198 | ERIS | Crawfish Draw 345/230kV Transformer Ckt 1 (DISIS-2017-001) | Current Study | Install a new 345/230kV Transformer at Crawfish Draw | 1085306.7817 | 9.495% | 11430070
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico | 143204 | ERIS | Crawfish Draw 765/345kV New Substation (DISIS-2017-001) | Current Study | Build a new Crawfish Draw 765/345kV Substation tapping the Tuco to Border 345kV Ckt 1 and Tuco to OKU 345kV Ckt 1. In addition, install a new 1000 MVar SVC for Dynamic Reactive Support at Crawfish Draw 765kV. Both the 765kV and the 345kV Crawfish Draw switchyards shall be constructed with breaker and a half bus schemes. Furthermore, interconnected double circuit lines connected to these switchyards or transformers connecting these switchyards shall not share adjacent breakers in the switchyard(s). | 15957396.8509 | 5.574% | 286282000
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico | 143207 | ERIS | Crawfish Draw 765/345kV New Transformer (DISIS-2017-001) | Current Study | Install two new 765/345kV Transformers at Crawfish Draw | 3612394.9376 | 9.031% | 40000000
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico | 143219 | ERIS | Crawfish Draw Tap to Tuco to Border 345kV Ckt 1 (DISIS-2017-001) (OKGE) | Current Study | Tap Tuco to Border 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 4652.0188 | 9.304% | 50000
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico | 143194 | ERIS | Crawfish Draw Tap to Tuco to Border 345kV Ckt 1 (DISIS-2017-001) (SWPS) | Current Study | Tap Tuco to Border 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 744323 | 9.304% | 8000000
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico | 143195 | ERIS | Crawfish Draw Tap to Tuco to OKU 345kV Ckt 1 (DISIS-2017-001) (AEPW) | Current Study | Tap Tuco to OKU 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 72462.1625 | 5.574% | 1300000
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico | 143220 | ERIS | Crawfish Draw Tap to Tuco to OKU 345kV Ckt 1 (DISIS-2017-001) (SWPS) | Current Study | Tap Tuco to OKU 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 445921 | 5.574% | 8000000
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico | 143211 | ERIS | Crawfish Draw to Seminole 765kV New Line Double Circuit (DISIS-2017-001) (OKGE) | Current Study | Build approximately 80 miles of new double circuit 765kV line from Crawfish Draw to Seminole | 62318665.6848 | 9.436% | 660408000
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico | 143221 | ERIS | Crawfish Draw to Seminole 765kV New Line Double Circuit (DISIS-2017-001) (SWPS) | Current Study | Build approximately 265 miles of new double circuit 765kV line from Crawfish Draw to Seminole | 62468892.9925 | 9.436% | 662000000
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico | 143209 | ERIS | Crossroads 765/345kV New Transformer (DISIS-2017-001) | Current Study | Expand Crossroads 765kV Substation and install a new 765/345 transformer | 1600635.7221 | 8.003% | 20000000
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico | 143325 | ERIS | Crossroads 765kV Reactive Support (DISIS-2017-001) | Current Study | Stability identified need to install 600 MVar SVC for Dynamic Reactive Support at Crossroads 765kV | 10865894.9186 | 8.003% | 135769200
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico | 143210 | ERIS | Crossroads to Crawfish Draw 765kV New Line (DISIS-2017-001) | Current Study | Build approximately 85 miles of new 765kV line from Crossroads to Crawfish Draw | 30412200.0355 | 8.003% | 380000000
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico | 143208 | ERIS | Seminole 765/345 New Transformer (DISIS-2017-001) | Current Study | Expand Seminole 345kV substation to include a new 765kV switchyard connected by a new 765/345kV transformer. In addition, install a new 600 MVar SVC for Dynamic Reactive Support at Seminole 765kV. | 15090599.3969 | 9.436% | 159919200
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico | 132971 | ERIS | Tolk 230 kV Substation GEN-2017-026 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-026 (235 MW/Wind), into the Point of Interconnection (POI) at Tolk 230 kV Substation. | 1543568 | 100% | 1543568
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico | 132970 | ERIS | Tolk 230 kV Substation GEN-2017-026 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-026 (235 MW/Wind), into the Point of Interconnection (POI) at Tolk 230 kV Substation. | 901002 | 100% | 901002
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico | 122568 | ERIS | Tolk 345/230 kV CKT 2 Transformer (DISIS-2016-002) | Contingent | Build new 345/230 kV Transformer Ckt 2 at Tolk to achieve a minimum emergency rating of 921 MVA on the Crossroads - Tolk 345 kV Ckt 1 line. | 0 | 0% | 14055360
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico | 143248 | ERIS | Tolk 345/230kV Transformer Ckt 3 (DISIS-2017-001) | Current Study | Install a new 345/230kV Transformer at Tolk | 2101412.0422 | 14.95% | 14055360
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico | 143250 | ERIS | Tolk to Tuco 345kV New Line (DISIS-2017-001) | Current Study | Build approximately 54 miles of new 345kV line from Tolk to Tuco | 8680682.6278 | 14.05% | 61799976
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico | 143251 | ERIS | Tuco to Crawfish Draw 345kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Tuco to Crawfish Draw 345kV 1.54 mile line to achieve a minimum light/emergency rating of 1094 MVA | 204071.3979 | 11.58% | 1762443
GEN-2017-027 | 14 - South Central Oklahoma | 132973 | ERIS | Pooleville - Ratliff 138 kV GEN-2017-027 Interconnection (Non-Shared NU) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-027 (140 MW/Wind), into the Point of Interconnection (POI) at Pooleville - Ratliff 138 kV. | 1396000 | 100% | 1396000
GEN-2017-027 | 14 - South Central Oklahoma | 132972 | ERIS | Pooleville - Ratliff 138 kV GEN-2017-027 Interconnection (TOIF) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-027 (140 MW/Wind), into the Point of Interconnection (POI) at Pooleville - Ratliff 138 kV. | 515000 | 100% | 515000
GEN-2017-028 | 01 - Woodward | 143119 | ERIS | El Reno 138 kV Switching Station GEN-2017-028 Interconnection (Non-Shared NU) (OKGE) | Interconnection | Potential interconnection impacts from the following generating facility, GEN-2017-028 (50 MW/Solar), into the Point of Interconnection (POI) at El Reno 138 kV Substation. | 15000 | 100% | 15000
GEN-2017-028 | 01 - Woodward | 132974 | ERIS | El Reno 138 kV Switching Station GEN-2017-028 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-028 (50 MW/Solar), into the Point of Interconnection (POI) at El Reno 138 kV Switching Station. | 400000 | 100% | 400000
GEN-2017-028 | 01 - Woodward | 143320 | NRIS | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Current Study | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek | 1015627.6303 | 1.445% | 70295174
GEN-2017-028 | 01 - Woodward | 143319 | NRIS | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Current Study | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek | 2022725.8878 | 1.445% | 140000000
GEN-2017-030 | 13 - Northeast Kansas/Northwest Missouri | 132977 | ERIS | Eastown - Iatan 345 kV GEN-2017-030 Interconnection (Non-Shared NU) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-030 (200 MW/Wind), into the Point of Interconnection (POI) at Eastown - Iatan 345 kV. | 12324396 | 100% | 12324396
GEN-2017-030 | 13 - Northeast Kansas/Northwest Missouri | 132976 | ERIS | Eastown - Iatan 345 kV GEN-2017-030 Interconnection (TOIF) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-030 (200 MW/Wind), into the Point of Interconnection (POI) at Eastown - Iatan 345 kV. | 1862044 | 100% | 1862044
GEN-2017-030 | 13 - Northeast Kansas/Northwest Missouri | 143259 | ERIS | Holt to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Current Study | Build approximately 26 miles of new 345kV line from Holt to Hoyt | 2327045.0385 | 3.973% | 58576716
GEN-2017-030 | 13 - Northeast Kansas/Northwest Missouri | 143225 | ERIS | Holt 345kV Terminal Upgrades (DISIS-2017-001) (TMO) | Current Study | Upgrade terminal equipment at Holt 345kV to accept Holt to Holt new line | 51918.6577 | 3.973% | 1306904
GEN-2017-030 | 13 - Northeast Kansas/Northwest Missouri | 143213 | ERIS | Holt to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Current Study | Build approximately 100 miles of new 345kV line from Holt to Hoyt | 6485650.4624 | 3.973% | 163257734
GEN-2017-031 | 09 - Nebraska | 143215 | ERIS | Cooper 345kV Terminal Upgrades (DISIS-2017-001) (NPPD) | Current Study | Upgrade terminal equipment at Cooper 345 kV line to achieve a minimum Spring/Emergency rating of 1295 MVA | 149097.6617 | 4.97% | 3000000
GEN-2017-031 | 09 - Nebraska | 143227 | ERIS | Cooper Joe 345kV New Substation (DISIS-2017-001) | Current Study | Build a new 345 kV substation at Cooper Joe. Tap the Cooper to St. Joe 345kV line 20 miles from St. Joe 345kV | 807307.9435 | 4.97% | 16243869
GEN-2017-031 | 09 - Nebraska | 143212 | ERIS | Cooper Joe to Cooper 345kV Rebuild (DISIS-2017-001) (KCPL) | Current Study | Rebuild Cooper Joe to Cooper 345 kV 22.2 miles line to achieve a minimum Spring/Emergency rating of 1295 MVA | 2009730.0616 | 4.97% | 40437842.97
GEN-2017-031 | 09 - Nebraska | 143214 | ERIS | Cooper Joe to Cooper 345kV Rebuild (DISIS-2017-001) (OPPD) | Current Study | Rebuild Cooper Joe to Cooper 345 kV 26.6 miles line to achieve a minimum Spring/Emergency rating of 1295 MVA | 1473085.4727 | 4.97% | 29640000
GEN-2017-031 | 09 - Nebraska | 143217 | ERIS | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Current Study | Build approximately 6 miles of new 345kV line from Cooper Joe to Hoyt | 691347.1421 | 4.97% | 13910618
GEN-2017-031 | 09 - Nebraska | 143218 | ERIS | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Current Study | Build approximately 60 miles of new 345kV line from Cooper Joe to Hoyt | 6571477.7308 | 4.97% | 132224914
GEN-2017-031 | 09 - Nebraska | 143259 | ERIS | Holt to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Current Study | Build approximately 26 miles of new 345kV line from Holt to Hoyt | 2876066.4011 | 4.91% | 58576716
GEN-2017-031 | 09 - Nebraska | 143225 | ERIS | Holt 345kV Terminal Upgrades (DISIS-2017-001) (TMO) | Current Study | Upgrade terminal equipment at Holt 345kV to accept Holt to Holt new line | 64167.8629 | 4.91% | 1306904
GEN-2017-031 | 09 - Nebraska | 143213 | ERIS | Holt to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Current Study | Build approximately 100 miles of new 345kV line from Holt to Hoyt | 8015814.749 | 4.91% | 163257734
GEN-2017-031 | 09 - Nebraska | 143205 | ERIS | Keystone to Sidney 345kV Ckt 2 (DISIS-2017-001) (NPPD) | Current Study | Build approximately 80 miles of new 345kV line from Keystone to Sidney | 129494671.4397 | 63.79% | 203000000
GEN-2017-031 | 09 - Nebraska | 143234 | ERIS | Keystone to Sidney 345kV Ckt 2 (DISIS-2017-001) (TSGT) | Current Study | Review for potential impacts to TSGT facilities from Keystone to Sidney Ckt 2 | 0 | 63.79% | 0
GEN-2017-031 | 09 - Nebraska | 143252 | ERIS | Potter County 345/230kV Transformer Ckt 2 (DISIS-2017-001) | Current Study | Install a new 345/230kV Transformer at Potter County | 1487931.8665 | 11.82% | 12583652
GEN-2017-031 | 09 - Nebraska | 143231 | ERIS | Sidney 345kV Terminal Upgrades (DISIS-2017-001) (BEPC) | Current Study | Upgrade terminal equipment at Sidney 345kV to accept Keystone to Sidney Ckt 2 | 3509306.8718 | 63.79% | 5501302
GEN-2017-031 | 09 - Nebraska | 143240 | ERIS | Smokey Hils to Summit 230kV Rebuild (DISIS-2017-001) (MIDW) | Current Study | Rebuild the existing Smokey Hills to Summit 230kV 16.1 mile line to achieve a minimum Light/Emergency rating of 375 MVA | 1509498.9566 | 9.148% | 16500000
GEN-2017-031 | 09 - Nebraska | 132979 | ERIS | Wildhorse - Covalt 115 kV GEN-2017-031 Interconnection (Non-Shared NU) (TSGT) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-031 (100 MW/Wind), into the Point of Interconnection (POI) at Wildhorse - Covalt 115 kV. | 736000 | 100% | 736000
GEN-2017-031 | 09 - Nebraska | 132978 | ERIS | Wildhorse - Covalt 115 kV GEN-2017-031 Interconnection (TOIF) (TSGT) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-031 (100 MW/Wind), into the Point of Interconnection (POI) at Wildhorse - Covalt 115 kV. | 3271000 | 100% | 3271000
GEN-2017-032 | 03 - Spearville | 132981 | ERIS | Finney - Lamar 345 kV GEN-2017-032 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-032 (200 MW/Wind), into the Point of Interconnection (POI) at Finney - Lamar 345 kV. | 12750261 | 100% | 12750261
GEN-2017-032 | 03 - Spearville | 132980 | ERIS | Finney - Lamar 345 kV GEN-2017-032 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-032 (200 MW/Wind), into the Point of Interconnection (POI) at Finney - Lamar 345 kV. | 1708037 | 100% | 1708037
GEN-2017-032 | 03 - Spearville | 143263 | ERIS | Finney 345kV Reactive Support (DISIS-2017-001) | Current Study | Install +250 MVAR Capacitor Bank(s) at Finney 345kV | 6122322.1775 | 98.62% | 6207750
GEN-2017-032 | 03 - Spearville | 143228 | ERIS | Finney to G17-032 Tap 345kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Finney to G17-032 Tap 345kV 78.75 mile line to achieve a minimum Summer/Emergency rating of 425 MVA | 150000 | 100% | 150000
GEN-2017-032 | 03 - Spearville | 143240 | ERIS | Smokey Hils to Summit 230kV Rebuild (DISIS-2017-001) (MIDW) | Current Study | Rebuild the existing Smokey Hills to Summit 230kV 16.1 mile line to achieve a minimum Light/Emergency rating of 375 MVA | 2988596.4456 | 18.11% | 16500000
GEN-2017-032 | 03 - Spearville | 143242 | ERIS | Smokey Hils to Summit 230kV Rebuild (DISIS-2017-001) (WERE) | Current Study | Rebuild the existing Smokey Hills to Summit 230kV 22.5 mile line to achieve a minimum Light/Emergency rating of 375 MVA | 7010356.1539 | 25.66% | 27323646
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico | 143204 | ERIS | Crawfish Draw 765/345kV New Substation (DISIS-2017-001) | Current Study | Build a new Crawfish Draw 765/345kV Substation tapping the Tuco to Border 345kV Ckt 1 and Tuco to OKU 345kV Ckt 1. In addition, install a new 1000 MVar SVC for Dynamic Reactive Support at Crawfish Draw 765kV. Both the 765kV and the 345kV Crawfish Draw switchyards shall be constructed with breaker and a half bus schemes. Furthermore, interconnected double circuit lines connected to these switchyards or transformers connecting these switchyards shall not share adjacent breakers in the switchyard(s). | 63143980.1847 | 22.06% | 286282000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico | 143207 | ERIS | Crawfish Draw 765/345kV New Transformer (DISIS-2017-001) | Current Study | Install two new 765/345kV Transformers at Crawfish Draw | 1898312.0714 | 4.746% | 40000000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico | 143219 | ERIS | Crawfish Draw Tap to Tuco to Border 345kV Ckt 1 (DISIS-2017-001) (OKGE) | Current Study | Tap Tuco to Border 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 1724.5438 | 3.449% | 50000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico | 143194 | ERIS | Crawfish Draw Tap to Tuco to Border 345kV Ckt 1 (DISIS-2017-001) (SWPS) | Current Study | Tap Tuco to Border 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 275927 | 3.449% | 8000000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico | 143195 | ERIS | Crawfish Draw Tap to Tuco to OKU 345kV Ckt 1 (DISIS-2017-001) (AEPW) | Current Study | Tap Tuco to OKU 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 286735.3125 | 22.06% | 1300000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico | 143220 | ERIS | Crawfish Draw Tap to Tuco to OKU 345kV Ckt 1 (DISIS-2017-001) (SWPS) | Current Study | Tap Tuco to OKU 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 1764525 | 22.06% | 8000000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico | 143211 | ERIS | Crawfish Draw to Seminole 765kV New Line Double Circuit (DISIS-2017-001) (OKGE) | Current Study | Build approximately 80 miles of new double circuit 765kV line from Crawfish Draw to Seminole | 14117383.9571 | 2.138% | 660408000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico | 143221 | ERIS | Crawfish Draw to Seminole 765kV New Line Double Circuit (DISIS-2017-001) (SWPS) | Current Study | Build approximately 265 miles of new double circuit 765kV line from Crawfish Draw to Seminole | 14151415.7606 | 2.138% | 662000000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico | 143209 | ERIS | Crossroads 765/345kV New Transformer (DISIS-2017-001) | Current Study | Expand Crossroads 765kV Substation and install a new 765/345 transformer | 232324.5692 | 1.162% | 20000000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico | 143325 | ERIS | Crossroads 765kV Reactive Support (DISIS-2017-001) | Current Study | Stability identified need to install 600 MVar SVC for Dynamic Reactive Support at Crossroads 765kV | 1577132.3366 | 1.162% | 135769200
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico | 143210 | ERIS | Crossroads to Crawfish Draw 765kV New Line (DISIS-2017-001) | Current Study | Build approximately 85 miles of new 765kV line from Crossroads to Crawfish Draw | 4414184.424 | 1.162% | 380000000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico | 132983 | ERIS | Oklaunion 345 kV Substation GEN-2017-033 Interconnection (Non-Shared NU) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-033 (200 MW/Wind), into the Point of Interconnection (POI) at Oklaunion 345 kV Substation. | 3877147.5 | 100% | 3877147.5
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico | 132982 | ERIS | Oklaunion 345 kV Substation GEN-2017-033 Interconnection (TOIF) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-033 (200 MW/Wind), into the Point of Interconnection (POI) at Oklaunion 345 kV Substation. | 1373275 | 100% | 1373275
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico | 143208 | ERIS | Seminole 765/345 New Transformer (DISIS-2017-001) | Current Study | Expand Seminole 345kV substation to include a new 765kV switchyard connected by a new 765/345kV transformer. In addition, install a new 600 MVar SVC for Dynamic Reactive Support at Seminole 765kV. | 3418552.7586 | 2.138% | 159919200
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico | 122568 | ERIS | Tolk 345/230 kV CKT 2 Transformer (DISIS-2016-002) | Contingent | Build new 345/230 kV Transformer Ckt 2 at Tolk to achieve a minimum emergency rating of 921 MVA on the Crossroads - Tolk 345 kV Ckt 1 line. | 0 | 0% | 14055360
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico | 143250 | ERIS | Tolk to Tuco 345kV New Line (DISIS-2017-001) | Current Study | Build approximately 54 miles of new 345kV line from Tolk to Tuco | 1219461.6121 | 1.973% | 61799976
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico | 143320 | NRIS | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Current Study | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek | 3679960.9121 | 5.235% | 70295174
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico | 143319 | NRIS | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Current Study | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek | 7329017.0346 | 5.235% | 140000000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico | 143323 | NRIS | Welsh to Wilkes 345kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Welsh to Wilkes 345kV 23.74 mile line to achieve a minimum summer/emergency rating of 972 MVA | 9386159.0215 | 23.35% | 40202865
GEN-2017-036 | 07 - Southwestern Oklahoma | 132985 | ERIS | Snyder - Cache 138 kV GEN-2017-036 Interconnection (Non-Shared NU) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-036 (100 MW/Solar), into the Point of Interconnection (POI) at Snyder 138 kV Substation. | 8198087 | 100% | 8198087
GEN-2017-036 | 07 - Southwestern Oklahoma | 132984 | ERIS | Snyder - Cahce 138 kV GEN-2017-036 Interconnection (TOIF) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-036 (100 MW/Solar), into the Point of Interconnection (POI) at Snyder 138 kV Substation. | 1337068 | 100% | 1337068
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico | 143198 | ERIS | Crawfish Draw 345/230kV Transformer Ckt 1 (DISIS-2017-001) | Current Study | Install a new 345/230kV Transformer at Crawfish Draw | 908241.4263 | 7.946% | 11430070
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico | 143204 | ERIS | Crawfish Draw 765/345kV New Substation (DISIS-2017-001) | Current Study | Build a new Crawfish Draw 765/345kV Substation tapping the Tuco to Border 345kV Ckt 1 and Tuco to OKU 345kV Ckt 1. In addition, install a new 1000 MVar SVC for Dynamic Reactive Support at Crawfish Draw 765kV. Both the 765kV and the 345kV Crawfish Draw switchyards shall be constructed with breaker and a half bus schemes. Furthermore, interconnected double circuit lines connected to these switchyards or transformers connecting these switchyards shall not share adjacent breakers in the switchyard(s). | 13714205.6117 | 4.79% | 286282000
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico | 143207 | ERIS | Crawfish Draw 765/345kV New Transformer (DISIS-2017-001) | Current Study | Install two new 765/345kV Transformers at Crawfish Draw | 3143881.4702 | 7.86% | 40000000
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico | 143219 | ERIS | Crawfish Draw Tap to Tuco to Border 345kV Ckt 1 (DISIS-2017-001) (OKGE) | Current Study | Tap Tuco to Border 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 4008.0188 | 8.016% | 50000
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico | 143194 | ERIS | Crawfish Draw Tap to Tuco to Border 345kV Ckt 1 (DISIS-2017-001) (SWPS) | Current Study | Tap Tuco to Border 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 641283 | 8.016% | 8000000
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico | 143195 | ERIS | Crawfish Draw Tap to Tuco to OKU 345kV Ckt 1 (DISIS-2017-001) (AEPW) | Current Study | Tap Tuco to OKU 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 62275.85 | 4.79% | 1300000
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico | 143220 | ERIS | Crawfish Draw Tap to Tuco to OKU 345kV Ckt 1 (DISIS-2017-001) (SWPS) | Current Study | Tap Tuco to OKU 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 383236 | 4.79% | 8000000
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico | 143211 | ERIS | Crawfish Draw to Seminole 765kV New Line Double Circuit (DISIS-2017-001) (OKGE) | Current Study | Build approximately 80 miles of new double circuit 765kV line from Crawfish Draw to Seminole | 53413407.4812 | 8.088% | 660408000
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico | 143221 | ERIS | Crawfish Draw to Seminole 765kV New Line Double Circuit (DISIS-2017-001) (SWPS) | Current Study | Build approximately 265 miles of new double circuit 765kV line from Crawfish Draw to Seminole | 53542167.4973 | 8.088% | 662000000
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico | 143209 | ERIS | Crossroads 765/345kV New Transformer (DISIS-2017-001) | Current Study | Expand Crossroads 765kV Substation and install a new 765/345 transformer | 1345634.2349 | 6.728% | 20000000
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico | 143325 | ERIS | Crossroads 765kV Reactive Support (DISIS-2017-001) | Current Study | Stability identified need to install 600 MVar SVC for Dynamic Reactive Support at Crossroads 765kV | 9134820.6175 | 6.728% | 135769200
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico | 143325 | ERIS | Crossroads 765kV Reactive Support (DISIS-2017-001) | Current Study | Stability identified need to install 600 MVar SVC for Dynamic Reactive Support at Crossroads 765kV | 1971874.0945 | 1.452% | 135769200
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico | 143210 | ERIS | Crossroads to Crawfish Draw 765kV New Line (DISIS-2017-001) | Current Study | Build approximately 85 miles of new 765kV line from Crossroads to Crawfish Draw | 25567152.4519 | 6.728% | 380000000
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico | 132991 | ERIS | Needmore 230 kV Substation GEN-2017-039 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-039 (200.1 MW/Wind), into the Point of Interconnection (POI) at Needmore 230 kV Substation. | 693659 | 100% | 693659
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico | 132990 | ERIS | Needmore 230 kV Substation GEN-2017-039 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-039 (200.1 MW/Wind), into the Point of Interconnection (POI) at Needmore 230 kV Substation. | 933132 | 100% | 933132
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico | 143208 | ERIS | Seminole 765/345 New Transformer (DISIS-2017-001) | Current Study | Expand Seminole 345kV substation to include a new 765kV switchyard connected by a new 765/345kV transformer. In addition, install a new 600 MVar SVC for Dynamic Reactive Support at Seminole 765kV. | 12934168.9445 | 8.088% | 159919200
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico | 122568 | ERIS | Tolk 345/230 kV CKT 2 Transformer (DISIS-2016-002) | Contingent | Build new 345/230 kV Transformer Ckt 2 at Tolk to achieve a minimum emergency rating of 921 MVA on the Crossroads - Tolk 345 kV Ckt 1 line. | 0 | 0% | 14055360
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico | 143248 | ERIS | Tolk 345/230kV Transformer Ckt 3 (DISIS-2017-001) | Current Study | Install a new 345/230kV Transformer at Tolk | 1577771.2091 | 11.23% | 14055360
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico | 143250 | ERIS | Tolk to Tuco 345kV New Line (DISIS-2017-001) | Current Study | Build approximately 54 miles of new 345kV line from Tolk to Tuco | 6585326.0757 | 10.66% | 61799976
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico | 143251 | ERIS | Tuco to Crawfish Draw 345kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Tuco to Crawfish Draw 345kV 1.54 mile line to achieve a minimum light/emergency rating of 1094 MVA | 175820.8711 | 9.976% | 1762443
GEN-2017-040 | 08 - North Oklahoma/South Central Kansas | 132993 | ERIS | Canadian River - Muskogee - Seminole 345 kV GEN-2017-040 Interconnection (Non-Shared NU) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-040 (200.1 MW/Wind), into the Point of Interconnection (POI) at Canadian River - Muskogee - Seminole 345 kV. | 5741321 | 100% | 5741321
GEN-2017-040 | 08 - North Oklahoma/South Central Kansas | 132992 | ERIS | Canadian River - Muskogee - Seminole 345 kV GEN-2017-040 Interconnection (TOIF) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-040 (200.1 MW/Wind), into the Point of Interconnection (POI) at Canadian River - Muskogee - Seminole 345 kV. | 599979 | 100% | 599979
GEN-2017-047 | 02 - Hitchland | 143192 | ERIS | Beaver County to Clark County 345kV New Line (DISIS-2017-001) (ITCGP) | Current Study | Build approximately 55 miles of new 345kV line from Beaver County to Clark County | 23871692.0017 | 33.4% | 71470025
GEN-2017-047 | 02 - Hitchland | 143191 | ERIS | Beaver County to Clark County 345kV New Line (DISIS-2017-001) (OKGE) | Current Study | Build approximately 70 miles of new 345kV line from Beaver County to Clark County | 30382151.4526 | 33.4% | 90961844
GEN-2017-047 | 02 - Hitchland | 143197 | ERIS | Beaver County to Grapeveine 345kV New Line (DISIS-2017-001) (OKGE) | Current Study | Build approximately 45 miles of new 345kV line from Beaver County to Grapevine | 21091981.0755 | 17.74% | 118875615
GEN-2017-047 | 02 - Hitchland | 143196 | ERIS | Beaver County to Grapeveine 345kV New Line (DISIS-2017-001) (SWPS) | Current Study | Build approximately 45 miles of new 345kV line from Beaver County to Grapevine | 0 | 17.74% | 0
GEN-2017-047 | 02 - Hitchland | 132997 | ERIS | Cole 115 kV Substation GEN-2017-047 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-047 (102 MW/Wind), into the Point of Interconnection (POI) at Cole 115 kV Substation. | 13148764 | 100% | 13148764
GEN-2017-047 | 02 - Hitchland | 132996 | ERIS | Cole 115 kV Substation GEN-2017-047 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-047 (102 MW/Wind), into the Point of Interconnection (POI) at Cole 115 kV Substation. | 759404 | 100% | 759404
GEN-2017-047 | 02 - Hitchland | 143216 | ERIS | Grapevine 345kV New Substation (DISIS-2017-001) | Current Study | Build a new 345kV substation at Grapevine | 6214344.2067 | 33.72% | 18427752
GEN-2017-047 | 02 - Hitchland | 143206 | ERIS | Grapevine to Chisholm 345kV New Line (DISIS-2017-001) (AEPW) | Current Study | Build approximately 35 miles of new 345kV line from Grapevine to Chisholm | 34916478.4109 | 33.72% | 103539840
GEN-2017-047 | 02 - Hitchland | 143203 | ERIS | Grapevine to Chisholm 345kV New Line (DISIS-2017-001) (SWPS) | Current Study | Build approximately 40 miles of new 345kV line from Grapevine to Chisholm | 0 | 33.72% | 0
GEN-2017-047 | 02 - Hitchland | 143245 | ERIS | Potter County to Grapevine 345kV New Line (DISIS-2017-001) | Current Study | Build approximately 65 miles of new 345kV line from Potter County to Grapevine | 19765897.6081 | 21.48% | 92000000
GEN-2017-047 | 02 - Hitchland | 143320 | NRIS | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Current Study | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek | 2086018.0687 | 2.968% | 70295174
GEN-2017-047 | 02 - Hitchland | 143319 | NRIS | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Current Study | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek | 4154517.4867 | 2.968% | 140000000
GEN-2017-048 | 16 - Western North Dakota | 143226 | ERIS | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | Current Study | Replace the existing Broadland 345/230kV Transformer to achieve a minimum Summer/Normal rating of 471 MVA | 3887196.7142 | 65.81% | 5906325
GEN-2017-048 | 16 - Western North Dakota | 143222 | ERIS | MERRCRT4 to Wishek 230kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing MERRCRT4 to Wishek 230kV 29.3 mile line to achieve a minimum Summer/Normal rating of 401 MVA | 5414927.1837 | 60.17% | 9000000
GEN-2017-048 | 16 - Western North Dakota | 143229 | ERIS | Napoleon SW to Wishek 230kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Napoleon SW to Wishek 230kV 24.89 mile line to achieve a minimum Summer/Normal rating of 407 MVA | 4512439.3197 | 60.17% | 7500000
GEN-2017-048 | 16 - Western North Dakota | 132999 | ERIS | Neset 230 kV Substation GEN-2017-048 Interconnection (Non-Shared NU) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-048 (300 MW/Wind), into the Point of Interconnection (POI) at Neset 230 kV Substation. | 1362742 | 100% | 1362742
GEN-2017-048 | 16 - Western North Dakota | 132998 | ERIS | Neset 230 kV Substation GEN-2017-048 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-048 (300 MW/Wind), into the Point of Interconnection (POI) at Neset 230 kV Substation. | 1617104 | 100% | 1617104
GEN-2017-048 | 16 - Western North Dakota | 143236 | ERIS | Neset to Tioga 230kV Rebuild (DISIS-2017-001) (BEPC) | Current Study | Rebuild the existing Neset to Tioga 230kV 1.0 mile line to achieve a minimum Summer/Emergency rating of 725 MVA | 192000 | 100% | 192000
GEN-2017-048 | 16 - Western North Dakota | 143237 | ERIS | Tioga 230kV Terminal Upgrades (DISIS-2017-001) (MDU) | Current Study | Upgrade terminal equipment at Tioga 230kV to achieve a minimum Summer/Emergency rating of 725 MVA | 800000 | 100% | 800000
GEN-2017-048 | 16 - Western North Dakota | 143326 | ERIS | Tioga 230kV Terminal Upgrades for Boundary Dam New Line (DISIS-2017-001) (MDU) | Current Study | Stability identified need to upgrade terminal equipment at Tioga 230kV to accept Boundary Dam CKT 2 | 800000 | 100% | 800000
GEN-2017-048 | 16 - Western North Dakota | 143327 | ERIS | Tioga to Boundary Dam 230kV New Line (DISIS-2017-001) (BEPC) | Current Study | Stability identified need to build approximately 57.5 miles of new 230kV line from Tioga to Boundary Dam (DISIS-2017-001) | 66566945 | 100% | 66566945
GEN-2017-051 | 07 - Southwestern Oklahoma | 133005 | ERIS | Lake Creek SW - Russell SW 69 kV GEN-2017-051 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-051 (30 MW/Solar), into the Point of Interconnection (POI) at Lake Creek SW - Russell SW 69 kV. | 4750000 | 100% | 4750000
GEN-2017-051 | 07 - Southwestern Oklahoma | 133004 | ERIS | Lake Creek SW - Russell SW 69 kV GEN-2017-051 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-051 (30 MW/Solar), into the Point of Interconnection (POI) at Lake Creek SW - Russell SW 69 kV. | 400000 | 100% | 400000
GEN-2017-052 | 03 - Spearville | 133007 | ERIS | Bear Creek - Johnson Corner 115 kV GEN-2017-052 Interconnection (Non-Shared NU) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-052 (25 MW/Solar), into the Point of Interconnection (POI) at Bear Creek - Johnson Corner 115 kV. | 3372070 | 100% | 3372070
GEN-2017-052 | 03 - Spearville | 133006 | ERIS | Bear Creek - Johnson Corner 115 kV GEN-2017-052 Interconnection (TOIF) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-052 (25 MW/Solar), into the Point of Interconnection (POI) at Bear Creek - Johnson Corner 115 kV. | 1662749 | 100% | 1662749
GEN-2017-052 | 03 - Spearville | 143240 | ERIS | Smokey Hils to Summit 230kV Rebuild (DISIS-2017-001) (MIDW) | Current Study | Rebuild the existing Smokey Hills to Summit 230kV 16.1 mile line to achieve a minimum Light/Emergency rating of 375 MVA | 358869.498 | 2.175% | 16500000
GEN-2017-052 | 03 - Spearville | 143242 | ERIS | Smokey Hils to Summit 230kV Rebuild (DISIS-2017-001) (WERE) | Current Study | Rebuild the existing Smokey Hills to Summit 230kV 22.5 mile line to achieve a minimum Light/Emergency rating of 375 MVA | 841800.8385 | 3.081% | 27323646
GEN-2017-055 | 09 - Nebraska | 143215 | ERIS | Cooper 345kV Terminal Upgrades (DISIS-2017-001) (NPPD) | Current Study | Upgrade terminal equipment at Cooper 345 kV line to achieve a minimum Spring/Emergency rating of 1295 MVA | 786595.7252 | 26.22% | 3000000
GEN-2017-055 | 09 - Nebraska | 143227 | ERIS | Cooper Joe 345kV New Substation (DISIS-2017-001) | Current Study | Build a new 345 kV substation at Cooper Joe. Tap the Cooper to St. Joe 345kV line 20 miles from St. Joe 345kV | 4259119.4236 | 26.22% | 16243869
GEN-2017-055 | 09 - Nebraska | 143212 | ERIS | Cooper Joe to Cooper 345kV Rebuild (DISIS-2017-001) (KCPL) | Current Study | Rebuild Cooper Joe to Cooper 345 kV 22.2 miles line to achieve a minimum Spring/Emergency rating of 1295 MVA | 10602745.0999 | 26.22% | 40437842.97
GEN-2017-055 | 09 - Nebraska | 143214 | ERIS | Cooper Joe to Cooper 345kV Rebuild (DISIS-2017-001) (OPPD) | Current Study | Rebuild Cooper Joe to Cooper 345 kV 26.6 miles line to achieve a minimum Spring/Emergency rating of 1295 MVA | 7771565.9808 | 26.22% | 29640000
GEN-2017-055 | 09 - Nebraska | 143217 | ERIS | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Current Study | Build approximately 6 miles of new 345kV line from Cooper Joe to Hoyt | 3647344.3192 | 26.22% | 13910618
GEN-2017-055 | 09 - Nebraska | 143218 | ERIS | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Current Study | Build approximately 60 miles of new 345kV line from Cooper Joe to Hoyt | 34669185.0018 | 26.22% | 132224914
GEN-2017-055 | 09 - Nebraska | 143259 | ERIS | Holt to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Current Study | Build approximately 26 miles of new 345kV line from Holt to Hoyt | 15144485.0091 | 25.85% | 58576716
GEN-2017-055 | 09 - Nebraska | 143225 | ERIS | Holt 345kV Terminal Upgrades (DISIS-2017-001) (TMO) | Current Study | Upgrade terminal equipment at Holt 345kV to accept Holt to Holt new line | 337888.3179 | 25.85% | 1306904
GEN-2017-055 | 09 - Nebraska | 143213 | ERIS | Holt to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Current Study | Build approximately 100 miles of new 345kV line from Holt to Hoyt | 42208823.7826 | 25.85% | 163257734
GEN-2017-055 | 09 - Nebraska | 143252 | ERIS | Potter County 345/230kV Transformer Ckt 2 (DISIS-2017-001) | Current Study | Install a new 345/230kV Transformer at Potter County | 2517313.5894 | 20% | 12583652
GEN-2017-055 | 09 - Nebraska | 133011 | ERIS | Wagener 115 kV Substation GEN-2017-055 Interconnection (Non-Shared NU) (LES) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-055 (228.3 MW/Solar), into the Point of Interconnection (POI) at Wagener 115 kV Substation. | 1080000 | 100% | 1080000
GEN-2017-055 | 09 - Nebraska | 133010 | ERIS | Wagener 115 kV Substation GEN-2017-055 Interconnection (TOIF) (LES) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-055 (228.3 MW/Solar), into the Point of Interconnection (POI) at Wagener 115 kV Substation. | 250000 | 100% | 250000
GEN-2017-055 | 09 - Nebraska | 143317 | NRIS | Mark Moore to Monolith 345kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Mark Moore to Monolith 345kV .75 mile line to achieve a minimum winter/normal rating of 1108 MVA | 2780510.0953 | 63.19% | 4400000
GEN-2017-055 | 09 - Nebraska | 143320 | NRIS | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Current Study | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek | 19326271.1039 | 27.49% | 70295174
GEN-2017-055 | 09 - Nebraska | 143319 | NRIS | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Current Study | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek | 38490237.6734 | 27.49% | 140000000
GEN-2017-057 | 10 - Southeast Oklahoma/Northeast Texas | 133013 | ERIS | Hosston 69 kV Substation GEN-2017-057 Interconnection (Non-Shared NU) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-057 (72.5 MW/Solar), into the Point of Interconnection (POI) at Houston 69 kV Substation. | 17032809 | 100% | 17032809
GEN-2017-057 | 10 - Southeast Oklahoma/Northeast Texas | 133012 | ERIS | Hosston 69 kV Substation GEN-2017-057 Interconnection (TOIF) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-057 (72.5 MW/Solar), into the Point of Interconnection (POI) at Houston 69 kV Substation. | 1120262 | 100% | 1120262
GEN-2017-058 | 02 - Hitchland | 143192 | ERIS | Beaver County to Clark County 345kV New Line (DISIS-2017-001) (ITCGP) | Current Study | Build approximately 55 miles of new 345kV line from Beaver County to Clark County | 23390760.4778 | 32.73% | 71470025
GEN-2017-058 | 02 - Hitchland | 143191 | ERIS | Beaver County to Clark County 345kV New Line (DISIS-2017-001) (OKGE) | Current Study | Build approximately 70 miles of new 345kV line from Beaver County to Clark County | 29770056.8263 | 32.73% | 90961844
GEN-2017-058 | 02 - Hitchland | 143197 | ERIS | Beaver County to Grapeveine 345kV New Line (DISIS-2017-001) (OKGE) | Current Study | Build approximately 45 miles of new 345kV line from Beaver County to Grapevine | 73002079.7324 | 61.41% | 118875615
GEN-2017-058 | 02 - Hitchland | 143196 | ERIS | Beaver County to Grapeveine 345kV New Line (DISIS-2017-001) (SWPS) | Current Study | Build approximately 45 miles of new 345kV line from Beaver County to Grapevine | 0 | 61.41% | 0
GEN-2017-058 | 02 - Hitchland | 143216 | ERIS | Grapevine 345kV New Substation (DISIS-2017-001) | Current Study | Build a new 345kV substation at Grapevine | 5883988.0144 | 31.93% | 18427752
GEN-2017-058 | 02 - Hitchland | 143206 | ERIS | Grapevine to Chisholm 345kV New Line (DISIS-2017-001) (AEPW) | Current Study | Build approximately 35 miles of new 345kV line from Grapevine to Chisholm | 33060309.1233 | 31.93% | 103539840
GEN-2017-058 | 02 - Hitchland | 143203 | ERIS | Grapevine to Chisholm 345kV New Line (DISIS-2017-001) (SWPS) | Current Study | Build approximately 40 miles of new 345kV line from Grapevine to Chisholm | 0 | 31.93% | 0
GEN-2017-058 | 02 - Hitchland | 133015 | ERIS | Hereford Northeast 115 kV Substation GEN-2017-058 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-058 (135 MW/Solar), into the Point of Interconnection (POI) at Hereford Northeast 115 kV Substation. | 1419861 | 100% | 1419861
GEN-2017-058 | 02 - Hitchland | 133014 | ERIS | Hereford Northeast 115 kV Substation GEN-2017-058 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-058 (135 MW/Solar), into the Point of Interconnection (POI) at Hereford Northeast 115 kV Substation. | 701784 | 100% | 701784
GEN-2017-058 | 02 - Hitchland | 143245 | ERIS | Potter County to Grapevine 345kV New Line (DISIS-2017-001) | Current Study | Build approximately 65 miles of new 345kV line from Potter County to Grapevine | 53332986.8873 | 57.97% | 92000000
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico | 143204 | ERIS | Crawfish Draw 765/345kV New Substation (DISIS-2017-001) | Current Study | Build a new Crawfish Draw 765/345kV Substation tapping the Tuco to Border 345kV Ckt 1 and Tuco to OKU 345kV Ckt 1. In addition, install a new 1000 MVar SVC for Dynamic Reactive Support at Crawfish Draw 765kV. Both the 765kV and the 345kV Crawfish Draw switchyards shall be constructed with breaker and a half bus schemes. Furthermore, interconnected double circuit lines connected to these switchyards or transformers connecting these switchyards shall not share adjacent breakers in the switchyard(s). | 6792555.7576 | 2.373% | 286282000
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico | 143207 | ERIS | Crawfish Draw 765/345kV New Transformer (DISIS-2017-001) | Current Study | Install two new 765/345kV Transformers at Crawfish Draw | 2536822.3569 | 6.342% | 40000000
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico | 143219 | ERIS | Crawfish Draw Tap to Tuco to Border 345kV Ckt 1 (DISIS-2017-001) (OKGE) | Current Study | Tap Tuco to Border 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 2012.8312 | 4.026% | 50000
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico | 143194 | ERIS | Crawfish Draw Tap to Tuco to Border 345kV Ckt 1 (DISIS-2017-001) (SWPS) | Current Study | Tap Tuco to Border 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 322053 | 4.026% | 8000000
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico | 143195 | ERIS | Crawfish Draw Tap to Tuco to OKU 345kV Ckt 1 (DISIS-2017-001) (AEPW) | Current Study | Tap Tuco to OKU 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 30844.775 | 2.373% | 1300000
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico | 143220 | ERIS | Crawfish Draw Tap to Tuco to OKU 345kV Ckt 1 (DISIS-2017-001) (SWPS) | Current Study | Tap Tuco to OKU 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 189814 | 2.373% | 8000000
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico | 143211 | ERIS | Crawfish Draw to Seminole 765kV New Line Double Circuit (DISIS-2017-001) (OKGE) | Current Study | Build approximately 80 miles of new double circuit 765kV line from Crawfish Draw to Seminole | 25002315.471 | 3.786% | 660408000
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico | 143221 | ERIS | Crawfish Draw to Seminole 765kV New Line Double Circuit (DISIS-2017-001) (SWPS) | Current Study | Build approximately 265 miles of new double circuit 765kV line from Crawfish Draw to Seminole | 25062586.8278 | 3.786% | 662000000
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico | 143209 | ERIS | Crossroads 765/345kV New Transformer (DISIS-2017-001) | Current Study | Expand Crossroads 765kV Substation and install a new 765/345 transformer | 43151.5601 | 0.2158% | 20000000
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico | 143325 | ERIS | Crossroads 765kV Reactive Support (DISIS-2017-001) | Current Study | Stability identified need to install 600 MVar SVC for Dynamic Reactive Support at Crossroads 765kV | 292735.3435 | 0.2156% | 135769200
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico | 143210 | ERIS | Crossroads to Crawfish Draw 765kV New Line (DISIS-2017-001) | Current Study | Build approximately 85 miles of new 765kV line from Crossroads to Crawfish Draw | 819327.4361 | 0.2156% | 380000000
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico | 143208 | ERIS | Seminole 765/345 New Transformer (DISIS-2017-001) | Current Study | Expand Seminole 345kV substation to include a new 765kV switchyard connected by a new 765/345kV transformer. In addition, install a new 600 MVar SVC for Dynamic Reactive Support at Seminole 765kV. | 6054365.0009 | 3.786% | 159919200
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico | 133017 | ERIS | Tuco 230 kV Substation GEN-2017-059 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-059 (90 MW/Solar), into the Point of Interconnection (POI) at Tuco 230 kV Substation. | 849034 | 100% | 849034
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico | 133016 | ERIS | Tuco 230 kV Substation GEN-2017-059 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-059 (90 MW/Solar), into the Point of Interconnection (POI) at Tuco 230 kV Substation. | 1231645 | 100% | 1231645
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico | 143251 | ERIS | Tuco to Crawfish Draw 345kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Tuco to Crawfish Draw 345kV 1.54 mile line to achieve a minimum light/emergency rating of 1094 MVA | 88297.4272 | 5.01% | 1762443
GEN-2017-060 | 12 - Northwest Arkansas | 133019 | ERIS | LaRussell Energy Center 161 kV Substation GEN-2017-060 Interconnection (Non-Shared NU) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-060 (149.4 MW/Wind), into the Point of Interconnection (POI) at LaRussell Energy Center 161 kV Substation. | 0 | 100% | 0
GEN-2017-060 | 12 - Northwest Arkansas | 133018 | ERIS | LaRussell Energy Center 161 kV Substation GEN-2017-060 Interconnection (TOIF) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-060 (149.4 MW/Wind), into the Point of Interconnection (POI) at LaRussell Energy Center 161 kV Substation. | 0 | 100% | 0
GEN-2017-061 | 08 - North Oklahoma/South Central Kansas | 143190 | ERIS | Afton to Ketchum 161kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Afton to Ketchum 161kV 12.8 mile line to achieve a minimum Summer/Emergency rating of 225 MVA | 360374.6016 | 39.78% | 906000
GEN-2017-061 | 08 - North Oklahoma/South Central Kansas | 133021 | ERIS | GRDA1 - CLARMR5 161 kV GEN-2017-061 Interconnection (Non-Shared NU) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-061 (101.5 MW/Solar), into the Point of Interconnection (POI) at GRDA1 - CLARMR5 161 kV. | 0 | 100% | 0
GEN-2017-061 | 08 - North Oklahoma/South Central Kansas | 133020 | ERIS | GRDA1 - CLARMR5 161 kV GEN-2017-061 Interconnection (TOIF) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-061 (101.5 MW/Solar), into the Point of Interconnection (POI) at GRDA1 - CLARMR5 161 kV. | 4548000 | 100% | 4548000
GEN-2017-061 | 08 - North Oklahoma/South Central Kansas | 143247 | ERIS | Pensacola to Ketchum 161kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Pensacole to Ketchum 161kV 4.8 mile line to achieve a minimum Summer/Emergency rating of 225 MVA | 690519.1041 | 39.78% | 1736000
GEN-2017-061 | 08 - North Oklahoma/South Central Kansas | 143320 | NRIS | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Current Study | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek | 1330167.2648 | 1.892% | 70295174
GEN-2017-061 | 08 - North Oklahoma/South Central Kansas | 143319 | NRIS | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Current Study | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek | 2649163.6122 | 1.892% | 140000000
GEN-2017-064 | 17 - Western South Dakota | 143224 | ERIS | G17-014 Tap to Philip Tap 230kV New Line (DISIS-2017-001) | Current Study | Convert existing Philip Tap to a ring bus substation and build approximately 6 miles of new 230kV from new substation to G17-014 Tap creating a double circuit 230kV line. | 11328827.7577 | 39.45% | 28715520
GEN-2017-064 | 17 - Western South Dakota | 143205 | ERIS | Keystone to Sidney 345kV Ckt 2 (DISIS-2017-001) (NPPD) | Current Study | Build approximately 80 miles of new 345kV line from Keystone to Sidney | 73505328.5603 | 36.21% | 203000000
GEN-2017-064 | 17 - Western South Dakota | 143234 | ERIS | Keystone to Sidney 345kV Ckt 2 (DISIS-2017-001) (TSGT) | Current Study | Review for potential impacts to TSGT facilities from Keystone to Sidney Ckt 2 | 0 | 36.21% | 0
GEN-2017-064 | 17 - Western South Dakota | 143231 | ERIS | Sidney 345kV Terminal Upgrades (DISIS-2017-001) (BEPC) | Current Study | Upgrade terminal equipment at Sidney 345kV to accept Keystone to Sidney Ckt 2 | 1991995.1282 | 36.21% | 5501302
GEN-2017-064 | 17 - Western South Dakota | 133023 | ERIS | Underwoord - Wayside 230 kV GEN-2017-064 Interconnection (Non-Shared NU) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-064 (110 MW/Solar), into the Point of Interconnection (POI) at Underwood - Wayside 230 kV. | 7102723 | 100% | 7102723
GEN-2017-064 | 17 - Western South Dakota | 133022 | ERIS | Underwoord - Wayside 230 kV GEN-2017-064 Interconnection (TOIF) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-064 (110 MW/Solar), into the Point of Interconnection (POI) at Underwood - Wayside 230 kV. | 311770 | 100% | 311770
GEN-2017-064 | 17 - Western South Dakota | 143312 | NRIS | Beulah 115kV Terminal Upgrades (DISIS-2017-001) (MDU) | Current Study | Upgrade terminal equipment at Beulah 115kV to achieve a minimum winter/emergency rating of 171 MVA | 80543.9331 | 32.22% | 250000
GEN-2017-064 | 17 - Western South Dakota | 143299 | NRIS | G17-064 Tap to Wayside 230kV Rebuild (DISIS-2017-001) (WAPA) | Current Study | Rebuild the existing G17-064 Tap to Wayside 230kV 38.05 mile line to achieve a minimum summer/emergency rating of 377 MVA | 0 | 47.97% | 0
GEN-2017-064 | 17 - Western South Dakota | 143304 | NRIS | Martin to Vetal Tap 115kV Rebuild (DISIS-2017-001) (WAPA) | Current Study | Rebuild the existing Martin to Vetal Tap 115kV 16.67 mile line to achieve a minimum summer/emergency rating of 95 MVA | 54315.1683 | 31.2% | 174097
GEN-2017-064 | 17 - Western South Dakota | 143316 | NRIS | Mission to Vetal Tap 115kV Rebuild (DISIS-2017-001) (WAPA) | Current Study | Rebuild the existing Mission to Vetal Tap 115kV 37.87 mile line to achieve a minimum summer/normal rating of 92 MVA | 184069.509 | 31.2% | 590000
GEN-2017-064 | 17 - Western South Dakota | 143320 | NRIS | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Current Study | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek | 5417096.5095 | 7.706% | 70295174
GEN-2017-064 | 17 - Western South Dakota | 143319 | NRIS | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Current Study | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek | 10788699.5391 | 7.706% | 140000000
GEN-2017-064 | 17 - Western South Dakota | 143302 | NRIS | Scottsbluff to Victory Hill 115kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Scottsbluff to Victory Hill 115kV 8.09 mile line to achieve a minimum summer/emergency rating of 177 MVA | 1385189.925 | 41.98% | 3300000
GEN-2017-064 | 17 - Western South Dakota | 143311 | NRIS | Stanton 115kV Terminal Upgrades (DISIS-2017-001) (BEPC) | Current Study | Upgrade terminal equipment at Stanton 115kV to achieve a minimum winter/emergency rating of 171 MVA | 8892.0502 | 32.22% | 27600
GEN-2017-064 | 17 - Western South Dakota | 143310 | NRIS | Stanton to Beulah 115kV Rebuild (DISIS-2017-001) (WAPA) | Current Study | Rebuild the existing Stanton to Beulah 115kV 13.41 mile line to achieve a minimum winter/emergency rating of 171 MVA | 1907280.3347 | 32.22% | 5920000
GEN-2017-064 | 17 - Western South Dakota | 143315 | NRIS | Vetal Tap Terminal Upgrades for Martin Rebuild (DISIS-2017-001) (BEPC) | Current Study | Upgrade terminal equipment at Vetal Tap 115kV to achieve a minimum summer/emergency rating of 95 MVA | 0 | 31.2% | 0
GEN-2017-064 | 17 - Western South Dakota | 143305 | NRIS | Vetal Tap Terminal Upgrades for Mission Rebuild (DISIS-2017-001) (BEPC) | Current Study | Upgrade terminal equipment at Vetal Tap 115kV 37.87 mile line to achieve a minimum summer/normal rating of 92 MVA | 0 | 31.2% | 0
GEN-2017-064 | 17 - Western South Dakota | 143298 | NRIS | Wayside 230kV Terminal Upgrades (DISIS-2017-001) (NPPD) | Current Study | Upgrade terminal equipment at Wayside 230kV to accept Wayside to Shannon new line | 3224481.2647 | 47.97% | 6721188
GEN-2017-064 | 17 - Western South Dakota | 143322 | NRIS | Wayside to Shannon 230kV New Line (DISIS-2017-001) (BEPC) | Current Study | Build approximately 54 miles of new 345kV line from Wayside to Shannon and install a 230/115kV transformer | 64357277.705 | 95.17% | 67621351
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico | 143204 | ERIS | Crawfish Draw 765/345kV New Substation (DISIS-2017-001) | Current Study | Build a new Crawfish Draw 765/345kV Substation tapping the Tuco to Border 345kV Ckt 1 and Tuco to OKU 345kV Ckt 1. In addition, install a new 1000 MVar SVC for Dynamic Reactive Support at Crawfish Draw 765kV. Both the 765kV and the 345kV Crawfish Draw switchyards shall be constructed with breaker and a half bus schemes. Furthermore, interconnected double circuit lines connected to these switchyards or transformers connecting these switchyards shall not share adjacent breakers in the switchyard(s). | 63238691.813 | 22.09% | 286282000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico | 143207 | ERIS | Crawfish Draw 765/345kV New Transformer (DISIS-2017-001) | Current Study | Install two new 765/345kV Transformers at Crawfish Draw | 1901159.5395 | 4.753% | 40000000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico | 143219 | ERIS | Crawfish Draw Tap to Tuco to Border 345kV Ckt 1 (DISIS-2017-001) (OKGE) | Current Study | Tap Tuco to Border 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 1727.1312 | 3.454% | 50000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico | 143194 | ERIS | Crawfish Draw Tap to Tuco to Border 345kV Ckt 1 (DISIS-2017-001) (SWPS) | Current Study | Tap Tuco to Border 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 276341 | 3.454% | 8000000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico | 143195 | ERIS | Crawfish Draw Tap to Tuco to OKU 345kV Ckt 1 (DISIS-2017-001) (AEPW) | Current Study | Tap Tuco to OKU 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 287165.45 | 22.09% | 1300000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico | 143220 | ERIS | Crawfish Draw Tap to Tuco to OKU 345kV Ckt 1 (DISIS-2017-001) (SWPS) | Current Study | Tap Tuco to OKU 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 1767172 | 22.09% | 8000000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico | 143211 | ERIS | Crawfish Draw to Seminole 765kV New Line Double Circuit (DISIS-2017-001) (OKGE) | Current Study | Build approximately 80 miles of new double circuit 765kV line from Crawfish Draw to Seminole | 14138560.0331 | 2.141% | 660408000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico | 143221 | ERIS | Crawfish Draw to Seminole 765kV New Line Double Circuit (DISIS-2017-001) (SWPS) | Current Study | Build approximately 265 miles of new double circuit 765kV line from Crawfish Draw to Seminole | 14172642.8842 | 2.141% | 662000000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico | 143209 | ERIS | Crossroads 765/345kV New Transformer (DISIS-2017-001) | Current Study | Expand Crossroads 765kV Substation and install a new 765/345 transformer | 232673.0561 | 1.163% | 20000000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico | 143325 | ERIS | Crossroads 765kV Reactive Support (DISIS-2017-001) | Current Study | Stability identified need to install 600 MVar SVC for Dynamic Reactive Support at Crossroads 765kV | 1579498.0351 | 1.163% | 135769200
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico | 143210 | ERIS | Crossroads to Crawfish Draw 765kV New Line (DISIS-2017-001) | Current Study | Build approximately 85 miles of new 765kV line from Crossroads to Crawfish Draw | 4420805.7006 | 1.163% | 380000000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico | 133025 | ERIS | Oklaunion 345 kV Substation GEN-2017-065 Interconnection (Non-Shared NU) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-065 (200.3 MW/Solar), into the Point of Interconnection (POI) at Oklaunion 345 kV Substation. | 3877147.5 | 100% | 3877147.5
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico | 133024 | ERIS | Oklaunion 345 kV Substation GEN-2017-065 Interconnection (TOIF) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-065 (200.3 MW/Solar), into the Point of Interconnection (POI) at Oklaunion 345 kV Substation. | 1373275 | 100% | 1373275
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico | 143208 | ERIS | Seminole 765/345 New Transformer (DISIS-2017-001) | Current Study | Expand Seminole 345kV substation to include a new 765kV switchyard connected by a new 765/345kV transformer. In addition, install a new 600 MVar SVC for Dynamic Reactive Support at Seminole 765kV. | 3423686.1649 | 2.141% | 159919200
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico | 122568 | ERIS | Tolk 345/230 kV CKT 2 Transformer (DISIS-2016-002) | Contingent | Build new 345/230 kV Transformer Ckt 2 at Tolk to achieve a minimum emergency rating of 921 MVA on the Crossroads - Tolk 345 kV Ckt 1 line. | 0 | 0% | 14055360
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico | 143250 | ERIS | Tolk to Tuco 345kV New Line (DISIS-2017-001) | Current Study | Build approximately 54 miles of new 345kV line from Tolk to Tuco | 1221290.8045 | 1.976% | 61799976
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico | 143320 | NRIS | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Current Study | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek | 3685480.8535 | 5.243% | 70295174
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico | 143319 | NRIS | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Current Study | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek | 7340010.5601 | 5.243% | 140000000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico | 143323 | NRIS | Welsh to Wilkes 345kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Welsh to Wilkes 345kV 23.74 mile line to achieve a minimum summer/emergency rating of 972 MVA | 9400238.26 | 23.38% | 40202865
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas | 143246 | ERIS | Neosho to G17-009 Tap Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Neosho to G17-009 345kV 18.17 mile line to achieve a minimum Winter/Emergency rating of 1260 MVA | 1075391.9902 | 3.27% | 32884027
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas | 133031 | ERIS | Wichita 345 kV Substation GEN-2017-068 Interconnection (Non-Shared NU) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-068 (103.5 MW/Solar), into the Point of Interconnection (POI) at Wichita 345 kV Substation. | 15017048 | 100% | 15017048
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas | 133030 | ERIS | Wichita 345 kV Substation GEN-2017-068 Interconnection (TOIF) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-068 (103.5 MW/Solar), into the Point of Interconnection (POI) at Wichita 345 kV Substation. | 1311181 | 100% | 1311181
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas | 122598 | ERIS | Wolf Creek to Blackberry 345kV | Contingent | Build a new 86 mile 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 0% | 142601178
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas | 143292 | NRIS | Benton 345/138kV Transformer Ckt 3 (DISIS-2017-001) | Current Study | Install a new 345/138kV Transformer at Benton | 8302968 | 100% | 8302968
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas | 143293 | NRIS | Gordon Evans to Maize 138kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Gordon Evans to Maize 138kV 4.9 mile line to achieve a minimum summer/emergency rating of 387 MVA | 2338290 | 100% | 2338290
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas | 143317 | NRIS | Mark Moore to Monolith 345kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Mark Moore to Monolith 345kV .75 mile line to achieve a minimum winter/normal rating of 1108 MVA | 374394.9638 | 8.509% | 4400000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas | 143320 | NRIS | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Current Study | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek | 4286468.3682 | 6.098% | 70295174
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas | 143319 | NRIS | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Current Study | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek | 8536938.4184 | 6.098% | 140000000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas | 143294 | NRIS | Wichita 345/138kV Tansformer Ckt 3 (DISIS-2017-001) | Current Study | Install a new 345/138kV Transformer at Wichita | 8302968 | 100% | 8302968
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico | 143198 | ERIS | Crawfish Draw 345/230kV Transformer Ckt 1 (DISIS-2017-001) | Current Study | Install a new 345/230kV Transformer at Crawfish Draw | 17205.1989 | 0.1505% | 11430070
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico | 143204 | ERIS | Crawfish Draw 765/345kV New Substation (DISIS-2017-001) | Current Study | Build a new Crawfish Draw 765/345kV Substation tapping the Tuco to Border 345kV Ckt 1 and Tuco to OKU 345kV Ckt 1. In addition, install a new 1000 MVar SVC for Dynamic Reactive Support at Crawfish Draw 765kV. Both the 765kV and the 345kV Crawfish Draw switchyards shall be constructed with breaker and a half bus schemes. Furthermore, interconnected double circuit lines connected to these switchyards or transformers connecting these switchyards shall not share adjacent breakers in the switchyard(s). | 236402.1329 | 0.08258% | 286282000
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico | 143207 | ERIS | Crawfish Draw 765/345kV New Transformer (DISIS-2017-001) | Current Study | Install two new 765/345kV Transformers at Crawfish Draw | 52965.4542 | 0.1324% | 40000000
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico | 143219 | ERIS | Crawfish Draw Tap to Tuco to Border 345kV Ckt 1 (DISIS-2017-001) (OKGE) | Current Study | Tap Tuco to Border 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 68.2562 | 0.1365% | 50000
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico | 143194 | ERIS | Crawfish Draw Tap to Tuco to Border 345kV Ckt 1 (DISIS-2017-001) (SWPS) | Current Study | Tap Tuco to Border 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 10921 | 0.1365% | 8000000
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico | 143195 | ERIS | Crawfish Draw Tap to Tuco to OKU 345kV Ckt 1 (DISIS-2017-001) (AEPW) | Current Study | Tap Tuco to OKU 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 1073.475 | 0.08257% | 1300000
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico | 143220 | ERIS | Crawfish Draw Tap to Tuco to OKU 345kV Ckt 1 (DISIS-2017-001) (SWPS) | Current Study | Tap Tuco to OKU 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 6606 | 0.08257% | 8000000
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico | 143211 | ERIS | Crawfish Draw to Seminole 765kV New Line Double Circuit (DISIS-2017-001) (OKGE) | Current Study | Build approximately 80 miles of new double circuit 765kV line from Crawfish Draw to Seminole | 930800.1684 | 0.1409% | 660408000
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico | 143221 | ERIS | Crawfish Draw to Seminole 765kV New Line Double Circuit (DISIS-2017-001) (SWPS) | Current Study | Build approximately 265 miles of new double circuit 765kV line from Crawfish Draw to Seminole | 933043.9842 | 0.1409% | 662000000
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico | 143209 | ERIS | Crossroads 765/345kV New Transformer (DISIS-2017-001) | Current Study | Expand Crossroads 765kV Substation and install a new 765/345 transformer | 24452.5507 | 0.1223% | 20000000
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico | 143325 | ERIS | Crossroads 765kV Reactive Support (DISIS-2017-001) | Current Study | Stability identified need to install 600 MVar SVC for Dynamic Reactive Support at Crossroads 765kV | 165987.886 | 0.1223% | 135769200
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico | 143210 | ERIS | Crossroads to Crawfish Draw 765kV New Line (DISIS-2017-001) | Current Study | Build approximately 85 miles of new 765kV line from Crossroads to Crawfish Draw | 464578.0979 | 0.1223% | 380000000
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico | 133033 | ERIS | Norton 115 kV Switching Station GEN-2017-069 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-069 (3.6 MW/Solar), into the Point of Interconnection (POI) at Norton 115 kV Switching Station. | 0 | 100% | 0
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico | 133032 | ERIS | Norton 115 kV Switching Station GEN-2017-069 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-069 (3.6 MW/Solar), into the Point of Interconnection (POI) at Norton 115 kV Switching Station. | 0 | 100% | 0
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico | 143241 | ERIS | Norton to Pleasant Hills 115kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Norton to Pleasant Hills 115kV 54.54 mile line to achieve a minimum Light/Emergency rating of 150 MVA | 14754.0984 | 9.836% | 150000
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico | 143208 | ERIS | Seminole 765/345 New Transformer (DISIS-2017-001) | Current Study | Expand Seminole 345kV substation to include a new 765kV switchyard connected by a new 765/345kV transformer. In addition, install a new 600 MVar SVC for Dynamic Reactive Support at Seminole 765kV. | 225398.1164 | 0.1409% | 159919200
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico | 122568 | ERIS | Tolk 345/230 kV CKT 2 Transformer (DISIS-2016-002) | Contingent | Build new 345/230 kV Transformer Ckt 2 at Tolk to achieve a minimum emergency rating of 921 MVA on the Crossroads - Tolk 345 kV Ckt 1 line. | 0 | 0% | 14055360
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico | 143248 | ERIS | Tolk 345/230kV Transformer Ckt 3 (DISIS-2017-001) | Current Study | Install a new 345/230kV Transformer at Tolk | 26406.1436 | 0.1879% | 14055360
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico | 143250 | ERIS | Tolk to Tuco 345kV New Line (DISIS-2017-001) | Current Study | Build approximately 54 miles of new 345kV line from Tolk to Tuco | 111947.6552 | 0.1811% | 61799976
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico | 143251 | ERIS | Tuco to Crawfish Draw 345kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Tuco to Crawfish Draw 345kV 1.54 mile line to achieve a minimum light/emergency rating of 1094 MVA | 2994.2159 | 0.1699% | 1762443
GEN-2017-071 | 08 - North Oklahoma/South Central Kansas | 133035 | ERIS | Greenwood 138 kV Substation GEN-2017-071 Interconnection (Non-Shared NU) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-071 (124.7 MW/Solar), into the Point of Interconnection (POI) at Greenwood 138 kV Substation. | 1721000 | 100% | 1721000
GEN-2017-071 | 08 - North Oklahoma/South Central Kansas | 133034 | ERIS | Greenwood 138 kV Substation GEN-2017-071 Interconnection (TOIF) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-071 (124.7 MW/Solar), into the Point of Interconnection (POI) at Greenwood 138 kV Substation. | 515000 | 100% | 515000
GEN-2017-071 | 08 - North Oklahoma/South Central Kansas | 122598 | ERIS | Wolf Creek to Blackberry 345kV | Contingent | Build a new 86 mile 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 0% | 142601178
GEN-2017-072 | 08 - North Oklahoma/South Central Kansas | 133037 | ERIS | Greenwood 138 kV Substation GEN-2017-072 Interconnection (Non-Shared NU) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-072 (52.2 MW/Solar), into the Point of Interconnection (POI) at Greenwood 138 kV Substation. | 1721000 | 100% | 1721000
GEN-2017-072 | 08 - North Oklahoma/South Central Kansas | 133036 | ERIS | Greenwood 138 kV Substation GEN-2017-072 Interconnection (TOIF) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-072 (52.2 MW/Solar), into the Point of Interconnection (POI) at Greenwood 138 kV Substation. | 515000 | 100% | 515000
GEN-2017-072 | 08 - North Oklahoma/South Central Kansas | 122598 | ERIS | Wolf Creek to Blackberry 345kV | Contingent | Build a new 86 mile 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 0% | 142601178
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas | 143190 | ERIS | Afton to Ketchum 161kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Afton to Ketchum 161kV 12.8 mile line to achieve a minimum Summer/Emergency rating of 225 MVA | 545625.3984 | 60.22% | 906000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas | 143265 | ERIS | Beaver to Eureka 161kV Rebuild (DISIS-2017-001) (AEP) | Current Study | Rebuild the existing Beaver to Eureka 161kV 1.22 mile line section to achieve a minimum light/emergency rating of 258 MVA | 0 | 24.89% | 0
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas | 143264 | ERIS | Beaver to Eureka 161kV Rebuild (DISIS-2017-001) (SWPA) | Current Study | Rebuild the existing Beaver to Eureka 161kV 6 mile line section to achieve a minimum light/emergency rating of 258 MVA | 1460822.3081 | 24.89% | 5869344
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas | 133039 | ERIS | Dry Gulch 161 kV Substation GEN-2017-073 Interconnection (Non-Shared NU) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-073 (72.5 MW/Solar), into the Point of Interconnection (POI) at Dry Gulch 161 kV Substation. | 50000 | 100% | 50000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas | 133038 | ERIS | Dry Gulch 161 kV Substation GEN-2017-073 Interconnection (TOIF) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-073 (72.5 MW/Solar), into the Point of Interconnection (POI) at Dry Gulch 161 kV Substation. | 1103400 | 100% | 1103400
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas | 143247 | ERIS | Pensacola to Ketchum 161kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Pensacole to Ketchum 161kV 4.8 mile line to achieve a minimum Summer/Emergency rating of 225 MVA | 1045480.8959 | 60.22% | 1736000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas | 143265 | ERIS | Beaver to Eureka 161kV Rebuild (DISIS-2017-001) (AEP) | Current Study | Rebuild the existing Beaver to Eureka 161kV 1.22 mile line section to achieve a minimum light/emergency rating of 258 MVA | 0 | 29.03% | 0
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas | 143264 | ERIS | Beaver to Eureka 161kV Rebuild (DISIS-2017-001) (SWPA) | Current Study | Rebuild the existing Beaver to Eureka 161kV 6 mile line section to achieve a minimum light/emergency rating of 258 MVA | 1704028.3384 | 29.03% | 5869344
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas | 133041 | ERIS | Pryor Junction 138 kV Substation GEN-2017-074 Interconnection (Non-Shared NU) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-074 (72.5 MW/Solar), into the Point of Interconnection (POI) at Pryor Junction 138 kV Substation. | 1365027 | 100% | 1365027
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas | 133040 | ERIS | Pryor Junction 138 kV Substation GEN-2017-074 Interconnection (TOIF) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-074 (72.5 MW/Solar), into the Point of Interconnection (POI) at Pryor Junction 138 kV Substation. | 1146800 | 100% | 1146800
GEN-2017-075 | 14 - South Central Oklahoma | 133043 | ERIS | Hugo - Sunnyside 345 kV GEN-2017-075 Interconnection (Non-Shared NU) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-075 (200 MW/Solar), into the Point of Interconnection (POI) at Hugo - Sunnyside 345 kV. | 1430000 | 100% | 1430000
GEN-2017-075 | 14 - South Central Oklahoma | 133042 | ERIS | Hugo - Sunnyside 345 kV GEN-2017-075 Interconnection (TOIF) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-075 (200 MW/Solar), into the Point of Interconnection (POI) at Hugo - Sunnyside 345 kV. | 915000 | 100% | 915000
GEN-2017-076 | 12 - Northwest Arkansas | 133045 | ERIS | Chamber Springs 161 kV Substation GEN-2017-076 Interconnection (Non-Shared NU) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-076 (52.2 MW/Solar), into the Point of Interconnection (POI) at Chamber Springs 161 kV Substation. | 1406646 | 100% | 1406646
GEN-2017-076 | 12 - Northwest Arkansas | 133044 | ERIS | Chamber Springs 161 kV Substation GEN-2017-076 Interconnection (TOIF) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-076 (52.2 MW/Solar), into the Point of Interconnection (POI) at Chamber Springs 161 kV Substation. | 1193983 | 100% | 1193983
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas | 143265 | ERIS | Beaver to Eureka 161kV Rebuild (DISIS-2017-001) (AEP) | Current Study | Rebuild the existing Beaver to Eureka 161kV 1.22 mile line section to achieve a minimum light/emergency rating of 258 MVA | 0 | 46.08% | 0
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas | 143264 | ERIS | Beaver to Eureka 161kV Rebuild (DISIS-2017-001) (SWPA) | Current Study | Rebuild the existing Beaver to Eureka 161kV 6 mile line section to achieve a minimum light/emergency rating of 258 MVA | 2704493.3536 | 46.08% | 5869344
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas | 133047 | ERIS | Explorer - Claremore 69 kV GEN-2017-077 Interconnection (Non-Shared NU) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-077 (124.7 MW/Solar), into the Point of Interconnection (POI) at Explorer - Claremore 69 kV. | 10334726 | 100% | 10334726
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas | 133046 | ERIS | Explorer - Claremore 69 kV GEN-2017-077 Interconnection (TOIF) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-077 (124.7 MW/Solar), into the Point of Interconnection (POI) at Explorer - Claremore 69 kV. | 1146800 | 100% | 1146800
GEN-2017-078 | 06 - South Texas Panhandle/New Mexico | 143198 | ERIS | Crawfish Draw 345/230kV Transformer Ckt 1 (DISIS-2017-001) | Current Study | Install a new 345/230kV Transformer at Crawfish Draw | 683698.6558 | 5.982% | 11430070
GEN-2017-078 | 06 - South Texas Panhandle/New Mexico | 143204 | ERIS | Crawfish Draw 765/345kV New Substation (DISIS-2017-001) | Current Study | Build a new Crawfish Draw 765/345kV Substation tapping the Tuco to Border 345kV Ckt 1 and Tuco to OKU 345kV Ckt 1. In addition, install a new 1000 MVar SVC for Dynamic Reactive Support at Crawfish Draw 765kV. Both the 765kV and the 345kV Crawfish Draw switchyards shall be constructed with breaker and a half bus schemes. Furthermore, interconnected double circuit lines connected to these switchyards or transformers connecting these switchyards shall not share adjacent breakers in the switchyard(s). | 20992791.8635 | 7.333% | 286282000
GEN-2017-078 | 06 - South Texas Panhandle/New Mexico | 143207 | ERIS | Crawfish Draw 765/345kV New Transformer (DISIS-2017-001) | Current Study | Install two new 765/345kV Transformers at Crawfish Draw | 2772106.4388 | 6.93% | 40000000
GEN-2017-078 | 06 - South Texas Panhandle/New Mexico | 143219 | ERIS | Crawfish Draw Tap to Tuco to Border 345kV Ckt 1 (DISIS-2017-001) (OKGE) | Current Study | Tap Tuco to Border 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 6371.6125 | 12.74% | 50000
GEN-2017-078 | 06 - South Texas Panhandle/New Mexico | 143194 | ERIS | Crawfish Draw Tap to Tuco to Border 345kV Ckt 1 (DISIS-2017-001) (SWPS) | Current Study | Tap Tuco to Border 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 1019458 | 12.74% | 8000000
GEN-2017-078 | 06 - South Texas Panhandle/New Mexico | 143195 | ERIS | Crawfish Draw Tap to Tuco to OKU 345kV Ckt 1 (DISIS-2017-001) (AEPW) | Current Study | Tap Tuco to OKU 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 95327.8625 | 7.333% | 1300000
GEN-2017-078 | 06 - South Texas Panhandle/New Mexico | 143220 | ERIS | Crawfish Draw Tap to Tuco to OKU 345kV Ckt 1 (DISIS-2017-001) (SWPS) | Current Study | Tap Tuco to OKU 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 586633 | 7.333% | 8000000
GEN-2017-078 | 06 - South Texas Panhandle/New Mexico | 143211 | ERIS | Crawfish Draw to Seminole 765kV New Line Double Circuit (DISIS-2017-001) (OKGE) | Current Study | Build approximately 80 miles of new double circuit 765kV line from Crawfish Draw to Seminole | 88526822.2424 | 13.4% | 660408000
GEN-2017-078 | 06 - South Texas Panhandle/New Mexico | 143221 | ERIS | Crawfish Draw to Seminole 765kV New Line Double Circuit (DISIS-2017-001) (SWPS) | Current Study | Build approximately 265 miles of new double circuit 765kV line from Crawfish Draw to Seminole | 88740227.7448 | 13.4% | 662000000
GEN-2017-078 | 06 - South Texas Panhandle/New Mexico | 143209 | ERIS | Crossroads 765/345kV New Transformer (DISIS-2017-001) | Current Study | Expand Crossroads 765kV Substation and install a new 765/345 transformer | 6627682.0279 | 33.14% | 20000000
GEN-2017-078 | 06 - South Texas Panhandle/New Mexico | 143325 | ERIS | Crossroads 765kV Reactive Support (DISIS-2017-001) | Current Study | Stability identified need to install 600 MVar SVC for Dynamic Reactive Support at Crossroads 765kV | 44991933.8128 | 33.14% | 135769200
GEN-2017-078 | 06 - South Texas Panhandle/New Mexico | 143210 | ERIS | Crossroads to Crawfish Draw 765kV New Line (DISIS-2017-001) | Current Study | Build approximately 85 miles of new 765kV line from Crossroads to Crawfish Draw | 125926460.853 | 33.14% | 380000000
GEN-2017-078 | 06 - South Texas Panhandle/New Mexico | 133049 | ERIS | Eddy County - Tolk 345 kV GEN-2017-078 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-078 (300 MW/Wind), into the Point of Interconnection (POI) at Eddy County - Tolk 345 kV. | 1098575 | 100% | 1098575
GEN-2017-078 | 06 - South Texas Panhandle/New Mexico | 133048 | ERIS | Eddy County - Tolk 345 kV GEN-2017-078 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-078 (300 MW/Wind), into the Point of Interconnection (POI) at Eddy County - Tolk 345 kV. | 1644416 | 100% | 1644416
GEN-2017-078 | 06 - South Texas Panhandle/New Mexico | 143208 | ERIS | Seminole 765/345 New Transformer (DISIS-2017-001) | Current Study | Expand Seminole 345kV substation to include a new 765kV switchyard connected by a new 765/345kV transformer. In addition, install a new 600 MVar SVC for Dynamic Reactive Support at Seminole 765kV. | 21436960.865 | 13.4% | 159919200
GEN-2017-078 | 06 - South Texas Panhandle/New Mexico | 122568 | ERIS | Tolk 345/230 kV CKT 2 Transformer (DISIS-2016-002) | Contingent | Build new 345/230 kV Transformer Ckt 2 at Tolk to achieve a minimum emergency rating of 921 MVA on the Crossroads - Tolk 345 kV Ckt 1 line. | 0 | 0% | 14055360
GEN-2017-078 | 06 - South Texas Panhandle/New Mexico | 143248 | ERIS | Tolk 345/230kV Transformer Ckt 3 (DISIS-2017-001) | Current Study | Install a new 345/230kV Transformer at Tolk | 970386.4667 | 6.904% | 14055360
GEN-2017-078 | 06 - South Texas Panhandle/New Mexico | 143250 | ERIS | Tolk to Tuco 345kV New Line (DISIS-2017-001) | Current Study | Build approximately 54 miles of new 345kV line from Tolk to Tuco | 2932193.6476 | 4.745% | 61799976
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico | 143198 | ERIS | Crawfish Draw 345/230kV Transformer Ckt 1 (DISIS-2017-001) | Current Study | Install a new 345/230kV Transformer at Crawfish Draw | 2424621.5337 | 21.21% | 11430070
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico | 143204 | ERIS | Crawfish Draw 765/345kV New Substation (DISIS-2017-001) | Current Study | Build a new Crawfish Draw 765/345kV Substation tapping the Tuco to Border 345kV Ckt 1 and Tuco to OKU 345kV Ckt 1. In addition, install a new 1000 MVar SVC for Dynamic Reactive Support at Crawfish Draw 765kV. Both the 765kV and the 345kV Crawfish Draw switchyards shall be constructed with breaker and a half bus schemes. Furthermore, interconnected double circuit lines connected to these switchyards or transformers connecting these switchyards shall not share adjacent breakers in the switchyard(s). | 35649514.1611 | 12.45% | 286282000
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico | 143207 | ERIS | Crawfish Draw 765/345kV New Transformer (DISIS-2017-001) | Current Study | Install two new 765/345kV Transformers at Crawfish Draw | 8070244.0096 | 20.18% | 40000000
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico | 143219 | ERIS | Crawfish Draw Tap to Tuco to Border 345kV Ckt 1 (DISIS-2017-001) (OKGE) | Current Study | Tap Tuco to Border 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 10392.8062 | 20.79% | 50000
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico | 143194 | ERIS | Crawfish Draw Tap to Tuco to Border 345kV Ckt 1 (DISIS-2017-001) (SWPS) | Current Study | Tap Tuco to Border 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 1662849 | 20.79% | 8000000
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico | 143195 | ERIS | Crawfish Draw Tap to Tuco to OKU 345kV Ckt 1 (DISIS-2017-001) (AEPW) | Current Study | Tap Tuco to OKU 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 161883.6375 | 12.45% | 1300000
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico | 143220 | ERIS | Crawfish Draw Tap to Tuco to OKU 345kV Ckt 1 (DISIS-2017-001) (SWPS) | Current Study | Tap Tuco to OKU 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 996207 | 12.45% | 8000000
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico | 143211 | ERIS | Crawfish Draw to Seminole 765kV New Line Double Circuit (DISIS-2017-001) (OKGE) | Current Study | Build approximately 80 miles of new double circuit 765kV line from Crawfish Draw to Seminole | 139222550.9981 | 21.08% | 660408000
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico | 143221 | ERIS | Crawfish Draw to Seminole 765kV New Line Double Circuit (DISIS-2017-001) (SWPS) | Current Study | Build approximately 265 miles of new double circuit 765kV line from Crawfish Draw to Seminole | 139558165.1959 | 21.08% | 662000000
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico | 143209 | ERIS | Crossroads 765/345kV New Transformer (DISIS-2017-001) | Current Study | Expand Crossroads 765kV Substation and install a new 765/345 transformer | 3575888.3154 | 17.88% | 20000000
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico | 143325 | ERIS | Crossroads 765kV Reactive Support (DISIS-2017-001) | Current Study | Stability identified need to install 600 MVar SVC for Dynamic Reactive Support at Crossroads 765kV | 24274871.6266 | 17.88% | 135769200
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico | 143210 | ERIS | Crossroads to Crawfish Draw 765kV New Line (DISIS-2017-001) | Current Study | Build approximately 85 miles of new 765kV line from Crossroads to Crawfish Draw | 67942149.0155 | 17.88% | 380000000
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico | 143208 | ERIS | Seminole 765/345 New Transformer (DISIS-2017-001) | Current Study | Expand Seminole 345kV substation to include a new 765kV switchyard connected by a new 765/345kV transformer. In addition, install a new 600 MVar SVC for Dynamic Reactive Support at Seminole 765kV. | 33713038.3136 | 21.08% | 159919200
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico | 133053 | ERIS | Tolk 230 kV Substation GEN-2017-080 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-080 (525 MW/Solar), into the Point of Interconnection (POI) at Tolk 230 kV Substation. | 2141174 | 100% | 2141174
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico | 133052 | ERIS | Tolk 230 kV Substation GEN-2017-080 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-080 (525 MW/Solar), into the Point of Interconnection (POI) at Tolk 230 kV Substation. | 840720 | 100% | 840720
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico | 122568 | ERIS | Tolk 345/230 kV CKT 2 Transformer (DISIS-2016-002) | Contingent | Build new 345/230 kV Transformer Ckt 2 at Tolk to achieve a minimum emergency rating of 921 MVA on the Crossroads - Tolk 345 kV Ckt 1 line. | 0 | 0% | 14055360
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico | 143248 | ERIS | Tolk 345/230kV Transformer Ckt 3 (DISIS-2017-001) | Current Study | Install a new 345/230kV Transformer at Tolk | 4694643.9241 | 33.4% | 14055360
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico | 143250 | ERIS | Tolk to Tuco 345kV New Line (DISIS-2017-001) | Current Study | Build approximately 54 miles of new 345kV line from Tolk to Tuco | 19393014.3814 | 31.38% | 61799976
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico | 143251 | ERIS | Tuco to Crawfish Draw 345kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Tuco to Crawfish Draw 345kV 1.54 mile line to achieve a minimum light/emergency rating of 1094 MVA | 455904.1168 | 25.87% | 1762443
GEN-2017-082 | 12 - Northwest Arkansas | 133057 | ERIS | Asbury Plant 161 kV Substation GEN-2017-082 Interconnection (Non-Shared NU) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-082 (149.4 MW/Solar), into the Point of Interconnection (POI) at Asbury Plant 161 kV Substation. | 0 | 100% | 0
GEN-2017-082 | 12 - Northwest Arkansas | 143123 | ERIS | Asbury Plant 161 kV Substation GEN-2017-082 Interconnection (Non-Shared NU) (WERE) | Interconnection | Potential interconnection impacts from the following generating facility, GEN-2017-082 (149.4 MW/Wind), into the Point of Interconnection (POI) at Asbury Plant 161 kV Substation. | 6649 | 100% | 6649
GEN-2017-082 | 12 - Northwest Arkansas | 133056 | ERIS | Asbury Plant 161 kV Substation GEN-2017-082 Interconnection (TOIF) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-082 (149.4 MW/Solar), into the Point of Interconnection (POI) at Asbury Plant 161 kV Substation. | 0 | 100% | 0
GEN-2017-085 | 09 - Nebraska | 143215 | ERIS | Cooper 345kV Terminal Upgrades (DISIS-2017-001) (NPPD) | Current Study | Upgrade terminal equipment at Cooper 345 kV line to achieve a minimum Spring/Emergency rating of 1295 MVA | 1801.4177 | 0.06005% | 3000000
GEN-2017-085 | 09 - Nebraska | 143227 | ERIS | Cooper Joe 345kV New Substation (DISIS-2017-001) | Current Study | Build a new 345 kV substation at Cooper Joe. Tap the Cooper to St. Joe 345kV line 20 miles from St. Joe 345kV | 9753.7072 | 0.06005% | 16243869
GEN-2017-085 | 09 - Nebraska | 143212 | ERIS | Cooper Joe to Cooper 345kV Rebuild (DISIS-2017-001) (KCPL) | Current Study | Rebuild Cooper Joe to Cooper 345 kV 22.2 miles line to achieve a minimum Spring/Emergency rating of 1295 MVA | 24281.0923 | 0.06005% | 40437842.97
GEN-2017-085 | 09 - Nebraska | 143214 | ERIS | Cooper Joe to Cooper 345kV Rebuild (DISIS-2017-001) (OPPD) | Current Study | Rebuild Cooper Joe to Cooper 345 kV 26.6 miles line to achieve a minimum Spring/Emergency rating of 1295 MVA | 17797.4769 | 0.06005% | 29640000
GEN-2017-085 | 09 - Nebraska | 143217 | ERIS | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Current Study | Build approximately 6 miles of new 345kV line from Cooper Joe to Hoyt | 8352.6957 | 0.06005% | 13910618
GEN-2017-085 | 09 - Nebraska | 143218 | ERIS | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Current Study | Build approximately 60 miles of new 345kV line from Cooper Joe to Hoyt | 79395.0691 | 0.06005% | 132224914
GEN-2017-085 | 09 - Nebraska | 133063 | ERIS | Friend 115 kV Substation GEN-2017-085 Interconnection (Non-Shared NU) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-085 (.6 MW/Wind), into the Point of Interconnection (POI) at Friend 115 kV Substation. | 0 | 100% | 0
GEN-2017-085 | 09 - Nebraska | 133062 | ERIS | Friend 115 kV Substation GEN-2017-085 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-085 (.6 MW/Wind), into the Point of Interconnection (POI) at Friend 115 kV Substation. | 0 | 100% | 0
GEN-2017-085 | 09 - Nebraska | 143259 | ERIS | Holt to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Current Study | Build approximately 26 miles of new 345kV line from Holt to Hoyt | 32314.2486 | 0.05517% | 58576716
GEN-2017-085 | 09 - Nebraska | 143225 | ERIS | Holt 345kV Terminal Upgrades (DISIS-2017-001) (TMO) | Current Study | Upgrade terminal equipment at Holt 345kV to accept Holt to Holt new line | 720.9626 | 0.05517% | 1306904
GEN-2017-085 | 09 - Nebraska | 143213 | ERIS | Holt to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Current Study | Build approximately 100 miles of new 345kV line from Holt to Hoyt | 90062.1007 | 0.05517% | 163257734
GEN-2017-085 | 09 - Nebraska | 143252 | ERIS | Potter County 345/230kV Transformer Ckt 2 (DISIS-2017-001) | Current Study | Install a new 345/230kV Transformer at Potter County | 6960.3256 | 0.05531% | 12583652
GEN-2017-085 | 09 - Nebraska | 143320 | NRIS | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Current Study | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek | 49827.0866 | 0.07088% | 70295174
GEN-2017-085 | 09 - Nebraska | 143319 | NRIS | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Current Study | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek | 99235.7188 | 0.07088% | 140000000
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas | 143246 | ERIS | Neosho to G17-009 Tap Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Neosho to G17-009 345kV 18.17 mile line to achieve a minimum Winter/Emergency rating of 1260 MVA | 1361914.5153 | 4.142% | 32884027
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas | 143125 | ERIS | Viola 345 kV Substation GEN-2017-086 Interconnection (Non-Shared NU) (OKGE) | Interconnection | Potential interconnection impacts from the following generating facility, GEN-2017-086 (150 MW/Wind), into the Point of Interconnection (POI) at Viola 345 kV Substation. | 20000 | 100% | 20000
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas | 133065 | ERIS | Viola 345 kV Substation GEN-2017-086 Interconnection (Non-Shared NU) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-086 (150 MW/Wind), into the Point of Interconnection (POI) at Viola 345 kV Substation. | 38569 | 100% | 38569
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas | 133064 | ERIS | Viola 345 kV Substation GEN-2017-086 Interconnection (TOIF) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-086 (150 MW/Wind), into the Point of Interconnection (POI) at Viola 345 kV Substation. | 0 | 100% | 0
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas | 122792 | ERIS | Viola 345/138kV Transformer CKT 2 (DISIS-2016-002-2) | Contingent | Build second 345/138/13.8kV transformer at Viola. | 0 | 0% | 9038339
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas | 122598 | ERIS | Wolf Creek to Blackberry 345kV | Contingent | Build a new 86 mile 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 0% | 142601178
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico | 133067 | ERIS | Clovis Interchange 115 kV Substation GEN-2017-087 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-087 (128 MW/Solar), into the Point of Interconnection (POI) at Clovis Interchange 115 kV Substation. | 3610830 | 100% | 3610830
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico | 133066 | ERIS | Clovis Interchange 115 kV Substation GEN-2017-087 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-087 (128 MW/Solar), into the Point of Interconnection (POI) at Clovis Interchange 115 kV Substation. | 634734 | 100% | 634734
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico | 143198 | ERIS | Crawfish Draw 345/230kV Transformer Ckt 1 (DISIS-2017-001) | Current Study | Install a new 345/230kV Transformer at Crawfish Draw | 607946.6654 | 5.319% | 11430070
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico | 143204 | ERIS | Crawfish Draw 765/345kV New Substation (DISIS-2017-001) | Current Study | Build a new Crawfish Draw 765/345kV Substation tapping the Tuco to Border 345kV Ckt 1 and Tuco to OKU 345kV Ckt 1. In addition, install a new 1000 MVar SVC for Dynamic Reactive Support at Crawfish Draw 765kV. Both the 765kV and the 345kV Crawfish Draw switchyards shall be constructed with breaker and a half bus schemes. Furthermore, interconnected double circuit lines connected to these switchyards or transformers connecting these switchyards shall not share adjacent breakers in the switchyard(s). | 8419801.7311 | 2.941% | 286282000
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico | 143207 | ERIS | Crawfish Draw 765/345kV New Transformer (DISIS-2017-001) | Current Study | Install two new 765/345kV Transformers at Crawfish Draw | 1880800.803 | 4.702% | 40000000
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico | 143219 | ERIS | Crawfish Draw Tap to Tuco to Border 345kV Ckt 1 (DISIS-2017-001) (OKGE) | Current Study | Tap Tuco to Border 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 2432.3187 | 4.865% | 50000
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico | 143194 | ERIS | Crawfish Draw Tap to Tuco to Border 345kV Ckt 1 (DISIS-2017-001) (SWPS) | Current Study | Tap Tuco to Border 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 389171 | 4.865% | 8000000
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico | 143195 | ERIS | Crawfish Draw Tap to Tuco to OKU 345kV Ckt 1 (DISIS-2017-001) (AEPW) | Current Study | Tap Tuco to OKU 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 38234.1375 | 2.941% | 1300000
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico | 143220 | ERIS | Crawfish Draw Tap to Tuco to OKU 345kV Ckt 1 (DISIS-2017-001) (SWPS) | Current Study | Tap Tuco to OKU 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 235287 | 2.941% | 8000000
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico | 143211 | ERIS | Crawfish Draw to Seminole 765kV New Line Double Circuit (DISIS-2017-001) (OKGE) | Current Study | Build approximately 80 miles of new double circuit 765kV line from Crawfish Draw to Seminole | 33142746.3573 | 5.019% | 660408000
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico | 143221 | ERIS | Crawfish Draw to Seminole 765kV New Line Double Circuit (DISIS-2017-001) (SWPS) | Current Study | Build approximately 265 miles of new double circuit 765kV line from Crawfish Draw to Seminole | 33222641.2893 | 5.019% | 662000000
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico | 143209 | ERIS | Crossroads 765/345kV New Transformer (DISIS-2017-001) | Current Study | Expand Crossroads 765kV Substation and install a new 765/345 transformer | 873581.9597 | 4.368% | 20000000
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico | 143325 | ERIS | Crossroads 765kV Reactive Support (DISIS-2017-001) | Current Study | Stability identified need to install 600 MVar SVC for Dynamic Reactive Support at Crossroads 765kV | 5930017.5855 | 4.368% | 135769200
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico | 143210 | ERIS | Crossroads to Crawfish Draw 765kV New Line (DISIS-2017-001) | Current Study | Build approximately 85 miles of new 765kV line from Crossroads to Crawfish Draw | 16597333.4341 | 4.368% | 380000000
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico | 143208 | ERIS | Seminole 765/345 New Transformer (DISIS-2017-001) | Current Study | Expand Seminole 345kV substation to include a new 765kV switchyard connected by a new 765/345kV transformer. In addition, install a new 600 MVar SVC for Dynamic Reactive Support at Seminole 765kV. | 8025585.0318 | 5.019% | 159919200
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico | 122568 | ERIS | Tolk 345/230 kV CKT 2 Transformer (DISIS-2016-002) | Contingent | Build new 345/230 kV Transformer Ckt 2 at Tolk to achieve a minimum emergency rating of 921 MVA on the Crossroads - Tolk 345 kV Ckt 1 line. | 0 | 0% | 14055360
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico | 143248 | ERIS | Tolk 345/230kV Transformer Ckt 3 (DISIS-2017-001) | Current Study | Install a new 345/230kV Transformer at Tolk | 938731.9312 | 6.679% | 14055360
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico | 143250 | ERIS | Tolk to Tuco 345kV New Line (DISIS-2017-001) | Current Study | Build approximately 54 miles of new 345kV line from Tolk to Tuco | 3984198.1197 | 6.447% | 61799976
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico | 143251 | ERIS | Tuco to Crawfish Draw 345kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Tuco to Crawfish Draw 345kV 1.54 mile line to achieve a minimum light/emergency rating of 1094 MVA | 106699.2018 | 6.054% | 1762443
GEN-2017-090 | 13 - Northeast Kansas/Northwest Missouri | 133069 | ERIS | Adrian 161 kV Substation GEN-2017-090 Interconnection (Non-Shared NU) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-090 (150 MW/Solar), into the Point of Interconnection (POI) at Adrian 161 kV Substation. | 10177602 | 100% | 10177602
GEN-2017-090 | 13 - Northeast Kansas/Northwest Missouri | 133068 | ERIS | Adrian 161 kV Substation GEN-2017-090 Interconnection (TOIF) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-090 (150 MW/Solar), into the Point of Interconnection (POI) at Adrian 161 kV Substation. | 824356 | 100% | 824356
GEN-2017-090 | 13 - Northeast Kansas/Northwest Missouri | 143259 | ERIS | Holt to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Current Study | Build approximately 26 miles of new 345kV line from Holt to Hoyt | 477875.4533 | 0.8158% | 58576716
GEN-2017-090 | 13 - Northeast Kansas/Northwest Missouri | 143225 | ERIS | Holt 345kV Terminal Upgrades (DISIS-2017-001) (TMO) | Current Study | Upgrade terminal equipment at Holt 345kV to accept Holt to Holt new line | 10661.8702 | 0.8158% | 1306904
GEN-2017-090 | 13 - Northeast Kansas/Northwest Missouri | 143213 | ERIS | Holt to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Current Study | Build approximately 100 miles of new 345kV line from Holt to Hoyt | 1331874.6485 | 0.8158% | 163257734
GEN-2017-092 | 08 - North Oklahoma/South Central Kansas | 133073 | ERIS | Canadian River - Muskogee - Seminole 345 kV GEN-2017-092 Interconnection (Non-Shared NU) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-092 (200 MW/Solar), into the Point of Interconnection (POI) at Canadian River - Muskogee - Seminole | 5741321 | 100% | 5741321
GEN-2017-092 | 08 - North Oklahoma/South Central Kansas | 133072 | ERIS | Canadian River - Muskogee - Seminole 345 kV GEN-2017-092 Interconnection (TOIF) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-092 (200 MW/Solar), into the Point of Interconnection (POI) at Canadian River - Muskogee - Seminole | 599979 | 100% | 599979
GEN-2017-094 | 15 - Eastern South Dakota | 122574 | ERIS | Fort Thompson - Huron 230 kV GEN-2017-094 Interconnection (Non-Shared NU) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-094 (200 MW/Wind), into the Point of Interconnection (POI) at Fort Thompson - Huron 230 kV. | 9000000 | 100% | 9000000
GEN-2017-094 | 15 - Eastern South Dakota | 122573 | ERIS | Fort Thompson - Huron 230 kV GEN-2017-094 Interconnection (TOIF) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-094 (200 MW/Wind), into the Point of Interconnection (POI) at Fort Thompson - Huron 230 kV. | 250000 | 100% | 250000
GEN-2017-094 | 15 - Eastern South Dakota | 143309 | NRIS | Appledorn to Watertown 230kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Watertown to Appledorn 230kV 55.3 mile line to achieve a minimum summer/emergency rating of 363 MVA | 3600000 | 100% | 3600000
GEN-2017-094 | 15 - Eastern South Dakota | 143307 | NRIS | Fort Randall to Lake Platte 230kV Rebuild (DISIS-2017-001) (WAPA) | Current Study | Rebuild the existing Fort Randall to Lake Platte 43.34 mile line to achieve a minimum summer/emergency rating of 335 MVA | 2000000 | 100% | 2000000
GEN-2017-094 | 15 - Eastern South Dakota | 143306 | NRIS | Fort Thompson to Fort Randall 230kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Fort Thompson to Fort Randall 87.32 mile line to achieve a minimum summer/emergency rating of 348 MVA | 23568000 | 100% | 23568000
GEN-2017-094 | 15 - Eastern South Dakota | 143320 | NRIS | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Current Study | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek | 11584600.1143 | 16.48% | 70295174
GEN-2017-094 | 15 - Eastern South Dakota | 143319 | NRIS | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Current Study | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek | 23071911.2524 | 16.48% | 140000000
GEN-2017-097 | 17 - Western South Dakota | 143224 | ERIS | G17-014 Tap to Philip Tap 230kV New Line (DISIS-2017-001) | Current Study | Convert existing Philip Tap to a ring bus substation and build approximately 6 miles of new 230kV from new substation to G17-014 Tap creating a double circuit 230kV line. | 6761811.7465 | 23.55% | 28715520
GEN-2017-097 | 17 - Western South Dakota | 133077 | ERIS | Underwood 115 kV Substation GEN-2017-097 Interconnection (Non-Shared NU) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-097 (128 MW/Solar), into the Point of Interconnection (POI) at Underwood 115 kV Substation. | 0 | 100% | 0
GEN-2017-097 | 17 - Western South Dakota | 133076 | ERIS | Underwood 115 kV Substation GEN-2017-097 Interconnection (TOIF) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-097 (128 MW/Solar), into the Point of Interconnection (POI) at Underwood 115 kV Substation. | 1208190 | 100% | 1208190
GEN-2017-099 | 03 - Spearville | 143263 | ERIS | Finney 345kV Reactive Support (DISIS-2017-001) | Current Study | Install +250 MVAR Capacitor Bank(s) at Finney 345kV | 28958.5839 | 0.4665% | 6207750
GEN-2017-099 | 03 - Spearville | 133079 | ERIS | Post Rock - Spearville 345 kV GEN-2017-099 Interconnection (Non-Shared NU) (ITCGP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-099 (200 MW/Wind), into the Point of Interconnection (POI) at Post Rock - Spearville 345 kV. | 15081109 | 100% | 15081109
GEN-2017-099 | 03 - Spearville | 133078 | ERIS | Post Rock - Spearville 345 kV GEN-2017-099 Interconnection (TOIF) (ITCGP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-099 (200 MW/Wind), into the Point of Interconnection (POI) at Post Rock - Spearville 345 kV. | 1054767 | 100% | 1054767
GEN-2017-099 | 03 - Spearville | 143240 | ERIS | Smokey Hils to Summit 230kV Rebuild (DISIS-2017-001) (MIDW) | Current Study | Rebuild the existing Smokey Hills to Summit 230kV 16.1 mile line to achieve a minimum Light/Emergency rating of 375 MVA | 4150461.2291 | 25.15% | 16500000
GEN-2017-099 | 03 - Spearville | 143242 | ERIS | Smokey Hils to Summit 230kV Rebuild (DISIS-2017-001) (WERE) | Current Study | Rebuild the existing Smokey Hills to Summit 230kV 22.5 mile line to achieve a minimum Light/Emergency rating of 375 MVA | 9735744.5038 | 35.63% | 27323646
GEN-2017-099 | 03 - Spearville | 143320 | NRIS | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Current Study | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek | 3210090.1968 | 4.567% | 70295174
GEN-2017-099 | 03 - Spearville | 143319 | NRIS | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Current Study | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek | 6393221.6392 | 4.567% | 140000000
GEN-2017-100 | 02 - Hitchland | 143192 | ERIS | Beaver County to Clark County 345kV New Line (DISIS-2017-001) (ITCGP) | Current Study | Build approximately 55 miles of new 345kV line from Beaver County to Clark County | 24207572.5205 | 33.87% | 71470025
GEN-2017-100 | 02 - Hitchland | 143191 | ERIS | Beaver County to Clark County 345kV New Line (DISIS-2017-001) (OKGE) | Current Study | Build approximately 70 miles of new 345kV line from Beaver County to Clark County | 30809635.7211 | 33.87% | 90961844
GEN-2017-100 | 02 - Hitchland | 143197 | ERIS | Beaver County to Grapeveine 345kV New Line (DISIS-2017-001) (OKGE) | Current Study | Build approximately 45 miles of new 345kV line from Beaver County to Grapevine | 24781554.1921 | 20.85% | 118875615
GEN-2017-100 | 02 - Hitchland | 143196 | ERIS | Beaver County to Grapeveine 345kV New Line (DISIS-2017-001) (SWPS) | Current Study | Build approximately 45 miles of new 345kV line from Beaver County to Grapevine | 0 | 20.85% | 0
GEN-2017-100 | 02 - Hitchland | 143216 | ERIS | Grapevine 345kV New Substation (DISIS-2017-001) | Current Study | Build a new 345kV substation at Grapevine | 6329419.7789 | 34.35% | 18427752
GEN-2017-100 | 02 - Hitchland | 143206 | ERIS | Grapevine to Chisholm 345kV New Line (DISIS-2017-001) (AEPW) | Current Study | Build approximately 35 miles of new 345kV line from Grapevine to Chisholm | 35563052.4657 | 34.35% | 103539840
GEN-2017-100 | 02 - Hitchland | 143203 | ERIS | Grapevine to Chisholm 345kV New Line (DISIS-2017-001) (SWPS) | Current Study | Build approximately 40 miles of new 345kV line from Grapevine to Chisholm | 0 | 34.35% | 0
GEN-2017-100 | 02 - Hitchland | 143245 | ERIS | Potter County to Grapevine 345kV New Line (DISIS-2017-001) | Current Study | Build approximately 65 miles of new 345kV line from Potter County to Grapevine | 18901115.5046 | 20.54% | 92000000
GEN-2017-100 | 02 - Hitchland | 133081 | ERIS | Texas County 115 kV Substation GEN-2017-100 Inteconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-100 (102.6 MW/Solar), into the Point of Interconnection (POI) at Texas County 115 kV Substation. | 17186637 | 100% | 17186637
GEN-2017-100 | 02 - Hitchland | 133080 | ERIS | Texas County 115 kV Substation GEN-2017-100 Inteconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-100 (102.6 MW/Solar), into the Point of Interconnection (POI) at Texas County 115 kV Substation. | 781840 | 100% | 781840
GEN-2017-100 | 02 - Hitchland | 143320 | NRIS | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | Current Study | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek | 2098288.7632 | 2.985% | 70295174
GEN-2017-100 | 02 - Hitchland | 143319 | NRIS | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | Current Study | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek | 4178955.8249 | 2.985% | 140000000
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico | 143198 | ERIS | Crawfish Draw 345/230kV Transformer Ckt 1 (DISIS-2017-001) | Current Study | Install a new 345/230kV Transformer at Crawfish Draw | 553564.0951 | 4.843% | 11430070
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico | 143204 | ERIS | Crawfish Draw 765/345kV New Substation (DISIS-2017-001) | Current Study | Build a new Crawfish Draw 765/345kV Substation tapping the Tuco to Border 345kV Ckt 1 and Tuco to OKU 345kV Ckt 1. In addition, install a new 1000 MVar SVC for Dynamic Reactive Support at Crawfish Draw 765kV. Both the 765kV and the 345kV Crawfish Draw switchyards shall be constructed with breaker and a half bus schemes. Furthermore, interconnected double circuit lines connected to these switchyards or transformers connecting these switchyards shall not share adjacent breakers in the switchyard(s). | 17272824.47 | 6.034% | 286282000
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico | 143207 | ERIS | Crawfish Draw 765/345kV New Transformer (DISIS-2017-001) | Current Study | Install two new 765/345kV Transformers at Crawfish Draw | 3283645.8758 | 8.209% | 40000000
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico | 143219 | ERIS | Crawfish Draw Tap to Tuco to Border 345kV Ckt 1 (DISIS-2017-001) (OKGE) | Current Study | Tap Tuco to Border 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 5135.625 | 10.27% | 50000
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico | 143194 | ERIS | Crawfish Draw Tap to Tuco to Border 345kV Ckt 1 (DISIS-2017-001) (SWPS) | Current Study | Tap Tuco to Border 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 821700 | 10.27% | 8000000
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico | 143195 | ERIS | Crawfish Draw Tap to Tuco to OKU 345kV Ckt 1 (DISIS-2017-001) (AEPW) | Current Study | Tap Tuco to OKU 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 78435.5 | 6.034% | 1300000
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico | 143220 | ERIS | Crawfish Draw Tap to Tuco to OKU 345kV Ckt 1 (DISIS-2017-001) (SWPS) | Current Study | Tap Tuco to OKU 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | 482680 | 6.034% | 8000000
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico | 143211 | ERIS | Crawfish Draw to Seminole 765kV New Line Double Circuit (DISIS-2017-001) (OKGE) | Current Study | Build approximately 80 miles of new double circuit 765kV line from Crawfish Draw to Seminole | 67205964.1901 | 10.18% | 660408000
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico | 143221 | ERIS | Crawfish Draw to Seminole 765kV New Line Double Circuit (DISIS-2017-001) (SWPS) | Current Study | Build approximately 265 miles of new double circuit 765kV line from Crawfish Draw to Seminole | 67367972.971 | 10.18% | 662000000
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico | 143209 | ERIS | Crossroads 765/345kV New Transformer (DISIS-2017-001) | Current Study | Expand Crossroads 765kV Substation and install a new 765/345 transformer | 2063322.8355 | 10.32% | 20000000
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico | 143325 | ERIS | Crossroads 765kV Reactive Support (DISIS-2017-001) | Current Study | Stability identified need to install 600 MVar SVC for Dynamic Reactive Support at Crossroads 765kV | 14007369.6483 | 10.32% | 135769200
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico | 143210 | ERIS | Crossroads to Crawfish Draw 765kV New Line (DISIS-2017-001) | Current Study | Build approximately 85 miles of new 765kV line from Crossroads to Crawfish Draw | 39204771.5265 | 10.32% | 380000000
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico | 133083 | ERIS | Hobbs 230 kV Substation GEN-2017-104 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-104 (240 MW/Solar), into the Point of Interconnection (POI) at Hobbs 230 kV Substation. | 2530072 | 100% | 2530072
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico | 133082 | ERIS | Hobbs 230 kV Substation GEN-2017-104 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-104 (240 MW/Solar), into the Point of Interconnection (POI) at Hobbs 230 kV Substation. | 1324666 | 100% | 1324666
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico | 143208 | ERIS | Seminole 765/345 New Transformer (DISIS-2017-001) | Current Study | Expand Seminole 345kV substation to include a new 765kV switchyard connected by a new 765/345kV transformer. In addition, install a new 600 MVar SVC for Dynamic Reactive Support at Seminole 765kV. | 16274065.4446 | 10.18% | 159919200
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico | 122568 | ERIS | Tolk 345/230 kV CKT 2 Transformer (DISIS-2016-002) | Contingent | Build new 345/230 kV Transformer Ckt 2 at Tolk to achieve a minimum emergency rating of 921 MVA on the Crossroads - Tolk 345 kV Ckt 1 line. | 0 | 0% | 14055360
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico | 143250 | ERIS | Tolk to Tuco 345kV New Line (DISIS-2017-001) | Current Study | Build approximately 54 miles of new 345kV line from Tolk to Tuco | 2364100.8008 | 3.825% | 61799976
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico | 143251 | ERIS | Tuco to Crawfish Draw 345kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Tuco to Crawfish Draw 345kV 1.54 mile line to achieve a minimum light/emergency rating of 1094 MVA | 225285.8875 | 12.78% | 1762443
Total | [6 empty] | 4818214558.78 |  | 586

## Upgrade Summary
Upgrade Type | Group | Assigned Study Number | Service Type | Upgrade Name | Upgrade ID | Upgrade Details | Transmission Owner(s) | Estimated Lead Time (months) | Total Upgrade Cost
Interconnection | 01 - Woodward | DISIS-2017-001-P2 | ERIS | Badger - Woodward 345 kV GEN-2017-011 Interconnection (Non-Shared NU) (OKGE) | 132951 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-011 (151.8 MW/Solar), into the Point of Interconnection (POI) at Badger - Woodward 345 kV. | OGE | 4 | 15000
Interconnection | 01 - Woodward | DISIS-2017-001-P2 | ERIS | Badger - Woodward 345 kV GEN-2017-011 Interconnection (TOIF) (OKGE) | 132950 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-011 (151.8 MW/Solar), into the Point of Interconnection (POI) at Badger - Woodward 345 kV. | OGE | 0 | 0
Interconnection | 01 - Woodward | DISIS-2017-001-P2 | ERIS | El Reno 138 kV Switching Station GEN-2017-028 Interconnection (Non-Shared NU) (OKGE) | 143119 | Potential interconnection impacts from the following generating facility, GEN-2017-028 (50 MW/Solar), into the Point of Interconnection (POI) at El Reno 138 kV Substation. | OGE | 4 | 15000
Interconnection | 01 - Woodward | DISIS-2017-001-P2 | ERIS | El Reno 138 kV Switching Station GEN-2017-028 Interconnection (TOIF) (WFEC) | 132974 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-028 (50 MW/Solar), into the Point of Interconnection (POI) at El Reno 138 kV Switching Station. | WFEC | 36 | 400000
Current Study | 02 - Hitchland | DISIS-2017-001-P2 | ERIS | Beaver County to Clark County 345kV New Line (DISIS-2017-001) (ITCGP) | 143192 | Build approximately 55 miles of new 345kV line from Beaver County to Clark County | ITCGP | 42 | 71470025
Current Study | 02 - Hitchland | DISIS-2017-001-P2 | ERIS | Beaver County to Clark County 345kV New Line (DISIS-2017-001) (OKGE) | 143191 | Build approximately 70 miles of new 345kV line from Beaver County to Clark County | OGE | 34 | 90961844
Current Study | 02 - Hitchland | DISIS-2017-001-P2 | ERIS | Beaver County to Grapeveine 345kV New Line (DISIS-2017-001) (OKGE) | 143197 | Build approximately 45 miles of new 345kV line from Beaver County to Grapevine | OGE | 34 | 118875615
Current Study | 02 - Hitchland | DISIS-2017-001-P2 | ERIS | Beaver County to Grapeveine 345kV New Line (DISIS-2017-001) (SWPS) | 143196 | Build approximately 45 miles of new 345kV line from Beaver County to Grapevine | SPS | 0 | 0
Interconnection | 02 - Hitchland | DISIS-2017-001-P2 | ERIS | Cole 115 kV Substation GEN-2017-047 Interconnection (Non-Shared NU) (SWPS) | 132997 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-047 (102 MW/Wind), into the Point of Interconnection (POI) at Cole 115 kV Substation. | SPS | 36 | 13148764
Interconnection | 02 - Hitchland | DISIS-2017-001-P2 | ERIS | Cole 115 kV Substation GEN-2017-047 Interconnection (TOIF) (SWPS) | 132996 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-047 (102 MW/Wind), into the Point of Interconnection (POI) at Cole 115 kV Substation. | SPS | 36 | 759404
Current Study | 02 - Hitchland | DISIS-2017-001-P2 | ERIS | Grapevine 345kV New Substation (DISIS-2017-001) | 143216 | Build a new 345kV substation at Grapevine | SPS | 36 | 18427752
Current Study | 02 - Hitchland | DISIS-2017-001-P2 | ERIS | Grapevine to Chisholm 345kV New Line (DISIS-2017-001) (AEPW) | 143206 | Build approximately 35 miles of new 345kV line from Grapevine to Chisholm | AEP | 42 | 103539840
Current Study | 02 - Hitchland | DISIS-2017-001-P2 | ERIS | Grapevine to Chisholm 345kV New Line (DISIS-2017-001) (SWPS) | 143203 | Build approximately 40 miles of new 345kV line from Grapevine to Chisholm | SPS | 0 | 0
Interconnection | 02 - Hitchland | DISIS-2017-001-P2 | ERIS | Hereford Northeast 115 kV Substation GEN-2017-058 Interconnection (Non-Shared NU) (SWPS) | 133015 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-058 (135 MW/Solar), into the Point of Interconnection (POI) at Hereford Northeast 115 kV Substation. | SPS | 36 | 1419861
Interconnection | 02 - Hitchland | DISIS-2017-001-P2 | ERIS | Hereford Northeast 115 kV Substation GEN-2017-058 Interconnection (TOIF) (SWPS) | 133014 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-058 (135 MW/Solar), into the Point of Interconnection (POI) at Hereford Northeast 115 kV Substation. | SPS | 36 | 701784
Current Study | 02 - Hitchland | DISIS-2017-001-P2 | ERIS | Potter County to Grapevine 345kV New Line (DISIS-2017-001) | 143245 | Build approximately 65 miles of new 345kV line from Potter County to Grapevine | SPS | 36 | 92000000
Interconnection | 02 - Hitchland | DISIS-2017-001-P2 | ERIS | Texas County 115 kV Substation GEN-2017-100 Inteconnection (Non-Shared NU) (SWPS) | 133081 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-100 (102.6 MW/Solar), into the Point of Interconnection (POI) at Texas County 115 kV Substation. | SPS | 36 | 17186637
Interconnection | 02 - Hitchland | DISIS-2017-001-P2 | ERIS | Texas County 115 kV Substation GEN-2017-100 Inteconnection (TOIF) (SWPS) | 133080 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-100 (102.6 MW/Solar), into the Point of Interconnection (POI) at Texas County 115 kV Substation. | SPS | 36 | 781840
Interconnection | 03 - Spearville | DISIS-2017-001-P2 | ERIS | Bear Creek - Johnson Corner 115 kV GEN-2017-052 Interconnection (Non-Shared NU) (SUNC) | 133007 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-052 (25 MW/Solar), into the Point of Interconnection (POI) at Bear Creek - Johnson Corner 115 kV. | SUNC | 24 | 3372070
Interconnection | 03 - Spearville | DISIS-2017-001-P2 | ERIS | Bear Creek - Johnson Corner 115 kV GEN-2017-052 Interconnection (TOIF) (SUNC) | 133006 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-052 (25 MW/Solar), into the Point of Interconnection (POI) at Bear Creek - Johnson Corner 115 kV. | SUNC | 24 | 1662749
Current Study | 03 - Spearville | DISIS-2017-001-P2 | ERIS | Degrassee 138kV Terminal Upgrades (DISIS-2017-001) (OKGE) | 143239 | Upgrade terminal equipment at Degrasse 138kV to achieve a minimum Spring/Emergency rating of 175 MVA | OGE | 0 | 0
Interconnection | 03 - Spearville | DISIS-2017-001-P2 | ERIS | Finney - Lamar 345 kV GEN-2017-032 Interconnection (Non-Shared NU) (SWPS) | 132981 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-032 (200 MW/Wind), into the Point of Interconnection (POI) at Finney - Lamar 345 kV. | SPS | 36 | 12750261
Interconnection | 03 - Spearville | DISIS-2017-001-P2 | ERIS | Finney - Lamar 345 kV GEN-2017-032 Interconnection (TOIF) (SWPS) | 132980 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-032 (200 MW/Wind), into the Point of Interconnection (POI) at Finney - Lamar 345 kV. | SPS | 36 | 1708037
Current Study | 03 - Spearville | DISIS-2017-001-P2 | ERIS | Finney 345kV Reactive Support (DISIS-2017-001) | 143263 | Install +250 MVAR Capacitor Bank(s) at Finney 345kV | SPS | 36 | 6207750
Current Study | 03 - Spearville | DISIS-2017-001-P2 | ERIS | Finney to G17-032 Tap 345kV Rebuild (DISIS-2017-001) | 143228 | Rebuild the existing Finney to G17-032 Tap 345kV 78.75 mile line to achieve a minimum Summer/Emergency rating of 425 MVA | SPS | 36 | 150000
Interconnection | 03 - Spearville | DISIS-2017-001-P2 | ERIS | Post Rock - Spearville 345 kV GEN-2017-021 Interconnection (Non-Shared NU) (ITCGP) | 132963 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-021 (200 MW/Wind), into the Point of Interconnection (POI) at Post Rock - Spearville 345 kV. | ITCGP | 36 | 15081109
Interconnection | 03 - Spearville | DISIS-2017-001-P2 | ERIS | Post Rock - Spearville 345 kV GEN-2017-021 Interconnection (TOIF) (ITCGP) | 132962 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-021 (200 MW/Wind), into the Point of Interconnection (POI) at Post Rock - Spearville 345 kV. | ITCGP | 36 | 1054767
Interconnection | 03 - Spearville | DISIS-2017-001-P2 | ERIS | Post Rock - Spearville 345 kV GEN-2017-099 Interconnection (Non-Shared NU) (ITCGP) | 133079 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-099 (200 MW/Wind), into the Point of Interconnection (POI) at Post Rock - Spearville 345 kV. | ITCGP | 36 | 15081109
Interconnection | 03 - Spearville | DISIS-2017-001-P2 | ERIS | Post Rock - Spearville 345 kV GEN-2017-099 Interconnection (TOIF) (ITCGP) | 133078 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-099 (200 MW/Wind), into the Point of Interconnection (POI) at Post Rock - Spearville 345 kV. | ITCGP | 36 | 1054767
Current Study | 03 - Spearville | DISIS-2017-001-P2 | ERIS | Rose Valley to Degrasse 138kV Rebuild (DISIS-2017-001) (WFEC) | 143238 | Rebuild the existing Rose Valley to Degrasse 138kV 3.2 mile line to achieve a minimum Spring/Emergency rating of 175 MVA | WFEC | 36 | 2080000
Interconnection | 03 - Spearville | DISIS-2017-001-P2 | ERIS | Thistle 345 kV Substation GEN-2017-018 Interconnection (Non-Shared NU) (ITCGP) | 132961 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-018 (190 MW/Solar), into the Point of Interconnection (POI) at Thistle 345 kV Substation. | ITCGP | 36 | 1412092
Interconnection | 03 - Spearville | DISIS-2017-001-P2 | ERIS | Thistle 345 kV Substation GEN-2017-018 Interconnection (Non-Shared NU) (OKGE) | 143117 | Potential interconnection impacts from the following generating facility, GEN-2017-018 (190 MW/Solar), into the Point of Interconnection (POI) at Thistle 345 kV Substation. | OGE | 6 | 30000
Interconnection | 03 - Spearville | DISIS-2017-001-P2 | ERIS | Thistle 345 kV Substation GEN-2017-018 Interconnection (Non-Shared NU) (WERE) | 143118 | Potential interconnection impacts from the following generating facility, GEN-2017-018 (190 MW/Solar), into the Point of Interconnection (POI) at Thistle 345 kV Substation. | Evergy | 36 | 13299
Interconnection | 03 - Spearville | DISIS-2017-001-P2 | ERIS | Thistle 345 kV Substation GEN-2017-018 Interconnection (TOIF) (ITCGP) | 132960 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-018 (190 MW/Solar), into the Point of Interconnection (POI) at Thistle 345 kV Substation. | ITCGP | 36 | 918132
Current Study | 03 - Spearville/09 - Nebraska | DISIS-2017-001-P2 | ERIS | Smokey Hils to Summit 230kV Rebuild (DISIS-2017-001) (MIDW) | 143240 | Rebuild the existing Smokey Hills to Summit 230kV 16.1 mile line to achieve a minimum Light/Emergency rating of 375 MVA | MIDW | 36 | 16500000
Current Study | 03 - Spearville/09 - Nebraska | DISIS-2017-001-P2 | ERIS | Smokey Hils to Summit 230kV Rebuild (DISIS-2017-001) (WERE) | 143242 | Rebuild the existing Smokey Hills to Summit 230kV 22.5 mile line to achieve a minimum Light/Emergency rating of 375 MVA | Evergy | 36 | 27323646
Interconnection | 04 - Northwest Kansas | DISIS-2017-001-P2 | ERIS | Elm Creek - Summit 345 kV GEN-2017-004 Interconnection (Non-Shared NU) (ITCGP) | 132937 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-004 (201.6 MW/Wind), into the Point of Interconnection (POI) at Elm Creek - Summit 345 kV. | ITCGP | 36 | 15081109
Interconnection | 04 - Northwest Kansas | DISIS-2017-001-P2 | ERIS | Elm Creek - Summit 345 kV GEN-2017-004 Interconnection (TOIF) (ITCGP) | 132936 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-004 (201.6 MW/Wind), into the Point of Interconnection (POI) at Elm Creek - Summit 345 kV. | ITCGP | 36 | 1054767
Interconnection | 04 - Northwest Kansas | DISIS-2017-001-P2 | ERIS | Mingo 345 kV Substation GEN-2017-013 Interconnection (Non-Shared NU) (SUNC) | 132955 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-013 (200 MW/Wind), into the Point of Interconnection (POI) at Mingo 345 kV Substation. | SUNC | 30 | 3269931
Interconnection | 04 - Northwest Kansas | DISIS-2017-001-P2 | ERIS | Mingo 345 kV Substation GEN-2017-013 Interconnection (TOIF) (SUNC) | 132954 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-013 (200 MW/Wind), into the Point of Interconnection (POI) at Mingo 345 kV Substation. | SUNC | 30 | 2447857
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Clovis Interchange 115 kV Substation GEN-2017-087 Interconnection (Non-Shared NU) (SWPS) | 133067 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-087 (128 MW/Solar), into the Point of Interconnection (POI) at Clovis Interchange 115 kV Substation. | SPS | 36 | 3610830
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Clovis Interchange 115 kV Substation GEN-2017-087 Interconnection (TOIF) (SWPS) | 133066 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-087 (128 MW/Solar), into the Point of Interconnection (POI) at Clovis Interchange 115 kV Substation. | SPS | 36 | 634734
Current Study | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Crawfish Draw 345/230kV Transformer Ckt 1 (DISIS-2017-001) | 143198 | Install a new 345/230kV Transformer at Crawfish Draw | SPS | 36 | 11430070
Current Study | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Crawfish Draw 765/345kV New Substation (DISIS-2017-001) | 143204 | Build a new Crawfish Draw 765/345kV Substation tapping the Tuco to Border 345kV Ckt 1 and Tuco to OKU 345kV Ckt 1. In addition, install a new 1000 MVar SVC for Dynamic Reactive Support at Crawfish Draw 765kV. Both the 765kV and the 345kV Crawfish Draw switchyards shall be constructed with breaker and a half bus schemes. Furthermore, interconnected double circuit lines connected to these switchyards or transformers connecting these switchyards shall not share adjacent breakers in the switchyard(s). | SPS | 36 | 286282000
Current Study | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Crawfish Draw 765/345kV New Transformer (DISIS-2017-001) | 143207 | Install two new 765/345kV Transformers at Crawfish Draw | SPS | 36 | 40000000
Current Study | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Crawfish Draw Tap to Tuco to Border 345kV Ckt 1 (DISIS-2017-001) (OKGE) | 143219 | Tap Tuco to Border 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | OGE | 36 | 50000
Current Study | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Crawfish Draw Tap to Tuco to Border 345kV Ckt 1 (DISIS-2017-001) (SWPS) | 143194 | Tap Tuco to Border 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | SPS | 36 | 8000000
Current Study | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Crawfish Draw Tap to Tuco to OKU 345kV Ckt 1 (DISIS-2017-001) (AEPW) | 143195 | Tap Tuco to OKU 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | AEP | 36 | 1300000
Current Study | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Crawfish Draw Tap to Tuco to OKU 345kV Ckt 1 (DISIS-2017-001) (SWPS) | 143220 | Tap Tuco to OKU 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation | SPS | 36 | 8000000
Current Study | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Crawfish Draw to Seminole 765kV New Line Double Circuit (DISIS-2017-001) (OKGE) | 143211 | Build approximately 80 miles of new double circuit 765kV line from Crawfish Draw to Seminole | OGE | 35 | 660408000
Current Study | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Crawfish Draw to Seminole 765kV New Line Double Circuit (DISIS-2017-001) (SWPS) | 143221 | Build approximately 265 miles of new double circuit 765kV line from Crawfish Draw to Seminole | SPS | 36 | 662000000
Current Study | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Crossroads 765/345kV New Transformer (DISIS-2017-001) | 143209 | Expand Crossroads 765kV Substation and install a new 765/345 transformer | SPS | 36 | 20000000
Current Study | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Crossroads 765kV Reactive Support (DISIS-2017-001) | 143325 | Stability identified need to install 600 MVar SVC for Dynamic Reactive Support at Crossroads 765kV | SPS | 36 | 135769200
Current Study | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Crossroads to Crawfish Draw 765kV New Line (DISIS-2017-001) | 143210 | Build approximately 85 miles of new 765kV line from Crossroads to Crawfish Draw | SPS | 36 | 380000000
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Eddy County - Tolk 345 kV GEN-2017-078 Interconnection (Non-Shared NU) (SWPS) | 133049 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-078 (300 MW/Wind), into the Point of Interconnection (POI) at Eddy County - Tolk 345 kV. | SPS | 36 | 1098575
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Eddy County - Tolk 345 kV GEN-2017-078 Interconnection (TOIF) (SWPS) | 133048 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-078 (300 MW/Wind), into the Point of Interconnection (POI) at Eddy County - Tolk 345 kV. | SPS | 36 | 1644416
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Hobbs 230 kV Substation GEN-2017-104 Interconnection (Non-Shared NU) (SWPS) | 133083 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-104 (240 MW/Solar), into the Point of Interconnection (POI) at Hobbs 230 kV Substation. | SPS | 36 | 2530072
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Hobbs 230 kV Substation GEN-2017-104 Interconnection (TOIF) (SWPS) | 133082 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-104 (240 MW/Solar), into the Point of Interconnection (POI) at Hobbs 230 kV Substation. | SPS | 36 | 1324666
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Needmore 230 kV Substation GEN-2017-039 Interconnection (Non-Shared NU) (SWPS) | 132991 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-039 (200.1 MW/Wind), into the Point of Interconnection (POI) at Needmore 230 kV Substation. | SPS | 36 | 693659
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Needmore 230 kV Substation GEN-2017-039 Interconnection (TOIF) (SWPS) | 132990 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-039 (200.1 MW/Wind), into the Point of Interconnection (POI) at Needmore 230 kV Substation. | SPS | 36 | 933132
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Newhart 115 kV Substation GEN-2016-172 Interconnection (Non-Shared NU) (SWPS) | 132931 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-172 (231 MW/Wind), into the Point of Interconnection (POI) at Newhart 115 kV Substation. | SPS | 36 | 705336
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Newhart 115 kV Substation GEN-2016-172 Interconnection (TOIF) (SWPS) | 132930 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-172 (231 MW/Wind), into the Point of Interconnection (POI) at Newhart 115 kV Substation. | SPS | 36 | 627807
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Norton 115 kV Switching Station GEN-2017-016 Interconnection (Non-Shared NU) (SWPS) | 132959 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-016 (33 MW/Solar), into the Point of Interconnection (POI) at Norton 115 kV Switching Station. | SPS | 36 | 1069895
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Norton 115 kV Switching Station GEN-2017-016 Interconnection (TOIF) (SWPS) | 132958 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-016 (33 MW/Solar), into the Point of Interconnection (POI) at Norton 115 kV Switching Station. | SPS | 36 | 617431
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Norton 115 kV Switching Station GEN-2017-069 Interconnection (Non-Shared NU) (SWPS) | 133033 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-069 (3.6 MW/Solar), into the Point of Interconnection (POI) at Norton 115 kV Switching Station. | SPS | 0 | 0
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Norton 115 kV Switching Station GEN-2017-069 Interconnection (TOIF) (SWPS) | 133032 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-069 (3.6 MW/Solar), into the Point of Interconnection (POI) at Norton 115 kV Switching Station. | SPS | 0 | 0
Current Study | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Norton to Pleasant Hills 115kV Rebuild (DISIS-2017-001) | 143241 | Rebuild the existing Norton to Pleasant Hills 115kV 54.54 mile line to achieve a minimum Light/Emergency rating of 150 MVA | SPS | 36 | 150000
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Oklaunion 345 kV Substation GEN-2017-033 Interconnection (Non-Shared NU) (AEPW) | 132983 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-033 (200 MW/Wind), into the Point of Interconnection (POI) at Oklaunion 345 kV Substation. | AEP | 36 | 3877147.5
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Oklaunion 345 kV Substation GEN-2017-033 Interconnection (TOIF) (AEPW) | 132982 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-033 (200 MW/Wind), into the Point of Interconnection (POI) at Oklaunion 345 kV Substation. | AEP | 36 | 1373275
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Oklaunion 345 kV Substation GEN-2017-065 Interconnection (Non-Shared NU) (AEPW) | 133025 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-065 (200.3 MW/Solar), into the Point of Interconnection (POI) at Oklaunion 345 kV Substation. | AEP | 36 | 3877147.5
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Oklaunion 345 kV Substation GEN-2017-065 Interconnection (TOIF) (AEPW) | 133024 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-065 (200.3 MW/Solar), into the Point of Interconnection (POI) at Oklaunion 345 kV Substation. | AEP | 36 | 1373275
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Pleasant Hill 230 kV Substation GEN-2017-007 Interconnection (Non-Shared NU) (SWPS) | 132943 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-007 (297.5 MW/Wind), into the Point of Interconnection (POI) at Pleasant Hill 230 kV Substation. | SPS | 36 | 1865013
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Pleasant Hill 230 kV Substation GEN-2017-007 Interconnection (TOIF) (SWPS) | 132942 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-007 (297.5 MW/Wind), into the Point of Interconnection (POI) at Pleasant Hill 230 kV Substation. | SPS | 36 | 1074589
Current Study | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Seminole 765/345 New Transformer (DISIS-2017-001) | 143208 | Expand Seminole 345kV substation to include a new 765kV switchyard connected by a new 765/345kV transformer. In addition, install a new 600 MVar SVC for Dynamic Reactive Support at Seminole 765kV. | OGE | 36 | 159919200
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Swisher 115 kV Substation GEN-2016-039 Interconnection (Non-Shared NU) (SWPS) | 132905 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-039 (112 MW/Solar), into the Point of Interconnection (POI) at Swisher 115 kV Substation. | SPS | 36 | 5147608
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Swisher 115 kV Substation GEN-2016-039 Interconnection (TOIF) (SWPS) | 132904 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-039 (112 MW/Solar), into the Point of Interconnection (POI) at Swisher 115 kV Substation. | SPS | 36 | 587191
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Tolk 230 kV Substation GEN-2017-026 Interconnection (Non-Shared NU) (SWPS) | 132971 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-026 (235 MW/Wind), into the Point of Interconnection (POI) at Tolk 230 kV Substation. | SPS | 36 | 1543568
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Tolk 230 kV Substation GEN-2017-026 Interconnection (TOIF) (SWPS) | 132970 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-026 (235 MW/Wind), into the Point of Interconnection (POI) at Tolk 230 kV Substation. | SPS | 36 | 901002
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Tolk 230 kV Substation GEN-2017-080 Interconnection (Non-Shared NU) (SWPS) | 133053 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-080 (525 MW/Solar), into the Point of Interconnection (POI) at Tolk 230 kV Substation. | SPS | 36 | 2141174
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Tolk 230 kV Substation GEN-2017-080 Interconnection (TOIF) (SWPS) | 133052 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-080 (525 MW/Solar), into the Point of Interconnection (POI) at Tolk 230 kV Substation. | SPS | 36 | 840720
Contingent | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Tolk 345/230 kV CKT 2 Transformer (DISIS-2016-002) | 122568 | Build new 345/230 kV Transformer Ckt 2 at Tolk to achieve a minimum emergency rating of 921 MVA on the Crossroads - Tolk 345 kV Ckt 1 line. | SPS | 24 | 14055360
Current Study | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Tolk 345/230kV Transformer Ckt 3 (DISIS-2017-001) | 143248 | Install a new 345/230kV Transformer at Tolk | SPS | 36 | 14055360
Current Study | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Tolk to Tuco 345kV New Line (DISIS-2017-001) | 143250 | Build approximately 54 miles of new 345kV line from Tolk to Tuco | SPS | 36 | 61799976
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Tuco 230 kV Substation GEN-2017-059 Interconnection (Non-Shared NU) (SWPS) | 133017 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-059 (90 MW/Solar), into the Point of Interconnection (POI) at Tuco 230 kV Substation. | SPS | 36 | 849034
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Tuco 230 kV Substation GEN-2017-059 Interconnection (TOIF) (SWPS) | 133016 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-059 (90 MW/Solar), into the Point of Interconnection (POI) at Tuco 230 kV Substation. | SPS | 36 | 1231645
Current Study | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Tuco to Crawfish Draw 345kV Rebuild (DISIS-2017-001) | 143251 | Rebuild the existing Tuco to Crawfish Draw 345kV 1.54 mile line to achieve a minimum light/emergency rating of 1094 MVA | SPS | 36 | 1762443
Interconnection | 07 - Southwestern Oklahoma | DISIS-2017-001-P2 | ERIS | Chisholm - Gracemont 345 kV GEN-2016-037 Interconnection (Non-Shared NU) (AEPW) | 132903 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-037 (300 MW/Wind), into the Point of Interconnection (POI) at Chisholm - Gracemont 345 kV. | AEP | 36 | 20639740
Interconnection | 07 - Southwestern Oklahoma | DISIS-2017-001-P2 | ERIS | Chisholm - Gracemont 345 kV GEN-2016-037 Interconnection (Non-Shared NU) (OKGE) | 143127 | Potential interconnection impacts from the following generating facility, GEN-2016-037 (300 MW/Wind), into the Point of Interconnection (POI) at Chisholm - Gracemont 345 kV. | OGE | 10 | 15000
Interconnection | 07 - Southwestern Oklahoma | DISIS-2017-001-P2 | ERIS | Chisholm - Gracemont 345 kV GEN-2016-037 Interconnection (TOIF) (AEPW) | 132902 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-037 (300 MW/Wind), into the Point of Interconnection (POI) at Chisholm - Gracemont 345 kV. | AEP | 36 | 1146800
Interconnection | 07 - Southwestern Oklahoma | DISIS-2017-001-P2 | ERIS | Lake Creek SW - Russell SW 69 kV GEN-2017-051 Interconnection (Non-Shared NU) (WFEC) | 133005 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-051 (30 MW/Solar), into the Point of Interconnection (POI) at Lake Creek SW - Russell SW 69 kV. | WFEC | 36 | 4750000
Interconnection | 07 - Southwestern Oklahoma | DISIS-2017-001-P2 | ERIS | Lake Creek SW - Russell SW 69 kV GEN-2017-051 Interconnection (TOIF) (WFEC) | 133004 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-051 (30 MW/Solar), into the Point of Interconnection (POI) at Lake Creek SW - Russell SW 69 kV. | WFEC | 36 | 400000
Interconnection | 07 - Southwestern Oklahoma | DISIS-2017-001-P2 | ERIS | Snyder - Cache 138 kV GEN-2017-036 Interconnection (Non-Shared NU) (AEPW) | 132985 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-036 (100 MW/Solar), into the Point of Interconnection (POI) at Snyder 138 kV Substation. | AEP | 36 | 8198087
Interconnection | 07 - Southwestern Oklahoma | DISIS-2017-001-P2 | ERIS | Snyder - Cahce 138 kV GEN-2017-036 Interconnection (TOIF) (AEPW) | 132984 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-036 (100 MW/Solar), into the Point of Interconnection (POI) at Snyder 138 kV Substation. | AEP | 36 | 1337068
Current Study | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Afton to Ketchum 161kV Rebuild (DISIS-2017-001) | 143190 | Rebuild the existing Afton to Ketchum 161kV 12.8 mile line to achieve a minimum Summer/Emergency rating of 225 MVA | GRDA | 18 | 906000
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Altoona - Parson 138 kV GEN-2017-022 Interconnection (Non-Shared NU) (WERE) | 132965 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-022 (65 MW/Solar), into the Point of Interconnection (POI) at Altoona - Parson 138 kV. | Evergy | 36 | 4790295
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Altoona - Parson 138 kV GEN-2017-022 Interconnection (TOIF) (WERE) | 132964 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-022 (65 MW/Solar), into the Point of Interconnection (POI) at Altoona - Parson 138 kV. | Evergy | 36 | 696118
Current Study | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Beaver to Eureka 161kV Rebuild (DISIS-2017-001) (AEP) | 143265 | Rebuild the existing Beaver to Eureka 161kV 1.22 mile line section to achieve a minimum light/emergency rating of 258 MVA | AEP | 0 | 0
Current Study | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Beaver to Eureka 161kV Rebuild (DISIS-2017-001) (SWPA) | 143264 | Rebuild the existing Beaver to Eureka 161kV 6 mile line section to achieve a minimum light/emergency rating of 258 MVA | SWPA | 36 | 5869344
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Canadian River - Muskogee - Seminole 345 kV GEN-2017-040 Interconnection (Non-Shared NU) (OKGE) | 132993 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-040 (200.1 MW/Wind), into the Point of Interconnection (POI) at Canadian River - Muskogee - Seminole 345 kV. | OGE | 18 | 5741321
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Canadian River - Muskogee - Seminole 345 kV GEN-2017-040 Interconnection (TOIF) (OKGE) | 132992 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-040 (200.1 MW/Wind), into the Point of Interconnection (POI) at Canadian River - Muskogee - Seminole 345 kV. | OGE | 18 | 599979
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Canadian River - Muskogee - Seminole 345 kV GEN-2017-092 Interconnection (Non-Shared NU) (OKGE) | 133073 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-092 (200 MW/Solar), into the Point of Interconnection (POI) at Canadian River - Muskogee - Seminole | OGE | 18 | 5741321
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Canadian River - Muskogee - Seminole 345 kV GEN-2017-092 Interconnection (TOIF) (OKGE) | 133072 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-092 (200 MW/Solar), into the Point of Interconnection (POI) at Canadian River - Muskogee - Seminole | OGE | 18 | 599979
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Dry Gulch 161 kV Substation GEN-2017-073 Interconnection (Non-Shared NU) (GRDA) | 133039 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-073 (72.5 MW/Solar), into the Point of Interconnection (POI) at Dry Gulch 161 kV Substation. | GRDA | 18 | 50000
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Dry Gulch 161 kV Substation GEN-2017-073 Interconnection (TOIF) (GRDA) | 133038 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-073 (72.5 MW/Solar), into the Point of Interconnection (POI) at Dry Gulch 161 kV Substation. | GRDA | 18 | 1103400
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Explorer - Claremore 69 kV GEN-2017-077 Interconnection (Non-Shared NU) (AEPW) | 133047 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-077 (124.7 MW/Solar), into the Point of Interconnection (POI) at Explorer - Claremore 69 kV. | AEP | 36 | 10334726
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Explorer - Claremore 69 kV GEN-2017-077 Interconnection (TOIF) (AEPW) | 133046 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-077 (124.7 MW/Solar), into the Point of Interconnection (POI) at Explorer - Claremore 69 kV. | AEP | 36 | 1146800
Current Study | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Franklin 161/69kV Transformer Ckt 2 (DISIS-2017-001) | 143230 | Install a new 161/69kV Transformer at Franklin | Evergy | 36 | 5320916
Current Study | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Franklin to G17-005 Tap 161kV Rebuild (DISIS-2017-001) | 143199 | Rebuild the existing Franklin to G17-005 Tap 161kV 20.56 mile line to achieve a minimum Winter/Emergency rating of 300 MVA | Evergy | 36 | 37570337
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | GRDA1 - CLARMR5 161 kV GEN-2017-061 Interconnection (Non-Shared NU) (GRDA) | 133021 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-061 (101.5 MW/Solar), into the Point of Interconnection (POI) at GRDA1 - CLARMR5 161 kV. | GRDA | 0 | 0
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | GRDA1 - CLARMR5 161 kV GEN-2017-061 Interconnection (TOIF) (GRDA) | 133020 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-061 (101.5 MW/Solar), into the Point of Interconnection (POI) at GRDA1 - CLARMR5 161 kV. | GRDA | 18 | 4548000
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Greenwood 138 kV Substation GEN-2017-071 Interconnection (Non-Shared NU) (OKGE) | 133035 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-071 (124.7 MW/Solar), into the Point of Interconnection (POI) at Greenwood 138 kV Substation. | OGE | 15 | 1721000
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Greenwood 138 kV Substation GEN-2017-071 Interconnection (TOIF) (OKGE) | 133034 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-071 (124.7 MW/Solar), into the Point of Interconnection (POI) at Greenwood 138 kV Substation. | OGE | 15 | 515000
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Greenwood 138 kV Substation GEN-2017-072 Interconnection (Non-Shared NU) (OKGE) | 133037 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-072 (52.2 MW/Solar), into the Point of Interconnection (POI) at Greenwood 138 kV Substation. | OGE | 15 | 1721000
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Greenwood 138 kV Substation GEN-2017-072 Interconnection (TOIF) (OKGE) | 133036 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-072 (52.2 MW/Solar), into the Point of Interconnection (POI) at Greenwood 138 kV Substation. | OGE | 15 | 515000
Current Study | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Litchfield to Asbury Plant 161kV Rebuild (DISIS-2017-001) (EMDE) | 143232 | Rebuild the existing Litchfield to Asbury Plant 161kV 5 mile line to achieve a minimum Winter/Emergency rating of 325 MVA | EMDE | 36 | 8610000
Current Study | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Litchfield to Asbury Plant 161kV Rebuild (DISIS-2017-001) (WERE) | 143235 | Rebuild the existing Litchfield to Asbury Plant 161kV 1.6 mile line to achieve a minimum Winter/Emergency rating of 325 MVA | Evergy | 36 | 2332649
Current Study | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Litchfield to Franklin 161kV Rebuild (DISIS-2017-001) | 143223 | Rebuild the existing Litchfield to Franklin 161kV 6.22 mile line to achieve a minimum Winter/Emergency rating of 300 MVA | Evergy | 36 | 10661540
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Marmaton - Litchfield 161 kV GEN-2017-005 Interconnection (Non-Shared NU) (WERE) | 132939 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-005 (195 MW/Wind), into the Point of Interconnection (POI) at Marmaton - Litchfield 161 kV. | Evergy | 36 | 9467883
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Marmaton - Litchfield 161 kV GEN-2017-005 Interconnection (TOIF) (WERE) | 132938 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-005 (195 MW/Wind), into the Point of Interconnection (POI) at Marmaton - Litchfield 161 kV. | Evergy | 36 | 833096
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Neosho - Caney River 345 kV GEN-2017-009 Interconnection (Non-Shared NU) (WERE) | 132947 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-009 (302.5 MW/Wind), into the Point of Interconnection (POI) at Neosho - Caney River 345 kV. | Evergy | 36 | 15017048
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Neosho - Caney River 345 kV GEN-2017-009 Interconnection (TOIF) (WERE) | 132946 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-009 (302.5 MW/Wind), into the Point of Interconnection (POI) at Neosho - Caney River 345 kV. | Evergy | 36 | 1311181
Current Study | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Neosho to G17-009 Tap Rebuild (DISIS-2017-001) | 143246 | Rebuild the existing Neosho to G17-009 345kV 18.17 mile line to achieve a minimum Winter/Emergency rating of 1260 MVA | Evergy | 36 | 32884027
Current Study | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Pensacola to Ketchum 161kV Rebuild (DISIS-2017-001) | 143247 | Rebuild the existing Pensacole to Ketchum 161kV 4.8 mile line to achieve a minimum Summer/Emergency rating of 225 MVA | GRDA | 18 | 1736000
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Pryor Junction 138 kV Substation GEN-2017-074 Interconnection (Non-Shared NU) (AEPW) | 133041 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-074 (72.5 MW/Solar), into the Point of Interconnection (POI) at Pryor Junction 138 kV Substation. | AEP | 30 | 1365027
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Pryor Junction 138 kV Substation GEN-2017-074 Interconnection (TOIF) (AEPW) | 133040 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-074 (72.5 MW/Solar), into the Point of Interconnection (POI) at Pryor Junction 138 kV Substation. | AEP | 30 | 1146800
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Viola 345 kV Substation GEN-2017-086 Interconnection (Non-Shared NU) (OKGE) | 143125 | Potential interconnection impacts from the following generating facility, GEN-2017-086 (150 MW/Wind), into the Point of Interconnection (POI) at Viola 345 kV Substation. | OGE | 4 | 20000
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Viola 345 kV Substation GEN-2017-086 Interconnection (Non-Shared NU) (WERE) | 133065 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-086 (150 MW/Wind), into the Point of Interconnection (POI) at Viola 345 kV Substation. | Evergy | 36 | 38569
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Viola 345 kV Substation GEN-2017-086 Interconnection (TOIF) (WERE) | 133064 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-086 (150 MW/Wind), into the Point of Interconnection (POI) at Viola 345 kV Substation. | Evergy | 0 | 0
Contingent | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Viola 345/138kV Transformer CKT 2 (DISIS-2016-002-2) | 122792 | Build second 345/138/13.8kV transformer at Viola. | Evergy | 24 | 9038339
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Wichita 345 kV Substation GEN-2017-068 Interconnection (Non-Shared NU) (WERE) | 133031 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-068 (103.5 MW/Solar), into the Point of Interconnection (POI) at Wichita 345 kV Substation. | Evergy | 36 | 15017048
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Wichita 345 kV Substation GEN-2017-068 Interconnection (TOIF) (WERE) | 133030 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-068 (103.5 MW/Solar), into the Point of Interconnection (POI) at Wichita 345 kV Substation. | Evergy | 36 | 1311181
Contingent | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Wolf Creek to Blackberry 345kV | 122598 | Build a new 86 mile 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | Evergy | 60 | 142601178
Current Study | 09 - Nebraska | DISIS-2017-001-P2 | ERIS | Cooper 345kV Terminal Upgrades (DISIS-2017-001) (NPPD) | 143215 | Upgrade terminal equipment at Cooper 345 kV line to achieve a minimum Spring/Emergency rating of 1295 MVA | NPPD | 36 | 3000000
Current Study | 09 - Nebraska | DISIS-2017-001-P2 | ERIS | Cooper Joe 345kV New Substation (DISIS-2017-001) | 143227 | Build a new 345 kV substation at Cooper Joe. Tap the Cooper to St. Joe 345kV line 20 miles from St. Joe 345kV | GMO | 36 | 16243869
Current Study | 09 - Nebraska | DISIS-2017-001-P2 | ERIS | Cooper Joe to Cooper 345kV Rebuild (DISIS-2017-001) (KCPL) | 143212 | Rebuild Cooper Joe to Cooper 345 kV 22.2 miles line to achieve a minimum Spring/Emergency rating of 1295 MVA | Evergy | 36 | 40437842.97
Current Study | 09 - Nebraska | DISIS-2017-001-P2 | ERIS | Cooper Joe to Cooper 345kV Rebuild (DISIS-2017-001) (OPPD) | 143214 | Rebuild Cooper Joe to Cooper 345 kV 26.6 miles line to achieve a minimum Spring/Emergency rating of 1295 MVA | OPPD | 36 | 29640000
Current Study | 09 - Nebraska | DISIS-2017-001-P2 | ERIS | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | 143217 | Build approximately 6 miles of new 345kV line from Cooper Joe to Hoyt | GMO | 36 | 13910618
Current Study | 09 - Nebraska | DISIS-2017-001-P2 | ERIS | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | 143218 | Build approximately 60 miles of new 345kV line from Cooper Joe to Hoyt | Evergy | 36 | 132224914
Current Study | 09 - Nebraska | DISIS-2017-001-P2 | ERIS | Dixon County to Twin Church 230kV Rebuild (DISIS-2017-001) | 143258 | Rebuild the existing Dixon County to Twin Church 230kV 27.7 mile line to achieve a minimum light/emergency rating of 325 MVA | NPPD | 36 | 24473199
Interconnection | 09 - Nebraska | DISIS-2017-001-P2 | ERIS | Friend 115 kV Substation GEN-2017-085 Interconnection (Non-Shared NU) (NPPD) | 133063 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-085 (.6 MW/Wind), into the Point of Interconnection (POI) at Friend 115 kV Substation. | NPPD | 0 | 0
Interconnection | 09 - Nebraska | DISIS-2017-001-P2 | ERIS | Friend 115 kV Substation GEN-2017-085 Interconnection (TOIF) (NPPD) | 133062 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-085 (.6 MW/Wind), into the Point of Interconnection (POI) at Friend 115 kV Substation. | NPPD | 0 | 0
Current Study | 09 - Nebraska | DISIS-2017-001-P2 | ERIS | Hoskins 345/230kV Transformer T4 Replacement (DISIS-2017-001) | 143200 | Replace the existing Hoskins 345/230kV Transformer to achieve a minimum emergency rating of 406 MVA | NPPD | 36 | 15200000
Current Study | 09 - Nebraska | DISIS-2017-001-P2 | ERIS | Keystone to Sidney 345kV Ckt 2 (DISIS-2017-001) (NPPD) | 143205 | Build approximately 80 miles of new 345kV line from Keystone to Sidney | NPPD | 36 | 203000000
Current Study | 09 - Nebraska | DISIS-2017-001-P2 | ERIS | Keystone to Sidney 345kV Ckt 2 (DISIS-2017-001) (TSGT) | 143234 | Review for potential impacts to TSGT facilities from Keystone to Sidney Ckt 2 | TSGT | 0 | 0
Interconnection | 09 - Nebraska | DISIS-2017-001-P2 | ERIS | Moore - Pauline 345 kV GEN-2017-008 Interconnection (Non-Shared NU) (NPPD) | 132945 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-008 (305 MW/Solar), into the Point of Interconnection (POI) at Moore - Pauline 345 kV Substation. | NPPD | 36 | 1200000
Interconnection | 09 - Nebraska | DISIS-2017-001-P2 | ERIS | Moore - Pauline 345 kV GEN-2017-008 Interconnection (TOIF) (NPPD) | 132944 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-008 (305 MW/Solar), into the Point of Interconnection (POI) at Moore - Pauline 345 kV Substation. | NPPD | 36 | 1200000
Current Study | 09 - Nebraska | DISIS-2017-001-P2 | ERIS | Potter County 345/230kV Transformer Ckt 2 (DISIS-2017-001) | 143252 | Install a new 345/230kV Transformer at Potter County | SPS | 36 | 12583652
Current Study | 09 - Nebraska | DISIS-2017-001-P2 | ERIS | Sidney 345kV Terminal Upgrades (DISIS-2017-001) (BEPC) | 143231 | Upgrade terminal equipment at Sidney 345kV to accept Keystone to Sidney Ckt 2 | BEPC | 20 | 5501302
Interconnection | 09 - Nebraska | DISIS-2017-001-P2 | ERIS | Turtle Creek 345 kV Substation GEN-2016-159 Interconnection (Non-Shared NU) (NPPD) | 132927 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-159 (427.8 MW/Wind), into the Point of Interconnection (POI) at Hoskins 345 kV Substation. | NPPD | 36 | 2900000
Interconnection | 09 - Nebraska | DISIS-2017-001-P2 | ERIS | Turtle Creek 345 kV Substation GEN-2016-159 Interconnection (TOIF) (NPPD) | 132926 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-159 (427.8 MW/Wind), into the Point of Interconnection (POI) at Hoskins 345 kV Substation. | NPPD | 36 | 2900000
Interconnection | 09 - Nebraska | DISIS-2017-001-P2 | ERIS | Wagener 115 kV Substation GEN-2017-055 Interconnection (Non-Shared NU) (LES) | 133011 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-055 (228.3 MW/Solar), into the Point of Interconnection (POI) at Wagener 115 kV Substation. | LES | 18 | 1080000
Interconnection | 09 - Nebraska | DISIS-2017-001-P2 | ERIS | Wagener 115 kV Substation GEN-2017-055 Interconnection (TOIF) (LES) | 133010 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-055 (228.3 MW/Solar), into the Point of Interconnection (POI) at Wagener 115 kV Substation. | LES | 18 | 250000
Interconnection | 09 - Nebraska | DISIS-2017-001-P2 | ERIS | Wildhorse - Covalt 115 kV GEN-2017-031 Interconnection (Non-Shared NU) (TSGT) | 132979 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-031 (100 MW/Wind), into the Point of Interconnection (POI) at Wildhorse - Covalt 115 kV. | TSGT | 24 | 736000
Interconnection | 09 - Nebraska | DISIS-2017-001-P2 | ERIS | Wildhorse - Covalt 115 kV GEN-2017-031 Interconnection (TOIF) (TSGT) | 132978 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-031 (100 MW/Wind), into the Point of Interconnection (POI) at Wildhorse - Covalt 115 kV. | TSGT | 24 | 3271000
Current Study | 09 - Nebraska/13 - Northeast Kansas/Northwest Missouri | DISIS-2017-001-P2 | ERIS | Holt to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | 143259 | Build approximately 26 miles of new 345kV line from Holt to Hoyt | GMO | 36 | 58576716
Current Study | 09 - Nebraska/13 - Northeast Kansas/Northwest Missouri | DISIS-2017-001-P2 | ERIS | Holt 345kV Terminal Upgrades (DISIS-2017-001) (TMO) | 143225 | Upgrade terminal equipment at Holt 345kV to accept Holt to Holt new line | TSMO | 36 | 1306904
Current Study | 09 - Nebraska/13 - Northeast Kansas/Northwest Missouri | DISIS-2017-001-P2 | ERIS | Holt to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | 143213 | Build approximately 100 miles of new 345kV line from Holt to Hoyt | Evergy | 36 | 163257734
Interconnection | 10 - Southeast Oklahoma/Northeast Texas | DISIS-2017-001-P2 | ERIS | Hosston 69 kV Substation GEN-2017-057 Interconnection (Non-Shared NU) (AEPW) | 133013 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-057 (72.5 MW/Solar), into the Point of Interconnection (POI) at Houston 69 kV Substation. | AEP | 36 | 17032809
Interconnection | 10 - Southeast Oklahoma/Northeast Texas | DISIS-2017-001-P2 | ERIS | Hosston 69 kV Substation GEN-2017-057 Interconnection (TOIF) (AEPW) | 133012 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-057 (72.5 MW/Solar), into the Point of Interconnection (POI) at Houston 69 kV Substation. | AEP | 36 | 1120262
Interconnection | 12 - Northwest Arkansas | DISIS-2017-001-P2 | ERIS | Asbury Plant 161 kV Substation GEN-2017-082 Interconnection (Non-Shared NU) (EDE) | 133057 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-082 (149.4 MW/Solar), into the Point of Interconnection (POI) at Asbury Plant 161 kV Substation. | EMDE | 0 | 0
Interconnection | 12 - Northwest Arkansas | DISIS-2017-001-P2 | ERIS | Asbury Plant 161 kV Substation GEN-2017-082 Interconnection (Non-Shared NU) (WERE) | 143123 | Potential interconnection impacts from the following generating facility, GEN-2017-082 (149.4 MW/Wind), into the Point of Interconnection (POI) at Asbury Plant 161 kV Substation. | Evergy | 36 | 6649
Interconnection | 12 - Northwest Arkansas | DISIS-2017-001-P2 | ERIS | Asbury Plant 161 kV Substation GEN-2017-082 Interconnection (TOIF) (EDE) | 133056 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-082 (149.4 MW/Solar), into the Point of Interconnection (POI) at Asbury Plant 161 kV Substation. | EMDE | 0 | 0
Interconnection | 12 - Northwest Arkansas | DISIS-2017-001-P2 | ERIS | Chamber Springs 161 kV Substation GEN-2017-076 Interconnection (Non-Shared NU) (AEPW) | 133045 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-076 (52.2 MW/Solar), into the Point of Interconnection (POI) at Chamber Springs 161 kV Substation. | AEP | 36 | 1406646
Interconnection | 12 - Northwest Arkansas | DISIS-2017-001-P2 | ERIS | Chamber Springs 161 kV Substation GEN-2017-076 Interconnection (TOIF) (AEPW) | 133044 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-076 (52.2 MW/Solar), into the Point of Interconnection (POI) at Chamber Springs 161 kV Substation. | AEP | 36 | 1193983
Interconnection | 12 - Northwest Arkansas | DISIS-2017-001-P2 | ERIS | LaRussell Energy Center 161 kV Substation GEN-2017-060 Interconnection (Non-Shared NU) (EDE) | 133019 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-060 (149.4 MW/Wind), into the Point of Interconnection (POI) at LaRussell Energy Center 161 kV Substation. | EMDE | 0 | 0
Interconnection | 12 - Northwest Arkansas | DISIS-2017-001-P2 | ERIS | LaRussell Energy Center 161 kV Substation GEN-2017-060 Interconnection (TOIF) (EDE) | 133018 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-060 (149.4 MW/Wind), into the Point of Interconnection (POI) at LaRussell Energy Center 161 kV Substation. | EMDE | 0 | 0
Interconnection | 13 - Northeast Kansas/Northwest Missouri | DISIS-2017-001-P2 | ERIS | Adrian 161 kV Substation GEN-2017-090 Interconnection (Non-Shared NU) (KCPL) | 133069 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-090 (150 MW/Solar), into the Point of Interconnection (POI) at Adrian 161 kV Substation. | Evergy | 36 | 10177602
Interconnection | 13 - Northeast Kansas/Northwest Missouri | DISIS-2017-001-P2 | ERIS | Adrian 161 kV Substation GEN-2017-090 Interconnection (TOIF) (KCPL) | 133068 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-090 (150 MW/Solar), into the Point of Interconnection (POI) at Adrian 161 kV Substation. | Evergy | 36 | 824356
Interconnection | 13 - Northeast Kansas/Northwest Missouri | DISIS-2017-001-P2 | ERIS | Eastown - Iatan 345 kV GEN-2017-030 Interconnection (Non-Shared NU) (KCPL) | 132977 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-030 (200 MW/Wind), into the Point of Interconnection (POI) at Eastown - Iatan 345 kV. | Evergy | 36 | 12324396
Interconnection | 13 - Northeast Kansas/Northwest Missouri | DISIS-2017-001-P2 | ERIS | Eastown - Iatan 345 kV GEN-2017-030 Interconnection (TOIF) (KCPL) | 132976 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-030 (200 MW/Wind), into the Point of Interconnection (POI) at Eastown - Iatan 345 kV. | Evergy | 36 | 1862044
Interconnection | 14 - South Central Oklahoma | DISIS-2017-001-P2 | ERIS | Frogville 138 kV Substation GEN-2017-024 Interconnection (Non-Shared NU) (WFEC) | 132969 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-024 (50 MW/Solar), into the Point of Interconnection (POI) at Frogville 138 kV Substation. | WFEC | 36 | 4750000
Interconnection | 14 - South Central Oklahoma | DISIS-2017-001-P2 | ERIS | Frogville 138 kV Substation GEN-2017-024 Interconnection (TOIF) (WFEC) | 132968 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-024 (50 MW/Solar), into the Point of Interconnection (POI) at Frogville 138 kV Substation. | WFEC | 36 | 400000
Interconnection | 14 - South Central Oklahoma | DISIS-2017-001-P2 | ERIS | Hugo - Sunnyside 345 kV GEN-2017-075 Interconnection (Non-Shared NU) (OKGE) | 133043 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-075 (200 MW/Solar), into the Point of Interconnection (POI) at Hugo - Sunnyside 345 kV. | OGE | 14 | 1430000
Interconnection | 14 - South Central Oklahoma | DISIS-2017-001-P2 | ERIS | Hugo - Sunnyside 345 kV GEN-2017-075 Interconnection (TOIF) (OKGE) | 133042 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-075 (200 MW/Solar), into the Point of Interconnection (POI) at Hugo - Sunnyside 345 kV. | OGE | 14 | 915000
Interconnection | 14 - South Central Oklahoma | DISIS-2017-001-P2 | ERIS | Hugo 138 kV Substation GEN-2017-023 Interconnection (Non-Shared NU) (WFEC) | 132967 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-023 (85 MW/Solar), into the Point of Interconnection (POI) at Hugo 138 kV Substaion. | WFEC | 0 | 0
Interconnection | 14 - South Central Oklahoma | DISIS-2017-001-P2 | ERIS | Hugo 138 kV Substation GEN-2017-023 Interconnection (TOIF) (WFEC) | 132966 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-023 (85 MW/Solar), into the Point of Interconnection (POI) at Hugo 138 kV Substaion. | WFEC | 36 | 750000
Interconnection | 14 - South Central Oklahoma | DISIS-2017-001-P2 | ERIS | Pooleville - Ratliff 138 kV GEN-2017-027 Interconnection (Non-Shared NU) (OKGE) | 132973 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-027 (140 MW/Wind), into the Point of Interconnection (POI) at Pooleville - Ratliff 138 kV. | OGE | 14 | 1396000
Interconnection | 14 - South Central Oklahoma | DISIS-2017-001-P2 | ERIS | Pooleville - Ratliff 138 kV GEN-2017-027 Interconnection (TOIF) (OKGE) | 132972 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-027 (140 MW/Wind), into the Point of Interconnection (POI) at Pooleville - Ratliff 138 kV. | OGE | 14 | 515000
Current Study | 14 - South Central Oklahoma | DISIS-2017-001-P2 | ERIS | Valiant 138kV Terminal Upgrades (DISIS-2017-001) (AEPW) | 143244 | Upgrade terminal equipment at Valiant to Hugo PP4 138kV to achieve a minimum winter/emergency rating of 305 MVA | AEP | 0 | 0
Current Study | 14 - South Central Oklahoma | DISIS-2017-001-P2 | ERIS | Valiant 138kV Terminal Upgrades (DISIS-2017-001) (WFEC) | 143243 | Upgrade terminal equipment at Valiant to Hugo PP4 138kV to achieve a minimum winter/emergency rating of 305 MVA | WFEC | 36 | 1490000
Interconnection | 15 - Eastern South Dakota | DISIS-2017-001-P2 | ERIS | Fort Thompson - Huron 230 kV GEN-2017-094 Interconnection (Non-Shared NU) (WAPA) | 122574 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-094 (200 MW/Wind), into the Point of Interconnection (POI) at Fort Thompson - Huron 230 kV. | WAPA | 36 | 9000000
Interconnection | 15 - Eastern South Dakota | DISIS-2017-001-P2 | ERIS | Fort Thompson - Huron 230 kV GEN-2017-094 Interconnection (TOIF) (WAPA) | 122573 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-094 (200 MW/Wind), into the Point of Interconnection (POI) at Fort Thompson - Huron 230 kV. | WAPA | 36 | 250000
Interconnection | 15 - Eastern South Dakota | DISIS-2017-001-P2 | ERIS | Fort Thompson - Leland Olds 345 kV GEN-2016-103 Interconnection (Non-Shared NU) (BEPC) | 132919 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-103 (250.7 MW/Wind), into the Point of Interconnection (POI) at Fort Thompson - Leland Olds 345 kV. | BEPC | 12 | 2005466
Interconnection | 15 - Eastern South Dakota | DISIS-2017-001-P2 | ERIS | Fort Thompson - Leland Olds 345 kV GEN-2016-103 Interconnection (TOIF) (BEPC) | 132918 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-103 (250.7 MW/Wind), into the Point of Interconnection (POI) at Fort Thompson - Leland Olds 345 kV. | BEPC | 12 | 1212933
Current Study | 15 - Eastern South Dakota | DISIS-2017-001-P2 | ERIS | Ft. Thompson 345kV Terminal Upgrades (DISIS-2017-001) (WAPA) | 143202 | Upgrade terminal equipment at Ft. Thompson 345kV to accept G16-017 Tap to Ft. Thompson Ckt 2 | WAPA | 36 | 7546339
Current Study | 15 - Eastern South Dakota | DISIS-2017-001-P2 | ERIS | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC) | 143201 | Build approximately 30 miles of new 345kV line from G16-017 Tap to Ft. Thompson | BEPC | 20 | 65900000
Current Study | 16 - Western North Dakota | DISIS-2017-001-P2 | ERIS | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | 143226 | Replace the existing Broadland 345/230kV Transformer to achieve a minimum Summer/Normal rating of 471 MVA | BEPC | 36 | 5906325
Current Study | 16 - Western North Dakota | DISIS-2017-001-P2 | ERIS | G17-010 Tap 230kV Reactive Support (DISIS-2017-001) | 143324 | Stability identified need to Install 135 MVar SVC for Dynamic Reactive Support at G17-010 Tap 230kV | BEPC | 36 | 30548070
Current Study | 16 - Western North Dakota | DISIS-2017-001-P2 | ERIS | MERRCRT4 to Wishek 230kV Rebuild (DISIS-2017-001) | 143222 | Rebuild the existing MERRCRT4 to Wishek 230kV 29.3 mile line to achieve a minimum Summer/Normal rating of 401 MVA | MDU | 36 | 9000000
Current Study | 16 - Western North Dakota | DISIS-2017-001-P2 | ERIS | Napoleon SW to Wishek 230kV Rebuild (DISIS-2017-001) | 143229 | Rebuild the existing Napoleon SW to Wishek 230kV 24.89 mile line to achieve a minimum Summer/Normal rating of 407 MVA | MDU | 36 | 7500000
Interconnection | 16 - Western North Dakota | DISIS-2017-001-P2 | ERIS | Neset 230 kV Substation GEN-2017-048 Interconnection (Non-Shared NU) (BEPC) | 132999 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-048 (300 MW/Wind), into the Point of Interconnection (POI) at Neset 230 kV Substation. | BEPC | 12 | 1362742
Interconnection | 16 - Western North Dakota | DISIS-2017-001-P2 | ERIS | Neset 230 kV Substation GEN-2017-048 Interconnection (TOIF) (BEPC) | 132998 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-048 (300 MW/Wind), into the Point of Interconnection (POI) at Neset 230 kV Substation. | BEPC | 12 | 1617104
Current Study | 16 - Western North Dakota | DISIS-2017-001-P2 | ERIS | Neset to Tioga 230kV Rebuild (DISIS-2017-001) (BEPC) | 143236 | Rebuild the existing Neset to Tioga 230kV 1.0 mile line to achieve a minimum Summer/Emergency rating of 725 MVA | BEPC | 12 | 192000
Interconnection | 16 - Western North Dakota | DISIS-2017-001-P2 | ERIS | Rhame 230 kV Substation GEN-2017-010 Interconnection (Non-Shared NU) (BEPC) | 132949 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-010 (200.1 MW/Wind), into the Point of Interconnection (POI) at Rhame 230 kV Substation. | BEPC | 12 | 1189064
Interconnection | 16 - Western North Dakota | DISIS-2017-001-P2 | ERIS | Rhame 230 kV Substation GEN-2017-010 Interconnection (TOIF) (BEPC) | 132948 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-010 (200.1 MW/Wind), into the Point of Interconnection (POI) at Rhame 230 kV Substation. | BEPC | 12 | 1608232
Current Study | 16 - Western North Dakota | DISIS-2017-001-P2 | ERIS | Tioga 230kV Terminal Upgrades (DISIS-2017-001) (MDU) | 143237 | Upgrade terminal equipment at Tioga 230kV to achieve a minimum Summer/Emergency rating of 725 MVA | MDU | 36 | 800000
Current Study | 16 - Western North Dakota | DISIS-2017-001-P2 | ERIS | Tioga 230kV Terminal Upgrades for Boundary Dam New Line (DISIS-2017-001) (MDU) | 143326 | Stability identified need to upgrade terminal equipment at Tioga 230kV to accept Boundary Dam CKT 2 | MDU | 36 | 800000
Current Study | 16 - Western North Dakota | DISIS-2017-001-P2 | ERIS | Tioga to Boundary Dam 230kV New Line (DISIS-2017-001) (BEPC) | 143327 | Stability identified need to build approximately 57.5 miles of new 230kV line from Tioga to Boundary Dam (DISIS-2017-001) | BEPC | 36 | 66566945
Current Study | 17 - Western South Dakota | DISIS-2017-001-P2 | ERIS | G17-014 Tap to Philip Tap 230kV New Line (DISIS-2017-001) | 143224 | Convert existing Philip Tap to a ring bus substation and build approximately 6 miles of new 230kV from new substation to G17-014 Tap creating a double circuit 230kV line. | WAPA, BEPC | 36 | 28715520
Interconnection | 17 - Western South Dakota | DISIS-2017-001-P2 | ERIS | Underwood - Philip 230 kV GEN-2017-014 Interconnection (Non-Shared NU) (WAPA) | 132957 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-014 (300 MW/Wind), into the Point of Interconnection (POI) at Underwood - Philip 230 kV. | WAPA | 36 | 4604916.81
Interconnection | 17 - Western South Dakota | DISIS-2017-001-P2 | ERIS | Underwood - Philip 230 kV GEN-2017-014 Interconnection (TOIF) (WAPA) | 132956 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-014 (300 MW/Wind), into the Point of Interconnection (POI) at Underwood - Philip 230 kV. | WAPA | 36 | 1000000
Interconnection | 17 - Western South Dakota | DISIS-2017-001-P2 | ERIS | Underwood 115 kV Substation GEN-2017-097 Interconnection (Non-Shared NU) (WAPA) | 133077 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-097 (128 MW/Solar), into the Point of Interconnection (POI) at Underwood 115 kV Substation. | WAPA | 0 | 0
Interconnection | 17 - Western South Dakota | DISIS-2017-001-P2 | ERIS | Underwood 115 kV Substation GEN-2017-097 Interconnection (TOIF) (WAPA) | 133076 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-097 (128 MW/Solar), into the Point of Interconnection (POI) at Underwood 115 kV Substation. | WAPA | 36 | 1208190
Interconnection | 17 - Western South Dakota | DISIS-2017-001-P2 | ERIS | Underwoord - Wayside 230 kV GEN-2017-064 Interconnection (Non-Shared NU) (WAPA) | 133023 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-064 (110 MW/Solar), into the Point of Interconnection (POI) at Underwood - Wayside 230 kV. | WAPA | 36 | 7102723
Interconnection | 17 - Western South Dakota | DISIS-2017-001-P2 | ERIS | Underwoord - Wayside 230 kV GEN-2017-064 Interconnection (TOIF) (WAPA) | 133022 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-064 (110 MW/Solar), into the Point of Interconnection (POI) at Underwood - Wayside 230 kV. | WAPA | 36 | 311770
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Altoona 69kV Terminal Upgrades (DISIS-2017-001) | 143295 | Upgrade terminal equipment at Altoona to Neodesha Jct. to achieve a minimum summer/emergency rating of 41 MVA | Evergy | 36 | 3325
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Appledorn to Watertown 230kV Rebuild (DISIS-2017-001) | 143309 | Rebuild the existing Watertown to Appledorn 230kV 55.3 mile line to achieve a minimum summer/emergency rating of 363 MVA | WAPA | 36 | 3600000
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Benton 345/138kV Transformer Ckt 3 (DISIS-2017-001) | 143292 | Install a new 345/138kV Transformer at Benton | Evergy | 30 | 8302968
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Beulah 115kV Terminal Upgrades (DISIS-2017-001) (MDU) | 143312 | Upgrade terminal equipment at Beulah 115kV to achieve a minimum winter/emergency rating of 171 MVA | MDU | 24 | 250000
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Fort Randall to Lake Platte 230kV Rebuild (DISIS-2017-001) (WAPA) | 143307 | Rebuild the existing Fort Randall to Lake Platte 43.34 mile line to achieve a minimum summer/emergency rating of 335 MVA | WAPA | 36 | 2000000
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Fort Thompson to Fort Randall 230kV Rebuild (DISIS-2017-001) | 143306 | Rebuild the existing Fort Thompson to Fort Randall 87.32 mile line to achieve a minimum summer/emergency rating of 348 MVA | WAPA | 36 | 23568000
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | G17-064 Tap to Wayside 230kV Rebuild (DISIS-2017-001) (WAPA) | 143299 | Rebuild the existing G17-064 Tap to Wayside 230kV 38.05 mile line to achieve a minimum summer/emergency rating of 377 MVA | WAPA | 36 | 0
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Gordon Evans to Maize 138kV Rebuild (DISIS-2017-001) | 143293 | Rebuild the existing Gordon Evans to Maize 138kV 4.9 mile line to achieve a minimum summer/emergency rating of 387 MVA | Evergy | 30 | 2338290
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Mark Moore to Monolith 345kV Rebuild (DISIS-2017-001) | 143317 | Rebuild the existing Mark Moore to Monolith 345kV .75 mile line to achieve a minimum winter/normal rating of 1108 MVA | NPPD | 36 | 4400000
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Martin to Vetal Tap 115kV Rebuild (DISIS-2017-001) (WAPA) | 143304 | Rebuild the existing Martin to Vetal Tap 115kV 16.67 mile line to achieve a minimum summer/emergency rating of 95 MVA | WAPA | 36 | 174097
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Martin to Wanblee 115kV Rebuild (DISIS-2017-001) | 143303 | Rebuild the existing Martin to Wanblee 115kV 20.86 mile line to achieve a minimum summer/emergency rating of 129 MVA | WAPA | 36 | 0
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Mission to Vetal Tap 115kV Rebuild (DISIS-2017-001) (WAPA) | 143316 | Rebuild the existing Mission to Vetal Tap 115kV 37.87 mile line to achieve a minimum summer/normal rating of 92 MVA | WAPA | 36 | 590000
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (ITCGP) | 143320 | Build approximately 40 miles of new 345kV line from Monolith to Elm Creek | ITCGP | 36 | 70295174
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Monoloith to Elm Creek 345kV New Line (DISIS-2017-001) (NPPD) | 143319 | Build approximately 62 miles of new 345kV line from Monolith to Elm Creek | NPPD | 36 | 140000000
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Neodesha Jct. 69kV Terminal Upgrades (DISIS-2017-001) | 143296 | Upgrade terminal equipment at Neodesha Jct. to achieve a minimum summer/emergency rating of 41 MVA | Evergy | 0 | 0
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Sarpy Co. S3456 to Council Bluffs 345kV Rebuild (DISIS-2017-001) (MEC) | 143301 | Rebuild the existing Sarpy Co S3456 to Council Bluffs 345kV 3.34 mile line to achieve a minimum winter/emergency rating of 1022 MVA | MEC | 36 | 5158606
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Sarpy Co. S3456 to Council Bluffs 345kV Rebuild (DISIS-2017-001) (OPPD) | 143300 | Rebuild the existing Sarpy Co S3456 to Council Bluffs 345kV 5.63 mile line section to achieve a minimum winter/emergency rating of 1022 MVA | OPPD | 18 | 216000
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Scottsbluff to Victory Hill 115kV Rebuild (DISIS-2017-001) | 143302 | Rebuild the existing Scottsbluff to Victory Hill 115kV 8.09 mile line to achieve a minimum summer/emergency rating of 177 MVA | NPPD | 36 | 3300000
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Stanton 115kV Terminal Upgrades (DISIS-2017-001) (BEPC) | 143311 | Upgrade terminal equipment at Stanton 115kV to achieve a minimum winter/emergency rating of 171 MVA | BEPC | 2 | 27600
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Stanton to Beulah 115kV Rebuild (DISIS-2017-001) (WAPA) | 143310 | Rebuild the existing Stanton to Beulah 115kV 13.41 mile line to achieve a minimum winter/emergency rating of 171 MVA | WAPA | 36 | 5920000
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Vetal Tap Terminal Upgrades for Martin Rebuild (DISIS-2017-001) (BEPC) | 143315 | Upgrade terminal equipment at Vetal Tap 115kV to achieve a minimum summer/emergency rating of 95 MVA | BEPC | 0 | 0
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Vetal Tap Terminal Upgrades for Mission Rebuild (DISIS-2017-001) (BEPC) | 143305 | Upgrade terminal equipment at Vetal Tap 115kV 37.87 mile line to achieve a minimum summer/normal rating of 92 MVA | BEPC | 0 | 0
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Wayside 230kV Terminal Upgrades (DISIS-2017-001) (NPPD) | 143298 | Upgrade terminal equipment at Wayside 230kV to accept Wayside to Shannon new line | NPPD | 36 | 6721188
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Wayside to Shannon 230kV New Line (DISIS-2017-001) (BEPC) | 143322 | Build approximately 54 miles of new 345kV line from Wayside to Shannon and install a 230/115kV transformer | BEPC | 36 | 67621351
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Welsh to Wilkes 345kV Rebuild (DISIS-2017-001) | 143323 | Rebuild the existing Welsh to Wilkes 345kV 23.74 mile line to achieve a minimum summer/emergency rating of 972 MVA | AEP | 42 | 40202865
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Wichita 345/138kV Tansformer Ckt 3 (DISIS-2017-001) | 143294 | Install a new 345/138kV Transformer at Wichita | Evergy | 36 | 8302968

## All Thermal
SOLUTIONTYPE | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.169 |  | P12:345:AEPW:LYDIA7:VALIANT7
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.169 |  | P12:345:AEPW:LYDIA7:VALIANT7
Non-Converge | 00NR | 0 | 24WP | GEN-2017-023 | 'FROM -> TO' | Non-Converge |  |  | 0.06586 |  | P12:345:AEPW:LYDIA7:VALIANT7
Non-Converge | 00NR | 0 | 24WP | GEN-2017-024 | 'FROM -> TO' | Non-Converge |  |  | 0.0603 |  | P12:345:AEPW:LYDIA7:VALIANT7
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.12827 |  | P12:345:AEPW:PITTSB-7:VALIANT7
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.12827 |  | P12:345:AEPW:PITTSB-7:VALIANT7
Non-Converge | 00NR | 0 | 24WP | GEN-2017-022 | 'FROM -> TO' | Non-Converge |  |  | 0.03206 |  | P12:345:GMO-OPPD:S3458-HOLT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-068 | 'FROM -> TO' | Non-Converge |  |  | 0.03418 |  | P12:345:GMO-OPPD:S3458-HOLT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.0307 |  | P12:345:GRDA:GRDA1 -TONECE
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.0307 |  | P12:345:GRDA:GRDA1 -TONECE
Non-Converge | 00NR | 0 | 24WP | GEN-2017-055 | 'FROM -> TO' | Non-Converge |  |  | 0.10432 |  | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Non-Converge | 00NR | 0 | 24WP | GEN-2017-055 | 'FROM -> TO' | Non-Converge |  |  | 0.10432 |  | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.03391 |  | P12:345:OKGE:BKRBKR295
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.03391 |  | P12:345:OKGE:BKRBKR295
Non-Converge | 00NR | 0 | 24WP | GEN-2017-055 | 'FROM -> TO' | Non-Converge |  |  | 0.35791 |  | P12:345:OPPD:S3458-COOPER
Non-Converge | 00NR | 0 | 24WP | GEN-2017-085 | 'FROM -> TO' | Non-Converge |  |  | 0.12345 |  | P12:345:OPPD:S3458-COOPER
Non-Converge | 00NR | 0 | 24WP | GEN-2017-018 | 'FROM -> TO' | Non-Converge |  |  | 0.12145 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 00NR | 0 | 24WP | GEN-2017-021 | 'FROM -> TO' | Non-Converge |  |  | 0.11054 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 00NR | 0 | 24WP | GEN-2017-099 | 'FROM -> TO' | Non-Converge |  |  | 0.11054 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 00NR | 0 | 24WP | GEN-2017-013 | 'FROM -> TO' | Non-Converge |  |  | 0.59711 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 00NR | 0 | 24WP | GEN-2017-064 | 'FROM -> TO' | Non-Converge |  |  | 0.04194 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 00NR | 0 | 24WP | GEN-2017-018 | 'FROM -> TO' | Non-Converge |  |  | 0.05939 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 00NR | 0 | 24WP | GEN-2017-021 | 'FROM -> TO' | Non-Converge |  |  | 0.04615 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 00NR | 0 | 24WP | GEN-2017-099 | 'FROM -> TO' | Non-Converge |  |  | 0.04615 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 00NR | 0 | 24WP | GEN-2017-013 | 'FROM -> TO' | Non-Converge |  |  | 0.49633 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 00NR | 0 | 24WP | GEN-2017-064 | 'FROM -> TO' | Non-Converge |  |  | 0.03837 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 00NR | 0 | 24WP | GEN-2017-018 | 'FROM -> TO' | Non-Converge |  |  | 0.05939 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Non-Converge | 00NR | 0 | 24WP | GEN-2017-021 | 'FROM -> TO' | Non-Converge |  |  | 0.04615 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Non-Converge | 00NR | 0 | 24WP | GEN-2017-099 | 'FROM -> TO' | Non-Converge |  |  | 0.04615 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Non-Converge | 00NR | 0 | 24WP | GEN-2017-013 | 'FROM -> TO' | Non-Converge |  |  | 0.49633 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Non-Converge | 00NR | 0 | 24WP | GEN-2017-064 | 'FROM -> TO' | Non-Converge |  |  | 0.03837 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Non-Converge | 00NR | 0 | 24WP | GEN-2017-018 | 'FROM -> TO' | Non-Converge |  |  | 0.11691 |  | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Non-Converge | 00NR | 0 | 24WP | GEN-2017-021 | 'FROM -> TO' | Non-Converge |  |  | 0.10665 |  | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Non-Converge | 00NR | 0 | 24WP | GEN-2017-099 | 'FROM -> TO' | Non-Converge |  |  | 0.10665 |  | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Non-Converge | 00NR | 0 | 24WP | GEN-2017-064 | 'FROM -> TO' | Non-Converge |  |  | 0.05117 |  | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Non-Converge | 00NR | 0 | 20SP | GEN-2017-018 | 'FROM -> TO' | Non-Converge |  |  | 0.10659 |  | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Non-Converge | 00NR | 0 | 20SP | GEN-2017-021 | 'FROM -> TO' | Non-Converge |  |  | 0.09837 |  | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Non-Converge | 00NR | 0 | 20SP | GEN-2017-099 | 'FROM -> TO' | Non-Converge |  |  | 0.09837 |  | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Non-Converge | 00NR | 0 | 20SP | GEN-2017-064 | 'FROM -> TO' | Non-Converge |  |  | 0.05946 |  | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Non-Converge | 00NR | 0 | 24WP | GEN-2017-028 | 'FROM -> TO' | Non-Converge |  |  | 0.03071 |  | P12:345:WERE:BENT-WICH_345::
Non-Converge | 00NR | 0 | 24WP | GEN-2017-047 | 'FROM -> TO' | Non-Converge |  |  | 0.03722 |  | P12:345:WERE:BENT-WICH_345::
Non-Converge | 00NR | 0 | 24WP | GEN-2017-100 | 'FROM -> TO' | Non-Converge |  |  | 0.03805 |  | P12:345:WERE:BENT-WICH_345::
Non-Converge | 00NR | 0 | 24WP | GEN-2017-018 | 'FROM -> TO' | Non-Converge |  |  | 0.05747 |  | P12:345:WERE:BENT-WICH_345::
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.03825 |  | P12:345:WERE:BENT-WICH_345::
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.03825 |  | P12:345:WERE:BENT-WICH_345::
Non-Converge | 00NR | 0 | 24WP | GEN-2017-068 | 'FROM -> TO' | Non-Converge |  |  | 0.2097 |  | P12:345:WERE:BENT-WICH_345::
Non-Converge | 00NR | 0 | 20SP | GEN-2017-094 | 'FROM -> TO' | Non-Converge |  |  | 0.03393 |  | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.03391 |  | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.03391 |  | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Non-Converge | 00NR | 0 | 24WP | GEN-2017-021 | 'FROM -> TO' | Non-Converge |  |  | 0.06282 |  | P13:230-345:MIDW:POST ROCK
Non-Converge | 00NR | 0 | 24WP | GEN-2017-099 | 'FROM -> TO' | Non-Converge |  |  | 0.06282 |  | P13:230-345:MIDW:POST ROCK
Non-Converge | 00NR | 0 | 24WP | GEN-2017-021 | 'FROM -> TO' | Non-Converge |  |  | 0.06282 |  | P13:230-345:MIDW:POST ROCK
Non-Converge | 00NR | 0 | 24WP | GEN-2017-099 | 'FROM -> TO' | Non-Converge |  |  | 0.06282 |  | P13:230-345:MIDW:POST ROCK
Non-Converge | 00NR | 0 | 24WP | GEN-2017-022 | 'FROM -> TO' | Non-Converge |  |  | 0.03206 |  | P14:345:GMO-OPPD:S3458 REACTOR
Non-Converge | 00NR | 0 | 24WP | GEN-2017-068 | 'FROM -> TO' | Non-Converge |  |  | 0.03418 |  | P14:345:GMO-OPPD:S3458 REACTOR
Non-Converge | 00NR | 0 | 20SP | GEN-2017-094 | 'FROM -> TO' | Non-Converge |  |  | 0.03393 |  | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Non-Converge | 00NR | 0 | 24WP | GEN-2017-022 | 'FROM -> TO' | Non-Converge |  |  | 0.03206 |  | P22:345:GMO-OPPD:S3458-HOLT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-068 | 'FROM -> TO' | Non-Converge |  |  | 0.03418 |  | P22:345:GMO-OPPD:S3458-HOLT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.169 |  | P23:345:AEPW:NW TEXARKANA CB 11810 NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.169 |  | P23:345:AEPW:NW TEXARKANA CB 11810 NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-023 | 'FROM -> TO' | Non-Converge |  |  | 0.06586 |  | P23:345:AEPW:NW TEXARKANA CB 11810 NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-024 | 'FROM -> TO' | Non-Converge |  |  | 0.0603 |  | P23:345:AEPW:NW TEXARKANA CB 11810 NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.16701 |  | P23:345:AEPW:NW TEXARKANA CB 11810 NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.16701 |  | P23:345:AEPW:NW TEXARKANA CB 11810 NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-023 | 'FROM -> TO' | Non-Converge |  |  | 0.06067 |  | P23:345:AEPW:NW TEXARKANA CB 11810 NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-024 | 'FROM -> TO' | Non-Converge |  |  | 0.05548 |  | P23:345:AEPW:NW TEXARKANA CB 11810 NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.169 |  | P23:345:AEPW:NW TEXARKANA CB 11820 NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.169 |  | P23:345:AEPW:NW TEXARKANA CB 11820 NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-023 | 'FROM -> TO' | Non-Converge |  |  | 0.06586 |  | P23:345:AEPW:NW TEXARKANA CB 11820 NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-024 | 'FROM -> TO' | Non-Converge |  |  | 0.0603 |  | P23:345:AEPW:NW TEXARKANA CB 11820 NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.16701 |  | P23:345:AEPW:NW TEXARKANA CB 11820 NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.16701 |  | P23:345:AEPW:NW TEXARKANA CB 11820 NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-023 | 'FROM -> TO' | Non-Converge |  |  | 0.06067 |  | P23:345:AEPW:NW TEXARKANA CB 11820 NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-024 | 'FROM -> TO' | Non-Converge |  |  | 0.05548 |  | P23:345:AEPW:NW TEXARKANA CB 11820 NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.12827 |  | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.12827 |  | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.08114 |  | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.08114 |  | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.12827 |  | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.12827 |  | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.12827 |  | P23:345:AEPW:VALLIANT CB 3409A NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.12827 |  | P23:345:AEPW:VALLIANT CB 3409A NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.1282 |  | P23:345:AEPW:VALLIANT CB 3417A NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.1282 |  | P23:345:AEPW:VALLIANT CB 3417A NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-023 | 'FROM -> TO' | Non-Converge |  |  | 0.22017 |  | P23:345:AEPW:VALLIANT CB 3417A NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-024 | 'FROM -> TO' | Non-Converge |  |  | 0.19726 |  | P23:345:AEPW:VALLIANT CB 3417A NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.169 |  | P23:345:AEPW:VALLIANT CB 3417A NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.169 |  | P23:345:AEPW:VALLIANT CB 3417A NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-023 | 'FROM -> TO' | Non-Converge |  |  | 0.06586 |  | P23:345:AEPW:VALLIANT CB 3417A NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-024 | 'FROM -> TO' | Non-Converge |  |  | 0.0603 |  | P23:345:AEPW:VALLIANT CB 3417A NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.16701 |  | P23:345:AEPW:VALLIANT CB 3417A NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.16701 |  | P23:345:AEPW:VALLIANT CB 3417A NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-023 | 'FROM -> TO' | Non-Converge |  |  | 0.06067 |  | P23:345:AEPW:VALLIANT CB 3417A NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-024 | 'FROM -> TO' | Non-Converge |  |  | 0.05548 |  | P23:345:AEPW:VALLIANT CB 3417A NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.12827 |  | P23:345:AEPW:VALLIANT CB 3421A NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.12827 |  | P23:345:AEPW:VALLIANT CB 3421A NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.169 |  | P23:345:AEPW:VALLIANT CB 3421A NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.169 |  | P23:345:AEPW:VALLIANT CB 3421A NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-023 | 'FROM -> TO' | Non-Converge |  |  | 0.06586 |  | P23:345:AEPW:VALLIANT CB 3421A NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-024 | 'FROM -> TO' | Non-Converge |  |  | 0.0603 |  | P23:345:AEPW:VALLIANT CB 3421A NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.16701 |  | P23:345:AEPW:VALLIANT CB 3421A NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.16701 |  | P23:345:AEPW:VALLIANT CB 3421A NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-023 | 'FROM -> TO' | Non-Converge |  |  | 0.06067 |  | P23:345:AEPW:VALLIANT CB 3421A NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-024 | 'FROM -> TO' | Non-Converge |  |  | 0.05548 |  | P23:345:AEPW:VALLIANT CB 3421A NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.169 |  | P23:345:AEPW:WELSH CB 11590 NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.169 |  | P23:345:AEPW:WELSH CB 11590 NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-023 | 'FROM -> TO' | Non-Converge |  |  | 0.06586 |  | P23:345:AEPW:WELSH CB 11590 NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-024 | 'FROM -> TO' | Non-Converge |  |  | 0.0603 |  | P23:345:AEPW:WELSH CB 11590 NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.16701 |  | P23:345:AEPW:WELSH CB 11590 NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.16701 |  | P23:345:AEPW:WELSH CB 11590 NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-023 | 'FROM -> TO' | Non-Converge |  |  | 0.06067 |  | P23:345:AEPW:WELSH CB 11590 NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-024 | 'FROM -> TO' | Non-Converge |  |  | 0.05548 |  | P23:345:AEPW:WELSH CB 11590 NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.04492 |  | P23:345:AEPW:WELSH CB 11990 NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.04492 |  | P23:345:AEPW:WELSH CB 11990 NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.04563 |  | P23:345:AEPW:WELSH CB 11990 NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.04563 |  | P23:345:AEPW:WELSH CB 11990 NBTB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.0307 |  | P23:345:GRDA:GRDA CB9580
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.0307 |  | P23:345:GRDA:GRDA CB9580
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.0307 |  | P23:345:GRDA:TONNECE CB90
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.0307 |  | P23:345:GRDA:TONNECE CB90
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.0307 |  | P23:345:GRDA:TONNECE CB9580
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.0307 |  | P23:345:GRDA:TONNECE CB9580
Non-Converge | 00NR | 0 | 24WP | GEN-2017-022 | 'FROM -> TO' | Non-Converge |  |  | 0.13847 |  | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Non-Converge | 00NR | 0 | 24WP | GEN-2017-068 | 'FROM -> TO' | Non-Converge |  |  | 0.09526 |  | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Non-Converge | 00NR | 0 | 24WP | GEN-2017-022 | 'FROM -> TO' | Non-Converge |  |  | 0.13847 |  | P23:345:KCPL-GMO:STILWELL_R2-5::STILWELL-PECULIAR-LACYGNE
Non-Converge | 00NR | 0 | 24WP | GEN-2017-068 | 'FROM -> TO' | Non-Converge |  |  | 0.09526 |  | P23:345:KCPL-GMO:STILWELL_R2-5::STILWELL-PECULIAR-LACYGNE
Non-Converge | 00NR | 0 | 24WP | GEN-2017-055 | 'FROM -> TO' | Non-Converge |  |  | 0.10432 |  | P23:345:MEC:ATCHISON CO 903
Non-Converge | 00NR | 0 | 24WP | GEN-2017-055 | 'FROM -> TO' | Non-Converge |  |  | 0.10432 |  | P23:345:MEC:ATCHISON CO 903
Non-Converge | 00NR | 0 | 20SP | GEN-2017-055 | 'FROM -> TO' | Non-Converge |  |  | 0.10509 |  | P23:345:MEC:ATCHISON CO 903
Non-Converge | 00NR | 0 | 24WP | GEN-2017-055 | 'FROM -> TO' | Non-Converge |  |  | 0.08555 |  | P23:345:OPPD:S3456-S3458&CB
Non-Converge | 00NR | 0 | 24WP | GEN-2017-055 | 'FROM -> TO' | Non-Converge |  |  | 0.35791 |  | P23:345:OPPD:S3458-COOPER
Non-Converge | 00NR | 0 | 24WP | GEN-2017-085 | 'FROM -> TO' | Non-Converge |  |  | 0.12345 |  | P23:345:OPPD:S3458-COOPER
Non-Converge | 00NR | 0 | 24WP | GEN-2017-022 | 'FROM -> TO' | Non-Converge |  |  | 0.03206 |  | P23:345:OPPD:S3458-HOLT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-068 | 'FROM -> TO' | Non-Converge |  |  | 0.03418 |  | P23:345:OPPD:S3458-HOLT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-047 | 'FROM -> TO' | Non-Converge |  |  | 0.03636 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 00NR | 0 | 24WP | GEN-2017-100 | 'FROM -> TO' | Non-Converge |  |  | 0.0373 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 00NR | 0 | 24WP | GEN-2017-018 | 'FROM -> TO' | Non-Converge |  |  | 0.05939 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 00NR | 0 | 24WP | GEN-2017-021 | 'FROM -> TO' | Non-Converge |  |  | 0.04615 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 00NR | 0 | 24WP | GEN-2017-099 | 'FROM -> TO' | Non-Converge |  |  | 0.04615 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 00NR | 0 | 24WP | GEN-2017-013 | 'FROM -> TO' | Non-Converge |  |  | 0.49633 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 00NR | 0 | 24WP | GEN-2017-064 | 'FROM -> TO' | Non-Converge |  |  | 0.03837 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 00NR | 0 | 24WP | GEN-2017-018 | 'FROM -> TO' | Non-Converge |  |  | 0.05939 |  | P23:345:SUNC:HLC_BRK382
Non-Converge | 00NR | 0 | 24WP | GEN-2017-021 | 'FROM -> TO' | Non-Converge |  |  | 0.04615 |  | P23:345:SUNC:HLC_BRK382
Non-Converge | 00NR | 0 | 24WP | GEN-2017-099 | 'FROM -> TO' | Non-Converge |  |  | 0.04615 |  | P23:345:SUNC:HLC_BRK382
Non-Converge | 00NR | 0 | 24WP | GEN-2017-013 | 'FROM -> TO' | Non-Converge |  |  | 0.49633 |  | P23:345:SUNC:HLC_BRK382
Non-Converge | 00NR | 0 | 24WP | GEN-2017-064 | 'FROM -> TO' | Non-Converge |  |  | 0.03837 |  | P23:345:SUNC:HLC_BRK382
Non-Converge | 00NR | 0 | 24WP | GEN-2017-018 | 'FROM -> TO' | Non-Converge |  |  | 0.12145 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 00NR | 0 | 24WP | GEN-2017-021 | 'FROM -> TO' | Non-Converge |  |  | 0.11054 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 00NR | 0 | 24WP | GEN-2017-099 | 'FROM -> TO' | Non-Converge |  |  | 0.11054 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 00NR | 0 | 24WP | GEN-2017-013 | 'FROM -> TO' | Non-Converge |  |  | 0.59711 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 00NR | 0 | 24WP | GEN-2017-064 | 'FROM -> TO' | Non-Converge |  |  | 0.04194 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 00NR | 0 | 24WP | GEN-2017-013 | 'FROM -> TO' | Non-Converge |  |  | 0.0499 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 00NR | 0 | 24WP | GEN-2017-013 | 'FROM -> TO' | Non-Converge |  |  | 0.0499 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 00NR | 0 | 24WP | GEN-2017-013 | 'FROM -> TO' | Non-Converge |  |  | 0.0499 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 00NR | 0 | 24WP | GEN-2017-013 | 'FROM -> TO' | Non-Converge |  |  | 0.0499 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 00NR | 0 | 24WP | GEN-2017-018 | 'FROM -> TO' | Non-Converge |  |  | 0.11691 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 00NR | 0 | 24WP | GEN-2017-021 | 'FROM -> TO' | Non-Converge |  |  | 0.10665 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 00NR | 0 | 24WP | GEN-2017-099 | 'FROM -> TO' | Non-Converge |  |  | 0.10665 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 00NR | 0 | 24WP | GEN-2017-064 | 'FROM -> TO' | Non-Converge |  |  | 0.05117 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 00NR | 0 | 24WP | GEN-2017-013 | 'FROM -> TO' | Non-Converge |  |  | 0.0499 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 00NR | 0 | 24WP | GEN-2017-013 | 'FROM -> TO' | Non-Converge |  |  | 0.0499 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 00NR | 0 | 20SP | GEN-2017-013 | 'FROM -> TO' | Non-Converge |  |  | 0.05248 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 00NR | 0 | 20SP | GEN-2017-013 | 'FROM -> TO' | Non-Converge |  |  | 0.05248 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 00NR | 0 | 20SP | GEN-2017-018 | 'FROM -> TO' | Non-Converge |  |  | 0.10659 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 00NR | 0 | 20SP | GEN-2017-021 | 'FROM -> TO' | Non-Converge |  |  | 0.09837 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 00NR | 0 | 20SP | GEN-2017-099 | 'FROM -> TO' | Non-Converge |  |  | 0.09837 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 00NR | 0 | 20SP | GEN-2017-064 | 'FROM -> TO' | Non-Converge |  |  | 0.05946 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 00NR | 0 | 24WP | GEN-2017-013 | 'FROM -> TO' | Non-Converge |  |  | 0.0499 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 00NR | 0 | 24WP | GEN-2017-013 | 'FROM -> TO' | Non-Converge |  |  | 0.0499 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 00NR | 0 | 24WP | GEN-2017-018 | 'FROM -> TO' | Non-Converge |  |  | 0.12145 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 00NR | 0 | 24WP | GEN-2017-021 | 'FROM -> TO' | Non-Converge |  |  | 0.11054 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 00NR | 0 | 24WP | GEN-2017-099 | 'FROM -> TO' | Non-Converge |  |  | 0.11054 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 00NR | 0 | 24WP | GEN-2017-013 | 'FROM -> TO' | Non-Converge |  |  | 0.59711 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 00NR | 0 | 24WP | GEN-2017-064 | 'FROM -> TO' | Non-Converge |  |  | 0.04194 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 00NR | 0 | 24WP | GEN-2017-013 | 'FROM -> TO' | Non-Converge |  |  | 0.0499 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 00NR | 0 | 24WP | GEN-2017-013 | 'FROM -> TO' | Non-Converge |  |  | 0.0499 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 00NR | 0 | 24WP | GEN-2017-018 | 'FROM -> TO' | Non-Converge |  |  | 0.11691 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 00NR | 0 | 24WP | GEN-2017-021 | 'FROM -> TO' | Non-Converge |  |  | 0.10665 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 00NR | 0 | 24WP | GEN-2017-099 | 'FROM -> TO' | Non-Converge |  |  | 0.10665 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 00NR | 0 | 24WP | GEN-2017-064 | 'FROM -> TO' | Non-Converge |  |  | 0.05117 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 00NR | 0 | 24WP | GEN-2017-013 | 'FROM -> TO' | Non-Converge |  |  | 0.0499 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 00NR | 0 | 24WP | GEN-2017-013 | 'FROM -> TO' | Non-Converge |  |  | 0.0499 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 00NR | 0 | 20SP | GEN-2017-013 | 'FROM -> TO' | Non-Converge |  |  | 0.05248 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 00NR | 0 | 20SP | GEN-2017-013 | 'FROM -> TO' | Non-Converge |  |  | 0.05248 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 00NR | 0 | 20SP | GEN-2017-018 | 'FROM -> TO' | Non-Converge |  |  | 0.10659 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 00NR | 0 | 20SP | GEN-2017-021 | 'FROM -> TO' | Non-Converge |  |  | 0.09837 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 00NR | 0 | 20SP | GEN-2017-099 | 'FROM -> TO' | Non-Converge |  |  | 0.09837 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 00NR | 0 | 20SP | GEN-2017-064 | 'FROM -> TO' | Non-Converge |  |  | 0.05946 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 00NR | 0 | 20SP | GEN-2017-013 | 'FROM -> TO' | Non-Converge |  |  | 0.05248 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 00NR | 0 | 20SP | GEN-2017-013 | 'FROM -> TO' | Non-Converge |  |  | 0.05248 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 00NR | 0 | 24WP | GEN-2017-018 | 'FROM -> TO' | Non-Converge |  |  | 0.12145 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 00NR | 0 | 24WP | GEN-2017-021 | 'FROM -> TO' | Non-Converge |  |  | 0.11054 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 00NR | 0 | 24WP | GEN-2017-099 | 'FROM -> TO' | Non-Converge |  |  | 0.11054 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 00NR | 0 | 24WP | GEN-2017-013 | 'FROM -> TO' | Non-Converge |  |  | 0.59711 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 00NR | 0 | 24WP | GEN-2017-064 | 'FROM -> TO' | Non-Converge |  |  | 0.04194 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 00NR | 0 | 24WP | GEN-2017-018 | 'FROM -> TO' | Non-Converge |  |  | 0.05939 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 00NR | 0 | 24WP | GEN-2017-021 | 'FROM -> TO' | Non-Converge |  |  | 0.04615 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 00NR | 0 | 24WP | GEN-2017-099 | 'FROM -> TO' | Non-Converge |  |  | 0.04615 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 00NR | 0 | 24WP | GEN-2017-013 | 'FROM -> TO' | Non-Converge |  |  | 0.49633 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 00NR | 0 | 24WP | GEN-2017-064 | 'FROM -> TO' | Non-Converge |  |  | 0.03837 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 00NR | 0 | 24WP | GEN-2017-018 | 'FROM -> TO' | Non-Converge |  |  | 0.06206 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 00NR | 0 | 24WP | GEN-2017-021 | 'FROM -> TO' | Non-Converge |  |  | 0.06439 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 00NR | 0 | 24WP | GEN-2017-099 | 'FROM -> TO' | Non-Converge |  |  | 0.06439 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 00NR | 0 | 24WP | GEN-2017-013 | 'FROM -> TO' | Non-Converge |  |  | 0.10078 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 00NR | 0 | 24WP | GEN-2017-018 | 'FROM -> TO' | Non-Converge |  |  | 0.06206 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 00NR | 0 | 24WP | GEN-2017-021 | 'FROM -> TO' | Non-Converge |  |  | 0.06439 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 00NR | 0 | 24WP | GEN-2017-099 | 'FROM -> TO' | Non-Converge |  |  | 0.06439 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 00NR | 0 | 24WP | GEN-2017-013 | 'FROM -> TO' | Non-Converge |  |  | 0.10078 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 00NR | 0 | 24WP | GEN-2017-018 | 'FROM -> TO' | Non-Converge |  |  | 0.12145 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 00NR | 0 | 24WP | GEN-2017-021 | 'FROM -> TO' | Non-Converge |  |  | 0.11054 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 00NR | 0 | 24WP | GEN-2017-099 | 'FROM -> TO' | Non-Converge |  |  | 0.11054 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 00NR | 0 | 24WP | GEN-2017-013 | 'FROM -> TO' | Non-Converge |  |  | 0.59711 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 00NR | 0 | 24WP | GEN-2017-064 | 'FROM -> TO' | Non-Converge |  |  | 0.04194 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 00NR | 0 | 24WP | GEN-2017-018 | 'FROM -> TO' | Non-Converge |  |  | 0.06206 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 00NR | 0 | 24WP | GEN-2017-021 | 'FROM -> TO' | Non-Converge |  |  | 0.06439 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 00NR | 0 | 24WP | GEN-2017-099 | 'FROM -> TO' | Non-Converge |  |  | 0.06439 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 00NR | 0 | 24WP | GEN-2017-013 | 'FROM -> TO' | Non-Converge |  |  | 0.10078 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 00NR | 0 | 24WP | GEN-2017-018 | 'FROM -> TO' | Non-Converge |  |  | 0.06206 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 00NR | 0 | 24WP | GEN-2017-021 | 'FROM -> TO' | Non-Converge |  |  | 0.06439 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 00NR | 0 | 24WP | GEN-2017-099 | 'FROM -> TO' | Non-Converge |  |  | 0.06439 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 00NR | 0 | 24WP | GEN-2017-013 | 'FROM -> TO' | Non-Converge |  |  | 0.10078 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 00NR | 0 | 24WP | GEN-2017-018 | 'FROM -> TO' | Non-Converge |  |  | 0.05939 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 00NR | 0 | 24WP | GEN-2017-021 | 'FROM -> TO' | Non-Converge |  |  | 0.04615 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 00NR | 0 | 24WP | GEN-2017-099 | 'FROM -> TO' | Non-Converge |  |  | 0.04615 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 00NR | 0 | 24WP | GEN-2017-013 | 'FROM -> TO' | Non-Converge |  |  | 0.49633 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 00NR | 0 | 24WP | GEN-2017-064 | 'FROM -> TO' | Non-Converge |  |  | 0.03837 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 00NR | 0 | 24WP | GEN-2017-013 | 'FROM -> TO' | Non-Converge |  |  | 0.0365 |  | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-064 | 'FROM -> TO' | Non-Converge |  |  | 0.03762 |  | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT
Non-Converge | 00NR | 0 | 20SP | GEN-2017-013 | 'FROM -> TO' | Non-Converge |  |  | 0.03638 |  | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT
Non-Converge | 00NR | 0 | 20SP | GEN-2017-064 | 'FROM -> TO' | Non-Converge |  |  | 0.03497 |  | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT
Non-Converge | 00NR | 0 | 20SP | GEN-2017-018 | 'FROM -> TO' | Non-Converge |  |  | 0.03944 |  | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT
Non-Converge | 00NR | 0 | 20SP | GEN-2017-085 | 'FROM -> TO' | Non-Converge |  |  | 0.17234 |  | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-013 | 'FROM -> TO' | Non-Converge |  |  | 0.0365 |  | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-064 | 'FROM -> TO' | Non-Converge |  |  | 0.03762 |  | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT
Non-Converge | 00NR | 0 | 20SP | GEN-2017-013 | 'FROM -> TO' | Non-Converge |  |  | 0.03638 |  | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT
Non-Converge | 00NR | 0 | 20SP | GEN-2017-064 | 'FROM -> TO' | Non-Converge |  |  | 0.03497 |  | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT
Non-Converge | 00NR | 0 | 20SP | GEN-2017-018 | 'FROM -> TO' | Non-Converge |  |  | 0.03944 |  | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT
Non-Converge | 00NR | 0 | 20SP | GEN-2017-085 | 'FROM -> TO' | Non-Converge |  |  | 0.17234 |  | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-028 | 'FROM -> TO' | Non-Converge |  |  | 0.03071 |  | P23:345:WERE:BENT_345-110::
Non-Converge | 00NR | 0 | 24WP | GEN-2017-047 | 'FROM -> TO' | Non-Converge |  |  | 0.03722 |  | P23:345:WERE:BENT_345-110::
Non-Converge | 00NR | 0 | 24WP | GEN-2017-100 | 'FROM -> TO' | Non-Converge |  |  | 0.03805 |  | P23:345:WERE:BENT_345-110::
Non-Converge | 00NR | 0 | 24WP | GEN-2017-018 | 'FROM -> TO' | Non-Converge |  |  | 0.05747 |  | P23:345:WERE:BENT_345-110::
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.03825 |  | P23:345:WERE:BENT_345-110::
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.03825 |  | P23:345:WERE:BENT_345-110::
Non-Converge | 00NR | 0 | 24WP | GEN-2017-068 | 'FROM -> TO' | Non-Converge |  |  | 0.2097 |  | P23:345:WERE:BENT_345-110::
Non-Converge | 00NR | 0 | 24WP | GEN-2017-100 | 'FROM -> TO' | Non-Converge |  |  | 0.03049 |  | P23:345:WERE:BENT_345-50::
Non-Converge | 00NR | 0 | 24WP | GEN-2017-018 | 'FROM -> TO' | Non-Converge |  |  | 0.03665 |  | P23:345:WERE:BENT_345-50::
Non-Converge | 00NR | 0 | 24WP | GEN-2017-068 | 'FROM -> TO' | Non-Converge |  |  | 0.12536 |  | P23:345:WERE:BENT_345-50::
Non-Converge | 00NR | 0 | 24WP | GEN-2017-022 | 'FROM -> TO' | Non-Converge |  |  | 0.10011 |  | P23:345:WERE:HOYT_345_BKRS::
Non-Converge | 00NR | 0 | 24WP | GEN-2017-068 | 'FROM -> TO' | Non-Converge |  |  | 0.08138 |  | P23:345:WERE:HOYT_345_BKRS::
Non-Converge | 00NR | 0 | 24WP | GEN-2017-022 | 'FROM -> TO' | Non-Converge |  |  | 0.06122 |  | P23:345:WERE:HOYT_345_BKRS::
Non-Converge | 00NR | 0 | 24WP | GEN-2017-068 | 'FROM -> TO' | Non-Converge |  |  | 0.05039 |  | P23:345:WERE:HOYT_345_BKRS::
Non-Converge | 00NR | 0 | 20SP | GEN-2017-022 | 'FROM -> TO' | Non-Converge |  |  | 0.04916 |  | P23:345:WERE:HOYT_345_BKRS::
Non-Converge | 00NR | 0 | 20SP | GEN-2017-068 | 'FROM -> TO' | Non-Converge |  |  | 0.03823 |  | P23:345:WERE:HOYT_345_BKRS::
Non-Converge | 00NR | 0 | 20SP | GEN-2017-022 | 'FROM -> TO' | Non-Converge |  |  | 0.07962 |  | P23:345:WERE:HOYT_345_BKRS::
Non-Converge | 00NR | 0 | 20SP | GEN-2017-068 | 'FROM -> TO' | Non-Converge |  |  | 0.06074 |  | P23:345:WERE:HOYT_345_BKRS::
Non-Converge | 00NR | 0 | 24WP | GEN-2017-068 | 'FROM -> TO' | Non-Converge |  |  | 0.065 |  | P23:345:WERE:LATH_BKRS::
Non-Converge | 00NR | 0 | 24WP | GEN-2017-068 | 'FROM -> TO' | Non-Converge |  |  | 0.065 |  | P23:345:WERE:LATH_BKRS::
Non-Converge | 00NR | 0 | 24WP | GEN-2017-022 | 'FROM -> TO' | Non-Converge |  |  | 0.04796 |  | P23:345:WERE:STRA_345-99::
Non-Converge | 00NR | 0 | 24WP | GEN-2017-068 | 'FROM -> TO' | Non-Converge |  |  | 0.03854 |  | P23:345:WERE:STRA_345-99::
Non-Converge | 00NR | 0 | 24WP | GEN-2017-028 | 'FROM -> TO' | Non-Converge |  |  | 0.03071 |  | P23:345:WERE:WICH_345-50::
Non-Converge | 00NR | 0 | 24WP | GEN-2017-047 | 'FROM -> TO' | Non-Converge |  |  | 0.03722 |  | P23:345:WERE:WICH_345-50::
Non-Converge | 00NR | 0 | 24WP | GEN-2017-100 | 'FROM -> TO' | Non-Converge |  |  | 0.03805 |  | P23:345:WERE:WICH_345-50::
Non-Converge | 00NR | 0 | 24WP | GEN-2017-018 | 'FROM -> TO' | Non-Converge |  |  | 0.05747 |  | P23:345:WERE:WICH_345-50::
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.03825 |  | P23:345:WERE:WICH_345-50::
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.03825 |  | P23:345:WERE:WICH_345-50::
Non-Converge | 00NR | 0 | 24WP | GEN-2017-068 | 'FROM -> TO' | Non-Converge |  |  | 0.2097 |  | P23:345:WERE:WICH_345-50::
Non-Converge | 00NR | 0 | 24WP | GEN-2017-028 | 'FROM -> TO' | Non-Converge |  |  | 0.03071 |  | P23:345:WERE:WICH_345-50::
Non-Converge | 00NR | 0 | 24WP | GEN-2017-047 | 'FROM -> TO' | Non-Converge |  |  | 0.03722 |  | P23:345:WERE:WICH_345-50::
Non-Converge | 00NR | 0 | 24WP | GEN-2017-100 | 'FROM -> TO' | Non-Converge |  |  | 0.03805 |  | P23:345:WERE:WICH_345-50::
Non-Converge | 00NR | 0 | 24WP | GEN-2017-018 | 'FROM -> TO' | Non-Converge |  |  | 0.05747 |  | P23:345:WERE:WICH_345-50::
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.03825 |  | P23:345:WERE:WICH_345-50::
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.03825 |  | P23:345:WERE:WICH_345-50::
Non-Converge | 00NR | 0 | 24WP | GEN-2017-068 | 'FROM -> TO' | Non-Converge |  |  | 0.2097 |  | P23:345:WERE:WICH_345-50::
Non-Converge | 00NR | 0 | 24WP | GEN-2017-061 | 'FROM -> TO' | Non-Converge |  |  | 0.13062 |  | P24:345:GRDA:GRDA CB400T
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.169 |  | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.169 |  | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-023 | 'FROM -> TO' | Non-Converge |  |  | 0.06586 |  | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-024 | 'FROM -> TO' | Non-Converge |  |  | 0.0603 |  | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.16701 |  | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.16701 |  | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-023 | 'FROM -> TO' | Non-Converge |  |  | 0.06067 |  | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-024 | 'FROM -> TO' | Non-Converge |  |  | 0.05548 |  | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.12827 |  | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.12827 |  | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.08114 |  | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.08114 |  | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.12827 |  | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.12827 |  | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.1282 |  | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.1282 |  | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-023 | 'FROM -> TO' | Non-Converge |  |  | 0.22017 |  | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-024 | 'FROM -> TO' | Non-Converge |  |  | 0.19726 |  | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.169 |  | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.169 |  | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-023 | 'FROM -> TO' | Non-Converge |  |  | 0.06586 |  | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-024 | 'FROM -> TO' | Non-Converge |  |  | 0.0603 |  | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.16701 |  | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.16701 |  | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-023 | 'FROM -> TO' | Non-Converge |  |  | 0.06067 |  | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-024 | 'FROM -> TO' | Non-Converge |  |  | 0.05548 |  | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.12827 |  | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.12827 |  | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.169 |  | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.169 |  | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-023 | 'FROM -> TO' | Non-Converge |  |  | 0.06586 |  | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-024 | 'FROM -> TO' | Non-Converge |  |  | 0.0603 |  | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.16701 |  | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.16701 |  | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-023 | 'FROM -> TO' | Non-Converge |  |  | 0.06067 |  | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-024 | 'FROM -> TO' | Non-Converge |  |  | 0.05548 |  | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.04492 |  | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.04492 |  | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.04563 |  | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.04563 |  | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Non-Converge | 00NR | 0 | 24WP | GEN-2017-033 | 'FROM -> TO' | Non-Converge |  |  | 0.0307 |  | P42:345:GRDA:TONNECE CB9580
Non-Converge | 00NR | 0 | 24WP | GEN-2017-065 | 'FROM -> TO' | Non-Converge |  |  | 0.0307 |  | P42:345:GRDA:TONNECE CB9580
Non-Converge | 00NR | 0 | 24WP | GEN-2017-055 | 'FROM -> TO' | Non-Converge |  |  | 0.08555 |  | P42:345:MEC-OPPD:S3456-S3458&CBL
Non-Converge | 00NR | 0 | 24WP | GEN-2017-013 | 'FROM -> TO' | Non-Converge |  |  | 0.05257 |  | P42:345:NPPD:BKR-AXT-3308
Non-Converge | 00NR | 0 | 24WP | GEN-2017-064 | 'FROM -> TO' | Non-Converge |  |  | 0.04612 |  | P42:345:NPPD:BKR-AXT-3308
Non-Converge | 00NR | 0 | 24WP | GEN-2017-055 | 'FROM -> TO' | Non-Converge |  |  | 0.10432 |  | P42:345:NPPD:BKR-CPR-3304
Non-Converge | 00NR | 0 | 24WP | GEN-2017-055 | 'FROM -> TO' | Non-Converge |  |  | 0.10432 |  | P42:345:NPPD:BKR-CPR-3304
Non-Converge | 00NR | 0 | 24WP | GEN-2017-013 | 'FROM -> TO' | Non-Converge |  |  | 0.04035 |  | P42:345:NPPD:BKR-GGS-3322
Non-Converge | 00NR | 0 | 24WP | GEN-2017-064 | 'FROM -> TO' | Non-Converge |  |  | 0.05704 |  | P42:345:NPPD:BKR-GGS-3322
Non-Converge | 00NR | 0 | 24WP | GEN-2017-022 | 'FROM -> TO' | Non-Converge |  |  | 0.03206 |  | P44:345:OPPD:S3458-HOL&R1
Non-Converge | 00NR | 0 | 24WP | GEN-2017-068 | 'FROM -> TO' | Non-Converge |  |  | 0.03418 |  | P44:345:OPPD:S3458-HOL&R1
Non-Converge | 00NR | 0 | 24WP | GEN-2017-055 | 'FROM -> TO' | Non-Converge |  |  | 0.08555 |  | P45:345:OPPD:S3456-S3458&CBL
Thermal | 00NR | 2 | 24SP | GEN-2017-033 | 'FROM -> TO' | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.09823 | 100.14 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-065 | 'FROM -> TO' | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.09823 | 100.14 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-023 | 'FROM -> TO' | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.06598 | 100.14 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-024 | 'FROM -> TO' | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.05997 | 100.14 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-033 | 'FROM -> TO' | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.09823 | 100.14 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-065 | 'FROM -> TO' | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.09823 | 100.14 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-024 | 'FROM -> TO' | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.06598 | 100.14 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-024 | 'FROM -> TO' | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.05997 | 100.14 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | 532791 BENTON 7 345 997897 BENT TX-2 138 1 |  | 440 | 0.04018 | 118.52 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 24SP | GEN-2017-068 | 'FROM -> TO' | 532791 BENTON 7 345 997898 BENT TX-2 138 1 |  | 440 | 0.04037 | 113.66 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 20SP | GEN-2017-068 | 'FROM -> TO' | 532791 BENTON 7 345 997902 BENT TX-2 138 1 |  | 440 | 0.03671 | 115.34 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | 532796 WICHITA7 345 997926 WICH TX-12 138 1 |  | 430 | 0.10394 | 104.61 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | 532796 WICHITA7 345 997926 WICH TX-12 138 1 |  | 430 | 0.10394 | 104.61 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 24SP | GEN-2017-068 | 'FROM -> TO' | 532796 WICHITA7 345 997927 WICH TX-12 138 1 |  | 430 | 0.10498 | 101.69 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24SP | GEN-2017-068 | 'FROM -> TO' | 532796 WICHITA7 345 997927 WICH TX-12 138 1 |  | 430 | 0.10498 | 101.69 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 20SP | GEN-2017-068 | 'FROM -> TO' | 532796 WICHITA7 345 997931 WICH TX-12 138 1 |  | 430 | 0.0905 | 109.58 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 20SP | GEN-2017-068 | 'FROM -> TO' | 532796 WICHITA7 345 997931 WICH TX-12 138 1 |  | 430 | 0.0905 | 109.58 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 20SP | GEN-2017-068 | 'FROM -> TO' | 532796 WICHITA7 345 997932 WICH TX-11 138 1 |  | 430 | 0.07364 | 104.44 | P23:345:WERE:WICH_345-80::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | 532986 BENTON 4 138 997897 BENT TX-2 138 1 |  | 440 | 0.04018 | 119.63 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 24SP | GEN-2017-068 | 'FROM -> TO' | 532986 BENTON 4 138 997898 BENT TX-2 138 1 |  | 440 | 0.04037 | 110.93 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 20SP | GEN-2017-068 | 'FROM -> TO' | 532986 BENTON 4 138 997902 BENT TX-2 138 1 |  | 440 | 0.03671 | 110.63 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | 533040 EVANS N4 138 533054 MAIZE 4 138 1 |  | 382 | 0.04843 | 103.63 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24SP | GEN-2017-068 | 'FROM -> TO' | 533040 EVANS N4 138 533054 MAIZE 4 138 1 |  | 382 | 0.04865 | 101.16 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | 533040 EVANS N4 138 533054 MAIZE 4 138 1 |  | 382 | 0.04843 | 103.63 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 24SP | GEN-2017-068 | 'FROM -> TO' | 533040 EVANS N4 138 533054 MAIZE 4 138 1 |  | 382 | 0.04865 | 101.16 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | 533040 EVANS N4 138 997926 WICH TX-12 138 1 |  | 430 | 0.10394 | 103.94 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | 533040 EVANS N4 138 997926 WICH TX-12 138 1 |  | 430 | 0.10394 | 103.94 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 24SP | GEN-2017-068 | 'FROM -> TO' | 533040 EVANS N4 138 997927 WICH TX-12 138 1 |  | 430 | 0.10498 | 100.77 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24SP | GEN-2017-068 | 'FROM -> TO' | 533040 EVANS N4 138 997927 WICH TX-12 138 1 |  | 430 | 0.10498 | 100.77 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 20SP | GEN-2017-068 | 'FROM -> TO' | 533040 EVANS N4 138 997931 WICH TX-12 138 1 |  | 430 | 0.0905 | 107.89 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 20SP | GEN-2017-068 | 'FROM -> TO' | 533040 EVANS N4 138 997931 WICH TX-12 138 1 |  | 430 | 0.0905 | 107.89 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 20SP | GEN-2017-068 | 'FROM -> TO' | 533040 EVANS N4 138 997932 WICH TX-11 138 1 |  | 430 | 0.07364 | 102.35 | P23:345:WERE:WICH_345-80::
Thermal | 00NR | 2 | 29SP | GEN-2017-022 | 'FROM -> TO' | 533673 ALTOO E2 69.0 533700 NEODJCT2 69.0 1 |  | 36 | 0.03494 | 100.86 | P13:069-138:WERE:LIBE_TX-1_138-69::
Thermal | 00NR | 2 | 24SP | GEN-2017-022 | 'FROM -> TO' | 533673 ALTOO E2 69.0 533700 NEODJCT2 69.0 1 |  | 36 | 0.03505 | 100.75 | P13:069-138:WERE:LIBE_TX-1_138-69::
Thermal | 00NR | 2 | 29SP | GEN-2017-022 | 'FROM -> TO' | 533673 ALTOO E2 69.0 533700 NEODJCT2 69.0 1 |  | 36 | 0.08084 | 113.17 | P13:069-138:WERE:MONT_TX-1_138-69::
Thermal | 00NR | 2 | 24SP | GEN-2017-022 | 'FROM -> TO' | 533673 ALTOO E2 69.0 533700 NEODJCT2 69.0 1 |  | 36 | 0.08109 | 111.34 | P13:069-138:WERE:MONT_TX-1_138-69::
Thermal | 00NR | 2 | 20SP | GEN-2017-022 | 'FROM -> TO' | 533673 ALTOO E2 69.0 533700 NEODJCT2 69.0 1 |  | 36 | 0.08105 | 109.39 | P13:069-138:WERE:MONT_TX-1_138-69::
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 533673 ALTOO E2 69.0 533700 NEODJCT2 69.0 1 |  | 36 | 0.0808 | 106.24 | P13:069-138:WERE:MONT_TX-1_138-69::
Thermal | 00NR | 2 | 19WP | GEN-2017-022 | 'FROM -> TO' | 533673 ALTOO E2 69.0 533700 NEODJCT2 69.0 1 |  | 36 | 0.08083 | 102.91 | P13:069-138:WERE:MONT_TX-1_138-69::
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 589024 G17-064-TAP 230 640404 WAYSIDE4 230 1 |  | 341 | 0.13415 | 110.77 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | 589024 G17-064-TAP 230 640404 WAYSIDE4 230 1 |  | 341 | 0.391 | 110.77 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | 589024 G17-064-TAP 230 640404 WAYSIDE4 230 1 |  | 341 | 0.39155 | 105.93 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | 589024 G17-064-TAP 230 640404 WAYSIDE4 230 1 |  | 341 | 0.13469 | 105.7 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 589024 G17-064-TAP 230 640404 WAYSIDE4 230 1 |  | 341 | 0.13276 | 103.23 | P12:345:UMZ:# 6230 #: OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 OR 652832-652532-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | 589024 G17-064-TAP 230 640404 WAYSIDE4 230 1 |  | 341 | 0.38397 | 103.23 | P12:345:UMZ:# 6230 #: OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 OR 652832-652532-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 589024 G17-064-TAP 230 640404 WAYSIDE4 230 1 |  | 341 | 0.13127 | 108.32 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | 589024 G17-064-TAP 230 640404 WAYSIDE4 230 1 |  | 341 | 0.38391 | 108.32 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | 589024 G17-064-TAP 230 640404 WAYSIDE4 230 1 |  | 341 | 0.38445 | 104.06 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | 589024 G17-064-TAP 230 640404 WAYSIDE4 230 1 |  | 341 | 0.13181 | 103.71 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-022 | 'FROM -> TO' | 635000 CBLUFFS3 345 645456 S3456 3 345 1 |  | 956 | 0.03198 | 108.2 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 635000 CBLUFFS3 345 645456 S3456 3 345 1 |  | 956 | 0.03315 | 101.14 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 19WP | GEN-2017-022 | 'FROM -> TO' | 635000 CBLUFFS3 345 645456 S3456 3 345 1 |  | 956 | 0.03198 | 108.2 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 635000 CBLUFFS3 345 645456 S3456 3 345 1 |  | 956 | 0.03315 | 101.14 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 19WP | GEN-2017-022 | 'FROM -> TO' | 635000 CBLUFFS3 345 645456 S3456 3 345 1 |  | 956 | 0.03198 | 106.3 | P23:345:MEC:ATCHISON CO 903
Thermal | 00NR | 2 | 19WP | GEN-2017-022 | 'FROM -> TO' | 635000 CBLUFFS3 345 645456 S3456 3 345 1 |  | 956 | 0.03198 | 108.2 | P42:345:NPPD:BKR-CPR-3304
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 635000 CBLUFFS3 345 645456 S3456 3 345 1 |  | 956 | 0.03315 | 101.14 | P42:345:NPPD:BKR-CPR-3304
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 640109 CHADRON7 115 640405 WAYSIDE7 115 1 |  | 160 | 0.07722 | 115.47 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | 640109 CHADRON7 115 640405 WAYSIDE7 115 1 |  | 160 | 0.24223 | 115.47 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 640109 CHADRON7 115 640405 WAYSIDE7 115 1 |  | 160 | 0.07766 | 107.64 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | 640109 CHADRON7 115 640405 WAYSIDE7 115 1 |  | 160 | 0.24349 | 107.64 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | 640109 CHADRON7 115 640405 WAYSIDE7 115 1 |  | 160 | 0.07799 | 104.43 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | 640109 CHADRON7 115 640405 WAYSIDE7 115 1 |  | 160 | 0.24382 | 104.4 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05016 | 100.04 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.04535 | 100.04 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03309 | 100.04 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.22639 | 100.04 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05016 | 100.04 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.04535 | 100.04 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03309 | 100.04 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.22639 | 100.04 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05016 | 100.06 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.04535 | 100.06 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03309 | 100.06 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.22639 | 100.06 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05016 | 100.06 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.04535 | 100.06 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03309 | 100.06 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.22639 | 100.06 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05212 | 105.86 | P12:345:GMO-OPPD:S3458-HOLT
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05093 | 105.86 | P12:345:GMO-OPPD:S3458-HOLT
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03863 | 105.86 | P12:345:GMO-OPPD:S3458-HOLT
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.22797 | 105.86 | P12:345:GMO-OPPD:S3458-HOLT
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05212 | 105.86 | P12:345:GMO-OPPD:S3458-HOLT
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05093 | 105.86 | P12:345:GMO-OPPD:S3458-HOLT
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03863 | 105.86 | P12:345:GMO-OPPD:S3458-HOLT
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.22797 | 105.86 | P12:345:GMO-OPPD:S3458-HOLT
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.04994 | 104.65 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05258 | 104.65 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03816 | 104.65 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.24672 | 104.65 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.04994 | 104.65 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05258 | 104.65 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03816 | 104.65 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.24672 | 104.65 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05423 | 115.84 | P12:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05353 | 115.84 | P12:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.04149 | 115.84 | P12:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.3569 | 115.84 | P12:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05423 | 115.84 | P12:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05353 | 115.84 | P12:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.04149 | 115.84 | P12:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.3569 | 115.84 | P12:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 19WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05299 | 101.09 | P12:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 19WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05122 | 101.09 | P12:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 19WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03883 | 101.09 | P12:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 19WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.36496 | 101.09 | P12:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 19WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05299 | 101.09 | P12:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 19WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05122 | 101.09 | P12:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 19WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03883 | 101.09 | P12:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 19WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.36496 | 101.09 | P12:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.11982 | 100.16 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.04471 | 100.16 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03057 | 100.16 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.22738 | 100.16 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.11982 | 100.16 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.04471 | 100.16 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03057 | 100.16 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.22738 | 100.16 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.04395 | 101.86 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.22825 | 101.86 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.04395 | 101.86 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.22825 | 101.86 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05212 | 105.86 | P14:345:GMO-OPPD:S3458 REACTOR
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05093 | 105.86 | P14:345:GMO-OPPD:S3458 REACTOR
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03863 | 105.86 | P14:345:GMO-OPPD:S3458 REACTOR
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.22797 | 105.86 | P14:345:GMO-OPPD:S3458 REACTOR
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05212 | 105.86 | P14:345:GMO-OPPD:S3458 REACTOR
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05093 | 105.86 | P14:345:GMO-OPPD:S3458 REACTOR
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03863 | 105.86 | P14:345:GMO-OPPD:S3458 REACTOR
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.22797 | 105.86 | P14:345:GMO-OPPD:S3458 REACTOR
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.04994 | 104.65 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05258 | 104.65 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03816 | 104.65 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.24672 | 104.65 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.04994 | 104.65 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05258 | 104.65 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03816 | 104.65 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.24672 | 104.65 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05212 | 105.86 | P22:345:GMO-OPPD:S3458-HOLT
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05093 | 105.86 | P22:345:GMO-OPPD:S3458-HOLT
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03863 | 105.86 | P22:345:GMO-OPPD:S3458-HOLT
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.22797 | 105.86 | P22:345:GMO-OPPD:S3458-HOLT
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05212 | 105.86 | P22:345:GMO-OPPD:S3458-HOLT
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05093 | 105.86 | P22:345:GMO-OPPD:S3458-HOLT
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03863 | 105.86 | P22:345:GMO-OPPD:S3458-HOLT
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.22797 | 105.86 | P22:345:GMO-OPPD:S3458-HOLT
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05423 | 115.84 | P22:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05353 | 115.84 | P22:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.04149 | 115.84 | P22:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.3569 | 115.84 | P22:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05423 | 115.84 | P22:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05353 | 115.84 | P22:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.04149 | 115.84 | P22:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.3569 | 115.84 | P22:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 19WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05299 | 101.09 | P22:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 19WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05122 | 101.09 | P22:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 19WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03883 | 101.09 | P22:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 19WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.36496 | 101.09 | P22:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 19WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05299 | 101.09 | P22:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 19WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05122 | 101.09 | P22:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 19WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03883 | 101.09 | P22:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 19WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.36496 | 101.09 | P22:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.04994 | 104.89 | P23:345:MEC:ATCHISON CO 903
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05258 | 104.89 | P23:345:MEC:ATCHISON CO 903
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03816 | 104.89 | P23:345:MEC:ATCHISON CO 903
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.24672 | 104.89 | P23:345:MEC:ATCHISON CO 903
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.04994 | 104.89 | P23:345:MEC:ATCHISON CO 903
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05258 | 104.89 | P23:345:MEC:ATCHISON CO 903
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03816 | 104.89 | P23:345:MEC:ATCHISON CO 903
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.24672 | 104.89 | P23:345:MEC:ATCHISON CO 903
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05423 | 115.84 | P23:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05353 | 115.84 | P23:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.04149 | 115.84 | P23:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.3569 | 115.84 | P23:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05423 | 115.84 | P23:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05353 | 115.84 | P23:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.04149 | 115.84 | P23:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.3569 | 115.84 | P23:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 19WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05299 | 101.09 | P23:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 19WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05122 | 101.09 | P23:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 19WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03883 | 101.09 | P23:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 19WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.36496 | 101.09 | P23:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 19WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05299 | 101.09 | P23:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 19WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05122 | 101.09 | P23:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 19WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03883 | 101.09 | P23:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 19WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.36496 | 101.09 | P23:345:OPPD:S3458-COOPER
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05212 | 105.86 | P23:345:OPPD:S3458-HOLT
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05093 | 105.86 | P23:345:OPPD:S3458-HOLT
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03863 | 105.86 | P23:345:OPPD:S3458-HOLT
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.22797 | 105.86 | P23:345:OPPD:S3458-HOLT
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05212 | 105.86 | P23:345:OPPD:S3458-HOLT
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05093 | 105.86 | P23:345:OPPD:S3458-HOLT
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03863 | 105.86 | P23:345:OPPD:S3458-HOLT
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.22797 | 105.86 | P23:345:OPPD:S3458-HOLT
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05339 | 100.32 | P23:345:SUNC:HLC_BRK188
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.04534 | 100.32 | P23:345:SUNC:HLC_BRK188
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03163 | 100.32 | P23:345:SUNC:HLC_BRK188
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.22692 | 100.32 | P23:345:SUNC:HLC_BRK188
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05339 | 100.32 | P23:345:SUNC:HLC_BRK188
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.04534 | 100.32 | P23:345:SUNC:HLC_BRK188
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03163 | 100.32 | P23:345:SUNC:HLC_BRK188
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.22692 | 100.32 | P23:345:SUNC:HLC_BRK188
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.04395 | 101.84 | P23:345:SUNC:MO_BRK188
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.22825 | 101.84 | P23:345:SUNC:MO_BRK188
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.04395 | 101.84 | P23:345:SUNC:MO_BRK188
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.22825 | 101.84 | P23:345:SUNC:MO_BRK188
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.11982 | 100.16 | P23:345:SUNC:MO_BRK382
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.04471 | 100.16 | P23:345:SUNC:MO_BRK382
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03057 | 100.16 | P23:345:SUNC:MO_BRK382
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.22738 | 100.16 | P23:345:SUNC:MO_BRK382
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.11982 | 100.16 | P23:345:SUNC:MO_BRK382
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.04471 | 100.16 | P23:345:SUNC:MO_BRK382
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03057 | 100.16 | P23:345:SUNC:MO_BRK382
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.22738 | 100.16 | P23:345:SUNC:MO_BRK382
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.04395 | 101.86 | P23:345:SUNC:MO_BRK388
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.22825 | 101.86 | P23:345:SUNC:MO_BRK388
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.04395 | 101.86 | P23:345:SUNC:MO_BRK388
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.22825 | 101.86 | P23:345:SUNC:MO_BRK388
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12004 | 100.37 | P23:345:SUNC:SB_BRK482
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.04464 | 100.37 | P23:345:SUNC:SB_BRK482
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03049 | 100.37 | P23:345:SUNC:SB_BRK482
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.2274 | 100.37 | P23:345:SUNC:SB_BRK482
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12004 | 100.37 | P23:345:SUNC:SB_BRK482
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.04464 | 100.37 | P23:345:SUNC:SB_BRK482
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03049 | 100.37 | P23:345:SUNC:SB_BRK482
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.2274 | 100.37 | P23:345:SUNC:SB_BRK482
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12004 | 100.33 | P23:345:SUNC:SB_BRK488
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.04464 | 100.33 | P23:345:SUNC:SB_BRK488
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03049 | 100.33 | P23:345:SUNC:SB_BRK488
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.2274 | 100.33 | P23:345:SUNC:SB_BRK488
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12004 | 100.33 | P23:345:SUNC:SB_BRK488
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.04464 | 100.33 | P23:345:SUNC:SB_BRK488
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03049 | 100.33 | P23:345:SUNC:SB_BRK488
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.2274 | 100.33 | P23:345:SUNC:SB_BRK488
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12004 | 100.15 | P23:345:SUNC:SB_BRK582
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.04464 | 100.15 | P23:345:SUNC:SB_BRK582
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03049 | 100.15 | P23:345:SUNC:SB_BRK582
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.2274 | 100.15 | P23:345:SUNC:SB_BRK582
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12004 | 100.15 | P23:345:SUNC:SB_BRK582
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.04464 | 100.15 | P23:345:SUNC:SB_BRK582
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03049 | 100.15 | P23:345:SUNC:SB_BRK582
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.2274 | 100.15 | P23:345:SUNC:SB_BRK582
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.04994 | 104.65 | P42:345:NPPD:BKR-CPR-3304
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05258 | 104.65 | P42:345:NPPD:BKR-CPR-3304
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03816 | 104.65 | P42:345:NPPD:BKR-CPR-3304
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.24672 | 104.65 | P42:345:NPPD:BKR-CPR-3304
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.04994 | 104.65 | P42:345:NPPD:BKR-CPR-3304
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05258 | 104.65 | P42:345:NPPD:BKR-CPR-3304
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03816 | 104.65 | P42:345:NPPD:BKR-CPR-3304
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.24672 | 104.65 | P42:345:NPPD:BKR-CPR-3304
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05427 | 115.71 | P42:345:NPPD:BKR-CPR-3316
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05346 | 115.71 | P42:345:NPPD:BKR-CPR-3316
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.04148 | 115.71 | P42:345:NPPD:BKR-CPR-3316
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.35872 | 115.71 | P42:345:NPPD:BKR-CPR-3316
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05427 | 115.71 | P42:345:NPPD:BKR-CPR-3316
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05346 | 115.71 | P42:345:NPPD:BKR-CPR-3316
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.04148 | 115.71 | P42:345:NPPD:BKR-CPR-3316
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.35872 | 115.71 | P42:345:NPPD:BKR-CPR-3316
Thermal | 00NR | 2 | 19WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05303 | 100.92 | P42:345:NPPD:BKR-CPR-3316
Thermal | 00NR | 2 | 19WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05114 | 100.92 | P42:345:NPPD:BKR-CPR-3316
Thermal | 00NR | 2 | 19WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03881 | 100.92 | P42:345:NPPD:BKR-CPR-3316
Thermal | 00NR | 2 | 19WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.36687 | 100.92 | P42:345:NPPD:BKR-CPR-3316
Thermal | 00NR | 2 | 19WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05303 | 100.92 | P42:345:NPPD:BKR-CPR-3316
Thermal | 00NR | 2 | 19WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05114 | 100.92 | P42:345:NPPD:BKR-CPR-3316
Thermal | 00NR | 2 | 19WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03881 | 100.92 | P42:345:NPPD:BKR-CPR-3316
Thermal | 00NR | 2 | 19WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.36687 | 100.92 | P42:345:NPPD:BKR-CPR-3316
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.04344 | 103.29 | P42:345:NPPD:BKR-RW-3302
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.22882 | 103.29 | P42:345:NPPD:BKR-RW-3302
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.04344 | 103.29 | P42:345:NPPD:BKR-RW-3302
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.22882 | 103.29 | P42:345:NPPD:BKR-RW-3302
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05212 | 105.86 | P44:345:OPPD:S3458-HOL&R1
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05093 | 105.86 | P44:345:OPPD:S3458-HOL&R1
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03863 | 105.86 | P44:345:OPPD:S3458-HOL&R1
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.22797 | 105.86 | P44:345:OPPD:S3458-HOL&R1
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05212 | 105.86 | P44:345:OPPD:S3458-HOL&R1
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.05093 | 105.86 | P44:345:OPPD:S3458-HOL&R1
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.03863 | 105.86 | P44:345:OPPD:S3458-HOL&R1
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.22797 | 105.86 | P44:345:OPPD:S3458-HOL&R1
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 640338 SCOTBLF7 115 640397 VICTRYH7 115 1 |  | 155 | 0.07968 | 114.22 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | 640338 SCOTBLF7 115 640397 VICTRYH7 115 1 |  | 155 | 0.19932 | 114.22 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 640338 SCOTBLF7 115 640397 VICTRYH7 115 1 |  | 155 | 0.08014 | 104.65 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | 640338 SCOTBLF7 115 640397 VICTRYH7 115 1 |  | 155 | 0.20117 | 104.65 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 640338 SCOTBLF7 115 640397 VICTRYH7 115 1 |  | 155 | 0.07968 | 114.21 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | 640338 SCOTBLF7 115 640397 VICTRYH7 115 1 |  | 155 | 0.19932 | 114.21 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 640338 SCOTBLF7 115 640397 VICTRYH7 115 1 |  | 155 | 0.08014 | 104.63 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | 640338 SCOTBLF7 115 640397 VICTRYH7 115 1 |  | 155 | 0.20117 | 104.63 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 00NR | 2 | 20SP_with_upgrades | GEN-2017-064 | 'FROM -> TO' | 640351 ST.FRANC 115 652482 MISSION7 115 1 |  | 72 | 0.03112 | 106.38 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 640404 WAYSIDE4 230 997300 WAYSIDE T1 115 1 |  | 187 | 0.07722 | 103.59 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | 640404 WAYSIDE4 230 997300 WAYSIDE T1 115 1 |  | 187 | 0.24223 | 103.59 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 640405 WAYSIDE7 115 997300 WAYSIDE T1 115 1 |  | 187 | 0.07722 | 101.82 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | 640405 WAYSIDE7 115 997300 WAYSIDE T1 115 1 |  | 187 | 0.24223 | 101.82 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03109 | 140.04 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.0329 | 140.04 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03111 | 125.22 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03236 | 124.71 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03414 | 124.7 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03069 | 121.01 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03099 | 108.52 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03109 | 140.04 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.0329 | 140.04 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03111 | 125.22 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03236 | 124.71 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03414 | 124.7 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03069 | 121.01 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03099 | 108.52 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 652479 MARTIN 7 115 652579 WANBLEE 7 115 1 |  | 120 | 0.05431 | 100.96 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 652479 MARTIN 7 115 652579 WANBLEE 7 115 1 |  | 120 | 0.05389 | 107.1 | P12:345:UMZ:# 6230 #: OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 OR 652832-652532-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | 652479 MARTIN 7 115 652579 WANBLEE 7 115 1 |  | 120 | 0.05426 | 104.1 | P12:345:UMZ:# 6230 #: OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 OR 652832-652532-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 652479 MARTIN 7 115 652579 WANBLEE 7 115 1 |  | 120 | 0.0593 | 107.39 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 652479 MARTIN 7 115 652579 WANBLEE 7 115 1 |  | 120 | 0.06015 | 102.1 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | 652479 MARTIN 7 115 652579 WANBLEE 7 115 1 |  | 120 | 0.06051 | 100.39 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 652479 MARTIN 7 115 652579 WANBLEE 7 115 1 |  | 120 | 0.05413 | 100.28 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.04261 | 107.78 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.04068 | 107.78 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 652482 MISSION7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.04261 | 103.95 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | 652482 MISSION7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.04068 | 103.95 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 652487 PHILIP 7 115 652579 WANBLEE 7 115 1 |  | 120 | 0.05431 | 104.18 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | 652487 PHILIP 7 115 652579 WANBLEE 7 115 1 |  | 120 | 0.05465 | 101.82 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 652487 PHILIP 7 115 652579 WANBLEE 7 115 1 |  | 120 | 0.04312 | 102.79 | P12:115:UMZ:# 5572 #: IN . PROPER N-1 (LINE) FOR 652475-652478-1
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 652487 PHILIP 7 115 652579 WANBLEE 7 115 1 |  | 120 | 0.04312 | 102.79 | P12:115:UMZW:# 144 #: GY-BO-FR IN SD. GY-BO-FR BONESTEEL HAS FAULT INTERUPTING DEVIECES (NOT BREAKERS)
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 652487 PHILIP 7 115 652579 WANBLEE 7 115 1 |  | 120 | 0.05389 | 110.33 | P12:345:UMZ:# 6230 #: OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 OR 652832-652532-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | 652487 PHILIP 7 115 652579 WANBLEE 7 115 1 |  | 120 | 0.05426 | 107.58 | P12:345:UMZ:# 6230 #: OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 OR 652832-652532-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 652487 PHILIP 7 115 652579 WANBLEE 7 115 1 |  | 120 | 0.0593 | 110.41 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 652487 PHILIP 7 115 652579 WANBLEE 7 115 1 |  | 120 | 0.06015 | 105.31 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | 652487 PHILIP 7 115 652579 WANBLEE 7 115 1 |  | 120 | 0.06051 | 103.83 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 652487 PHILIP 7 115 652579 WANBLEE 7 115 1 |  | 120 | 0.05232 | 101.54 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 652487 PHILIP 7 115 652579 WANBLEE 7 115 1 |  | 120 | 0.05328 | 101.81 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 652487 PHILIP 7 115 652579 WANBLEE 7 115 1 |  | 120 | 0.05328 | 102.12 | P23:345:UMZW:# 2411 #: FT2 IN SD. FT2 3392 BKR FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 652487 PHILIP 7 115 652579 WANBLEE 7 115 1 |  | 120 | 0.05328 | 102.12 | P23:345:UMZW:# 2412 #: FT2 IN SD. FT2 3396 BKR FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 652487 PHILIP 7 115 652579 WANBLEE 7 115 1 |  | 120 | 0.05328 | 101.83 | P23:345:UMZW:# 704 #: FT2 IN SD. BREAKER FAULT (3392)
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 652487 PHILIP 7 115 652579 WANBLEE 7 115 1 |  | 120 | 0.05328 | 101.83 | P23:345:UMZW:# 705 #: FT2 IN SD. BREAKER FAULT (3396)
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 652487 PHILIP 7 115 652579 WANBLEE 7 115 1 |  | 120 | 0.05413 | 103.49 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | 652487 PHILIP 7 115 652579 WANBLEE 7 115 1 |  | 120 | 0.05446 | 101.24 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 320 | 0.04287 | 100.37 | P12:230:UMZW:# 694 #: FT IN SD. FT-LP LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 320 | 0.03586 | 108.4 | P12:345:UMZ:# 6230 #: OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 OR 652832-652532-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-094 | 'FROM -> TO' | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 320 | 0.03984 | 101.88 | P12:345:UMZ:# 6230 #: OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 OR 652832-652532-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.03519 | 104.44 | P12:345:UMZ:# 6230 #: OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 OR 652832-652532-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652530 WATERTN4 230 652582 APPLEDORN 4 230 1 |  | 352 | 0.03036 | 103.14 | P12:230:UMZW:# 137 #: GF IN MN. GF-FB LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-094 | 'FROM -> TO' | 652530 WATERTN4 230 652582 APPLEDORN 4 230 1 |  | 352 | 0.03007 | 101.96 | P12:230:UMZW:# 137 #: GF IN MN. GF-FB LINE FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03109 | 141.42 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.0329 | 141.42 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03111 | 126.2 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03236 | 126.16 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03414 | 126.15 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03069 | 122 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03099 | 109.53 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03109 | 141.42 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.0329 | 141.42 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03111 | 126.2 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03236 | 126.16 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03414 | 126.15 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03069 | 122 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03099 | 109.53 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 661008 BEULAH 7 115 1 |  | 132 | 0.03109 | 128.88 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 661008 BEULAH 7 115 1 |  | 132 | 0.0329 | 128.88 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 661008 BEULAH 7 115 1 |  | 132 | 0.03111 | 115.07 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 661008 BEULAH 7 115 1 |  | 132 | 0.03236 | 114.97 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 661008 BEULAH 7 115 1 |  | 132 | 0.03414 | 114.96 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 661008 BEULAH 7 115 1 |  | 132 | 0.03069 | 111.23 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 661008 BEULAH 7 115 1 |  | 132 | 0.03109 | 128.88 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 661008 BEULAH 7 115 1 |  | 132 | 0.0329 | 128.88 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 661008 BEULAH 7 115 1 |  | 132 | 0.03111 | 115.07 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 661008 BEULAH 7 115 1 |  | 132 | 0.03236 | 114.97 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 661008 BEULAH 7 115 1 |  | 132 | 0.03414 | 114.96 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 661008 BEULAH 7 115 1 |  | 132 | 0.03069 | 111.23 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Non-Converge | 01ALL | 0 |  |  | '' | None |  |  |  |  | None
Thermal | 01ALL | 2 |  |  | '' | None |  |  |  |  | None
Non-Converge | 02ALL | 0 | 24L | GEN-2017-047 | '' | Non-Converge |  |  | 0.16595 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 02ALL | 0 | 24L | GEN-2017-047 | '' | Non-Converge |  |  | 0.09 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 02ALL | 0 | 24L | GEN-2017-058 | '' | Non-Converge |  |  | 0.11328 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 02ALL | 0 | 24L | GEN-2017-058 | '' | Non-Converge |  |  | 0.05269 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 02ALL | 0 | 24L | GEN-2017-100 | '' | Non-Converge |  |  | 0.16774 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 02ALL | 0 | 24L | GEN-2017-100 | '' | Non-Converge |  |  | 0.09126 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 02ALL | 0 | 24L | GEN-2017-047 | '' | Non-Converge |  |  | 0.16595 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 02ALL | 0 | 24L | GEN-2017-047 | '' | Non-Converge |  |  | 0.07811 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 02ALL | 0 | 24L | GEN-2017-058 | '' | Non-Converge |  |  | 0.11328 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 02ALL | 0 | 24L | GEN-2017-058 | '' | Non-Converge |  |  | 0.05995 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 02ALL | 0 | 24L | GEN-2017-100 | '' | Non-Converge |  |  | 0.16774 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 02ALL | 0 | 24L | GEN-2017-100 | '' | Non-Converge |  |  | 0.07874 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 02ALL | 0 | 19WP | GEN-2017-047 | '' | Non-Converge |  |  | 0.23879 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 19WP | GEN-2017-047 | '' | Non-Converge |  |  | 0.23855 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20G | GEN-2017-047 | '' | Non-Converge |  |  | 0.23736 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20G | GEN-2017-047 | '' | Non-Converge |  |  | 0.23712 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20SP | GEN-2017-047 | '' | Non-Converge |  |  | 0.23879 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20SP | GEN-2017-047 | '' | Non-Converge |  |  | 0.23855 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24L | GEN-2017-047 | '' | Non-Converge |  |  | 0.22458 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24L | GEN-2017-047 | '' | Non-Converge |  |  | 0.22435 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24WP | GEN-2017-047 | '' | Non-Converge |  |  | 0.23895 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24WP | GEN-2017-047 | '' | Non-Converge |  |  | 0.23871 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 29SP | GEN-2017-047 | '' | Non-Converge |  |  | 0.24266 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 29SP | GEN-2017-047 | '' | Non-Converge |  |  | 0.24242 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 19WP | GEN-2017-058 | '' | Non-Converge |  |  | 0.131 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 19WP | GEN-2017-058 | '' | Non-Converge |  |  | 0.13087 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20G | GEN-2017-058 | '' | Non-Converge |  |  | 0.12711 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20G | GEN-2017-058 | '' | Non-Converge |  |  | 0.12698 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20SP | GEN-2017-058 | '' | Non-Converge |  |  | 0.12855 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20SP | GEN-2017-058 | '' | Non-Converge |  |  | 0.12842 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24L | GEN-2017-058 | '' | Non-Converge |  |  | 0.11426 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24L | GEN-2017-058 | '' | Non-Converge |  |  | 0.11414 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24WP | GEN-2017-058 | '' | Non-Converge |  |  | 0.12863 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24WP | GEN-2017-058 | '' | Non-Converge |  |  | 0.1285 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 29SP | GEN-2017-058 | '' | Non-Converge |  |  | 0.1323 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 29SP | GEN-2017-058 | '' | Non-Converge |  |  | 0.13216 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 19WP | GEN-2017-100 | '' | Non-Converge |  |  | 0.24237 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 19WP | GEN-2017-100 | '' | Non-Converge |  |  | 0.24213 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20G | GEN-2017-100 | '' | Non-Converge |  |  | 0.24097 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20G | GEN-2017-100 | '' | Non-Converge |  |  | 0.24073 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20SP | GEN-2017-100 | '' | Non-Converge |  |  | 0.2424 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20SP | GEN-2017-100 | '' | Non-Converge |  |  | 0.24216 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24L | GEN-2017-100 | '' | Non-Converge |  |  | 0.22819 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24L | GEN-2017-100 | '' | Non-Converge |  |  | 0.22796 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24WP | GEN-2017-100 | '' | Non-Converge |  |  | 0.24256 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24WP | GEN-2017-100 | '' | Non-Converge |  |  | 0.24232 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 29SP | GEN-2017-100 | '' | Non-Converge |  |  | 0.24627 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 29SP | GEN-2017-100 | '' | Non-Converge |  |  | 0.24602 |  | P42:345:OKGE:SB_BAER7314
Thermal | 02ALL | 2 |  |  | '' | None |  |  |  |  | None
Non-Converge | 03ALL | 0 | 29SP | GEN-2017-032 | '' | Non-Converge |  |  | 0.75787 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 03ALL | 0 | 29SP | GEN-2017-018 | '' | Non-Converge |  |  | 0.07021 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 03ALL | 0 | 29SP | GEN-2017-021 | '' | Non-Converge |  |  | 0.18078 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 03ALL | 0 | 29SP | GEN-2017-099 | '' | Non-Converge |  |  | 0.18078 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 03ALL | 0 | 29SP | GEN-2017-018 | '' | Non-Converge |  |  | 0.04814 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 03ALL | 0 | 29SP | GEN-2017-021 | '' | Non-Converge |  |  | 0.06089 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 03ALL | 0 | 29SP | GEN-2017-032 | '' | Non-Converge |  |  | 0.24369 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 03ALL | 0 | 29SP | GEN-2017-099 | '' | Non-Converge |  |  | 0.06089 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 03ALL | 0 |  |  | '' | None |  |  |  |  | None
Thermal | 03ALL | 2 | 20G | GEN-2017-018 | 'FROM -> TO' | 515853 DGRASSE4 138 520436 ROSEVLY4 138 1 | 160 |  | 0.03089 | 100.26 | System Intact
Thermal | 03ALL | 2 | 29SP | GEN-2017-032 | 'FROM -> TO' | 523853 FINNEY 7 345 588754 G17-032-TAP 345 1 | 380 |  | 1 | 111.75 | System Intact
Thermal | 03ALL | 2 | 24L | GEN-2017-021 | 'FROM -> TO' | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 319 |  | 0.05259 | 104.17 | System Intact
Thermal | 03ALL | 2 | 24L | GEN-2017-032 | 'FROM -> TO' | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 319 |  | 0.03521 | 104.17 | System Intact
Thermal | 03ALL | 2 | 24L | GEN-2017-052 | 'FROM -> TO' | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 319 |  | 0.03347 | 104.17 | System Intact
Thermal | 03ALL | 2 | 24L | GEN-2017-099 | 'FROM -> TO' | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 319 |  | 0.05259 | 104.17 | System Intact
Non-Converge | 04ALL | 0 |  |  | '' | None |  |  |  |  | None
Thermal | 04ALL | 2 |  |  | '' | None |  |  |  |  | None
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-039 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 20G | GEN-2016-039 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-039 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24L | GEN-2016-039 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-039 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-039 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-039 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-172 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 20G | GEN-2016-172 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-172 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24L | GEN-2016-172 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-172 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-172 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-172 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-007 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 20G | GEN-2017-007 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-007 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24L | GEN-2017-007 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-007 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-007 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-007 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-016 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 20G | GEN-2017-016 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-016 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24L | GEN-2017-016 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-016 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-016 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-016 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-026 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 20G | GEN-2017-026 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-026 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24L | GEN-2017-026 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-026 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-026 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-026 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-033 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 20G | GEN-2017-033 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-033 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24L | GEN-2017-033 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-033 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-033 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-033 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-039 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-039 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24L | GEN-2017-039 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-039 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-039 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-039 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-059 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 20G | GEN-2017-059 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-059 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24L | GEN-2017-059 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-059 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-059 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-059 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-065 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 20G | GEN-2017-065 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-065 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24L | GEN-2017-065 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-065 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-065 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-065 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-069 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 20G | GEN-2017-069 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-069 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24L | GEN-2017-069 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-069 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-069 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-069 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-078 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-078 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24L | GEN-2017-078 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-078 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-078 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-078 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-080 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-080 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24L | GEN-2017-080 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-080 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-080 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-080 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-087 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 20G | GEN-2017-087 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-087 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24L | GEN-2017-087 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-087 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-087 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-087 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-104 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 20G | GEN-2017-104 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-104 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24L | GEN-2017-104 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-104 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-104 | '' | Non-Converge |  |  |  |  | System Intact
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-104 | '' | Non-Converge |  |  |  |  | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 523771 GRAPEVINE 6 230 524044 NICHOLS 6 230 1 | 318.7 |  | 0.0483 | 102.94 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-172 | 'FROM -> TO' | 523771 GRAPEVINE 6 230 524044 NICHOLS 6 230 1 | 318.7 |  | 0.04878 | 102.94 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 523771 GRAPEVINE 6 230 524044 NICHOLS 6 230 1 | 318.7 |  | 0.03081 | 102.94 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 523771 GRAPEVINE 6 230 524044 NICHOLS 6 230 1 | 318.7 |  | 0.03081 | 102.94 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 523771 GRAPEVINE 6 230 524044 NICHOLS 6 230 1 | 318.7 |  | 0.03062 | 102.94 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 524502 NORTON 3 115 524768 PLSNT_HILL 3 115 1 |  | 128.1 | 1 | 108.44 | P12:115:SPS:W58.1.NORTON.LOPEZ
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 524502 NORTON 3 115 524768 PLSNT_HILL 3 115 1 |  | 128.1 | 1 | 108.44 | P12:115:SPS:W58.1.NORTON.LOPEZ
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 524502 NORTON 3 115 524768 PLSNT_HILL 3 115 1 |  | 128.1 | 1 | 108.43 | P12:115:SPS:W58.1.NORTON.LOPEZ
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 524502 NORTON 3 115 524768 PLSNT_HILL 3 115 1 |  | 128.1 | 1 | 108.43 | P12:115:SPS:W58.1.NORTON.LOPEZ
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 524502 NORTON 3 115 524768 PLSNT_HILL 3 115 1 |  | 128.1 | 1 | 108.39 | P12:115:SPS:W58.1.NORTON.LOPEZ
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 524502 NORTON 3 115 524768 PLSNT_HILL 3 115 1 |  | 128.1 | 1 | 108.39 | P12:115:SPS:W58.1.NORTON.LOPEZ
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 524502 NORTON 3 115 524768 PLSNT_HILL 3 115 1 |  | 128.1 | 1 | 108.36 | P12:115:SPS:W58.1.NORTON.LOPEZ
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 524502 NORTON 3 115 524768 PLSNT_HILL 3 115 1 |  | 128.1 | 1 | 108.36 | P12:115:SPS:W58.1.NORTON.LOPEZ
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 524502 NORTON 3 115 524768 PLSNT_HILL 3 115 1 |  | 128.1 | 1 | 114.39 | P12:115:SPS:W59.1.LOPEZ.CMPBLL
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 524502 NORTON 3 115 524768 PLSNT_HILL 3 115 1 |  | 128.1 | 1 | 114.39 | P12:115:SPS:W59.1.LOPEZ.CMPBLL
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 524502 NORTON 3 115 524768 PLSNT_HILL 3 115 1 |  | 128.1 | 1 | 109.08 | P12:115:SPS:W59.1.LOPEZ.CMPBLL
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 524502 NORTON 3 115 524768 PLSNT_HILL 3 115 1 |  | 128.1 | 1 | 109.08 | P12:115:SPS:W59.1.LOPEZ.CMPBLL
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 524502 NORTON 3 115 524768 PLSNT_HILL 3 115 1 |  | 128.1 | 1 | 109.02 | P12:115:SPS:W59.1.LOPEZ.CMPBLL
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 524502 NORTON 3 115 524768 PLSNT_HILL 3 115 1 |  | 128.1 | 1 | 109.02 | P12:115:SPS:W59.1.LOPEZ.CMPBLL
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 524502 NORTON 3 115 524768 PLSNT_HILL 3 115 1 |  | 128.1 | 1 | 108.08 | P12:115:SPS:W59.1.LOPEZ.CMPBLL
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 524502 NORTON 3 115 524768 PLSNT_HILL 3 115 1 |  | 128.1 | 1 | 108.08 | P12:115:SPS:W59.1.LOPEZ.CMPBLL
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 524502 NORTON 3 115 524768 PLSNT_HILL 3 115 1 |  | 128.1 | 1 | 106.48 | P12:115:SPS:W59.1.LOPEZ.CMPBLL
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 524502 NORTON 3 115 524768 PLSNT_HILL 3 115 1 |  | 128.1 | 1 | 106.48 | P12:115:SPS:W59.1.LOPEZ.CMPBLL
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 524502 NORTON 3 115 524768 PLSNT_HILL 3 115 1 | 128.1 |  | 1 | 111.11 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 524502 NORTON 3 115 524768 PLSNT_HILL 3 115 1 | 128.1 |  | 1 | 111.11 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 524502 NORTON 3 115 524768 PLSNT_HILL 3 115 1 | 128.1 |  | 1 | 103.46 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 524502 NORTON 3 115 524768 PLSNT_HILL 3 115 1 | 128.1 |  | 1 | 103.46 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 524502 NORTON 3 115 524768 PLSNT_HILL 3 115 1 | 128.1 |  | 1 | 100.9 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 524502 NORTON 3 115 524768 PLSNT_HILL 3 115 1 | 128.1 |  | 1 | 100.9 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525454 HALE_CNTY 3 115 525828 TUCO_INT 3 115 1 | 79.7 |  | 0.09096 | 114.43 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-172 | 'FROM -> TO' | 525454 HALE_CNTY 3 115 525828 TUCO_INT 3 115 1 | 79.7 |  | 0.06569 | 114.43 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 |  | 478 | 0.20376 | 122.08 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 |  | 478 | 0.24269 | 122.08 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 |  | 478 | 0.21339 | 122.08 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 |  | 478 | 0.24269 | 122.08 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 137.77 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 137.77 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 137.77 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 137.77 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 137.77 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 137.77 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 137.77 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 137.77 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 137.77 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 137.77 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 133.95 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 133.95 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 133.95 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 133.95 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 133.95 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 133.95 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 133.95 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 133.95 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 133.95 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 133.95 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 125.75 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 125.75 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 125.75 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 125.75 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 125.75 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 125.75 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 125.75 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 125.75 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 125.75 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 125.75 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 111.6 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.6 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 111.6 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.6 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.6 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 111.6 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.6 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 111.6 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.6 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 111.6 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 137.74 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 137.74 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 137.74 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 137.74 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 137.74 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 137.74 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 137.74 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 137.74 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 137.74 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 137.74 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 133.9 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 133.9 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 133.9 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 133.9 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 133.9 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 133.9 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 133.9 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 133.9 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 133.9 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 133.9 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 125.62 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 125.62 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 125.62 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 125.62 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 125.62 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 125.62 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 125.62 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 125.62 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 125.62 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 125.62 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 111.57 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.57 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 111.57 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.57 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.57 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 111.57 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.57 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 111.57 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.57 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 111.57 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 137.45 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 137.45 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 137.45 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 137.45 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 137.45 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 137.45 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 137.45 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 137.45 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 137.45 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 137.45 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 111.33 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.33 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 111.33 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.33 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.33 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 111.33 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.33 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 111.33 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.33 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 111.33 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 138.02 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 138.02 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 138.02 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.02 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.02 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 138.02 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.02 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 138.02 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.02 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 138.02 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 134.19 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 134.19 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 134.19 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.19 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.19 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 134.19 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.19 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 134.19 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.19 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 134.19 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 125.99 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 125.99 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 125.99 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 125.99 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 125.99 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 125.99 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 125.99 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 125.99 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 125.99 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 125.99 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 111.83 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.83 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 111.83 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.83 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.83 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 111.83 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.83 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 111.83 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.83 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 111.83 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 135.97 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 135.97 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 135.97 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 135.97 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 135.97 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 135.97 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 135.97 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 135.97 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 135.97 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 135.97 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 127.52 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 127.52 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 127.52 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 127.52 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 127.52 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 127.52 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 127.52 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 127.52 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 127.52 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 127.52 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 114.26 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 114.26 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 114.26 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 114.26 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 114.26 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 114.26 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 114.26 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 114.26 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 114.26 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 114.26 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 138.28 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 138.28 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 138.28 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.28 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.28 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 138.28 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.28 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 138.28 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.28 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 138.28 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 134.46 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 134.46 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 134.46 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.46 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.46 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 134.46 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.46 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 134.46 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.46 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 134.46 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.27 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.27 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.27 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.27 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.27 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.27 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.27 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.27 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.27 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.27 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.28 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.28 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.28 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.28 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.28 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.28 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.28 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.28 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.28 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.28 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 138.16 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 138.16 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 138.16 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.16 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.16 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 138.16 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.16 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 138.16 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.16 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 138.16 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 134.34 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 134.34 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 134.34 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.34 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.34 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 134.34 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.34 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 134.34 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.34 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 134.34 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 138.43 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 138.43 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 138.43 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.43 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.43 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 138.43 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.43 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 138.43 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.43 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 138.43 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 134.53 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 134.53 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 134.53 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.53 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.53 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 134.53 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.53 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 134.53 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.53 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 134.53 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.43 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.43 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.43 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.43 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.43 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.43 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.43 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.43 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.43 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.43 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 112.22 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 112.22 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 112.22 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.22 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.22 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 112.22 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.22 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 112.22 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.22 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 112.22 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 138.27 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 138.27 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 138.27 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.27 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.27 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 138.27 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.27 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 138.27 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.27 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 138.27 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 134.46 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 134.46 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 134.46 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.46 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.46 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 134.46 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.46 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 134.46 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.46 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 134.46 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.25 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.25 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.25 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.25 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.25 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.25 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.25 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.25 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.25 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.25 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.76 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.76 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.76 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.76 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.76 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.76 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.76 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.76 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.76 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.76 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 132.88 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 132.88 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 132.88 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.88 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.88 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 132.88 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.88 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 132.88 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.88 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 132.88 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.66 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.66 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.66 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.66 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.66 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.66 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.66 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.66 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.66 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.66 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.28 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.28 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.28 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.28 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.28 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.28 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.28 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.28 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.28 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.28 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 125.12 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 125.12 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 125.12 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 125.12 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 125.12 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 125.12 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 125.12 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 125.12 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 125.12 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 125.12 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26202 | 157.38 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 157.38 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 157.38 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27985 | 157.38 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 157.38 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23967 | 157.38 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 157.38 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25806 | 157.38 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 138.27 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 138.27 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 138.27 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.27 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.27 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 138.27 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.27 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 138.27 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.27 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 138.27 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 134.46 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 134.46 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 134.46 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.46 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.46 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 134.46 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.46 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 134.46 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.46 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 134.46 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.25 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.25 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.25 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.25 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.25 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.25 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.25 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.25 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.25 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.25 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.28 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.28 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.28 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.28 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.28 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.28 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.28 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.28 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.28 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.28 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.26 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.26 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.26 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.26 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.26 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.26 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.26 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.26 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.26 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.26 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21206 | 126.28 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.28 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.28 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.28 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3386 | 126.28 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3131 | 126.28 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.28 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.28 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3386 | 126.28 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.28 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.57 | P11:345:OKGE:BKRBKR_GSU05
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.57 | P11:345:OKGE:BKRBKR_GSU05
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.57 | P11:345:OKGE:BKRBKR_GSU05
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.57 | P11:345:OKGE:BKRBKR_GSU05
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.57 | P11:345:OKGE:BKRBKR_GSU05
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.57 | P11:345:OKGE:BKRBKR_GSU05
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.57 | P11:345:OKGE:BKRBKR_GSU05
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.57 | P11:345:OKGE:BKRBKR_GSU05
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.57 | P11:345:OKGE:BKRBKR_GSU05
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.57 | P11:345:OKGE:BKRBKR_GSU05
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.57 | P11:345:OKGE:BKRBKR_GSU06
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.57 | P11:345:OKGE:BKRBKR_GSU06
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.57 | P11:345:OKGE:BKRBKR_GSU06
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.57 | P11:345:OKGE:BKRBKR_GSU06
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.57 | P11:345:OKGE:BKRBKR_GSU06
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.57 | P11:345:OKGE:BKRBKR_GSU06
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.57 | P11:345:OKGE:BKRBKR_GSU06
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.57 | P11:345:OKGE:BKRBKR_GSU06
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.57 | P11:345:OKGE:BKRBKR_GSU06
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.57 | P11:345:OKGE:BKRBKR_GSU06
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 138.8 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 138.8 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 138.8 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.8 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.8 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 138.8 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.8 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 138.8 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.8 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 138.8 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 113.15 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 113.15 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 113.15 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 113.15 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 113.15 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 113.15 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 113.15 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 113.15 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 113.15 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 113.15 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 138.8 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 138.8 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 138.8 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.8 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.8 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 138.8 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.8 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 138.8 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.8 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 138.8 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 113.27 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 113.27 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 113.27 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 113.27 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 113.27 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 113.27 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 113.27 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 113.27 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 113.27 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 113.27 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.57 | P11:345:OKGE:BKRBKR_GSU22
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.57 | P11:345:OKGE:BKRBKR_GSU22
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.57 | P11:345:OKGE:BKRBKR_GSU22
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.57 | P11:345:OKGE:BKRBKR_GSU22
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.57 | P11:345:OKGE:BKRBKR_GSU22
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.57 | P11:345:OKGE:BKRBKR_GSU22
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.57 | P11:345:OKGE:BKRBKR_GSU22
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.57 | P11:345:OKGE:BKRBKR_GSU22
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.57 | P11:345:OKGE:BKRBKR_GSU22
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.57 | P11:345:OKGE:BKRBKR_GSU22
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 138.27 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 138.27 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 138.27 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.27 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.27 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 138.27 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.27 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 138.27 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.27 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 138.27 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 134.45 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 134.45 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 134.45 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.45 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.45 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 134.45 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.45 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 134.45 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.45 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 134.45 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.26 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.26 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.26 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.26 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.26 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.26 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.26 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.26 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.26 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.26 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 112.14 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 112.14 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 112.14 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.14 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.14 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 112.14 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.14 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 112.14 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.14 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 112.14 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 138.27 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 138.27 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 138.27 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.27 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.27 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 138.27 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.27 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 138.27 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.27 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 138.27 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 134.45 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 134.45 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 134.45 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.45 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.45 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 134.45 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.45 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 134.45 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.45 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 134.45 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.26 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.26 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.26 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.26 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.26 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.26 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.26 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.26 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.26 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.26 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 112.14 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 112.14 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 112.14 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.14 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.14 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 112.14 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.14 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 112.14 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.14 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 112.14 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 138.27 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 138.27 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 138.27 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.27 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.27 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 138.27 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.27 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 138.27 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.27 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 138.27 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 134.45 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 134.45 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 134.45 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.45 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.45 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 134.45 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.45 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 134.45 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.45 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 134.45 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.26 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.26 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.26 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.26 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.26 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.26 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.26 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.26 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.26 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.26 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 112.15 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 112.15 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 112.15 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.15 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.15 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 112.15 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.15 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 112.15 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.15 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 112.15 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 137.53 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 137.53 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 137.53 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 137.53 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 137.53 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 137.53 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 137.53 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 137.53 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 137.53 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 137.53 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 133.66 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 133.66 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 133.66 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 133.66 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 133.66 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 133.66 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 133.66 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 133.66 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 133.66 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 133.66 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 125.32 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 125.32 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 125.32 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 125.32 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 125.32 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 125.32 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 125.32 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 125.32 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 125.32 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 125.32 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 111.35 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.35 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 111.35 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.35 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.35 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 111.35 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.35 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 111.35 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.35 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 111.35 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 138.16 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 138.16 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 138.16 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.16 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.16 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 138.16 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.16 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 138.16 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.16 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 138.16 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 134.34 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 134.34 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 134.34 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.34 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.34 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 134.34 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.34 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 134.34 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.34 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 134.34 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.15 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.15 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.15 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.15 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.15 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.15 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.15 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.15 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.15 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.15 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 138.16 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 138.16 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 138.16 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.16 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.16 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 138.16 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.16 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 138.16 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.16 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 138.16 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 134.34 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 134.34 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 134.34 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.34 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.34 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 134.34 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.34 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 134.34 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.34 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 134.34 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.15 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.15 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.15 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.15 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.15 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.15 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.15 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.15 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.15 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.15 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26202 | 158.33 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 158.33 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 158.33 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27985 | 158.33 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 158.33 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23967 | 158.33 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 158.33 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25806 | 158.33 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 134.65 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 134.65 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 134.65 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.65 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.65 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 134.65 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.65 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 134.65 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.65 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 134.65 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.46 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.46 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.46 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.46 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.46 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.46 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.46 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.46 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.46 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.46 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.43 | P11:HV:EES::TURKCOAL:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.43 | P11:HV:EES::TURKCOAL:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.43 | P11:HV:EES::TURKCOAL:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.43 | P11:HV:EES::TURKCOAL:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.43 | P11:HV:EES::TURKCOAL:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.43 | P11:HV:EES::TURKCOAL:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.43 | P11:HV:EES::TURKCOAL:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.43 | P11:HV:EES::TURKCOAL:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.43 | P11:HV:EES::TURKCOAL:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.43 | P11:HV:EES::TURKCOAL:1
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26207 | 158.7 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25828 | 158.7 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30728 | 158.7 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2801 | 158.7 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25828 | 158.7 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23953 | 158.7 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30728 | 158.7 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25802 | 158.7 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20512 | 138.72 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22475 | 138.72 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28982 | 138.72 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28603 | 138.72 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33503 | 138.72 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30785 | 138.72 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28603 | 138.72 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21179 | 138.72 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33503 | 138.72 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28577 | 138.72 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20549 | 134.98 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22512 | 134.98 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2902 | 134.98 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28641 | 134.98 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33541 | 134.98 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30822 | 134.98 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28641 | 134.98 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21141 | 134.98 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33541 | 134.98 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28615 | 134.98 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21305 | 126.8 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23165 | 126.8 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28974 | 126.8 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28633 | 126.8 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33888 | 126.8 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31339 | 126.8 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28633 | 126.8 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21899 | 126.8 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33888 | 126.8 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28594 | 126.8 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21214 | 112.61 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23179 | 112.61 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29703 | 112.61 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29338 | 112.61 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34198 | 112.61 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31479 | 112.61 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29338 | 112.61 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20482 | 112.61 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34198 | 112.61 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2931 | 112.61 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20424 | 135.88 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22271 | 135.88 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28978 | 135.88 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 135.88 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33481 | 135.88 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30763 | 135.88 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 135.88 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21195 | 135.88 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33481 | 135.88 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 135.88 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20461 | 132.2 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22308 | 132.2 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29015 | 132.2 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.2 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33518 | 132.2 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.308 | 132.2 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.2 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21158 | 132.2 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33518 | 132.2 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 132.2 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21126 | 109.77 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22975 | 109.77 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 109.77 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 109.77 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34175 | 109.77 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31457 | 109.77 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 109.77 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20499 | 109.77 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34175 | 109.77 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29315 | 109.77 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26208 | 157.35 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25839 | 157.35 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30712 | 157.35 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27994 | 157.35 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25839 | 157.35 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23966 | 157.35 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30712 | 157.35 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25812 | 157.35 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20426 | 133.27 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22273 | 133.27 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28978 | 133.27 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28609 | 133.27 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33482 | 133.27 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30764 | 133.27 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28609 | 133.27 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21196 | 133.27 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33482 | 133.27 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28582 | 133.27 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20463 | 129.74 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2231 | 129.74 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29016 | 129.74 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28647 | 129.74 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3352 | 129.74 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30802 | 129.74 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28647 | 129.74 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21158 | 129.74 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3352 | 129.74 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2862 | 129.74 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21217 | 121.99 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22952 | 121.99 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28971 | 121.99 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28641 | 121.99 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3387 | 121.99 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31325 | 121.99 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28641 | 121.99 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21922 | 121.99 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3387 | 121.99 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28601 | 121.99 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21127 | 106.68 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22976 | 106.68 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 106.68 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29344 | 106.68 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34176 | 106.68 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31458 | 106.68 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29344 | 106.68 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20499 | 106.68 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34176 | 106.68 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29315 | 106.68 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 137.21 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 137.21 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 137.21 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 137.21 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 137.21 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 137.21 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 137.21 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 137.21 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 137.21 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 137.21 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 111.09 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.09 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 111.09 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.09 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.09 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 111.09 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.09 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 111.09 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.09 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 111.09 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20131 | 138.56 | P12:115:SPS:T28A.1.LAMTON.PLANTX
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21904 | 138.56 | P12:115:SPS:T28A.1.LAMTON.PLANTX
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29138 | 138.56 | P12:115:SPS:T28A.1.LAMTON.PLANTX
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28789 | 138.56 | P12:115:SPS:T28A.1.LAMTON.PLANTX
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33607 | 138.56 | P12:115:SPS:T28A.1.LAMTON.PLANTX
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30875 | 138.56 | P12:115:SPS:T28A.1.LAMTON.PLANTX
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28789 | 138.56 | P12:115:SPS:T28A.1.LAMTON.PLANTX
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2114 | 138.56 | P12:115:SPS:T28A.1.LAMTON.PLANTX
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33607 | 138.56 | P12:115:SPS:T28A.1.LAMTON.PLANTX
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2876 | 138.56 | P12:115:SPS:T28A.1.LAMTON.PLANTX
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20832 | 112.32 | P12:115:SPS:T28A.1.LAMTON.PLANTX
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22607 | 112.32 | P12:115:SPS:T28A.1.LAMTON.PLANTX
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29857 | 112.32 | P12:115:SPS:T28A.1.LAMTON.PLANTX
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29519 | 112.32 | P12:115:SPS:T28A.1.LAMTON.PLANTX
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34304 | 112.32 | P12:115:SPS:T28A.1.LAMTON.PLANTX
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31572 | 112.32 | P12:115:SPS:T28A.1.LAMTON.PLANTX
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29519 | 112.32 | P12:115:SPS:T28A.1.LAMTON.PLANTX
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20441 | 112.32 | P12:115:SPS:T28A.1.LAMTON.PLANTX
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34304 | 112.32 | P12:115:SPS:T28A.1.LAMTON.PLANTX
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29488 | 112.32 | P12:115:SPS:T28A.1.LAMTON.PLANTX
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20502 | 139.92 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22419 | 139.92 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29168 | 139.92 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28813 | 139.92 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33693 | 139.92 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30882 | 139.92 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28813 | 139.92 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21168 | 139.92 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33693 | 139.92 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28783 | 139.92 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20548 | 135.57 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22465 | 135.57 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29214 | 135.57 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28859 | 135.57 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33739 | 135.57 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30928 | 135.57 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28859 | 135.57 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21122 | 135.57 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33739 | 135.57 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28829 | 135.57 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 114.23 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23126 | 114.23 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29923 | 114.23 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29604 | 114.23 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34373 | 114.23 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31564 | 114.23 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29604 | 114.23 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20476 | 114.23 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34373 | 114.23 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2957 | 114.23 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 112.67 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23126 | 112.67 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29923 | 112.67 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29604 | 112.67 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34373 | 112.67 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31564 | 112.67 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29604 | 112.67 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20476 | 112.67 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34373 | 112.67 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2957 | 112.67 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2047 | 133.56 | P12:115:SPS:T35.1.TERRY.YOAKUM
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22316 | 133.56 | P12:115:SPS:T35.1.TERRY.YOAKUM
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 133.56 | P12:115:SPS:T35.1.TERRY.YOAKUM
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28646 | 133.56 | P12:115:SPS:T35.1.TERRY.YOAKUM
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33518 | 133.56 | P12:115:SPS:T35.1.TERRY.YOAKUM
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30789 | 133.56 | P12:115:SPS:T35.1.TERRY.YOAKUM
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28646 | 133.56 | P12:115:SPS:T35.1.TERRY.YOAKUM
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21161 | 133.56 | P12:115:SPS:T35.1.TERRY.YOAKUM
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33518 | 133.56 | P12:115:SPS:T35.1.TERRY.YOAKUM
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 133.56 | P12:115:SPS:T35.1.TERRY.YOAKUM
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21135 | 110.82 | P12:115:SPS:T35.1.TERRY.YOAKUM
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22982 | 110.82 | P12:115:SPS:T35.1.TERRY.YOAKUM
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 110.82 | P12:115:SPS:T35.1.TERRY.YOAKUM
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29344 | 110.82 | P12:115:SPS:T35.1.TERRY.YOAKUM
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34175 | 110.82 | P12:115:SPS:T35.1.TERRY.YOAKUM
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31446 | 110.82 | P12:115:SPS:T35.1.TERRY.YOAKUM
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29344 | 110.82 | P12:115:SPS:T35.1.TERRY.YOAKUM
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20502 | 110.82 | P12:115:SPS:T35.1.TERRY.YOAKUM
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34175 | 110.82 | P12:115:SPS:T35.1.TERRY.YOAKUM
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29315 | 110.82 | P12:115:SPS:T35.1.TERRY.YOAKUM
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20421 | 137.96 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22268 | 137.96 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28978 | 137.96 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.286 | 137.96 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 137.96 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3076 | 137.96 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.286 | 137.96 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 137.96 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 137.96 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 137.96 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 134.15 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22305 | 134.15 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29015 | 134.15 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28637 | 134.15 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.15 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30797 | 134.15 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28637 | 134.15 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21155 | 134.15 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.15 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 134.15 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 125.96 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 125.96 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 125.96 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 125.96 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 125.96 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 125.96 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 125.96 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 125.96 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 125.96 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 125.96 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 111.83 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.83 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.297 | 111.83 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29337 | 111.83 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.83 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31454 | 111.83 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29337 | 111.83 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 111.83 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.83 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 111.83 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26251 | 159.07 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25885 | 159.07 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30751 | 159.07 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2803 | 159.07 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25885 | 159.07 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23968 | 159.07 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30751 | 159.07 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25857 | 159.07 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20531 | 138.61 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22376 | 138.61 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2905 | 138.61 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28683 | 138.61 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33549 | 138.61 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30828 | 138.61 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28683 | 138.61 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2117 | 138.61 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33549 | 138.61 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28656 | 138.61 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20565 | 134.95 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2241 | 134.95 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29084 | 134.95 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28718 | 134.95 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33584 | 134.95 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30862 | 134.95 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28718 | 134.95 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21135 | 134.95 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33584 | 134.95 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2869 | 134.95 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21315 | 126.9 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23047 | 126.9 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29039 | 126.9 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28711 | 126.9 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33929 | 126.9 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31378 | 126.9 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28711 | 126.9 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21895 | 126.9 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33929 | 126.9 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2867 | 126.9 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21236 | 112.33 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23082 | 112.33 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29774 | 112.33 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29421 | 112.33 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34247 | 112.33 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31525 | 112.33 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29421 | 112.33 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2047 | 112.33 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34247 | 112.33 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29392 | 112.33 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20493 | 138.46 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22339 | 138.46 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29024 | 138.46 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28657 | 138.46 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33524 | 138.46 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30804 | 138.46 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28657 | 138.46 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21179 | 138.46 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33524 | 138.46 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2863 | 138.46 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20386 | 138.52 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22207 | 138.52 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29565 | 138.52 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29419 | 138.52 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33615 | 138.52 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3089 | 138.52 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29419 | 138.52 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21116 | 138.52 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33615 | 138.52 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29366 | 138.52 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20426 | 134.54 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22247 | 134.54 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29605 | 134.54 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29459 | 134.54 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33655 | 134.54 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3093 | 134.54 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29459 | 134.54 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21076 | 134.54 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33655 | 134.54 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29406 | 134.54 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21173 | 126.38 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22886 | 126.38 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29522 | 126.38 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29399 | 126.38 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33993 | 126.38 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3144 | 126.38 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29399 | 126.38 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21833 | 126.38 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33993 | 126.38 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29336 | 126.38 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21087 | 112.4 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22909 | 112.4 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30283 | 112.4 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30148 | 112.4 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34312 | 112.4 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31586 | 112.4 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30148 | 112.4 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20418 | 112.4 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34312 | 112.4 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30094 | 112.4 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26792 | 159.02 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26647 | 159.02 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30843 | 159.02 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28118 | 159.02 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26647 | 159.02 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23888 | 159.02 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30843 | 159.02 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26594 | 159.02 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20386 | 138.79 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22207 | 138.79 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29565 | 138.79 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29419 | 138.79 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33615 | 138.79 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3089 | 138.79 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29419 | 138.79 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21116 | 138.79 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33615 | 138.79 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29366 | 138.79 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20426 | 134.8 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22247 | 134.8 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29605 | 134.8 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29459 | 134.8 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33655 | 134.8 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3093 | 134.8 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29459 | 134.8 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21076 | 134.8 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33655 | 134.8 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29406 | 134.8 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21173 | 126.6 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22886 | 126.6 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29522 | 126.6 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29399 | 126.6 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33993 | 126.6 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3144 | 126.6 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29399 | 126.6 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21833 | 126.6 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33993 | 126.6 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29336 | 126.6 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21087 | 112.77 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22909 | 112.77 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30283 | 112.77 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30148 | 112.77 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34312 | 112.77 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31586 | 112.77 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30148 | 112.77 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20418 | 112.77 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34312 | 112.77 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30094 | 112.77 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26319 | 158.94 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25947 | 158.94 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30827 | 158.94 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28109 | 158.94 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25947 | 158.94 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23897 | 158.94 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30827 | 158.94 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25921 | 158.94 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21069 | 139.13 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22543 | 139.13 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29091 | 139.13 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2872 | 139.13 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33599 | 139.13 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30881 | 139.13 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2872 | 139.13 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21125 | 139.13 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33599 | 139.13 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28693 | 139.13 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21772 | 112.84 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23248 | 112.84 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29814 | 112.84 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29455 | 112.84 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34295 | 112.84 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31576 | 112.84 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29455 | 112.84 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20427 | 112.84 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34295 | 112.84 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29427 | 112.84 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20425 | 137.57 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22271 | 137.57 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28975 | 137.57 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28606 | 137.57 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33477 | 137.57 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30756 | 137.57 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28606 | 137.57 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21194 | 137.57 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33477 | 137.57 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28579 | 137.57 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21127 | 111.38 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22974 | 111.38 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29696 | 111.38 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29341 | 111.38 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34171 | 111.38 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3145 | 111.38 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29341 | 111.38 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20498 | 111.38 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34171 | 111.38 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29312 | 111.38 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 111.53 | P12:115:SPS:T83.1.SP-FKFD.ALLEN
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.53 | P12:115:SPS:T83.1.SP-FKFD.ALLEN
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29698 | 111.53 | P12:115:SPS:T83.1.SP-FKFD.ALLEN
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29342 | 111.53 | P12:115:SPS:T83.1.SP-FKFD.ALLEN
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.53 | P12:115:SPS:T83.1.SP-FKFD.ALLEN
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 111.53 | P12:115:SPS:T83.1.SP-FKFD.ALLEN
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29342 | 111.53 | P12:115:SPS:T83.1.SP-FKFD.ALLEN
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 111.53 | P12:115:SPS:T83.1.SP-FKFD.ALLEN
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.53 | P12:115:SPS:T83.1.SP-FKFD.ALLEN
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 111.53 | P12:115:SPS:T83.1.SP-FKFD.ALLEN
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 110.45 | P12:115:SPS:T86.1.AMASTH.SPGDRW
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 110.45 | P12:115:SPS:T86.1.AMASTH.SPGDRW
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 110.45 | P12:115:SPS:T86.1.AMASTH.SPGDRW
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 110.45 | P12:115:SPS:T86.1.AMASTH.SPGDRW
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 110.45 | P12:115:SPS:T86.1.AMASTH.SPGDRW
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 110.45 | P12:115:SPS:T86.1.AMASTH.SPGDRW
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 110.45 | P12:115:SPS:T86.1.AMASTH.SPGDRW
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 110.45 | P12:115:SPS:T86.1.AMASTH.SPGDRW
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 110.45 | P12:115:SPS:T86.1.AMASTH.SPGDRW
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 110.45 | P12:115:SPS:T86.1.AMASTH.SPGDRW
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.86 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.86 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.86 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.86 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.86 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.86 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.86 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.86 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.86 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.86 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 110.41 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 110.41 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 110.41 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 110.41 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 110.41 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 110.41 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 110.41 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 110.41 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 110.41 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 110.41 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26417 | 159.12 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26037 | 159.12 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30773 | 159.12 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28036 | 159.12 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26037 | 159.12 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23972 | 159.12 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30773 | 159.12 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26014 | 159.12 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20449 | 138.2 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22304 | 138.2 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29182 | 138.2 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28802 | 138.2 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33538 | 138.2 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30802 | 138.2 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28802 | 138.2 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 138.2 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33538 | 138.2 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28779 | 138.2 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20488 | 134.53 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22343 | 134.53 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29221 | 134.53 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28841 | 134.53 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33577 | 134.53 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30841 | 134.53 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28841 | 134.53 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21168 | 134.53 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33577 | 134.53 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28818 | 134.53 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21249 | 126.41 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22991 | 126.41 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29201 | 126.41 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28858 | 126.41 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33931 | 126.41 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31361 | 126.41 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28858 | 126.41 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2194 | 126.41 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33931 | 126.41 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28823 | 126.41 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2115 | 111.85 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23007 | 111.85 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29902 | 111.85 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29534 | 111.85 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34232 | 111.85 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31496 | 111.85 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29534 | 111.85 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20511 | 111.85 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34232 | 111.85 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2951 | 111.85 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 137.39 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 137.39 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 137.39 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 137.39 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 137.39 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 137.39 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 137.39 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 137.39 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 137.39 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 137.39 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 111.19 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.19 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 111.19 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.19 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.19 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 111.19 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.19 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 111.19 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.19 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 111.19 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20342 | 137.43 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21924 | 137.43 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29104 | 137.43 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2874 | 137.43 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33599 | 137.43 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30875 | 137.43 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2874 | 137.43 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21135 | 137.43 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33599 | 137.43 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28713 | 137.43 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21045 | 111.14 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22628 | 111.14 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29824 | 111.14 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29471 | 111.14 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34297 | 111.14 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31572 | 111.14 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29471 | 111.14 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20436 | 111.14 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34297 | 111.14 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29442 | 111.14 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2621 | 158.37 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25841 | 158.37 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30716 | 158.37 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27998 | 158.37 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25841 | 158.37 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23966 | 158.37 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30716 | 158.37 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25814 | 158.37 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20429 | 135.48 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22277 | 135.48 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28981 | 135.48 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28612 | 135.48 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33486 | 135.48 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30768 | 135.48 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28612 | 135.48 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21196 | 135.48 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33486 | 135.48 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28585 | 135.48 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20467 | 131.84 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22314 | 131.84 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29018 | 131.84 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28649 | 131.84 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33524 | 131.84 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30806 | 131.84 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28649 | 131.84 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21158 | 131.84 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33524 | 131.84 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28622 | 131.84 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21226 | 124.36 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22961 | 124.36 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 124.36 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28648 | 124.36 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33879 | 124.36 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31335 | 124.36 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28648 | 124.36 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21922 | 124.36 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33879 | 124.36 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28607 | 124.36 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2113 | 108.95 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22979 | 108.95 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29702 | 108.95 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29346 | 108.95 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3418 | 108.95 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31462 | 108.95 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29346 | 108.95 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.205 | 108.95 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3418 | 108.95 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29318 | 108.95 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20404 | 137.69 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22278 | 137.69 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29012 | 137.69 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28646 | 137.69 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33511 | 137.69 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30789 | 137.69 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28646 | 137.69 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21177 | 137.69 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33511 | 137.69 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 137.69 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20442 | 133.93 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22317 | 133.93 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2905 | 133.93 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28684 | 133.93 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33549 | 133.93 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30828 | 133.93 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28684 | 133.93 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21139 | 133.93 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33549 | 133.93 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28656 | 133.93 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21106 | 111.33 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22982 | 111.33 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29734 | 111.33 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2938 | 111.33 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34205 | 111.33 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31483 | 111.33 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2938 | 111.33 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20481 | 111.33 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34205 | 111.33 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29351 | 111.33 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26264 | 158.97 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25897 | 158.97 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3078 | 158.97 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28032 | 158.97 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25897 | 158.97 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23954 | 158.97 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3078 | 158.97 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25869 | 158.97 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20449 | 138.21 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22315 | 138.21 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29025 | 138.21 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28659 | 138.21 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33541 | 138.21 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30793 | 138.21 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28659 | 138.21 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21193 | 138.21 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33541 | 138.21 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28631 | 138.21 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20489 | 134.49 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22354 | 134.49 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29065 | 134.49 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28698 | 134.49 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33581 | 134.49 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30833 | 134.49 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28698 | 134.49 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21153 | 134.49 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33581 | 134.49 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28671 | 134.49 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21243 | 126.16 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22994 | 126.16 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 126.16 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28687 | 126.16 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33923 | 126.16 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31339 | 126.16 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28687 | 126.16 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21917 | 126.16 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33923 | 126.16 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28646 | 126.16 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21151 | 112.19 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23018 | 112.19 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29751 | 112.19 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29401 | 112.19 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34234 | 112.19 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31486 | 112.19 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29401 | 112.19 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20497 | 112.19 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34234 | 112.19 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29371 | 112.19 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26214 | 157.97 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25846 | 157.97 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30724 | 157.97 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28006 | 157.97 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25846 | 157.97 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2397 | 157.97 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30724 | 157.97 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25819 | 157.97 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20437 | 135.35 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22283 | 135.35 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28979 | 135.35 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2861 | 135.35 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33489 | 135.35 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3077 | 135.35 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2861 | 135.35 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21206 | 135.35 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33489 | 135.35 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28583 | 135.35 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20476 | 131.56 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22322 | 131.56 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29018 | 131.56 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28649 | 131.56 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33528 | 131.56 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30809 | 131.56 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28649 | 131.56 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21167 | 131.56 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33528 | 131.56 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28622 | 131.56 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21243 | 124.46 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22974 | 124.46 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28967 | 124.46 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28639 | 124.46 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33881 | 124.46 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31336 | 124.46 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28639 | 124.46 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21952 | 124.46 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33881 | 124.46 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.46 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21138 | 108.68 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22986 | 108.68 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.297 | 108.68 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29346 | 108.68 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34183 | 108.68 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31464 | 108.68 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29346 | 108.68 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2051 | 108.68 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34183 | 108.68 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29317 | 108.68 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20427 | 137.12 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22273 | 137.12 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28978 | 137.12 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28609 | 137.12 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33482 | 137.12 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30766 | 137.12 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28609 | 137.12 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21202 | 137.12 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33482 | 137.12 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28582 | 137.12 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20462 | 133.19 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22309 | 133.19 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29013 | 133.19 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28644 | 133.19 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33517 | 133.19 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30801 | 133.19 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28644 | 133.19 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21167 | 133.19 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33517 | 133.19 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28617 | 133.19 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21129 | 110.62 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22978 | 110.62 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29701 | 110.62 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29345 | 110.62 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34178 | 110.62 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31461 | 110.62 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29345 | 110.62 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20505 | 110.62 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34178 | 110.62 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29316 | 110.62 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 138.18 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 138.18 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2898 | 138.18 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28624 | 138.18 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.18 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 138.18 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28624 | 138.18 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21193 | 138.18 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.18 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28624 | 138.18 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20459 | 134.34 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 134.34 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29017 | 134.34 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28661 | 134.34 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33515 | 134.34 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 134.34 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28661 | 134.34 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 134.34 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33515 | 134.34 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2866 | 134.34 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.15 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.15 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28973 | 126.15 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28661 | 126.15 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3386 | 126.15 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.15 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28661 | 126.15 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.15 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3386 | 126.15 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28661 | 126.15 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 112.03 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 112.03 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29702 | 112.03 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29359 | 112.03 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.03 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 112.03 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29359 | 112.03 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 112.03 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.03 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29359 | 112.03 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26488 | 159.34 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26152 | 159.34 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30932 | 159.34 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28202 | 159.34 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26152 | 159.34 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2385 | 159.34 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30932 | 159.34 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26121 | 159.34 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20436 | 139.2 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22415 | 139.2 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29252 | 139.2 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28916 | 139.2 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33696 | 139.2 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30966 | 139.2 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28916 | 139.2 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21086 | 139.2 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33696 | 139.2 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28885 | 139.2 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20479 | 135.11 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22458 | 135.11 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29295 | 135.11 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28959 | 135.11 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33739 | 135.11 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31009 | 135.11 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28959 | 135.11 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21043 | 135.11 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33739 | 135.11 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28928 | 135.11 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21226 | 126.75 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23094 | 126.75 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29253 | 126.75 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28955 | 126.75 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34087 | 126.75 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3153 | 126.75 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28955 | 126.75 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21796 | 126.75 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34087 | 126.75 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28911 | 126.75 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21138 | 113.09 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23119 | 113.09 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29973 | 113.09 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2965 | 113.09 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34392 | 113.09 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31662 | 113.09 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2965 | 113.09 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20388 | 113.09 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34392 | 113.09 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29618 | 113.09 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20421 | 138.12 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22268 | 138.12 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29 | 138.12 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28675 | 138.12 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3348 | 138.12 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30761 | 138.12 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28675 | 138.12 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 138.12 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3348 | 138.12 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28632 | 138.12 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20457 | 134.3 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22304 | 134.3 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29036 | 134.3 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28711 | 134.3 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33517 | 134.3 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30797 | 134.3 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28711 | 134.3 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21155 | 134.3 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33517 | 134.3 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28669 | 134.3 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21206 | 126.13 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22941 | 126.13 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28987 | 126.13 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28694 | 126.13 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33862 | 126.13 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31312 | 126.13 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28694 | 126.13 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21913 | 126.13 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33862 | 126.13 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28641 | 126.13 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21122 | 112.01 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22971 | 112.01 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2972 | 112.01 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29407 | 112.01 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34174 | 112.01 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31454 | 112.01 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29407 | 112.01 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20495 | 112.01 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34174 | 112.01 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29363 | 112.01 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26202 | 155.03 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 155.03 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27985 | 155.03 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23967 | 155.03 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 155.03 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25806 | 155.03 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 139.11 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 139.11 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 139.11 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 139.11 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 139.11 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 139.11 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 139.11 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 139.11 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 135.48 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 135.48 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 135.48 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 135.48 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 135.48 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 135.48 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 135.48 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 135.48 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 127.18 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 127.18 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 127.18 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 127.18 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 127.18 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 127.18 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 127.18 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 127.18 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 112.85 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 112.85 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 112.85 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.85 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 112.85 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 112.85 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.85 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 112.85 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 138.13 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 138.13 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2898 | 138.13 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28624 | 138.13 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.13 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 138.13 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28624 | 138.13 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21193 | 138.13 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.13 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28479 | 138.13 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20459 | 134.3 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 134.3 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29017 | 134.3 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28661 | 134.3 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33515 | 134.3 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 134.3 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28661 | 134.3 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 134.3 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33515 | 134.3 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28516 | 134.3 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 112.03 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 112.03 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29702 | 112.03 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29359 | 112.03 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.03 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 112.03 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29359 | 112.03 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 112.03 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.03 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29206 | 112.03 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2042 | 138.1 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22267 | 138.1 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29004 | 138.1 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28687 | 138.1 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3348 | 138.1 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30761 | 138.1 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28687 | 138.1 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 138.1 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3348 | 138.1 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28641 | 138.1 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20457 | 134.36 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22304 | 134.36 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2904 | 134.36 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28723 | 134.36 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33517 | 134.36 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30798 | 134.36 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28723 | 134.36 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21155 | 134.36 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33517 | 134.36 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28678 | 134.36 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21205 | 126.15 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2294 | 126.15 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2899 | 126.15 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28704 | 126.15 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33862 | 126.15 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31312 | 126.15 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28704 | 126.15 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21913 | 126.15 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33862 | 126.15 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28648 | 126.15 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21122 | 111.98 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22971 | 111.98 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29724 | 111.98 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29418 | 111.98 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34174 | 111.98 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31455 | 111.98 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29418 | 111.98 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20495 | 111.98 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34174 | 111.98 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29372 | 111.98 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26202 | 158.28 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 158.28 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 158.28 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27985 | 158.28 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 158.28 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23967 | 158.28 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 158.28 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25806 | 158.28 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.78 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.78 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.78 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.78 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.78 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.78 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.78 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.78 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.78 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.78 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 133.15 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 133.15 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 133.15 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 133.15 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 133.15 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 133.15 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 133.15 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 133.15 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 133.15 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 133.15 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 125.07 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 125.07 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 125.07 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 125.07 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 125.07 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 125.07 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 125.07 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 125.07 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 125.07 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 125.07 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 110.5 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 110.5 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 110.5 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 110.5 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 110.5 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 110.5 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 110.5 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 110.5 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 110.5 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 110.5 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26202 | 156.71 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 156.71 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 156.71 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27985 | 156.71 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 156.71 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23967 | 156.71 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 156.71 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25806 | 156.71 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 133.98 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 133.98 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 133.98 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 133.98 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 133.98 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 133.98 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 133.98 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 133.98 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 133.98 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 133.98 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 130.21 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 130.21 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 130.21 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 130.21 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 130.21 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 130.21 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 130.21 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 130.21 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 130.21 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 130.21 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 107.64 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 107.64 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 107.64 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 107.64 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 107.64 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 107.64 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 107.64 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 107.64 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 107.64 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 107.64 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 135.15 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 135.15 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 135.15 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 135.15 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 135.15 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 135.15 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 135.15 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 135.15 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 135.15 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 135.15 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 131.4 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 131.4 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 131.4 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 131.4 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 131.4 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 131.4 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 131.4 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 131.4 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 131.4 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 131.4 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 106.19 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 106.19 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 106.19 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 106.19 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 106.19 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 106.19 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 106.19 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 106.19 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 106.19 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 106.19 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20493 | 138.46 | P12:115:SPS-AEPW:KIRBY3:SHAM3WT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22339 | 138.46 | P12:115:SPS-AEPW:KIRBY3:SHAM3WT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29024 | 138.46 | P12:115:SPS-AEPW:KIRBY3:SHAM3WT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28657 | 138.46 | P12:115:SPS-AEPW:KIRBY3:SHAM3WT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33524 | 138.46 | P12:115:SPS-AEPW:KIRBY3:SHAM3WT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30804 | 138.46 | P12:115:SPS-AEPW:KIRBY3:SHAM3WT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28657 | 138.46 | P12:115:SPS-AEPW:KIRBY3:SHAM3WT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21179 | 138.46 | P12:115:SPS-AEPW:KIRBY3:SHAM3WT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33524 | 138.46 | P12:115:SPS-AEPW:KIRBY3:SHAM3WT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28629 | 138.46 | P12:115:SPS-AEPW:KIRBY3:SHAM3WT
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26202 | 156.09 | P12:138:OKGE:BKRBKR347
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 156.09 | P12:138:OKGE:BKRBKR347
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 156.09 | P12:138:OKGE:BKRBKR347
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27985 | 156.09 | P12:138:OKGE:BKRBKR347
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 156.09 | P12:138:OKGE:BKRBKR347
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23967 | 156.09 | P12:138:OKGE:BKRBKR347
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 156.09 | P12:138:OKGE:BKRBKR347
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25806 | 156.09 | P12:138:OKGE:BKRBKR347
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2041 | 137.5 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22256 | 137.5 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28954 | 137.5 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28585 | 137.5 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33455 | 137.5 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30736 | 137.5 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28585 | 137.5 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21243 | 137.5 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33455 | 137.5 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28558 | 137.5 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21113 | 111.41 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2296 | 111.41 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29676 | 111.41 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29321 | 111.41 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34151 | 111.41 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31431 | 111.41 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29321 | 111.41 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20545 | 111.41 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34151 | 111.41 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29293 | 111.41 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20548 | 139.55 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22393 | 139.55 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29067 | 139.55 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.287 | 139.55 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33567 | 139.55 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30845 | 139.55 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.287 | 139.55 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21154 | 139.55 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33567 | 139.55 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28673 | 139.55 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20583 | 135.75 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22428 | 135.75 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29102 | 135.75 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28735 | 135.75 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33601 | 135.75 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3088 | 135.75 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28735 | 135.75 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21119 | 135.75 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33601 | 135.75 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28708 | 135.75 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21332 | 127.58 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23065 | 127.58 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29056 | 127.58 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28729 | 127.58 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33947 | 127.58 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31396 | 127.58 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28729 | 127.58 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21878 | 127.58 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33947 | 127.58 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28688 | 127.58 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21252 | 113.26 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.231 | 113.26 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29791 | 113.26 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29438 | 113.26 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34264 | 113.26 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31543 | 113.26 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29438 | 113.26 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20454 | 113.26 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34264 | 113.26 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29409 | 113.26 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26202 | 156.87 | P12:230:AEPW:SWEETWT6:BUFFCK6
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 156.87 | P12:230:AEPW:SWEETWT6:BUFFCK6
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 156.87 | P12:230:AEPW:SWEETWT6:BUFFCK6
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27985 | 156.87 | P12:230:AEPW:SWEETWT6:BUFFCK6
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 156.87 | P12:230:AEPW:SWEETWT6:BUFFCK6
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23967 | 156.87 | P12:230:AEPW:SWEETWT6:BUFFCK6
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 156.87 | P12:230:AEPW:SWEETWT6:BUFFCK6
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25806 | 156.87 | P12:230:AEPW:SWEETWT6:BUFFCK6
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20558 | 172.32 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26813 | 172.32 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26476 | 172.32 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3129 | 172.32 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28545 | 172.32 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26476 | 172.32 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24009 | 172.32 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3129 | 172.32 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26445 | 172.32 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21834 | 147.26 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23664 | 147.26 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29919 | 147.26 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29582 | 147.26 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34396 | 147.26 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31651 | 147.26 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29582 | 147.26 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20903 | 147.26 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34396 | 147.26 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29551 | 147.26 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21834 | 145.7 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23664 | 145.7 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29919 | 145.7 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29582 | 145.7 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34395 | 145.7 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3165 | 145.7 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29582 | 145.7 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20903 | 145.7 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34395 | 145.7 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2955 | 145.7 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22608 | 137.85 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24325 | 137.85 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29888 | 137.85 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29591 | 137.85 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34759 | 137.85 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32189 | 137.85 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29591 | 137.85 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21664 | 137.85 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34759 | 137.85 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29546 | 137.85 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22578 | 118.67 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2441 | 118.67 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30681 | 118.67 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30356 | 118.67 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35133 | 118.67 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32388 | 118.67 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30356 | 118.67 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20163 | 118.67 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35133 | 118.67 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30323 | 118.67 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20558 | 168.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26813 | 168.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26476 | 168.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3129 | 168.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28545 | 168.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26476 | 168.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24009 | 168.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3129 | 168.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26445 | 168.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21834 | 144.38 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23664 | 144.38 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29919 | 144.38 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29582 | 144.38 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34396 | 144.38 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31651 | 144.38 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29582 | 144.38 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20903 | 144.38 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34396 | 144.38 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29551 | 144.38 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21834 | 142.64 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23664 | 142.64 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29919 | 142.64 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29582 | 142.64 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34395 | 142.64 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3165 | 142.64 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29582 | 142.64 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20903 | 142.64 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34395 | 142.64 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2955 | 142.64 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22608 | 134.7 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24325 | 134.7 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29888 | 134.7 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29591 | 134.7 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34759 | 134.7 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32189 | 134.7 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29591 | 134.7 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21664 | 134.7 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34759 | 134.7 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29546 | 134.7 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22578 | 115.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2441 | 115.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30681 | 115.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30356 | 115.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35133 | 115.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32388 | 115.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30356 | 115.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20163 | 115.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35133 | 115.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30323 | 115.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2025 | 140.45 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22081 | 140.45 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29124 | 140.45 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28702 | 140.45 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33777 | 140.45 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30989 | 140.45 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28702 | 140.45 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21105 | 140.45 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33777 | 140.45 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2868 | 140.45 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20293 | 135.83 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22125 | 135.83 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29168 | 135.83 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28746 | 135.83 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33821 | 135.83 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31032 | 135.83 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28746 | 135.83 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21061 | 135.83 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33821 | 135.83 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28724 | 135.83 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21046 | 127.26 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22765 | 127.26 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29114 | 127.26 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28733 | 127.26 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34151 | 127.26 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3153 | 127.26 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28733 | 127.26 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2182 | 127.26 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34151 | 127.26 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28698 | 127.26 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20942 | 114.84 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2277 | 114.84 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29743 | 114.84 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29289 | 114.84 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34456 | 114.84 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31674 | 114.84 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29289 | 114.84 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20414 | 114.84 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34456 | 114.84 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29271 | 114.84 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20397 | 137.32 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22244 | 137.32 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28948 | 137.32 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28579 | 137.32 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33449 | 137.32 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3073 | 137.32 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28579 | 137.32 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21231 | 137.32 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33449 | 137.32 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28552 | 137.32 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26431 | 167.34 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26065 | 167.34 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30932 | 167.34 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2822 | 167.34 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26065 | 167.34 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2399 | 167.34 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30932 | 167.34 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26037 | 167.34 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20899 | 143.28 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22724 | 143.28 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29365 | 143.28 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28999 | 143.28 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33866 | 143.28 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31154 | 143.28 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28999 | 143.28 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21055 | 143.28 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33866 | 143.28 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28972 | 143.28 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20918 | 141.49 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22742 | 141.49 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29384 | 141.49 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29018 | 141.49 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33885 | 141.49 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31173 | 141.49 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29018 | 141.49 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21036 | 141.49 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33885 | 141.49 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28991 | 141.49 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21728 | 134.01 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23431 | 134.01 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29359 | 134.01 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29034 | 134.01 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34259 | 134.01 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31709 | 134.01 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29034 | 134.01 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21805 | 134.01 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34259 | 134.01 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28993 | 134.01 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2162 | 116.64 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23446 | 116.64 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30106 | 116.64 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29753 | 116.64 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3458 | 116.64 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31867 | 116.64 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29753 | 116.64 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2034 | 116.64 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3458 | 116.64 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29724 | 116.64 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20168 | 202.21 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21802 | 202.21 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28441 | 202.21 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28062 | 202.21 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32967 | 202.21 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3035 | 202.21 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28062 | 202.21 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23285 | 202.21 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32967 | 202.21 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28036 | 202.21 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23622 | 189.53 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25255 | 189.53 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31894 | 189.53 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31515 | 189.53 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36421 | 189.53 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-033 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21298 | 189.53 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33804 | 189.53 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-065 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21298 | 189.53 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31515 | 189.53 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36421 | 189.53 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31489 | 189.53 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23614 | 181.38 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25248 | 181.38 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31887 | 181.38 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31508 | 181.38 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36413 | 181.38 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21291 | 181.38 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33796 | 181.38 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21291 | 181.38 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31508 | 181.38 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36413 | 181.38 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31482 | 181.38 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24826 | 176.88 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26262 | 176.88 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31975 | 176.88 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31644 | 176.88 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36965 | 176.88 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2393 | 176.88 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34442 | 176.88 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2393 | 176.88 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31644 | 176.88 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2069 | 176.88 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36965 | 176.88 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31603 | 176.88 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24423 | 153.17 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26059 | 153.17 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32719 | 153.17 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32354 | 153.17 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.37215 | 153.17 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22092 | 153.17 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34597 | 153.17 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22092 | 153.17 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32354 | 153.17 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.37215 | 153.17 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32327 | 153.17 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26143 | 156.04 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25775 | 156.04 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30645 | 156.04 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27925 | 156.04 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25775 | 156.04 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24054 | 156.04 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30645 | 156.04 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25748 | 156.04 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20322 | 137.36 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22168 | 137.36 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28865 | 137.36 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28496 | 137.36 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33366 | 137.36 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30647 | 137.36 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28496 | 137.36 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21333 | 137.36 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33366 | 137.36 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28469 | 137.36 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20357 | 132.69 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22203 | 132.69 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.289 | 132.69 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28532 | 132.69 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33402 | 132.69 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30683 | 132.69 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28532 | 132.69 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21297 | 132.69 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33402 | 132.69 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28505 | 132.69 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.211 | 124.4 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22834 | 124.4 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28847 | 124.4 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28517 | 124.4 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33739 | 124.4 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31189 | 124.4 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28517 | 124.4 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22065 | 124.4 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33739 | 124.4 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28477 | 124.4 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 112.02 | P12:345:AEPW:R.S.S.-7:COGENT7
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 112.02 | P12:345:AEPW:R.S.S.-7:COGENT7
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 112.02 | P12:345:AEPW:R.S.S.-7:COGENT7
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.02 | P12:345:AEPW:R.S.S.-7:COGENT7
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.02 | P12:345:AEPW:R.S.S.-7:COGENT7
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 112.02 | P12:345:AEPW:R.S.S.-7:COGENT7
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.02 | P12:345:AEPW:R.S.S.-7:COGENT7
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 112.02 | P12:345:AEPW:R.S.S.-7:COGENT7
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.02 | P12:345:AEPW:R.S.S.-7:COGENT7
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 112.02 | P12:345:AEPW:R.S.S.-7:COGENT7
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26191 | 159.18 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25822 | 159.18 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30693 | 159.18 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27973 | 159.18 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25822 | 159.18 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23982 | 159.18 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30693 | 159.18 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25795 | 159.18 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20404 | 136.73 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22251 | 136.73 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28952 | 136.73 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28584 | 136.73 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33454 | 136.73 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30734 | 136.73 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28584 | 136.73 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21232 | 136.73 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33454 | 136.73 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28557 | 136.73 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20435 | 133.56 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22282 | 133.56 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28984 | 133.56 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28615 | 133.56 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33485 | 133.56 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30766 | 133.56 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28615 | 133.56 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.212 | 133.56 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33485 | 133.56 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28588 | 133.56 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21182 | 125.34 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22917 | 125.34 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28935 | 125.34 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28606 | 125.34 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33828 | 125.34 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31278 | 125.34 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28606 | 125.34 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21962 | 125.34 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33828 | 125.34 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28565 | 125.34 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.211 | 110.86 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22949 | 110.86 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29669 | 110.86 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29313 | 110.86 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34143 | 110.86 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31423 | 110.86 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29313 | 110.86 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20541 | 110.86 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34143 | 110.86 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29285 | 110.86 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25967 | 152.04 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25601 | 152.04 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30467 | 152.04 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27749 | 152.04 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25601 | 152.04 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24369 | 152.04 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30467 | 152.04 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25574 | 152.04 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20125 | 134.93 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21962 | 134.93 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 134.93 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28242 | 134.93 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33108 | 134.93 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3039 | 134.93 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28242 | 134.93 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21728 | 134.93 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33108 | 134.93 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28215 | 134.93 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20169 | 129.7 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22006 | 129.7 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28652 | 129.7 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28287 | 129.7 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33152 | 129.7 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30435 | 129.7 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28287 | 129.7 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21684 | 129.7 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33152 | 129.7 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28259 | 129.7 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20906 | 121.17 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22627 | 121.17 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28576 | 121.17 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2825 | 121.17 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3347 | 121.17 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30919 | 121.17 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2825 | 121.17 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22486 | 121.17 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3347 | 121.17 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28209 | 121.17 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20832 | 108.5 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22671 | 108.5 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29336 | 108.5 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28983 | 108.5 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33808 | 108.5 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31091 | 108.5 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28983 | 108.5 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21026 | 108.5 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33808 | 108.5 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28954 | 108.5 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26431 | 167.08 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26065 | 167.08 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30932 | 167.08 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2822 | 167.08 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26065 | 167.08 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2399 | 167.08 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30932 | 167.08 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26037 | 167.08 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20899 | 144.48 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22724 | 144.48 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29365 | 144.48 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28999 | 144.48 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33866 | 144.48 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31154 | 144.48 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28999 | 144.48 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21055 | 144.48 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33866 | 144.48 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28972 | 144.48 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20918 | 142.69 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22742 | 142.69 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29384 | 142.69 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29018 | 142.69 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33885 | 142.69 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31173 | 142.69 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29018 | 142.69 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21036 | 142.69 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33885 | 142.69 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28991 | 142.69 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21728 | 135.36 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23431 | 135.36 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29359 | 135.36 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29034 | 135.36 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34259 | 135.36 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31709 | 135.36 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29034 | 135.36 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21805 | 135.36 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34259 | 135.36 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28993 | 135.36 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2162 | 117.87 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23446 | 117.87 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30106 | 117.87 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29753 | 117.87 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3458 | 117.87 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31867 | 117.87 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29753 | 117.87 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2034 | 117.87 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3458 | 117.87 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29724 | 117.87 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20168 | 177.5 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21802 | 177.5 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28441 | 177.5 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28062 | 177.5 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32967 | 177.5 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3035 | 177.5 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28062 | 177.5 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23285 | 177.5 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32967 | 177.5 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28036 | 177.5 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23622 | 156.91 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25255 | 156.91 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31894 | 156.91 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31515 | 156.91 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36421 | 156.91 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33804 | 156.91 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31515 | 156.91 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36421 | 156.91 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31489 | 156.91 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23614 | 150.42 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25248 | 150.42 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31887 | 150.42 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31508 | 150.42 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36413 | 150.42 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33796 | 150.42 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31508 | 150.42 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36413 | 150.42 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31482 | 150.42 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24826 | 143.06 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26262 | 143.06 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31975 | 143.06 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31644 | 143.06 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36965 | 143.06 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34442 | 143.06 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31644 | 143.06 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2069 | 143.06 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36965 | 143.06 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31603 | 143.06 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24423 | 122.69 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26059 | 122.69 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32719 | 122.69 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32354 | 122.69 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.37215 | 122.69 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34597 | 122.69 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32354 | 122.69 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.37215 | 122.69 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32327 | 122.69 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26191 | 159.18 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25822 | 159.18 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30693 | 159.18 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27973 | 159.18 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25822 | 159.18 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23982 | 159.18 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30693 | 159.18 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25795 | 159.18 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26282 | 162.4 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25917 | 162.4 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30781 | 162.4 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28062 | 162.4 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25917 | 162.4 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24011 | 162.4 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30781 | 162.4 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25889 | 162.4 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20571 | 140.53 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22414 | 140.53 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29067 | 140.53 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28701 | 140.53 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33566 | 140.53 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30847 | 140.53 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28701 | 140.53 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21226 | 140.53 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33566 | 140.53 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28674 | 140.53 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.206 | 136.89 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22443 | 136.89 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29096 | 136.89 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2873 | 136.89 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33595 | 136.89 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30876 | 136.89 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2873 | 136.89 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21197 | 136.89 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33595 | 136.89 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28703 | 136.89 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21361 | 128.9 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23091 | 128.9 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29052 | 128.9 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28725 | 128.9 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33944 | 128.9 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31392 | 128.9 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28725 | 128.9 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21963 | 128.9 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33944 | 128.9 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28685 | 128.9 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21278 | 114.03 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23124 | 114.03 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29794 | 114.03 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29442 | 114.03 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34267 | 114.03 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31547 | 114.03 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29442 | 114.03 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20524 | 114.03 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34267 | 114.03 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29413 | 114.03 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26282 | 162.4 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25916 | 162.4 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30781 | 162.4 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28062 | 162.4 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25916 | 162.4 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24011 | 162.4 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30781 | 162.4 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25889 | 162.4 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20571 | 140.53 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22414 | 140.53 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29067 | 140.53 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28701 | 140.53 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33566 | 140.53 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30847 | 140.53 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28701 | 140.53 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21226 | 140.53 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33566 | 140.53 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28674 | 140.53 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.206 | 136.89 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22443 | 136.89 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29096 | 136.89 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2873 | 136.89 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33595 | 136.89 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30876 | 136.89 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2873 | 136.89 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21197 | 136.89 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33595 | 136.89 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28703 | 136.89 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21361 | 128.9 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2309 | 128.9 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29052 | 128.9 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28725 | 128.9 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33944 | 128.9 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31392 | 128.9 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28725 | 128.9 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21963 | 128.9 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33944 | 128.9 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28685 | 128.9 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21278 | 114.03 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23123 | 114.03 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29794 | 114.03 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29442 | 114.03 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34267 | 114.03 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31547 | 114.03 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29442 | 114.03 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20524 | 114.03 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34267 | 114.03 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29413 | 114.03 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2624 | 159.38 | P12:345:OKGE:BKBK443NEW3
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25871 | 159.38 | P12:345:OKGE:BKBK443NEW3
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30741 | 159.38 | P12:345:OKGE:BKBK443NEW3
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28021 | 159.38 | P12:345:OKGE:BKBK443NEW3
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25871 | 159.38 | P12:345:OKGE:BKBK443NEW3
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23962 | 159.38 | P12:345:OKGE:BKBK443NEW3
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30741 | 159.38 | P12:345:OKGE:BKBK443NEW3
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25844 | 159.38 | P12:345:OKGE:BKBK443NEW3
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26266 | 159.32 | P12:345:OKGE:BKRBKR143
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25897 | 159.32 | P12:345:OKGE:BKRBKR143
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30767 | 159.32 | P12:345:OKGE:BKRBKR143
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28047 | 159.32 | P12:345:OKGE:BKRBKR143
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25897 | 159.32 | P12:345:OKGE:BKRBKR143
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23944 | 159.32 | P12:345:OKGE:BKRBKR143
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30767 | 159.32 | P12:345:OKGE:BKRBKR143
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2587 | 159.32 | P12:345:OKGE:BKRBKR143
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25915 | 161.15 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25554 | 161.15 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30412 | 161.15 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27695 | 161.15 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25554 | 161.15 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24584 | 161.15 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30412 | 161.15 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25526 | 161.15 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20345 | 139.17 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22175 | 139.17 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28749 | 139.17 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28388 | 139.17 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33245 | 139.17 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30528 | 139.17 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28388 | 139.17 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21751 | 139.17 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33245 | 139.17 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2836 | 139.17 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20371 | 136.19 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22201 | 136.19 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28775 | 136.19 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28414 | 136.19 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33271 | 136.19 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30554 | 136.19 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28414 | 136.19 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21725 | 136.19 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33271 | 136.19 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28385 | 136.19 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21128 | 128.28 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2284 | 128.28 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28699 | 128.28 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28378 | 128.28 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33593 | 128.28 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3104 | 128.28 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28378 | 128.28 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22547 | 128.28 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33593 | 128.28 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28337 | 128.28 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20382 | 137.03 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22224 | 137.03 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28893 | 137.03 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28526 | 137.03 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33393 | 137.03 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30675 | 137.03 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28526 | 137.03 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21373 | 137.03 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33393 | 137.03 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28499 | 137.03 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21087 | 110.77 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22931 | 110.77 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29619 | 110.77 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29265 | 110.77 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34092 | 110.77 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31373 | 110.77 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29265 | 110.77 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20672 | 110.77 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34092 | 110.77 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29236 | 110.77 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20382 | 137.03 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22224 | 137.03 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28893 | 137.03 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28526 | 137.03 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33393 | 137.03 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30675 | 137.03 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28526 | 137.03 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21373 | 137.03 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33393 | 137.03 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28499 | 137.03 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21087 | 110.77 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22931 | 110.77 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29619 | 110.77 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29265 | 110.77 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34092 | 110.77 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31373 | 110.77 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29265 | 110.77 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20672 | 110.77 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34092 | 110.77 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29236 | 110.77 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26231 | 159.35 | P12:345:OKGE:BKRBKR21
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25863 | 159.35 | P12:345:OKGE:BKRBKR21
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30732 | 159.35 | P12:345:OKGE:BKRBKR21
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28015 | 159.35 | P12:345:OKGE:BKRBKR21
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25863 | 159.35 | P12:345:OKGE:BKRBKR21
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23996 | 159.35 | P12:345:OKGE:BKRBKR21
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30732 | 159.35 | P12:345:OKGE:BKRBKR21
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25836 | 159.35 | P12:345:OKGE:BKRBKR21
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21277 | 127.33 | P12:345:OKGE:BKRBKR21
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23005 | 127.33 | P12:345:OKGE:BKRBKR21
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29009 | 127.33 | P12:345:OKGE:BKRBKR21
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2868 | 127.33 | P12:345:OKGE:BKRBKR21
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33903 | 127.33 | P12:345:OKGE:BKRBKR21
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31353 | 127.33 | P12:345:OKGE:BKRBKR21
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2868 | 127.33 | P12:345:OKGE:BKRBKR21
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21936 | 127.33 | P12:345:OKGE:BKRBKR21
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33903 | 127.33 | P12:345:OKGE:BKRBKR21
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28639 | 127.33 | P12:345:OKGE:BKRBKR21
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26484 | 162.88 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26118 | 162.88 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30985 | 162.88 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2827 | 162.88 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26118 | 162.88 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23858 | 162.88 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30985 | 162.88 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2609 | 162.88 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20792 | 141.48 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22622 | 141.48 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29279 | 141.48 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28913 | 141.48 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3378 | 141.48 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31065 | 141.48 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28913 | 141.48 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21063 | 141.48 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3378 | 141.48 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28885 | 141.48 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2081 | 138.65 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2264 | 138.65 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29298 | 138.65 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28931 | 138.65 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33798 | 138.65 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31083 | 138.65 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28931 | 138.65 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21045 | 138.65 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33798 | 138.65 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28904 | 138.65 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21623 | 131.04 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23334 | 131.04 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29285 | 131.04 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28959 | 131.04 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34182 | 131.04 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31632 | 131.04 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28959 | 131.04 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.218 | 131.04 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34182 | 131.04 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28918 | 131.04 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21498 | 115.6 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2333 | 115.6 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30005 | 115.6 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29652 | 115.6 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34479 | 115.6 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31764 | 115.6 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29652 | 115.6 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20362 | 115.6 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34479 | 115.6 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29623 | 115.6 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26272 | 159.69 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25906 | 159.69 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30771 | 159.69 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28052 | 159.69 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25906 | 159.69 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24005 | 159.69 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30771 | 159.69 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25878 | 159.69 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20551 | 139.55 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22395 | 139.55 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29055 | 139.55 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28689 | 139.55 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33555 | 139.55 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30835 | 139.55 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28689 | 139.55 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21222 | 139.55 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33555 | 139.55 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28662 | 139.55 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20581 | 136.1 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22425 | 136.1 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29085 | 136.1 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28719 | 136.1 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33585 | 136.1 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30865 | 136.1 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28719 | 136.1 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.1 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33585 | 136.1 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28692 | 136.1 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21341 | 128 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23071 | 128 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29041 | 128 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28714 | 128 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33933 | 128 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31382 | 128 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28714 | 128 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21957 | 128 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33933 | 128 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28673 | 128 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26272 | 159.7 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25906 | 159.7 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30772 | 159.7 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28052 | 159.7 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25906 | 159.7 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24006 | 159.7 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30772 | 159.7 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25878 | 159.7 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20552 | 139.56 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22396 | 139.56 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29055 | 139.56 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28689 | 139.56 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33555 | 139.56 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30836 | 139.56 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28689 | 139.56 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21222 | 139.56 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33555 | 139.56 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28662 | 139.56 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20582 | 136.11 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22426 | 136.11 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29085 | 136.11 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28719 | 136.11 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33585 | 136.11 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30866 | 136.11 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28719 | 136.11 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.11 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33585 | 136.11 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28692 | 136.11 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21341 | 128.01 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23072 | 128.01 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29041 | 128.01 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28714 | 128.01 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33933 | 128.01 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31382 | 128.01 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28714 | 128.01 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21957 | 128.01 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33933 | 128.01 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28674 | 128.01 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21258 | 113.1 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23104 | 113.1 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29782 | 113.1 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29429 | 113.1 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34255 | 113.1 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31535 | 113.1 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29429 | 113.1 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2052 | 113.1 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34255 | 113.1 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.294 | 113.1 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20874 | 110.78 | P12:345:OKGE:BKRBKR349
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22711 | 110.78 | P12:345:OKGE:BKRBKR349
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29337 | 110.78 | P12:345:OKGE:BKRBKR349
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28987 | 110.78 | P12:345:OKGE:BKRBKR349
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33809 | 110.78 | P12:345:OKGE:BKRBKR349
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3109 | 110.78 | P12:345:OKGE:BKRBKR349
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28987 | 110.78 | P12:345:OKGE:BKRBKR349
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21099 | 110.78 | P12:345:OKGE:BKRBKR349
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33809 | 110.78 | P12:345:OKGE:BKRBKR349
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28958 | 110.78 | P12:345:OKGE:BKRBKR349
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20379 | 137.36 | P12:345:OKGE:BKRBKR357_2
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22226 | 137.36 | P12:345:OKGE:BKRBKR357_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28926 | 137.36 | P12:345:OKGE:BKRBKR357_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28558 | 137.36 | P12:345:OKGE:BKRBKR357_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33427 | 137.36 | P12:345:OKGE:BKRBKR357_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30708 | 137.36 | P12:345:OKGE:BKRBKR357_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28558 | 137.36 | P12:345:OKGE:BKRBKR357_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21259 | 137.36 | P12:345:OKGE:BKRBKR357_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33427 | 137.36 | P12:345:OKGE:BKRBKR357_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28531 | 137.36 | P12:345:OKGE:BKRBKR357_2
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26249 | 159.15 | P12:345:OKGE:BKRBKR4193
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25882 | 159.15 | P12:345:OKGE:BKRBKR4193
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30749 | 159.15 | P12:345:OKGE:BKRBKR4193
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28027 | 159.15 | P12:345:OKGE:BKRBKR4193
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25882 | 159.15 | P12:345:OKGE:BKRBKR4193
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23968 | 159.15 | P12:345:OKGE:BKRBKR4193
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30749 | 159.15 | P12:345:OKGE:BKRBKR4193
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25855 | 159.15 | P12:345:OKGE:BKRBKR4193
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26249 | 159.15 | P12:345:OKGE:BKRBKR4194
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25883 | 159.15 | P12:345:OKGE:BKRBKR4194
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30749 | 159.15 | P12:345:OKGE:BKRBKR4194
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28027 | 159.15 | P12:345:OKGE:BKRBKR4194
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25883 | 159.15 | P12:345:OKGE:BKRBKR4194
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23968 | 159.15 | P12:345:OKGE:BKRBKR4194
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30749 | 159.15 | P12:345:OKGE:BKRBKR4194
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25855 | 159.15 | P12:345:OKGE:BKRBKR4194
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2101 | 172.23 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2778 | 172.23 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27396 | 172.23 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32304 | 172.23 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29658 | 172.23 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27396 | 172.23 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23261 | 172.23 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32304 | 172.23 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27371 | 172.23 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22506 | 154.44 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24206 | 154.44 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30976 | 154.44 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30592 | 154.44 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35499 | 154.44 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32854 | 154.44 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30592 | 154.44 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20066 | 154.44 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35499 | 154.44 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30567 | 154.44 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22519 | 148.11 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24218 | 148.11 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30988 | 148.11 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30604 | 148.11 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35511 | 148.11 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32866 | 148.11 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30604 | 148.11 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20053 | 148.11 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35511 | 148.11 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30579 | 148.11 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23579 | 140.69 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25108 | 140.69 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31046 | 140.69 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30707 | 140.69 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36009 | 140.69 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33482 | 140.69 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30707 | 140.69 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20842 | 140.69 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36009 | 140.69 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30667 | 140.69 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23262 | 123.87 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24963 | 123.87 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31753 | 123.87 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31384 | 123.87 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36247 | 123.87 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33601 | 123.87 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31384 | 123.87 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36247 | 123.87 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31357 | 123.87 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26267 | 159.52 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25899 | 159.52 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30769 | 159.52 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28049 | 159.52 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25899 | 159.52 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23925 | 159.52 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30769 | 159.52 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25872 | 159.52 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20524 | 139.42 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2237 | 139.42 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2907 | 139.42 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28701 | 139.42 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33571 | 139.42 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30852 | 139.42 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28701 | 139.42 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21122 | 139.42 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33571 | 139.42 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28674 | 139.42 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21313 | 127.32 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23046 | 127.32 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29062 | 127.32 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28733 | 127.32 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33955 | 127.32 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31405 | 127.32 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28733 | 127.32 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21844 | 127.32 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33955 | 127.32 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28692 | 127.32 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26267 | 159.52 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25899 | 159.52 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30769 | 159.52 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28049 | 159.52 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25899 | 159.52 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23925 | 159.52 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30769 | 159.52 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25872 | 159.52 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20524 | 139.42 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2237 | 139.42 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2907 | 139.42 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28701 | 139.42 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33571 | 139.42 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30852 | 139.42 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28701 | 139.42 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21122 | 139.42 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33571 | 139.42 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28674 | 139.42 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21313 | 127.32 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23046 | 127.32 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29062 | 127.32 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28733 | 127.32 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33955 | 127.32 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31405 | 127.32 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28733 | 127.32 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21844 | 127.32 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33955 | 127.32 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28692 | 127.32 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26202 | 151.82 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 151.82 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 151.82 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27985 | 151.82 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 151.82 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23967 | 151.82 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 151.82 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25806 | 151.82 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 135.79 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 135.79 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 135.79 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 135.79 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 135.79 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 135.79 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 135.79 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 135.79 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 135.79 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 135.79 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 109.72 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 109.72 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 109.72 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 109.72 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 109.72 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 109.72 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 109.72 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 109.72 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 109.72 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 109.72 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26202 | 152.86 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 152.86 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 152.86 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27985 | 152.86 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 152.86 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23967 | 152.86 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 152.86 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25806 | 152.86 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 135.99 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 135.99 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 135.99 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 135.99 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 135.99 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 135.99 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 135.99 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 135.99 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 135.99 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 135.99 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 132.62 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 132.62 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 132.62 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.62 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.62 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 132.62 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.62 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 132.62 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.62 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 132.62 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.37 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.37 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.37 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.37 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.37 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.37 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.37 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.37 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.37 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.37 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 109.92 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 109.92 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 109.92 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 109.92 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 109.92 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 109.92 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 109.92 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 109.92 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 109.92 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 109.92 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26202 | 155.23 | P12:345:OKGE:BKRBKR608
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 155.23 | P12:345:OKGE:BKRBKR608
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 155.23 | P12:345:OKGE:BKRBKR608
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27985 | 155.23 | P12:345:OKGE:BKRBKR608
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 155.23 | P12:345:OKGE:BKRBKR608
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23967 | 155.23 | P12:345:OKGE:BKRBKR608
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 155.23 | P12:345:OKGE:BKRBKR608
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25806 | 155.23 | P12:345:OKGE:BKRBKR608
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20404 | 136.73 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22251 | 136.73 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28952 | 136.73 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28584 | 136.73 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33454 | 136.73 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30734 | 136.73 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28584 | 136.73 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21232 | 136.73 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33454 | 136.73 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28557 | 136.73 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20435 | 133.56 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22282 | 133.56 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28984 | 133.56 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28615 | 133.56 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33485 | 133.56 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30766 | 133.56 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28615 | 133.56 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.212 | 133.56 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33485 | 133.56 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28588 | 133.56 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21182 | 125.34 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22917 | 125.34 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28935 | 125.34 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28606 | 125.34 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33828 | 125.34 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31278 | 125.34 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28606 | 125.34 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21962 | 125.34 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33828 | 125.34 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28565 | 125.34 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.211 | 110.86 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22949 | 110.86 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29669 | 110.86 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29313 | 110.86 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34143 | 110.86 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31423 | 110.86 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29313 | 110.86 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20541 | 110.86 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34143 | 110.86 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29285 | 110.86 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25967 | 152.04 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25601 | 152.04 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30467 | 152.04 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27749 | 152.04 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25601 | 152.04 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24369 | 152.04 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30467 | 152.04 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25574 | 152.04 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20125 | 134.93 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21962 | 134.93 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 134.93 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28242 | 134.93 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33108 | 134.93 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3039 | 134.93 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28242 | 134.93 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21728 | 134.93 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33108 | 134.93 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28215 | 134.93 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20169 | 129.7 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22006 | 129.7 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28652 | 129.7 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28287 | 129.7 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33152 | 129.7 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30435 | 129.7 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28287 | 129.7 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21684 | 129.7 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33152 | 129.7 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28259 | 129.7 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20906 | 121.17 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22627 | 121.17 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28576 | 121.17 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2825 | 121.17 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3347 | 121.17 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30919 | 121.17 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2825 | 121.17 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22486 | 121.17 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3347 | 121.17 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28209 | 121.17 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20832 | 108.5 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22671 | 108.5 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29336 | 108.5 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28983 | 108.5 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33808 | 108.5 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31091 | 108.5 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28983 | 108.5 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21026 | 108.5 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33808 | 108.5 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28954 | 108.5 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26431 | 167.08 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26065 | 167.08 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30932 | 167.08 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2822 | 167.08 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26065 | 167.08 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2399 | 167.08 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30932 | 167.08 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26037 | 167.08 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20899 | 144.48 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22724 | 144.48 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29365 | 144.48 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28999 | 144.48 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33866 | 144.48 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31154 | 144.48 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28999 | 144.48 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21055 | 144.48 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33866 | 144.48 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28972 | 144.48 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20918 | 142.69 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22742 | 142.69 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29384 | 142.69 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29018 | 142.69 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33885 | 142.69 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31173 | 142.69 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29018 | 142.69 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21036 | 142.69 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33885 | 142.69 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28991 | 142.69 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21728 | 135.36 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23431 | 135.36 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29359 | 135.36 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29034 | 135.36 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34259 | 135.36 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31709 | 135.36 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29034 | 135.36 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21805 | 135.36 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34259 | 135.36 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28993 | 135.36 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2162 | 117.87 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23446 | 117.87 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30106 | 117.87 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29753 | 117.87 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3458 | 117.87 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31867 | 117.87 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29753 | 117.87 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2034 | 117.87 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3458 | 117.87 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29724 | 117.87 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26258 | 159.29 | P12:345:OKGE-ITC:BKRBKR502_1
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25889 | 159.29 | P12:345:OKGE-ITC:BKRBKR502_1
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 159.29 | P12:345:OKGE-ITC:BKRBKR502_1
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2804 | 159.29 | P12:345:OKGE-ITC:BKRBKR502_1
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25889 | 159.29 | P12:345:OKGE-ITC:BKRBKR502_1
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23929 | 159.29 | P12:345:OKGE-ITC:BKRBKR502_1
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 159.29 | P12:345:OKGE-ITC:BKRBKR502_1
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25862 | 159.29 | P12:345:OKGE-ITC:BKRBKR502_1
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26258 | 159.29 | P12:345:OKGE-ITC:BKRBKR503_1
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25889 | 159.29 | P12:345:OKGE-ITC:BKRBKR503_1
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 159.29 | P12:345:OKGE-ITC:BKRBKR503_1
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2804 | 159.29 | P12:345:OKGE-ITC:BKRBKR503_1
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25889 | 159.29 | P12:345:OKGE-ITC:BKRBKR503_1
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23929 | 159.29 | P12:345:OKGE-ITC:BKRBKR503_1
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 159.29 | P12:345:OKGE-ITC:BKRBKR503_1
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25862 | 159.29 | P12:345:OKGE-ITC:BKRBKR503_1
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2101 | 172.33 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2778 | 172.33 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27396 | 172.33 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32304 | 172.33 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29658 | 172.33 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27396 | 172.33 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23261 | 172.33 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32304 | 172.33 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27371 | 172.33 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22506 | 154.45 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24206 | 154.45 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30976 | 154.45 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30592 | 154.45 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35499 | 154.45 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32854 | 154.45 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30592 | 154.45 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20066 | 154.45 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35499 | 154.45 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30567 | 154.45 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22519 | 148.16 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24218 | 148.16 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30988 | 148.16 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30604 | 148.16 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35511 | 148.16 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32866 | 148.16 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30604 | 148.16 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20053 | 148.16 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35511 | 148.16 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30579 | 148.16 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23579 | 140.71 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25108 | 140.71 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31046 | 140.71 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30707 | 140.71 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36009 | 140.71 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33482 | 140.71 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30707 | 140.71 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20842 | 140.71 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36009 | 140.71 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30667 | 140.71 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23262 | 123.9 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24963 | 123.9 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31753 | 123.9 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31384 | 123.9 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36247 | 123.9 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33601 | 123.9 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31384 | 123.9 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36247 | 123.9 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31357 | 123.9 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26245 | 159.68 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25877 | 159.68 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30747 | 159.68 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28027 | 159.68 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25877 | 159.68 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23948 | 159.68 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30747 | 159.68 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2585 | 159.68 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20498 | 139.41 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22344 | 139.41 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29042 | 139.41 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28673 | 139.41 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33543 | 139.41 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30823 | 139.41 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28673 | 139.41 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21152 | 139.41 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33543 | 139.41 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28646 | 139.41 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20531 | 135.65 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22378 | 135.65 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29075 | 135.65 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28707 | 135.65 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33576 | 135.65 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30857 | 135.65 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28707 | 135.65 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21118 | 135.65 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33576 | 135.65 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2868 | 135.65 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21285 | 127.56 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23019 | 127.56 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29032 | 127.56 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28703 | 127.56 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33925 | 127.56 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31375 | 127.56 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28703 | 127.56 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21875 | 127.56 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33925 | 127.56 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28663 | 127.56 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21201 | 113.24 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23049 | 113.24 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29764 | 113.24 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29409 | 113.24 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34239 | 113.24 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31519 | 113.24 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29409 | 113.24 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20454 | 113.24 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34239 | 113.24 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29381 | 113.24 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26245 | 159.68 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25877 | 159.68 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30747 | 159.68 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28027 | 159.68 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25877 | 159.68 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23948 | 159.68 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30747 | 159.68 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2585 | 159.68 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20498 | 139.41 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22344 | 139.41 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29042 | 139.41 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28673 | 139.41 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33543 | 139.41 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30823 | 139.41 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28673 | 139.41 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21152 | 139.41 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33543 | 139.41 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28646 | 139.41 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20531 | 135.65 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22378 | 135.65 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29075 | 135.65 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28707 | 135.65 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33576 | 135.65 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30857 | 135.65 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28707 | 135.65 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21118 | 135.65 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33576 | 135.65 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2868 | 135.65 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21285 | 127.56 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23019 | 127.56 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29032 | 127.56 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28703 | 127.56 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33925 | 127.56 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31375 | 127.56 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28703 | 127.56 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21875 | 127.56 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33925 | 127.56 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28663 | 127.56 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21201 | 113.24 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23049 | 113.24 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29764 | 113.24 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29409 | 113.24 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34239 | 113.24 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31519 | 113.24 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29409 | 113.24 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20454 | 113.24 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34239 | 113.24 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29381 | 113.24 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26258 | 159.29 | P12:345:PWT:THIS-DGRS_345_1::FUTURE
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25889 | 159.29 | P12:345:PWT:THIS-DGRS_345_1::FUTURE
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 159.29 | P12:345:PWT:THIS-DGRS_345_1::FUTURE
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2804 | 159.29 | P12:345:PWT:THIS-DGRS_345_1::FUTURE
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25889 | 159.29 | P12:345:PWT:THIS-DGRS_345_1::FUTURE
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23929 | 159.29 | P12:345:PWT:THIS-DGRS_345_1::FUTURE
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 159.29 | P12:345:PWT:THIS-DGRS_345_1::FUTURE
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25862 | 159.29 | P12:345:PWT:THIS-DGRS_345_1::FUTURE
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26258 | 159.29 | P12:345:PWT:THIS-DGRS_345_2::FUTURE
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25889 | 159.29 | P12:345:PWT:THIS-DGRS_345_2::FUTURE
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 159.29 | P12:345:PWT:THIS-DGRS_345_2::FUTURE
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2804 | 159.29 | P12:345:PWT:THIS-DGRS_345_2::FUTURE
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25889 | 159.29 | P12:345:PWT:THIS-DGRS_345_2::FUTURE
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23929 | 159.29 | P12:345:PWT:THIS-DGRS_345_2::FUTURE
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 159.29 | P12:345:PWT:THIS-DGRS_345_2::FUTURE
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25862 | 159.29 | P12:345:PWT:THIS-DGRS_345_2::FUTURE
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26511 | 165.5 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26148 | 165.5 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31008 | 165.5 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28284 | 165.5 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26148 | 165.5 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23809 | 165.5 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31008 | 165.5 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26121 | 165.5 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20984 | 142.37 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22834 | 142.37 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29449 | 142.37 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29086 | 142.37 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33945 | 142.37 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31222 | 142.37 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29086 | 142.37 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20871 | 142.37 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33945 | 142.37 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29058 | 142.37 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2102 | 137.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2287 | 137.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29485 | 137.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29122 | 137.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33981 | 137.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31258 | 137.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29122 | 137.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20835 | 137.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33981 | 137.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29094 | 137.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21777 | 129.21 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23514 | 129.21 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29442 | 129.21 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29119 | 129.21 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34331 | 129.21 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31777 | 129.21 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29119 | 129.21 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21595 | 129.21 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34331 | 129.21 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29078 | 129.21 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21698 | 116.98 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23549 | 116.98 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30182 | 116.98 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29832 | 116.98 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34652 | 116.98 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31928 | 116.98 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29832 | 116.98 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20163 | 116.98 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34652 | 116.98 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29803 | 116.98 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20276 | 184.36 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21862 | 184.36 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30617 | 184.36 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30101 | 184.36 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3265 | 184.36 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31396 | 184.36 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30101 | 184.36 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33869 | 184.36 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3265 | 184.36 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30142 | 184.36 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24L | GEN-2017-104 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24294 | 184.36 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25304 | 150.1 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26889 | 150.1 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35645 | 150.1 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35129 | 150.1 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.37678 | 150.1 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36423 | 150.1 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35129 | 150.1 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28842 | 150.1 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.37678 | 150.1 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3517 | 150.1 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24WP | GEN-2017-104 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29322 | 150.1 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25398 | 148.81 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27178 | 148.81 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36788 | 148.81 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36229 | 148.81 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.38487 | 148.81 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.37692 | 148.81 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36229 | 148.81 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28586 | 148.81 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.38487 | 148.81 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36282 | 148.81 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 19WP | GEN-2017-104 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33702 | 148.81 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25621 | 148.38 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27206 | 148.38 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35962 | 148.38 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35446 | 148.38 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.37994 | 148.38 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3674 | 148.38 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35446 | 148.38 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28525 | 148.38 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.37994 | 148.38 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35486 | 148.38 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24SP | GEN-2017-104 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29638 | 148.38 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21306 | 127.16 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1)
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23042 | 127.16 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29035 | 127.16 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28707 | 127.16 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33926 | 127.16 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31374 | 127.16 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28707 | 127.16 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21899 | 127.16 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33926 | 127.16 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28666 | 127.16 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26283 | 160.98 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25915 | 160.98 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30784 | 160.98 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28064 | 160.98 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25915 | 160.98 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23915 | 160.98 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30784 | 160.98 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25888 | 160.98 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20574 | 139.53 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22422 | 139.53 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29114 | 139.53 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28746 | 139.53 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33614 | 139.53 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30894 | 139.53 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28746 | 139.53 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21084 | 139.53 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33614 | 139.53 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28718 | 139.53 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26262 | 160.1 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25894 | 160.1 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30763 | 160.1 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28044 | 160.1 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25894 | 160.1 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23928 | 160.1 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30763 | 160.1 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25867 | 160.1 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20536 | 139.33 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22384 | 139.33 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2908 | 139.33 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28711 | 139.33 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33581 | 139.33 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30861 | 139.33 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28711 | 139.33 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21111 | 139.33 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33581 | 139.33 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28684 | 139.33 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26271 | 159.78 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25904 | 159.78 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30771 | 159.78 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2805 | 159.78 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25904 | 159.78 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2395 | 159.78 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30771 | 159.78 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25877 | 159.78 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20528 | 139.75 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22377 | 139.75 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29051 | 139.75 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28685 | 139.75 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33551 | 139.75 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3083 | 139.75 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28685 | 139.75 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2117 | 139.75 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33551 | 139.75 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28657 | 139.75 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21312 | 127.89 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23048 | 127.89 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29039 | 127.89 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28711 | 127.89 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3393 | 127.89 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31378 | 127.89 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28711 | 127.89 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21898 | 127.89 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3393 | 127.89 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28671 | 127.89 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26287 | 160.82 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25919 | 160.82 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30788 | 160.82 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28068 | 160.82 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25919 | 160.82 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23911 | 160.82 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30788 | 160.82 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25892 | 160.82 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20585 | 139.47 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22433 | 139.47 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29125 | 139.47 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28757 | 139.47 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33626 | 139.47 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30906 | 139.47 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28757 | 139.47 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21073 | 139.47 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33626 | 139.47 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2873 | 139.47 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21097 | 113.14 | P12:500:EES-EAI:ARK_NU:FTSMTH:1
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22947 | 113.14 | P12:500:EES-EAI:ARK_NU:FTSMTH:1
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29671 | 113.14 | P12:500:EES-EAI:ARK_NU:FTSMTH:1
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29315 | 113.14 | P12:500:EES-EAI:ARK_NU:FTSMTH:1
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34145 | 113.14 | P12:500:EES-EAI:ARK_NU:FTSMTH:1
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31425 | 113.14 | P12:500:EES-EAI:ARK_NU:FTSMTH:1
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29315 | 113.14 | P12:500:EES-EAI:ARK_NU:FTSMTH:1
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20529 | 113.14 | P12:500:EES-EAI:ARK_NU:FTSMTH:1
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34145 | 113.14 | P12:500:EES-EAI:ARK_NU:FTSMTH:1
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29286 | 113.14 | P12:500:EES-EAI:ARK_NU:FTSMTH:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21188 | 125.2 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22924 | 125.2 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28947 | 125.2 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28617 | 125.2 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3384 | 125.2 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3129 | 125.2 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28617 | 125.2 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21939 | 125.2 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3384 | 125.2 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28577 | 125.2 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21182 | 125.34 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22917 | 125.34 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28935 | 125.34 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28606 | 125.34 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33828 | 125.34 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31278 | 125.34 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28606 | 125.34 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21962 | 125.34 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33828 | 125.34 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28565 | 125.34 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.43 | P12:HV:EES::TURK 4%:1(1)
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.43 | P12:HV:EES::TURK 4%:1(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.43 | P12:HV:EES::TURK 4%:1(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.43 | P12:HV:EES::TURK 4%:1(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.43 | P12:HV:EES::TURK 4%:1(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.43 | P12:HV:EES::TURK 4%:1(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.43 | P12:HV:EES::TURK 4%:1(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.43 | P12:HV:EES::TURK 4%:1(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.43 | P12:HV:EES::TURK 4%:1(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.43 | P12:HV:EES::TURK 4%:1(1)
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 137.45 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 137.45 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 137.45 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 137.45 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 137.45 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 137.45 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 137.45 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 137.45 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 137.45 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 137.45 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 138.01 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 138.01 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 138.01 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.01 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.01 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 138.01 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.01 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 138.01 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.01 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 138.01 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 125.98 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 125.98 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 125.98 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 125.98 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 125.98 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 125.98 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 125.98 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 125.98 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 125.98 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 125.98 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20548 | 139.54 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22393 | 139.54 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29067 | 139.54 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.287 | 139.54 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33567 | 139.54 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30845 | 139.54 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.287 | 139.54 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21154 | 139.54 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33567 | 139.54 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28673 | 139.54 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20583 | 135.76 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22428 | 135.76 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29102 | 135.76 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28735 | 135.76 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33601 | 135.76 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3088 | 135.76 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28735 | 135.76 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21119 | 135.76 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33601 | 135.76 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28708 | 135.76 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21332 | 127.57 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23065 | 127.57 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29056 | 127.57 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28729 | 127.57 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33947 | 127.57 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31396 | 127.57 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28729 | 127.57 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21878 | 127.57 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33947 | 127.57 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28688 | 127.57 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21252 | 113.25 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.231 | 113.25 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29791 | 113.25 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29438 | 113.25 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34264 | 113.25 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31543 | 113.25 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29438 | 113.25 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20454 | 113.25 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34264 | 113.25 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29409 | 113.25 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 138.44 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 138.44 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 138.44 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.44 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.44 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 138.44 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.44 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 138.44 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.44 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 138.44 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 134.53 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 134.53 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 134.53 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.53 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.53 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 134.53 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.53 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 134.53 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.53 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 134.53 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.43 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.43 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.43 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.43 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.43 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.43 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.43 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.43 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.43 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.43 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 112.22 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 112.22 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 112.22 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.22 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.22 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 112.22 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.22 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 112.22 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.22 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 112.22 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20398 | 137.36 | P13:138-345:OKGE:BKRBKR_3W034
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22243 | 137.36 | P13:138-345:OKGE:BKRBKR_3W034
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28941 | 137.36 | P13:138-345:OKGE:BKRBKR_3W034
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28572 | 137.36 | P13:138-345:OKGE:BKRBKR_3W034
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33442 | 137.36 | P13:138-345:OKGE:BKRBKR_3W034
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30723 | 137.36 | P13:138-345:OKGE:BKRBKR_3W034
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28572 | 137.36 | P13:138-345:OKGE:BKRBKR_3W034
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21257 | 137.36 | P13:138-345:OKGE:BKRBKR_3W034
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33442 | 137.36 | P13:138-345:OKGE:BKRBKR_3W034
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28545 | 137.36 | P13:138-345:OKGE:BKRBKR_3W034
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20393 | 137.32 | P13:138-345:OKGE:BKRBKR_3W035
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22238 | 137.32 | P13:138-345:OKGE:BKRBKR_3W035
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28934 | 137.32 | P13:138-345:OKGE:BKRBKR_3W035
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28565 | 137.32 | P13:138-345:OKGE:BKRBKR_3W035
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33435 | 137.32 | P13:138-345:OKGE:BKRBKR_3W035
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30716 | 137.32 | P13:138-345:OKGE:BKRBKR_3W035
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28565 | 137.32 | P13:138-345:OKGE:BKRBKR_3W035
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2127 | 137.32 | P13:138-345:OKGE:BKRBKR_3W035
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33435 | 137.32 | P13:138-345:OKGE:BKRBKR_3W035
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28538 | 137.32 | P13:138-345:OKGE:BKRBKR_3W035
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 138.27 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 138.27 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 138.27 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.27 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.27 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 138.27 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.27 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 138.27 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.27 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 138.27 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 134.45 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 134.45 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 134.45 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.45 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.45 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 134.45 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.45 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 134.45 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.45 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 134.45 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.26 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.26 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.26 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.26 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.26 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.26 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.26 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.26 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.26 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.26 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 112.14 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 112.14 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 112.14 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.14 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.14 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 112.14 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.14 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 112.14 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.14 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 112.14 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26202 | 158.14 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 158.14 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 158.14 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27985 | 158.14 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 158.14 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23967 | 158.14 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 158.14 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25806 | 158.14 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.27 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.27 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.27 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.27 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.27 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.27 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.27 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.27 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.27 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.27 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 138.27 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 138.27 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 138.27 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.27 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.27 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 138.27 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.27 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 138.27 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.27 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 138.27 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 134.45 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 134.45 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 134.45 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.45 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.45 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 134.45 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.45 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 134.45 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.45 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 134.45 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.26 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.26 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.26 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.26 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.26 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.26 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.26 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.26 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.26 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.26 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 112.14 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 112.14 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 112.14 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.14 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.14 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 112.14 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.14 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 112.14 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.14 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 112.14 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.28 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.28 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.28 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.28 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.28 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.28 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.28 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.28 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.28 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.28 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26202 | 157.32 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 157.32 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 157.32 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27985 | 157.32 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 157.32 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23967 | 157.32 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 157.32 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25806 | 157.32 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 125.2 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 125.2 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 125.2 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 125.2 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 125.2 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 125.2 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 125.2 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 125.2 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 125.2 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 125.2 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26202 | 158.06 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 158.06 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 158.06 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27985 | 158.06 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 158.06 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23967 | 158.06 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 158.06 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25806 | 158.06 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.27 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.27 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.27 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.27 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.27 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.27 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.27 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.27 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.27 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.27 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 138.28 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 138.28 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 138.28 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.28 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.28 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 138.28 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.28 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 138.28 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.28 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 138.28 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.27 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.27 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.27 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.27 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.27 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.27 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.27 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.27 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.27 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.27 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 138.27 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 138.27 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 138.27 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.27 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.27 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 138.27 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.27 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 138.27 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.27 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 138.27 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 134.46 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 134.46 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 134.46 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.46 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.46 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 134.46 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.46 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 134.46 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.46 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 134.46 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.82 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.82 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.82 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.82 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.82 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.82 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.82 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.82 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.82 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.82 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 132.95 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 132.95 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 132.95 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.95 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.95 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 132.95 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.95 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 132.95 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.95 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 132.95 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.73 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.73 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.73 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.73 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.73 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.73 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.73 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.73 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.73 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.73 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26202 | 157.38 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 157.38 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 157.38 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27985 | 157.38 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 157.38 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23967 | 157.38 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 157.38 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25806 | 157.38 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 138.27 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 138.27 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 138.27 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.27 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.27 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 138.27 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.27 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 138.27 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.27 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 138.27 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 134.46 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 134.46 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 134.46 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.46 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.46 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 134.46 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.46 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 134.46 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.46 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 134.46 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.25 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.25 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.25 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.25 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.25 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.25 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.25 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.25 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.25 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.25 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 138.27 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 138.27 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 138.27 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.27 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.27 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 138.27 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.27 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 138.27 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.27 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 138.27 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 134.45 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 134.45 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 134.45 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.45 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.45 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 134.45 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.45 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 134.45 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.45 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 134.45 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.26 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.26 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.26 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.26 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.26 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.26 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.26 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.26 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.26 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.26 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 112.14 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 112.14 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 112.14 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.14 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.14 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 112.14 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.14 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 112.14 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.14 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 112.14 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 138.27 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 138.27 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 138.27 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.27 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.27 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 138.27 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.27 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 138.27 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.27 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 138.27 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 134.45 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 134.45 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 134.45 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.45 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.45 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 134.45 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.45 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 134.45 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.45 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 134.45 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.26 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.26 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.26 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.26 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.26 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.26 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.26 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.26 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.26 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.26 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 112.14 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 112.14 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 112.14 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.14 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.14 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 112.14 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.14 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 112.14 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.14 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 112.14 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 138.27 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 138.27 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 138.27 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.27 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.27 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 138.27 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.27 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 138.27 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.27 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 138.27 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 134.45 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 134.45 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 134.45 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.45 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.45 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 134.45 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.45 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 134.45 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.45 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 134.45 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.26 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.26 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.26 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.26 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.26 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.26 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.26 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.26 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.26 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.26 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 112.14 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 112.14 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 112.14 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.14 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.14 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 112.14 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.14 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 112.14 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.14 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 112.14 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 138.27 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 138.27 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 138.27 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.27 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.27 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 138.27 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.27 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 138.27 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.27 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 138.27 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 134.45 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 134.45 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 134.45 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.45 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.45 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 134.45 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.45 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 134.45 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.45 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 134.45 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.26 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.26 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.26 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.26 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.26 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.26 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.26 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.26 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.26 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.26 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 112.15 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 112.15 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 112.15 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.15 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.15 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 112.15 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.15 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 112.15 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.15 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 112.15 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20276 | 184.36 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21862 | 184.36 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30617 | 184.36 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30101 | 184.36 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3265 | 184.36 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31396 | 184.36 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30101 | 184.36 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33869 | 184.36 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3265 | 184.36 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30142 | 184.36 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-104 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24294 | 184.36 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25304 | 150.11 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26889 | 150.11 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35645 | 150.11 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35129 | 150.11 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.37678 | 150.11 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36423 | 150.11 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35129 | 150.11 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28842 | 150.11 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.37678 | 150.11 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3517 | 150.11 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-104 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29322 | 150.11 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25398 | 148.81 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27178 | 148.81 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36788 | 148.81 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36229 | 148.81 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.38487 | 148.81 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.37692 | 148.81 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36229 | 148.81 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28586 | 148.81 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.38487 | 148.81 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36282 | 148.81 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-104 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33702 | 148.81 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25621 | 148.38 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27206 | 148.38 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35962 | 148.38 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35446 | 148.38 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.37994 | 148.38 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3674 | 148.38 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35446 | 148.38 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28525 | 148.38 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.37994 | 148.38 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35486 | 148.38 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-104 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29638 | 148.38 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20406 | 137.11 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22254 | 137.11 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2896 | 137.11 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28591 | 137.11 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33461 | 137.11 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30742 | 137.11 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28591 | 137.11 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21215 | 137.11 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33461 | 137.11 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28564 | 137.11 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20441 | 133.41 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22288 | 133.41 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28994 | 133.41 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28625 | 133.41 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33495 | 133.41 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30776 | 133.41 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28625 | 133.41 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2118 | 133.41 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33495 | 133.41 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 133.41 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21188 | 125.2 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22924 | 125.2 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28947 | 125.2 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28617 | 125.2 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3384 | 125.2 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3129 | 125.2 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28617 | 125.2 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21939 | 125.2 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3384 | 125.2 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28577 | 125.2 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21106 | 110.97 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22955 | 110.97 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2968 | 110.97 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29324 | 110.97 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34154 | 110.97 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31434 | 110.97 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29324 | 110.97 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2052 | 110.97 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34154 | 110.97 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29295 | 110.97 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20406 | 137.12 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22254 | 137.12 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2896 | 137.12 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28591 | 137.12 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33461 | 137.12 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30742 | 137.12 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28591 | 137.12 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21215 | 137.12 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33461 | 137.12 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28564 | 137.12 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20441 | 133.43 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22288 | 133.43 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28994 | 133.43 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28625 | 133.43 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33495 | 133.43 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30776 | 133.43 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28625 | 133.43 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2118 | 133.43 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33495 | 133.43 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 133.43 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21188 | 125.22 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22924 | 125.22 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28947 | 125.22 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28617 | 125.22 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3384 | 125.22 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3129 | 125.22 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28617 | 125.22 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21939 | 125.22 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3384 | 125.22 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28577 | 125.22 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21106 | 111 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22955 | 111 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2968 | 111 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29324 | 111 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34154 | 111 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31434 | 111 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29324 | 111 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2052 | 111 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34154 | 111 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29295 | 111 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20406 | 137.11 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22254 | 137.11 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2896 | 137.11 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28591 | 137.11 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33461 | 137.11 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30742 | 137.11 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28591 | 137.11 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21215 | 137.11 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33461 | 137.11 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28564 | 137.11 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20441 | 133.41 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22288 | 133.41 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28994 | 133.41 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28625 | 133.41 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33495 | 133.41 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30776 | 133.41 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28625 | 133.41 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2118 | 133.41 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33495 | 133.41 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 133.41 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21188 | 125.2 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22924 | 125.2 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28947 | 125.2 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28617 | 125.2 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3384 | 125.2 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3129 | 125.2 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28617 | 125.2 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21939 | 125.2 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3384 | 125.2 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28577 | 125.2 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21106 | 110.97 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22955 | 110.97 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2968 | 110.97 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29324 | 110.97 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34154 | 110.97 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31434 | 110.97 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29324 | 110.97 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2052 | 110.97 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34154 | 110.97 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29295 | 110.97 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20396 | 137.37 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22243 | 137.37 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28947 | 137.37 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28578 | 137.37 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33448 | 137.37 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30729 | 137.37 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28578 | 137.37 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21233 | 137.37 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33448 | 137.37 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28551 | 137.37 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20396 | 137.37 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22243 | 137.37 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28947 | 137.37 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28578 | 137.37 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33448 | 137.37 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30729 | 137.37 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28578 | 137.37 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21233 | 137.37 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33448 | 137.37 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28551 | 137.37 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20396 | 137.37 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22243 | 137.37 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28947 | 137.37 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28578 | 137.37 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33448 | 137.37 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30729 | 137.37 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28578 | 137.37 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21233 | 137.37 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33448 | 137.37 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28551 | 137.37 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26439 | 167.63 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26073 | 167.63 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3094 | 167.63 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28228 | 167.63 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26073 | 167.63 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23988 | 167.63 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3094 | 167.63 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26045 | 167.63 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20912 | 143.7 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22735 | 143.7 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29377 | 143.7 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29011 | 143.7 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33878 | 143.7 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31166 | 143.7 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29011 | 143.7 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2105 | 143.7 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33878 | 143.7 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28983 | 143.7 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20931 | 141.8 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22754 | 141.8 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29396 | 141.8 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2903 | 141.8 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33897 | 141.8 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31185 | 141.8 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2903 | 141.8 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21031 | 141.8 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33897 | 141.8 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29002 | 141.8 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21741 | 134.31 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23443 | 134.31 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2937 | 134.31 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29045 | 134.31 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3427 | 134.31 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31721 | 134.31 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29045 | 134.31 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.218 | 134.31 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3427 | 134.31 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29004 | 134.31 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21633 | 116.94 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23458 | 116.94 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30118 | 116.94 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29765 | 116.94 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34592 | 116.94 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3188 | 116.94 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29765 | 116.94 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20334 | 116.94 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34592 | 116.94 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29736 | 116.94 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20169 | 202.23 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21803 | 202.23 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28441 | 202.23 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28062 | 202.23 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32968 | 202.23 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30351 | 202.23 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28062 | 202.23 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23285 | 202.23 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32968 | 202.23 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28036 | 202.23 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23623 | 189.5 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25257 | 189.5 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31895 | 189.5 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31516 | 189.5 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36421 | 189.5 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-033 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21299 | 189.5 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33804 | 189.5 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-065 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21299 | 189.5 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31516 | 189.5 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36421 | 189.5 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3149 | 189.5 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23615 | 181.41 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25249 | 181.41 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31888 | 181.41 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31508 | 181.41 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36414 | 181.41 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21291 | 181.41 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33797 | 181.41 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21291 | 181.41 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31508 | 181.41 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36414 | 181.41 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31482 | 181.41 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24828 | 176.36 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26263 | 176.36 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31975 | 176.36 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31645 | 176.36 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36965 | 176.36 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23931 | 176.36 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34442 | 176.36 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23931 | 176.36 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31645 | 176.36 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2069 | 176.36 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36965 | 176.36 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31603 | 176.36 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24425 | 153.12 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26061 | 153.12 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3272 | 153.12 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32355 | 153.12 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.37216 | 153.12 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22093 | 153.12 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34598 | 153.12 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22093 | 153.12 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32355 | 153.12 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.37216 | 153.12 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32327 | 153.12 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20225 | 204.34 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21856 | 204.34 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28464 | 204.34 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28087 | 204.34 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32989 | 204.34 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30372 | 204.34 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28087 | 204.34 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23325 | 204.34 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32989 | 204.34 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28061 | 204.34 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23732 | 189.99 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25363 | 189.99 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31971 | 189.99 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31594 | 189.99 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36496 | 189.99 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-033 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21388 | 189.99 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33878 | 189.99 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-065 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21388 | 189.99 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31594 | 189.99 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36496 | 189.99 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31568 | 189.99 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23717 | 183.06 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25348 | 183.06 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31956 | 183.06 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31579 | 183.06 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36481 | 183.06 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21374 | 183.06 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33864 | 183.06 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21374 | 183.06 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31579 | 183.06 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36481 | 183.06 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31553 | 183.06 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24943 | 178.43 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26375 | 178.43 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32051 | 178.43 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31723 | 178.43 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3704 | 178.43 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24031 | 178.43 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34516 | 178.43 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24031 | 178.43 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31723 | 178.43 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20684 | 178.43 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3704 | 178.43 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31681 | 178.43 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24539 | 154.07 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26172 | 154.07 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32801 | 154.07 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32438 | 154.07 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.37295 | 154.07 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22188 | 154.07 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34677 | 154.07 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22188 | 154.07 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32438 | 154.07 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.37295 | 154.07 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3241 | 154.07 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20397 | 137.32 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22244 | 137.32 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28948 | 137.32 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28579 | 137.32 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33449 | 137.32 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3073 | 137.32 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28579 | 137.32 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21231 | 137.32 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33449 | 137.32 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28552 | 137.32 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20168 | 177.5 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21802 | 177.5 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28441 | 177.5 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28062 | 177.5 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32967 | 177.5 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3035 | 177.5 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28062 | 177.5 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23285 | 177.5 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32967 | 177.5 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28036 | 177.5 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23622 | 156.91 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25255 | 156.91 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31894 | 156.91 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31515 | 156.91 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36421 | 156.91 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33804 | 156.91 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31515 | 156.91 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36421 | 156.91 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31489 | 156.91 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23614 | 150.42 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25248 | 150.42 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31887 | 150.42 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31508 | 150.42 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36413 | 150.42 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33796 | 150.42 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31508 | 150.42 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36413 | 150.42 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31482 | 150.42 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24826 | 143.06 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26262 | 143.06 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31975 | 143.06 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31644 | 143.06 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36965 | 143.06 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34442 | 143.06 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31644 | 143.06 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2069 | 143.06 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36965 | 143.06 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31603 | 143.06 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24423 | 122.69 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26059 | 122.69 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32719 | 122.69 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32354 | 122.69 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.37215 | 122.69 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34597 | 122.69 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32354 | 122.69 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.37215 | 122.69 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32327 | 122.69 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20168 | 176.8 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21802 | 176.8 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28441 | 176.8 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28062 | 176.8 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32967 | 176.8 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3035 | 176.8 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28062 | 176.8 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23285 | 176.8 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32967 | 176.8 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28036 | 176.8 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23622 | 156.43 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25255 | 156.43 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31894 | 156.43 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31515 | 156.43 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36421 | 156.43 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33804 | 156.43 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31515 | 156.43 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36421 | 156.43 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31489 | 156.43 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23614 | 149.89 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25248 | 149.89 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31887 | 149.89 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31508 | 149.89 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36413 | 149.89 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33796 | 149.89 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31508 | 149.89 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36413 | 149.89 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31482 | 149.89 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24826 | 142.76 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26262 | 142.76 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31975 | 142.76 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31644 | 142.76 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36965 | 142.76 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34442 | 142.76 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31644 | 142.76 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2069 | 142.76 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36965 | 142.76 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31603 | 142.76 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24423 | 122.11 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26059 | 122.11 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32719 | 122.11 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32354 | 122.11 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.37215 | 122.11 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34597 | 122.11 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32354 | 122.11 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.37215 | 122.11 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32327 | 122.11 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26076 | 154.75 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25708 | 154.75 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30577 | 154.75 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27857 | 154.75 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25708 | 154.75 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24137 | 154.75 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30577 | 154.75 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25681 | 154.75 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20231 | 136.84 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22076 | 136.84 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28766 | 136.84 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28398 | 136.84 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33267 | 136.84 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30548 | 136.84 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28398 | 136.84 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21447 | 136.84 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33267 | 136.84 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28371 | 136.84 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20274 | 131.77 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2212 | 131.77 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28809 | 131.77 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28441 | 131.77 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3331 | 131.77 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30591 | 131.77 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28441 | 131.77 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21404 | 131.77 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3331 | 131.77 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28414 | 131.77 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21013 | 123.48 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22746 | 123.48 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2875 | 123.48 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28421 | 123.48 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33643 | 123.48 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31092 | 123.48 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28421 | 123.48 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22178 | 123.48 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33643 | 123.48 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28381 | 123.48 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20933 | 110.69 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2278 | 110.69 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29488 | 110.69 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29133 | 110.69 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33961 | 110.69 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31242 | 110.69 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29133 | 110.69 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2075 | 110.69 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33961 | 110.69 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29104 | 110.69 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26147 | 155.95 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2578 | 155.95 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30647 | 155.95 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2793 | 155.95 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2578 | 155.95 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24146 | 155.95 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30647 | 155.95 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25752 | 155.95 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20357 | 136.49 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22195 | 136.49 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28863 | 136.49 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28496 | 136.49 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33364 | 136.49 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30647 | 136.49 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28496 | 136.49 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2143 | 136.49 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33364 | 136.49 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28469 | 136.49 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2038 | 132.26 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22218 | 132.26 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28886 | 132.26 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28519 | 132.26 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33387 | 132.26 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3067 | 132.26 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28519 | 132.26 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21407 | 132.26 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33387 | 132.26 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28492 | 132.26 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21132 | 123.8 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22855 | 123.8 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28828 | 123.8 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.285 | 123.8 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33722 | 123.8 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31172 | 123.8 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.285 | 123.8 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22189 | 123.8 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33722 | 123.8 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2846 | 123.8 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21051 | 110.68 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22891 | 110.68 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29577 | 110.68 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29223 | 110.68 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34051 | 110.68 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31333 | 110.68 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29223 | 110.68 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20741 | 110.68 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34051 | 110.68 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29195 | 110.68 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25992 | 152.1 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25626 | 152.1 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30491 | 152.1 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27774 | 152.1 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25626 | 152.1 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24367 | 152.1 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30491 | 152.1 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25599 | 152.1 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20156 | 134.73 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21991 | 134.73 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28632 | 134.73 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28266 | 134.73 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33131 | 134.73 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30414 | 134.73 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28266 | 134.73 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21727 | 134.73 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33131 | 134.73 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28239 | 134.73 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20192 | 129.49 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22027 | 129.49 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28667 | 129.49 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28302 | 129.49 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33167 | 129.49 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3045 | 129.49 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28302 | 129.49 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21691 | 129.49 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33167 | 129.49 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28275 | 129.49 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20933 | 120.97 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22651 | 120.97 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28591 | 120.97 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28266 | 120.97 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33486 | 120.97 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30935 | 120.97 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28266 | 120.97 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22495 | 120.97 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33486 | 120.97 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28225 | 120.97 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20858 | 108.54 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22695 | 108.54 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29354 | 108.54 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29002 | 108.54 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33826 | 108.54 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31109 | 108.54 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29002 | 108.54 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2103 | 108.54 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33826 | 108.54 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28973 | 108.54 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25967 | 152.04 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25601 | 152.04 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30467 | 152.04 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27749 | 152.04 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25601 | 152.04 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24369 | 152.04 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30467 | 152.04 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25574 | 152.04 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20125 | 134.93 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21962 | 134.93 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 134.93 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28242 | 134.93 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33108 | 134.93 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3039 | 134.93 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28242 | 134.93 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21728 | 134.93 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33108 | 134.93 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28215 | 134.93 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20169 | 129.7 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22006 | 129.7 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28652 | 129.7 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28287 | 129.7 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33152 | 129.7 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30435 | 129.7 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28287 | 129.7 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21684 | 129.7 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33152 | 129.7 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28259 | 129.7 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20906 | 121.17 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22627 | 121.17 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28576 | 121.17 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2825 | 121.17 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3347 | 121.17 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30919 | 121.17 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2825 | 121.17 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22486 | 121.17 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3347 | 121.17 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28209 | 121.17 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20832 | 108.5 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22671 | 108.5 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29336 | 108.5 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28983 | 108.5 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33808 | 108.5 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31091 | 108.5 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28983 | 108.5 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21026 | 108.5 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33808 | 108.5 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28954 | 108.5 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26431 | 167.33 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26065 | 167.33 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30932 | 167.33 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2822 | 167.33 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26065 | 167.33 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2399 | 167.33 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30932 | 167.33 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26037 | 167.33 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20899 | 143.45 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22724 | 143.45 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29365 | 143.45 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28999 | 143.45 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33866 | 143.45 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31154 | 143.45 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28999 | 143.45 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21055 | 143.45 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33866 | 143.45 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28972 | 143.45 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20918 | 141.67 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22742 | 141.67 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29384 | 141.67 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29018 | 141.67 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33885 | 141.67 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31173 | 141.67 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29018 | 141.67 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21036 | 141.67 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33885 | 141.67 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28991 | 141.67 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21728 | 134.19 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23431 | 134.19 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29359 | 134.19 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29034 | 134.19 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34259 | 134.19 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31709 | 134.19 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29034 | 134.19 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21805 | 134.19 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34259 | 134.19 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28993 | 134.19 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2162 | 116.82 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23446 | 116.82 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30106 | 116.82 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29753 | 116.82 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3458 | 116.82 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31867 | 116.82 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29753 | 116.82 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2034 | 116.82 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3458 | 116.82 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29724 | 116.82 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26431 | 167.34 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26065 | 167.34 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30932 | 167.34 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2822 | 167.34 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26065 | 167.34 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2399 | 167.34 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30932 | 167.34 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26037 | 167.34 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20899 | 143.46 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22724 | 143.46 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29365 | 143.46 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28999 | 143.46 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33866 | 143.46 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31154 | 143.46 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28999 | 143.46 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21055 | 143.46 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33866 | 143.46 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28972 | 143.46 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20918 | 141.67 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22742 | 141.67 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29384 | 141.67 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29018 | 141.67 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33885 | 141.67 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31173 | 141.67 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29018 | 141.67 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21036 | 141.67 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33885 | 141.67 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28991 | 141.67 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21728 | 134.2 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23431 | 134.2 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29359 | 134.2 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29034 | 134.2 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34259 | 134.2 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31709 | 134.2 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29034 | 134.2 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21805 | 134.2 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34259 | 134.2 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28993 | 134.2 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2162 | 116.82 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23446 | 116.82 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30106 | 116.82 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29753 | 116.82 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3458 | 116.82 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31867 | 116.82 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29753 | 116.82 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2034 | 116.82 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3458 | 116.82 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29724 | 116.82 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26431 | 167.21 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26065 | 167.21 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30932 | 167.21 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2822 | 167.21 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26065 | 167.21 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2399 | 167.21 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30932 | 167.21 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26037 | 167.21 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20899 | 143.41 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22724 | 143.41 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29365 | 143.41 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28999 | 143.41 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33866 | 143.41 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31154 | 143.41 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28999 | 143.41 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21055 | 143.41 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33866 | 143.41 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28972 | 143.41 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20918 | 141.6 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22742 | 141.6 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29384 | 141.6 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29018 | 141.6 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33885 | 141.6 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31173 | 141.6 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29018 | 141.6 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21036 | 141.6 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33885 | 141.6 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28991 | 141.6 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21728 | 134.15 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23431 | 134.15 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29359 | 134.15 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29034 | 134.15 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34259 | 134.15 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31709 | 134.15 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29034 | 134.15 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21805 | 134.15 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34259 | 134.15 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28993 | 134.15 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2162 | 116.79 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23446 | 116.79 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30106 | 116.79 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29753 | 116.79 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3458 | 116.79 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31867 | 116.79 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29753 | 116.79 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2034 | 116.79 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3458 | 116.79 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29724 | 116.79 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26143 | 156.03 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25775 | 156.03 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30644 | 156.03 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27925 | 156.03 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25775 | 156.03 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24054 | 156.03 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30644 | 156.03 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25748 | 156.03 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20322 | 137.37 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22167 | 137.37 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28865 | 137.37 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28496 | 137.37 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33366 | 137.37 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30647 | 137.37 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28496 | 137.37 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21333 | 137.37 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33366 | 137.37 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28469 | 137.37 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20357 | 132.69 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22203 | 132.69 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.289 | 132.69 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28532 | 132.69 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33402 | 132.69 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30682 | 132.69 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28532 | 132.69 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21297 | 132.69 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33402 | 132.69 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28505 | 132.69 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.211 | 124.4 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22833 | 124.4 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28847 | 124.4 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28517 | 124.4 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33739 | 124.4 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31189 | 124.4 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28517 | 124.4 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22065 | 124.4 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33739 | 124.4 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28477 | 124.4 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26138 | 155.84 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2577 | 155.84 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30639 | 155.84 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2792 | 155.84 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2577 | 155.84 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2406 | 155.84 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30639 | 155.84 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25742 | 155.84 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20313 | 137.32 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22159 | 137.32 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28856 | 137.32 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28487 | 137.32 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33357 | 137.32 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30638 | 137.32 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28487 | 137.32 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21342 | 137.32 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33357 | 137.32 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2846 | 137.32 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20349 | 132.62 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22195 | 132.62 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28892 | 132.62 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28524 | 132.62 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33393 | 132.62 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30674 | 132.62 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28524 | 132.62 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21306 | 132.62 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33393 | 132.62 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28496 | 132.62 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21092 | 124.24 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22825 | 124.24 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28838 | 124.24 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28509 | 124.24 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33731 | 124.24 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31181 | 124.24 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28509 | 124.24 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22074 | 124.24 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33731 | 124.24 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28469 | 124.24 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26184 | 159.83 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25815 | 159.83 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30685 | 159.83 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27966 | 159.83 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25815 | 159.83 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23992 | 159.83 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30685 | 159.83 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25788 | 159.83 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2046 | 139.32 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22307 | 139.32 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29012 | 139.32 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28643 | 139.32 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33514 | 139.32 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30794 | 139.32 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28643 | 139.32 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21164 | 139.32 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33514 | 139.32 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28616 | 139.32 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20493 | 135.67 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2234 | 135.67 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29046 | 135.67 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28677 | 135.67 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33547 | 135.67 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30828 | 135.67 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28677 | 135.67 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21131 | 135.67 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33547 | 135.67 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2865 | 135.67 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21245 | 127.53 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22979 | 127.53 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29002 | 127.53 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28672 | 127.53 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33895 | 127.53 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31345 | 127.53 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28672 | 127.53 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21887 | 127.53 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33895 | 127.53 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28632 | 127.53 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21164 | 113.14 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23013 | 113.14 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29736 | 113.14 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29381 | 113.14 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34211 | 113.14 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31491 | 113.14 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29381 | 113.14 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20465 | 113.14 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34211 | 113.14 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29352 | 113.14 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26191 | 159.18 | P23:345:GRDA:CLEVLND CB13280
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25822 | 159.18 | P23:345:GRDA:CLEVLND CB13280
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30693 | 159.18 | P23:345:GRDA:CLEVLND CB13280
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27973 | 159.18 | P23:345:GRDA:CLEVLND CB13280
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25822 | 159.18 | P23:345:GRDA:CLEVLND CB13280
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23982 | 159.18 | P23:345:GRDA:CLEVLND CB13280
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30693 | 159.18 | P23:345:GRDA:CLEVLND CB13280
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25795 | 159.18 | P23:345:GRDA:CLEVLND CB13280
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26202 | 157.38 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 157.38 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 157.38 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27985 | 157.38 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 157.38 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23967 | 157.38 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 157.38 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25806 | 157.38 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20421 | 138.29 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 138.29 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 138.29 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.29 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.29 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 138.29 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.29 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21193 | 138.29 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.29 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 138.29 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 134.48 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 134.48 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 134.48 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.48 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33515 | 134.48 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 134.48 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.48 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 134.48 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33515 | 134.48 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 134.48 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21206 | 126.27 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.27 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.27 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.27 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3386 | 126.27 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.27 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.27 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.27 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3386 | 126.27 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.27 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 112.15 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 112.15 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29698 | 112.15 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29342 | 112.15 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.15 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 112.15 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29342 | 112.15 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 112.15 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.15 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 112.15 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 138.27 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 138.27 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 138.27 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.27 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.27 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 138.27 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.27 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 138.27 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.27 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 138.27 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 134.46 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 134.46 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 134.46 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.46 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.46 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 134.46 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.46 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 134.46 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.46 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 134.46 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.26 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.26 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.26 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.26 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.26 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.26 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.26 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.26 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.26 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.26 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 112.14 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 112.14 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 112.14 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.14 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.14 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 112.14 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.14 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 112.14 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.14 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 112.14 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20419 | 138.76 | P23:345:MEC:LOUISA 964
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22267 | 138.76 | P23:345:MEC:LOUISA 964
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28975 | 138.76 | P23:345:MEC:LOUISA 964
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28606 | 138.76 | P23:345:MEC:LOUISA 964
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33476 | 138.76 | P23:345:MEC:LOUISA 964
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30757 | 138.76 | P23:345:MEC:LOUISA 964
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28606 | 138.76 | P23:345:MEC:LOUISA 964
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21195 | 138.76 | P23:345:MEC:LOUISA 964
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33476 | 138.76 | P23:345:MEC:LOUISA 964
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28579 | 138.76 | P23:345:MEC:LOUISA 964
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21121 | 112.64 | P23:345:MEC:LOUISA 964
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2297 | 112.64 | P23:345:MEC:LOUISA 964
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29696 | 112.64 | P23:345:MEC:LOUISA 964
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2934 | 112.64 | P23:345:MEC:LOUISA 964
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34171 | 112.64 | P23:345:MEC:LOUISA 964
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31451 | 112.64 | P23:345:MEC:LOUISA 964
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2934 | 112.64 | P23:345:MEC:LOUISA 964
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20499 | 112.64 | P23:345:MEC:LOUISA 964
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34171 | 112.64 | P23:345:MEC:LOUISA 964
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29312 | 112.64 | P23:345:MEC:LOUISA 964
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 138.28 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 138.28 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 138.28 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.28 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.28 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 138.28 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.28 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 138.28 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.28 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 138.28 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.28 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.28 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.28 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.28 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.28 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.28 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.28 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.28 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.28 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.28 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 112.14 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 112.14 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 112.14 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.14 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.14 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 112.14 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.14 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 112.14 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.14 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 112.14 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.83 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.83 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.83 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.83 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.83 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.83 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.83 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.83 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.83 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.83 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 132.95 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 132.95 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 132.95 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.95 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.95 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 132.95 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.95 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 132.95 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.95 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 132.95 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.73 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.73 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.73 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.73 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.73 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.73 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.73 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.73 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.73 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.73 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 110.66 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 110.66 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 110.66 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 110.66 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 110.66 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 110.66 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 110.66 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 110.66 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 110.66 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 110.66 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 138.27 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 138.27 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 138.27 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.27 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.27 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 138.27 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.27 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 138.27 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.27 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 138.27 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 134.45 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 134.45 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 134.45 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.45 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.45 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 134.45 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.45 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 134.45 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.45 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 134.45 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.26 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.26 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.26 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.26 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.26 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.26 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.26 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.26 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.26 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.26 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 112.14 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 112.14 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 112.14 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.14 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.14 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 112.14 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.14 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 112.14 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.14 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 112.14 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 138.27 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 138.27 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 138.27 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.27 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.27 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 138.27 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.27 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 138.27 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.27 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 138.27 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 134.45 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 134.45 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 134.45 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.45 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.45 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 134.45 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.45 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 134.45 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.45 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 134.45 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.26 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.26 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.26 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.26 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.26 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.26 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.26 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.26 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.26 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.26 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 112.14 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 112.14 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 112.14 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.14 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.14 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 112.14 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.14 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 112.14 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.14 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 112.14 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 138.27 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 138.27 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 138.27 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.27 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.27 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 138.27 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.27 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 138.27 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.27 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 138.27 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 134.45 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 134.45 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 134.45 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.45 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.45 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 134.45 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.45 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 134.45 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.45 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 134.45 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.26 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.26 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.26 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.26 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.26 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.26 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.26 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.26 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.26 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.26 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 112.14 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 112.14 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 112.14 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.14 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.14 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 112.14 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.14 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 112.14 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.14 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 112.14 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 138.27 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 138.27 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 138.27 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.27 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.27 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 138.27 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.27 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 138.27 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.27 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 138.27 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 134.45 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 134.45 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 134.45 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.45 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.45 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 134.45 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.45 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 134.45 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.45 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 134.45 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.26 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.26 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.26 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.26 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.26 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.26 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.26 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.26 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.26 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.26 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 112.15 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 112.15 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 112.15 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.15 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.15 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 112.15 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.15 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 112.15 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.15 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 112.15 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21306 | 127.18 | P23:345:SUNC:BU_BRK488
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23042 | 127.18 | P23:345:SUNC:BU_BRK488
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29035 | 127.18 | P23:345:SUNC:BU_BRK488
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28707 | 127.18 | P23:345:SUNC:BU_BRK488
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33926 | 127.18 | P23:345:SUNC:BU_BRK488
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31374 | 127.18 | P23:345:SUNC:BU_BRK488
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28707 | 127.18 | P23:345:SUNC:BU_BRK488
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21899 | 127.18 | P23:345:SUNC:BU_BRK488
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33926 | 127.18 | P23:345:SUNC:BU_BRK488
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28666 | 127.18 | P23:345:SUNC:BU_BRK488
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20522 | 139.23 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22371 | 139.23 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29047 | 139.23 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2868 | 139.23 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33547 | 139.23 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30826 | 139.23 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2868 | 139.23 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21172 | 139.23 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33547 | 139.23 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28653 | 139.23 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21306 | 127.39 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23042 | 127.39 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29035 | 127.39 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28707 | 127.39 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33926 | 127.39 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31374 | 127.39 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28707 | 127.39 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21899 | 127.39 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33926 | 127.39 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28666 | 127.39 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21305 | 127.16 | P23:345:SUNC:HLC_BRK182
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23042 | 127.16 | P23:345:SUNC:HLC_BRK182
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29034 | 127.16 | P23:345:SUNC:HLC_BRK182
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28706 | 127.16 | P23:345:SUNC:HLC_BRK182
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33925 | 127.16 | P23:345:SUNC:HLC_BRK182
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31374 | 127.16 | P23:345:SUNC:HLC_BRK182
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28706 | 127.16 | P23:345:SUNC:HLC_BRK182
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21899 | 127.16 | P23:345:SUNC:HLC_BRK182
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33925 | 127.16 | P23:345:SUNC:HLC_BRK182
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28666 | 127.16 | P23:345:SUNC:HLC_BRK182
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26507 | 165.41 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26145 | 165.41 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31004 | 165.41 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2828 | 165.41 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26145 | 165.41 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23815 | 165.41 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31004 | 165.41 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26117 | 165.41 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20971 | 142.32 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2282 | 142.32 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29434 | 142.32 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29071 | 142.32 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3393 | 142.32 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31206 | 142.32 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29071 | 142.32 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20888 | 142.32 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3393 | 142.32 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29043 | 142.32 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21761 | 129.26 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23498 | 129.26 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29425 | 129.26 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29102 | 129.26 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34314 | 129.26 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3176 | 129.26 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29102 | 129.26 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21614 | 129.26 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34314 | 129.26 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29061 | 129.26 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26525 | 166.16 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26163 | 166.16 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31022 | 166.16 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28298 | 166.16 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26163 | 166.16 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23798 | 166.16 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31022 | 166.16 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26135 | 166.16 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21012 | 142.76 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22862 | 142.76 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29475 | 142.76 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29112 | 142.76 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33972 | 142.76 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31248 | 142.76 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29112 | 142.76 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20848 | 142.76 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33972 | 142.76 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29085 | 142.76 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21049 | 137.33 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22899 | 137.33 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29512 | 137.33 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29149 | 137.33 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34008 | 137.33 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31285 | 137.33 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29149 | 137.33 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20811 | 137.33 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34008 | 137.33 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29122 | 137.33 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21804 | 129.29 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23541 | 129.29 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29468 | 129.29 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29145 | 129.29 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34357 | 129.29 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31803 | 129.29 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29145 | 129.29 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21572 | 129.29 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34357 | 129.29 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29104 | 129.29 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21726 | 117.36 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23577 | 117.36 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30208 | 117.36 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29859 | 117.36 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34678 | 117.36 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31954 | 117.36 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29859 | 117.36 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20139 | 117.36 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34678 | 117.36 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29829 | 117.36 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26266 | 160.38 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25898 | 160.38 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30767 | 160.38 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28047 | 160.38 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25898 | 160.38 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23925 | 160.38 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30767 | 160.38 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25871 | 160.38 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20545 | 139.34 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22393 | 139.34 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29088 | 139.34 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2872 | 139.34 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33589 | 139.34 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30869 | 139.34 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2872 | 139.34 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21103 | 139.34 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33589 | 139.34 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28693 | 139.34 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21249 | 113.29 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23098 | 113.29 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29812 | 113.29 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29457 | 113.29 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34286 | 113.29 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31565 | 113.29 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29457 | 113.29 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20405 | 113.29 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34286 | 113.29 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29428 | 113.29 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26283 | 161 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25915 | 161 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30784 | 161 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28064 | 161 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25915 | 161 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23915 | 161 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30784 | 161 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25888 | 161 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20574 | 139.53 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22422 | 139.53 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29114 | 139.53 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28746 | 139.53 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33614 | 139.53 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30894 | 139.53 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28746 | 139.53 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21084 | 139.53 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33614 | 139.53 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28718 | 139.53 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21278 | 113.51 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23127 | 113.51 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29837 | 113.51 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29482 | 113.51 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34311 | 113.51 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3159 | 113.51 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29482 | 113.51 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20386 | 113.51 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34311 | 113.51 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29454 | 113.51 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26287 | 160.78 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25919 | 160.78 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30788 | 160.78 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28068 | 160.78 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25919 | 160.78 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23911 | 160.78 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30788 | 160.78 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25892 | 160.78 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20585 | 139.47 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22433 | 139.47 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29125 | 139.47 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28757 | 139.47 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33626 | 139.47 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30906 | 139.47 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28757 | 139.47 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21073 | 139.47 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33626 | 139.47 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2873 | 139.47 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21288 | 113.42 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23138 | 113.42 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29848 | 113.42 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29493 | 113.42 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34322 | 113.42 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31601 | 113.42 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29493 | 113.42 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20375 | 113.42 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34322 | 113.42 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29464 | 113.42 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26283 | 160.98 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25915 | 160.98 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30784 | 160.98 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28064 | 160.98 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25915 | 160.98 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23915 | 160.98 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30784 | 160.98 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25888 | 160.98 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20574 | 139.53 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22422 | 139.53 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29114 | 139.53 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28746 | 139.53 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33614 | 139.53 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30894 | 139.53 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28746 | 139.53 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21084 | 139.53 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33614 | 139.53 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28718 | 139.53 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21278 | 113.51 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23127 | 113.51 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29837 | 113.51 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29482 | 113.51 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34311 | 113.51 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3159 | 113.51 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29482 | 113.51 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20386 | 113.51 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34311 | 113.51 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29454 | 113.51 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26287 | 160.82 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25919 | 160.82 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30788 | 160.82 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28068 | 160.82 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25919 | 160.82 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23911 | 160.82 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30788 | 160.82 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25892 | 160.82 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20585 | 139.47 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22433 | 139.47 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29125 | 139.47 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28757 | 139.47 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33626 | 139.47 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30906 | 139.47 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28757 | 139.47 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21073 | 139.47 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33626 | 139.47 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2873 | 139.47 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21288 | 113.42 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23138 | 113.42 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29848 | 113.42 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29493 | 113.42 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34322 | 113.42 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31601 | 113.42 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29493 | 113.42 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20375 | 113.42 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34322 | 113.42 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29464 | 113.42 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26286 | 161.15 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25918 | 161.15 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30787 | 161.15 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28067 | 161.15 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25918 | 161.15 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23913 | 161.15 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30787 | 161.15 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25891 | 161.15 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20581 | 139.63 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22429 | 139.63 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2912 | 139.63 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28752 | 139.63 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3362 | 139.63 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.309 | 139.63 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28752 | 139.63 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21079 | 139.63 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3362 | 139.63 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28725 | 139.63 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26286 | 161.04 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25918 | 161.04 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30787 | 161.04 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28067 | 161.04 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25918 | 161.04 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23913 | 161.04 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30787 | 161.04 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25891 | 161.04 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20581 | 139.62 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22429 | 139.62 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2912 | 139.62 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28752 | 139.62 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3362 | 139.62 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.309 | 139.62 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28752 | 139.62 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21079 | 139.62 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3362 | 139.62 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28725 | 139.62 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26286 | 161.16 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25918 | 161.16 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30787 | 161.16 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28067 | 161.16 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25918 | 161.16 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23913 | 161.16 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30787 | 161.16 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25891 | 161.16 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20581 | 139.64 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22429 | 139.64 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2912 | 139.64 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28752 | 139.64 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3362 | 139.64 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.309 | 139.64 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28752 | 139.64 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21079 | 139.64 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3362 | 139.64 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28725 | 139.64 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2627 | 159.44 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25903 | 159.44 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3077 | 159.44 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28049 | 159.44 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25903 | 159.44 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23949 | 159.44 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3077 | 159.44 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25876 | 159.44 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20522 | 139.53 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2237 | 139.53 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29046 | 139.53 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28679 | 139.53 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33546 | 139.53 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30825 | 139.53 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28679 | 139.53 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21173 | 139.53 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33546 | 139.53 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28652 | 139.53 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21305 | 127.62 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23041 | 127.62 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29034 | 127.62 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28706 | 127.62 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33925 | 127.62 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31374 | 127.62 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28706 | 127.62 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.219 | 127.62 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33925 | 127.62 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28665 | 127.62 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26251 | 159.84 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25882 | 159.84 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30752 | 159.84 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28032 | 159.84 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25882 | 159.84 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23946 | 159.84 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30752 | 159.84 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25855 | 159.84 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20507 | 139.59 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22354 | 139.59 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2905 | 139.59 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28681 | 139.59 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33551 | 139.59 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30831 | 139.59 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28681 | 139.59 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21147 | 139.59 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33551 | 139.59 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28654 | 139.59 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2054 | 135.82 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22387 | 135.82 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29083 | 135.82 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28714 | 135.82 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33584 | 135.82 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30864 | 135.82 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28714 | 135.82 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21114 | 135.82 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33584 | 135.82 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28687 | 135.82 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21295 | 127.75 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23029 | 127.75 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29041 | 127.75 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28711 | 127.75 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33933 | 127.75 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31383 | 127.75 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28711 | 127.75 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2187 | 127.75 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33933 | 127.75 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28671 | 127.75 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2121 | 113.41 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23059 | 113.41 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29773 | 113.41 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29418 | 113.41 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34247 | 113.41 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31527 | 113.41 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29418 | 113.41 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20449 | 113.41 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34247 | 113.41 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29389 | 113.41 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26251 | 159.84 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25882 | 159.84 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30752 | 159.84 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28032 | 159.84 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25882 | 159.84 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23946 | 159.84 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30752 | 159.84 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25855 | 159.84 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20507 | 139.59 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22354 | 139.59 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2905 | 139.59 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28681 | 139.59 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33551 | 139.59 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30831 | 139.59 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28681 | 139.59 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21147 | 139.59 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33551 | 139.59 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28654 | 139.59 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2054 | 135.82 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22387 | 135.82 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29083 | 135.82 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28714 | 135.82 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33584 | 135.82 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30864 | 135.82 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28714 | 135.82 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21114 | 135.82 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33584 | 135.82 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28687 | 135.82 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21295 | 127.75 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23029 | 127.75 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29041 | 127.75 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28711 | 127.75 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33933 | 127.75 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31383 | 127.75 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28711 | 127.75 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2187 | 127.75 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33933 | 127.75 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28671 | 127.75 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2121 | 113.41 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23059 | 113.41 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29773 | 113.41 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29418 | 113.41 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34247 | 113.41 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31527 | 113.41 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29418 | 113.41 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20449 | 113.41 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34247 | 113.41 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29389 | 113.41 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 138.16 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 138.16 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 138.16 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.16 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.16 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 138.16 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.16 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 138.16 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.16 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 138.16 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 134.34 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 134.34 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 134.34 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.34 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.34 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 134.34 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.34 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 134.34 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.34 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 134.34 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.15 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.15 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.15 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.15 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.15 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.15 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.15 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.15 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.15 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.15 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 112.02 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 112.02 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 112.02 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.02 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.02 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 112.02 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.02 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 112.02 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.02 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 112.02 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 138.16 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 138.16 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 138.16 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.16 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.16 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 138.16 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.16 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 138.16 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.16 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 138.16 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 134.34 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 134.34 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 134.34 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.34 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.34 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 134.34 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.34 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 134.34 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.34 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 134.34 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.15 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.15 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.15 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.15 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.15 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.15 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.15 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.15 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.15 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.15 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 112.03 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 112.03 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 112.03 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.03 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.03 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 112.03 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.03 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 112.03 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.03 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 112.03 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20423 | 138.16 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2227 | 138.16 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28978 | 138.16 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28609 | 138.16 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3348 | 138.16 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3076 | 138.16 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28609 | 138.16 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 138.16 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3348 | 138.16 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28582 | 138.16 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2046 | 134.34 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22307 | 134.34 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29015 | 134.34 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28646 | 134.34 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33517 | 134.34 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30797 | 134.34 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28646 | 134.34 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21154 | 134.34 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33517 | 134.34 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28619 | 134.34 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21208 | 126.15 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22943 | 126.15 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28969 | 126.15 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28639 | 126.15 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33862 | 126.15 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31312 | 126.15 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28639 | 126.15 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21912 | 126.15 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33862 | 126.15 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28599 | 126.15 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21124 | 112.03 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22973 | 112.03 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.297 | 112.03 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29344 | 112.03 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34174 | 112.03 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31454 | 112.03 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29344 | 112.03 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20495 | 112.03 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34174 | 112.03 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29315 | 112.03 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21249 | 127.24 | P23:345:WERE:WICH_345-50::
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22983 | 127.24 | P23:345:WERE:WICH_345-50::
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28999 | 127.24 | P23:345:WERE:WICH_345-50::
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2867 | 127.24 | P23:345:WERE:WICH_345-50::
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33892 | 127.24 | P23:345:WERE:WICH_345-50::
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31342 | 127.24 | P23:345:WERE:WICH_345-50::
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2867 | 127.24 | P23:345:WERE:WICH_345-50::
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21903 | 127.24 | P23:345:WERE:WICH_345-50::
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33892 | 127.24 | P23:345:WERE:WICH_345-50::
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2863 | 127.24 | P23:345:WERE:WICH_345-50::
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26203 | 158.43 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25834 | 158.43 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 158.43 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27985 | 158.43 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25834 | 158.43 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23967 | 158.43 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 158.43 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25807 | 158.43 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2046 | 134.69 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22307 | 134.69 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29015 | 134.69 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28646 | 134.69 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33517 | 134.69 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30798 | 134.69 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28646 | 134.69 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21154 | 134.69 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33517 | 134.69 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28619 | 134.69 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21208 | 126.5 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22943 | 126.5 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2897 | 126.5 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28639 | 126.5 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33862 | 126.5 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31312 | 126.5 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28639 | 126.5 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21912 | 126.5 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33862 | 126.5 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28599 | 126.5 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26202 | 158.37 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 158.37 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 158.37 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27985 | 158.37 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 158.37 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23968 | 158.37 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 158.37 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25806 | 158.37 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20459 | 134.74 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 134.74 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 134.74 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.74 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.74 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 134.74 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 134.74 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 134.74 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 134.74 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 134.74 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.55 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.55 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.55 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.55 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.55 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.55 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.55 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.55 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.55 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.55 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 138.28 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 138.28 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 138.28 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.28 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.28 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 138.28 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.28 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 138.28 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.28 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 138.28 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21206 | 126.28 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.28 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.28 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.28 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.28 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.28 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.28 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.28 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.28 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.28 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26202 | 157.32 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 157.32 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 157.32 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27985 | 157.32 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 157.32 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23967 | 157.32 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 157.32 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25806 | 157.32 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 137.28 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 137.28 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 137.28 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 137.28 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 137.28 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 137.28 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 137.28 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 137.28 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 137.28 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 137.28 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21206 | 125.19 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 125.19 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 125.19 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 125.19 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3386 | 125.19 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 125.19 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 125.19 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 125.19 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3386 | 125.19 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 125.19 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26202 | 158.06 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 158.06 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 158.06 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27985 | 158.06 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 158.06 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23967 | 158.06 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 158.06 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25806 | 158.06 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 138.27 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 138.27 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 138.27 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.27 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.27 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 138.27 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.27 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 138.27 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.27 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 138.27 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21206 | 126.27 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.27 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.27 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.27 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.27 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.27 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.27 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.27 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.27 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.27 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26202 | 158.13 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 158.13 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 158.13 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27984 | 158.13 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 158.13 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23967 | 158.13 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 158.13 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25806 | 158.13 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 138.26 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 138.26 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 138.26 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.26 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.26 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 138.26 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 138.26 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 138.26 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 138.26 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 138.26 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21206 | 126.26 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.26 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.26 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.26 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3386 | 126.26 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.26 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.26 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.26 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3386 | 126.26 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.26 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21097 | 113.14 | P23:500:EES-EAI:ARK_NU:B5106
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22947 | 113.14 | P23:500:EES-EAI:ARK_NU:B5106
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29671 | 113.14 | P23:500:EES-EAI:ARK_NU:B5106
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29315 | 113.14 | P23:500:EES-EAI:ARK_NU:B5106
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34145 | 113.14 | P23:500:EES-EAI:ARK_NU:B5106
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31425 | 113.14 | P23:500:EES-EAI:ARK_NU:B5106
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29315 | 113.14 | P23:500:EES-EAI:ARK_NU:B5106
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20529 | 113.14 | P23:500:EES-EAI:ARK_NU:B5106
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34145 | 113.14 | P23:500:EES-EAI:ARK_NU:B5106
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29286 | 113.14 | P23:500:EES-EAI:ARK_NU:B5106
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20409 | 137.06 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22257 | 137.06 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28963 | 137.06 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28594 | 137.06 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33465 | 137.06 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30746 | 137.06 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28594 | 137.06 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21209 | 137.06 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33465 | 137.06 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28567 | 137.06 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20444 | 133.51 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22292 | 133.51 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28998 | 133.51 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28629 | 133.51 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.335 | 133.51 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3078 | 133.51 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28629 | 133.51 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21174 | 133.51 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.335 | 133.51 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28602 | 133.51 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 125.22 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22928 | 125.22 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28952 | 125.22 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28622 | 125.22 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33845 | 125.22 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31295 | 125.22 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28622 | 125.22 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21932 | 125.22 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33845 | 125.22 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28582 | 125.22 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21111 | 111 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2296 | 111 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29685 | 111 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29329 | 111 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34159 | 111 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31439 | 111 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29329 | 111 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20513 | 111 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34159 | 111 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29301 | 111 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20409 | 136.96 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22256 | 136.96 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28963 | 136.96 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28594 | 136.96 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33464 | 136.96 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30745 | 136.96 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28594 | 136.96 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2121 | 136.96 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33464 | 136.96 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28567 | 136.96 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20443 | 133.41 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22291 | 133.41 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28997 | 133.41 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28628 | 133.41 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33499 | 133.41 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30779 | 133.41 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28628 | 133.41 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21175 | 133.41 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33499 | 133.41 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28601 | 133.41 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21191 | 125.12 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22927 | 125.12 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28951 | 125.12 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28621 | 125.12 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33844 | 125.12 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31294 | 125.12 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28621 | 125.12 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21934 | 125.12 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33844 | 125.12 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 125.12 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2111 | 110.92 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22959 | 110.92 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29684 | 110.92 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29328 | 110.92 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34158 | 110.92 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31439 | 110.92 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29328 | 110.92 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20514 | 110.92 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34158 | 110.92 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.293 | 110.92 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.57 | P41:345:OKGE:SB_MUGE7384
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.57 | P41:345:OKGE:SB_MUGE7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.57 | P41:345:OKGE:SB_MUGE7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.57 | P41:345:OKGE:SB_MUGE7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.57 | P41:345:OKGE:SB_MUGE7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.57 | P41:345:OKGE:SB_MUGE7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.57 | P41:345:OKGE:SB_MUGE7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.57 | P41:345:OKGE:SB_MUGE7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.57 | P41:345:OKGE:SB_MUGE7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.57 | P41:345:OKGE:SB_MUGE7384
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20393 | 136.21 | P41:345:OKGE:SB_MUGE7385
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2224 | 136.21 | P41:345:OKGE:SB_MUGE7385
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28946 | 136.21 | P41:345:OKGE:SB_MUGE7385
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28577 | 136.21 | P41:345:OKGE:SB_MUGE7385
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33447 | 136.21 | P41:345:OKGE:SB_MUGE7385
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30728 | 136.21 | P41:345:OKGE:SB_MUGE7385
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28577 | 136.21 | P41:345:OKGE:SB_MUGE7385
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21229 | 136.21 | P41:345:OKGE:SB_MUGE7385
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33447 | 136.21 | P41:345:OKGE:SB_MUGE7385
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2855 | 136.21 | P41:345:OKGE:SB_MUGE7385
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21104 | 112.36 | P41:345:OKGE:SB_SEOL7382
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2295 | 112.36 | P41:345:OKGE:SB_SEOL7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29656 | 112.36 | P41:345:OKGE:SB_SEOL7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29301 | 112.36 | P41:345:OKGE:SB_SEOL7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3413 | 112.36 | P41:345:OKGE:SB_SEOL7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3141 | 112.36 | P41:345:OKGE:SB_SEOL7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29301 | 112.36 | P41:345:OKGE:SB_SEOL7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20591 | 112.36 | P41:345:OKGE:SB_SEOL7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3413 | 112.36 | P41:345:OKGE:SB_SEOL7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29272 | 112.36 | P41:345:OKGE:SB_SEOL7382
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21087 | 112.04 | P41:345:OKGE:SB_SEOL7383
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22931 | 112.04 | P41:345:OKGE:SB_SEOL7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29619 | 112.04 | P41:345:OKGE:SB_SEOL7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29265 | 112.04 | P41:345:OKGE:SB_SEOL7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34092 | 112.04 | P41:345:OKGE:SB_SEOL7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31373 | 112.04 | P41:345:OKGE:SB_SEOL7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29265 | 112.04 | P41:345:OKGE:SB_SEOL7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20672 | 112.04 | P41:345:OKGE:SB_SEOL7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34092 | 112.04 | P41:345:OKGE:SB_SEOL7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29236 | 112.04 | P41:345:OKGE:SB_SEOL7383
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20406 | 137.12 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22254 | 137.12 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2896 | 137.12 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28591 | 137.12 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33461 | 137.12 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30742 | 137.12 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28591 | 137.12 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21215 | 137.12 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33461 | 137.12 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28564 | 137.12 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20441 | 133.43 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22288 | 133.43 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28994 | 133.43 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28625 | 133.43 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33495 | 133.43 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30776 | 133.43 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28625 | 133.43 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2118 | 133.43 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33495 | 133.43 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 133.43 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21188 | 125.22 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22924 | 125.22 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28947 | 125.22 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28617 | 125.22 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3384 | 125.22 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3129 | 125.22 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28617 | 125.22 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21939 | 125.22 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3384 | 125.22 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28577 | 125.22 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21106 | 111 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22955 | 111 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2968 | 111 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29324 | 111 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34154 | 111 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31434 | 111 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29324 | 111 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2052 | 111 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34154 | 111 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29295 | 111 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20406 | 137.11 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22254 | 137.11 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2896 | 137.11 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28591 | 137.11 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33461 | 137.11 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30742 | 137.11 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28591 | 137.11 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21215 | 137.11 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33461 | 137.11 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28564 | 137.11 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20441 | 133.41 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22288 | 133.41 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28994 | 133.41 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28625 | 133.41 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33495 | 133.41 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30776 | 133.41 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28625 | 133.41 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2118 | 133.41 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33495 | 133.41 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 133.41 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21188 | 125.2 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22924 | 125.2 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28947 | 125.2 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28617 | 125.2 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3384 | 125.2 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3129 | 125.2 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28617 | 125.2 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21939 | 125.2 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3384 | 125.2 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28577 | 125.2 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21106 | 110.97 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22955 | 110.97 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2968 | 110.97 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29324 | 110.97 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34154 | 110.97 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31434 | 110.97 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29324 | 110.97 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2052 | 110.97 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34154 | 110.97 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29295 | 110.97 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20396 | 137.37 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22243 | 137.37 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28947 | 137.37 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28578 | 137.37 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33448 | 137.37 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30729 | 137.37 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28578 | 137.37 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21233 | 137.37 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33448 | 137.37 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28551 | 137.37 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20396 | 137.37 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22243 | 137.37 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28947 | 137.37 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28578 | 137.37 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33448 | 137.37 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30729 | 137.37 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28578 | 137.37 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21233 | 137.37 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33448 | 137.37 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28551 | 137.37 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20396 | 137.37 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22243 | 137.37 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28947 | 137.37 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28578 | 137.37 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33448 | 137.37 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30729 | 137.37 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28578 | 137.37 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21233 | 137.37 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33448 | 137.37 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28551 | 137.37 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26439 | 167.63 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26073 | 167.63 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3094 | 167.63 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28228 | 167.63 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26073 | 167.63 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23988 | 167.63 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3094 | 167.63 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26045 | 167.63 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20912 | 143.7 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22735 | 143.7 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29377 | 143.7 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29011 | 143.7 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33878 | 143.7 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31166 | 143.7 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29011 | 143.7 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2105 | 143.7 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33878 | 143.7 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28983 | 143.7 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20931 | 141.8 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22754 | 141.8 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29396 | 141.8 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2903 | 141.8 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33897 | 141.8 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31185 | 141.8 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2903 | 141.8 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21031 | 141.8 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33897 | 141.8 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29002 | 141.8 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21741 | 134.31 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23443 | 134.31 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2937 | 134.31 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29045 | 134.31 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3427 | 134.31 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31721 | 134.31 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29045 | 134.31 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.218 | 134.31 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3427 | 134.31 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29004 | 134.31 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21633 | 116.94 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23458 | 116.94 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30118 | 116.94 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29765 | 116.94 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34592 | 116.94 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3188 | 116.94 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29765 | 116.94 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20334 | 116.94 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34592 | 116.94 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29736 | 116.94 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20225 | 204.34 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21856 | 204.34 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28464 | 204.34 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28087 | 204.34 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32989 | 204.34 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30372 | 204.34 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28087 | 204.34 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23325 | 204.34 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32989 | 204.34 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28061 | 204.34 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23732 | 189.99 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25363 | 189.99 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31971 | 189.99 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31594 | 189.99 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36496 | 189.99 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-033 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21388 | 189.99 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33878 | 189.99 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-065 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21388 | 189.99 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31594 | 189.99 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36496 | 189.99 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31568 | 189.99 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23717 | 183.06 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25348 | 183.06 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31956 | 183.06 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31579 | 183.06 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36481 | 183.06 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21374 | 183.06 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33864 | 183.06 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21374 | 183.06 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31579 | 183.06 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36481 | 183.06 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31553 | 183.06 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24943 | 178.43 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26375 | 178.43 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32051 | 178.43 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31723 | 178.43 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3704 | 178.43 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24031 | 178.43 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34516 | 178.43 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24031 | 178.43 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31723 | 178.43 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20684 | 178.43 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3704 | 178.43 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31681 | 178.43 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24539 | 154.07 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26172 | 154.07 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32801 | 154.07 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32438 | 154.07 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.37295 | 154.07 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22188 | 154.07 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34677 | 154.07 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22188 | 154.07 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32438 | 154.07 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.37295 | 154.07 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3241 | 154.07 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20397 | 137.32 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22244 | 137.32 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28948 | 137.32 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28579 | 137.32 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33449 | 137.32 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3073 | 137.32 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28579 | 137.32 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21231 | 137.32 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33449 | 137.32 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28552 | 137.32 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20168 | 177.5 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21802 | 177.5 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28441 | 177.5 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28062 | 177.5 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32967 | 177.5 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3035 | 177.5 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28062 | 177.5 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23285 | 177.5 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32967 | 177.5 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28036 | 177.5 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23622 | 156.91 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25255 | 156.91 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31894 | 156.91 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31515 | 156.91 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36421 | 156.91 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33804 | 156.91 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31515 | 156.91 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36421 | 156.91 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31489 | 156.91 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23614 | 150.42 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25248 | 150.42 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31887 | 150.42 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31508 | 150.42 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36413 | 150.42 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33796 | 150.42 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31508 | 150.42 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36413 | 150.42 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31482 | 150.42 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24826 | 143.06 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26262 | 143.06 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31975 | 143.06 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31644 | 143.06 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36965 | 143.06 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34442 | 143.06 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31644 | 143.06 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2069 | 143.06 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36965 | 143.06 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31603 | 143.06 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24423 | 122.69 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26059 | 122.69 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32719 | 122.69 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32354 | 122.69 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.37215 | 122.69 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34597 | 122.69 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32354 | 122.69 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.37215 | 122.69 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32327 | 122.69 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20168 | 176.8 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21802 | 176.8 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28441 | 176.8 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28062 | 176.8 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32967 | 176.8 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3035 | 176.8 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28062 | 176.8 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23285 | 176.8 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32967 | 176.8 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28036 | 176.8 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23622 | 156.43 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25255 | 156.43 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31894 | 156.43 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31515 | 156.43 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36421 | 156.43 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33804 | 156.43 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31515 | 156.43 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36421 | 156.43 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31489 | 156.43 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23614 | 149.89 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25248 | 149.89 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31887 | 149.89 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31508 | 149.89 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36413 | 149.89 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33796 | 149.89 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31508 | 149.89 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36413 | 149.89 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31482 | 149.89 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24826 | 142.76 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26262 | 142.76 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31975 | 142.76 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31644 | 142.76 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36965 | 142.76 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34442 | 142.76 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31644 | 142.76 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2069 | 142.76 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36965 | 142.76 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31603 | 142.76 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24423 | 122.11 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26059 | 122.11 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32719 | 122.11 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32354 | 122.11 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.37215 | 122.11 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34597 | 122.11 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32354 | 122.11 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.37215 | 122.11 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32327 | 122.11 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26076 | 154.75 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25708 | 154.75 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30577 | 154.75 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27857 | 154.75 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25708 | 154.75 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24137 | 154.75 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30577 | 154.75 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25681 | 154.75 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20231 | 136.84 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22076 | 136.84 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28766 | 136.84 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28398 | 136.84 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33267 | 136.84 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30548 | 136.84 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28398 | 136.84 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21447 | 136.84 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33267 | 136.84 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28371 | 136.84 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20274 | 131.77 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2212 | 131.77 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28809 | 131.77 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28441 | 131.77 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3331 | 131.77 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30591 | 131.77 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28441 | 131.77 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21404 | 131.77 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3331 | 131.77 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28414 | 131.77 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21013 | 123.48 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22746 | 123.48 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2875 | 123.48 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28421 | 123.48 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33643 | 123.48 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31092 | 123.48 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28421 | 123.48 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22178 | 123.48 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33643 | 123.48 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28381 | 123.48 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20933 | 110.69 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2278 | 110.69 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29488 | 110.69 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29133 | 110.69 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33961 | 110.69 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31242 | 110.69 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29133 | 110.69 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2075 | 110.69 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33961 | 110.69 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29104 | 110.69 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26147 | 155.95 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2578 | 155.95 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30647 | 155.95 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2793 | 155.95 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2578 | 155.95 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24146 | 155.95 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30647 | 155.95 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25752 | 155.95 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20357 | 136.49 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22195 | 136.49 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28863 | 136.49 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28496 | 136.49 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33364 | 136.49 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30647 | 136.49 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28496 | 136.49 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2143 | 136.49 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33364 | 136.49 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28469 | 136.49 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2038 | 132.26 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22218 | 132.26 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28886 | 132.26 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28519 | 132.26 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33387 | 132.26 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3067 | 132.26 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28519 | 132.26 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21407 | 132.26 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33387 | 132.26 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28492 | 132.26 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21132 | 123.8 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22855 | 123.8 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28828 | 123.8 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.285 | 123.8 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33722 | 123.8 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31172 | 123.8 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.285 | 123.8 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22189 | 123.8 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33722 | 123.8 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2846 | 123.8 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21051 | 110.68 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22891 | 110.68 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29577 | 110.68 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29223 | 110.68 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34051 | 110.68 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31333 | 110.68 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29223 | 110.68 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20741 | 110.68 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34051 | 110.68 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29195 | 110.68 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25992 | 152.1 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25626 | 152.1 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30491 | 152.1 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27774 | 152.1 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25626 | 152.1 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24367 | 152.1 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30491 | 152.1 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25599 | 152.1 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20156 | 134.73 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21991 | 134.73 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28632 | 134.73 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28266 | 134.73 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33131 | 134.73 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30414 | 134.73 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28266 | 134.73 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21727 | 134.73 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33131 | 134.73 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28239 | 134.73 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20192 | 129.49 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22027 | 129.49 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28667 | 129.49 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28302 | 129.49 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33167 | 129.49 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3045 | 129.49 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28302 | 129.49 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21691 | 129.49 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33167 | 129.49 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28275 | 129.49 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20933 | 120.97 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22651 | 120.97 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28591 | 120.97 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28266 | 120.97 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33486 | 120.97 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30935 | 120.97 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28266 | 120.97 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22495 | 120.97 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33486 | 120.97 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28225 | 120.97 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20858 | 108.54 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22695 | 108.54 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29354 | 108.54 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29002 | 108.54 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33826 | 108.54 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31109 | 108.54 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29002 | 108.54 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2103 | 108.54 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33826 | 108.54 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28973 | 108.54 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25967 | 152.04 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25601 | 152.04 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30467 | 152.04 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27749 | 152.04 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25601 | 152.04 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24369 | 152.04 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30467 | 152.04 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25574 | 152.04 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20125 | 134.93 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21962 | 134.93 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 134.93 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28242 | 134.93 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33108 | 134.93 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3039 | 134.93 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28242 | 134.93 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21728 | 134.93 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33108 | 134.93 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28215 | 134.93 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20169 | 129.7 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22006 | 129.7 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28652 | 129.7 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28287 | 129.7 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33152 | 129.7 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30435 | 129.7 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28287 | 129.7 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21684 | 129.7 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33152 | 129.7 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28259 | 129.7 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20906 | 121.17 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22627 | 121.17 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28576 | 121.17 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2825 | 121.17 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3347 | 121.17 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30919 | 121.17 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2825 | 121.17 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22486 | 121.17 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3347 | 121.17 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28209 | 121.17 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20832 | 108.5 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22671 | 108.5 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29336 | 108.5 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28983 | 108.5 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33808 | 108.5 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31091 | 108.5 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28983 | 108.5 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21026 | 108.5 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33808 | 108.5 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28954 | 108.5 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26431 | 167.33 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26065 | 167.33 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30932 | 167.33 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2822 | 167.33 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26065 | 167.33 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2399 | 167.33 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30932 | 167.33 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26037 | 167.33 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20899 | 143.45 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22724 | 143.45 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29365 | 143.45 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28999 | 143.45 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33866 | 143.45 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31154 | 143.45 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28999 | 143.45 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21055 | 143.45 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33866 | 143.45 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28972 | 143.45 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20918 | 141.67 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22742 | 141.67 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29384 | 141.67 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29018 | 141.67 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33885 | 141.67 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31173 | 141.67 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29018 | 141.67 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21036 | 141.67 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33885 | 141.67 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28991 | 141.67 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21728 | 134.19 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23431 | 134.19 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29359 | 134.19 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29034 | 134.19 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34259 | 134.19 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31709 | 134.19 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29034 | 134.19 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21805 | 134.19 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34259 | 134.19 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28993 | 134.19 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2162 | 116.82 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23446 | 116.82 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30106 | 116.82 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29753 | 116.82 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3458 | 116.82 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31867 | 116.82 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29753 | 116.82 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2034 | 116.82 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3458 | 116.82 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29724 | 116.82 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26431 | 167.34 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26065 | 167.34 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30932 | 167.34 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2822 | 167.34 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26065 | 167.34 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2399 | 167.34 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30932 | 167.34 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26037 | 167.34 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20899 | 143.46 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22724 | 143.46 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29365 | 143.46 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28999 | 143.46 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33866 | 143.46 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31154 | 143.46 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28999 | 143.46 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21055 | 143.46 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33866 | 143.46 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28972 | 143.46 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20918 | 141.67 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22742 | 141.67 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29384 | 141.67 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29018 | 141.67 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33885 | 141.67 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31173 | 141.67 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29018 | 141.67 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21036 | 141.67 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33885 | 141.67 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28991 | 141.67 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21728 | 134.2 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23431 | 134.2 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29359 | 134.2 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29034 | 134.2 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34259 | 134.2 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31709 | 134.2 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29034 | 134.2 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21805 | 134.2 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34259 | 134.2 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28993 | 134.2 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2162 | 116.82 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23446 | 116.82 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30106 | 116.82 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29753 | 116.82 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3458 | 116.82 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31867 | 116.82 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29753 | 116.82 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2034 | 116.82 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3458 | 116.82 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29724 | 116.82 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26431 | 167.21 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26065 | 167.21 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30932 | 167.21 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2822 | 167.21 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26065 | 167.21 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2399 | 167.21 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30932 | 167.21 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26037 | 167.21 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20899 | 143.41 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22724 | 143.41 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29365 | 143.41 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28999 | 143.41 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33866 | 143.41 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31154 | 143.41 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28999 | 143.41 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21055 | 143.41 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33866 | 143.41 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28972 | 143.41 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20918 | 141.6 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22742 | 141.6 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29384 | 141.6 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29018 | 141.6 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33885 | 141.6 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31173 | 141.6 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29018 | 141.6 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21036 | 141.6 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33885 | 141.6 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28991 | 141.6 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21728 | 134.15 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23431 | 134.15 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29359 | 134.15 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29034 | 134.15 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34259 | 134.15 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31709 | 134.15 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29034 | 134.15 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21805 | 134.15 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34259 | 134.15 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28993 | 134.15 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2162 | 116.79 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23446 | 116.79 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30106 | 116.79 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29753 | 116.79 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3458 | 116.79 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31867 | 116.79 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29753 | 116.79 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2034 | 116.79 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3458 | 116.79 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29724 | 116.79 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26143 | 156.03 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25775 | 156.03 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30644 | 156.03 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27925 | 156.03 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25775 | 156.03 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24054 | 156.03 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30644 | 156.03 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25748 | 156.03 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20322 | 137.37 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22167 | 137.37 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28865 | 137.37 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28496 | 137.37 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33366 | 137.37 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30647 | 137.37 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28496 | 137.37 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21333 | 137.37 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33366 | 137.37 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28469 | 137.37 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20357 | 132.69 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22203 | 132.69 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.289 | 132.69 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28532 | 132.69 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33402 | 132.69 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30682 | 132.69 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28532 | 132.69 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21297 | 132.69 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33402 | 132.69 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28505 | 132.69 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.211 | 124.4 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22833 | 124.4 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28847 | 124.4 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28517 | 124.4 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33739 | 124.4 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31189 | 124.4 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28517 | 124.4 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22065 | 124.4 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33739 | 124.4 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28477 | 124.4 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26138 | 155.84 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2577 | 155.84 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30639 | 155.84 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2792 | 155.84 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2577 | 155.84 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2406 | 155.84 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30639 | 155.84 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25742 | 155.84 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20313 | 137.32 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22159 | 137.32 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28856 | 137.32 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28487 | 137.32 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33357 | 137.32 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30638 | 137.32 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28487 | 137.32 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21342 | 137.32 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33357 | 137.32 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2846 | 137.32 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20349 | 132.62 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22195 | 132.62 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28892 | 132.62 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28524 | 132.62 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33393 | 132.62 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30674 | 132.62 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28524 | 132.62 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21306 | 132.62 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33393 | 132.62 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28496 | 132.62 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21092 | 124.24 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22825 | 124.24 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28838 | 124.24 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28509 | 124.24 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33731 | 124.24 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31181 | 124.24 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28509 | 124.24 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22074 | 124.24 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33731 | 124.24 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28469 | 124.24 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26191 | 159.18 | P42:345:GRDA:CLEVLND CB13280
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25822 | 159.18 | P42:345:GRDA:CLEVLND CB13280
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30693 | 159.18 | P42:345:GRDA:CLEVLND CB13280
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27973 | 159.18 | P42:345:GRDA:CLEVLND CB13280
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25822 | 159.18 | P42:345:GRDA:CLEVLND CB13280
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23982 | 159.18 | P42:345:GRDA:CLEVLND CB13280
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30693 | 159.18 | P42:345:GRDA:CLEVLND CB13280
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25795 | 159.18 | P42:345:GRDA:CLEVLND CB13280
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 137.73 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 137.73 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 137.73 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 137.73 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 137.73 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3076 | 137.73 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 137.73 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 137.73 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 137.73 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 137.73 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20459 | 133.89 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 133.89 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 133.89 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 133.89 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 133.89 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 133.89 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 133.89 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21155 | 133.89 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 133.89 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 133.89 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 125.62 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 125.62 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28969 | 125.62 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 125.62 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 125.62 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 125.62 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 125.62 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21913 | 125.62 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 125.62 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 125.62 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 111.56 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.56 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 111.56 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.56 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.56 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31454 | 111.56 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.56 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 111.56 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.56 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 111.56 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26293 | 161.01 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25925 | 161.01 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30794 | 161.01 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28074 | 161.01 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25925 | 161.01 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23906 | 161.01 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30794 | 161.01 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25898 | 161.01 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20597 | 139.59 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22445 | 139.59 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29136 | 139.59 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28768 | 139.59 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33637 | 139.59 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30917 | 139.59 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28768 | 139.59 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21063 | 139.59 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33637 | 139.59 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28741 | 139.59 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21301 | 113.54 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2315 | 113.54 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29859 | 113.54 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29505 | 113.54 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34333 | 113.54 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31613 | 113.54 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29505 | 113.54 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20364 | 113.54 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34333 | 113.54 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29476 | 113.54 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21226 | 127.13 | P42:345:NPPD:BKR-SW-3308
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22962 | 127.13 | P42:345:NPPD:BKR-SW-3308
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28985 | 127.13 | P42:345:NPPD:BKR-SW-3308
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28655 | 127.13 | P42:345:NPPD:BKR-SW-3308
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33877 | 127.13 | P42:345:NPPD:BKR-SW-3308
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31328 | 127.13 | P42:345:NPPD:BKR-SW-3308
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28655 | 127.13 | P42:345:NPPD:BKR-SW-3308
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21902 | 127.13 | P42:345:NPPD:BKR-SW-3308
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33877 | 127.13 | P42:345:NPPD:BKR-SW-3308
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28615 | 127.13 | P42:345:NPPD:BKR-SW-3308
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20875 | 110.76 | P42:345:OKGE:SB_ARIA7381
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22712 | 110.76 | P42:345:OKGE:SB_ARIA7381
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29338 | 110.76 | P42:345:OKGE:SB_ARIA7381
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28988 | 110.76 | P42:345:OKGE:SB_ARIA7381
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33809 | 110.76 | P42:345:OKGE:SB_ARIA7381
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31091 | 110.76 | P42:345:OKGE:SB_ARIA7381
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28988 | 110.76 | P42:345:OKGE:SB_ARIA7381
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21098 | 110.76 | P42:345:OKGE:SB_ARIA7381
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33809 | 110.76 | P42:345:OKGE:SB_ARIA7381
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28959 | 110.76 | P42:345:OKGE:SB_ARIA7381
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26265 | 159.32 | P42:345:OKGE:SB_ARIA7382
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25897 | 159.32 | P42:345:OKGE:SB_ARIA7382
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30766 | 159.32 | P42:345:OKGE:SB_ARIA7382
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28047 | 159.32 | P42:345:OKGE:SB_ARIA7382
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25897 | 159.32 | P42:345:OKGE:SB_ARIA7382
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23945 | 159.32 | P42:345:OKGE:SB_ARIA7382
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30766 | 159.32 | P42:345:OKGE:SB_ARIA7382
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2587 | 159.32 | P42:345:OKGE:SB_ARIA7382
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21076 | 184.33 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27105 | 184.33 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26786 | 184.33 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31568 | 184.33 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28803 | 184.33 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26786 | 184.33 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23978 | 184.33 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31568 | 184.33 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26752 | 184.33 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22342 | 154.35 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24232 | 154.35 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30262 | 154.35 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29943 | 154.35 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34725 | 154.35 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3196 | 154.35 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29943 | 154.35 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2082 | 154.35 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34725 | 154.35 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29909 | 154.35 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22317 | 153.03 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24207 | 153.03 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30237 | 153.03 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29918 | 153.03 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.347 | 153.03 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31935 | 153.03 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29918 | 153.03 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20846 | 153.03 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.347 | 153.03 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29884 | 153.03 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23102 | 146.01 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24885 | 146.01 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30232 | 146.01 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29951 | 146.01 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35086 | 146.01 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32503 | 146.01 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29951 | 146.01 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21588 | 146.01 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35086 | 146.01 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29904 | 146.01 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23094 | 124.96 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24986 | 124.96 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31032 | 124.96 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30724 | 124.96 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35471 | 124.96 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32706 | 124.96 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30724 | 124.96 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20072 | 124.96 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35471 | 124.96 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30688 | 124.96 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26249 | 159.15 | P42:345:OKGE:SB_BAER7318
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25882 | 159.15 | P42:345:OKGE:SB_BAER7318
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30749 | 159.15 | P42:345:OKGE:SB_BAER7318
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28027 | 159.15 | P42:345:OKGE:SB_BAER7318
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25882 | 159.15 | P42:345:OKGE:SB_BAER7318
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23968 | 159.15 | P42:345:OKGE:SB_BAER7318
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30749 | 159.15 | P42:345:OKGE:SB_BAER7318
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25855 | 159.15 | P42:345:OKGE:SB_BAER7318
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26249 | 159.19 | P42:345:OKGE:SB_BAER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25883 | 159.19 | P42:345:OKGE:SB_BAER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30749 | 159.19 | P42:345:OKGE:SB_BAER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28027 | 159.19 | P42:345:OKGE:SB_BAER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25883 | 159.19 | P42:345:OKGE:SB_BAER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23968 | 159.19 | P42:345:OKGE:SB_BAER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30749 | 159.19 | P42:345:OKGE:SB_BAER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25855 | 159.19 | P42:345:OKGE:SB_BAER7384
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2101 | 172.33 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2778 | 172.33 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27396 | 172.33 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32304 | 172.33 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29658 | 172.33 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27396 | 172.33 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23261 | 172.33 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32304 | 172.33 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27371 | 172.33 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22506 | 154.45 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24206 | 154.45 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30976 | 154.45 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30592 | 154.45 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35499 | 154.45 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32854 | 154.45 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30592 | 154.45 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20066 | 154.45 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35499 | 154.45 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30567 | 154.45 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22519 | 148.16 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24218 | 148.16 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30988 | 148.16 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30604 | 148.16 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35511 | 148.16 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32866 | 148.16 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30604 | 148.16 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20053 | 148.16 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35511 | 148.16 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30579 | 148.16 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23579 | 140.71 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25108 | 140.71 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31046 | 140.71 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30707 | 140.71 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36009 | 140.71 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33482 | 140.71 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30707 | 140.71 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20842 | 140.71 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36009 | 140.71 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30667 | 140.71 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23262 | 123.9 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24963 | 123.9 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31753 | 123.9 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31384 | 123.9 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36247 | 123.9 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33601 | 123.9 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31384 | 123.9 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36247 | 123.9 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31357 | 123.9 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2101 | 172.23 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2778 | 172.23 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27396 | 172.23 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32304 | 172.23 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29658 | 172.23 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27396 | 172.23 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23261 | 172.23 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32304 | 172.23 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27371 | 172.23 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22506 | 154.44 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24206 | 154.44 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30976 | 154.44 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30592 | 154.44 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35499 | 154.44 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32854 | 154.44 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30592 | 154.44 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20066 | 154.44 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35499 | 154.44 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30567 | 154.44 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22519 | 148.11 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24218 | 148.11 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30988 | 148.11 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30604 | 148.11 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35511 | 148.11 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32866 | 148.11 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30604 | 148.11 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20053 | 148.11 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35511 | 148.11 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30579 | 148.11 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23579 | 140.69 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25108 | 140.69 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31046 | 140.69 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30707 | 140.69 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36009 | 140.69 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33482 | 140.69 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30707 | 140.69 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20842 | 140.69 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36009 | 140.69 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30667 | 140.69 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23262 | 123.87 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24963 | 123.87 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31753 | 123.87 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31384 | 123.87 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36247 | 123.87 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33601 | 123.87 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31384 | 123.87 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36247 | 123.87 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31357 | 123.87 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2101 | 172.28 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2778 | 172.28 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27396 | 172.28 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32304 | 172.28 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29658 | 172.28 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27396 | 172.28 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23261 | 172.28 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32304 | 172.28 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27371 | 172.28 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22506 | 154.47 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24206 | 154.47 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30976 | 154.47 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30592 | 154.47 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35499 | 154.47 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32854 | 154.47 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30592 | 154.47 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20066 | 154.47 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35499 | 154.47 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30567 | 154.47 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22519 | 148.16 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24218 | 148.16 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30988 | 148.16 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30604 | 148.16 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35511 | 148.16 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32866 | 148.16 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30604 | 148.16 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20053 | 148.16 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35511 | 148.16 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30579 | 148.16 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23579 | 140.74 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25108 | 140.74 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31046 | 140.74 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30707 | 140.74 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36009 | 140.74 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33482 | 140.74 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30707 | 140.74 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20842 | 140.74 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36009 | 140.74 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30667 | 140.74 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23262 | 123.92 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24963 | 123.92 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31753 | 123.92 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31384 | 123.92 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36247 | 123.92 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33601 | 123.92 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31384 | 123.92 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36247 | 123.92 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31357 | 123.92 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26249 | 153.71 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25882 | 153.71 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30749 | 153.71 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28027 | 153.71 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25882 | 153.71 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23968 | 153.71 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30749 | 153.71 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25855 | 153.71 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20521 | 136.58 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2237 | 136.58 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29044 | 136.58 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28677 | 136.58 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33543 | 136.58 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30821 | 136.58 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28677 | 136.58 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21173 | 136.58 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33543 | 136.58 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2865 | 136.58 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21225 | 110.38 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23076 | 110.38 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29768 | 110.38 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29414 | 110.38 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3424 | 110.38 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31518 | 110.38 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29414 | 110.38 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20474 | 110.38 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3424 | 110.38 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29385 | 110.38 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26249 | 152.57 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25883 | 152.57 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30749 | 152.57 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28027 | 152.57 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25883 | 152.57 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23968 | 152.57 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30749 | 152.57 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25855 | 152.57 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20521 | 136.37 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22371 | 136.37 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29044 | 136.37 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28677 | 136.37 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33543 | 136.37 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30822 | 136.37 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28677 | 136.37 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21173 | 136.37 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33543 | 136.37 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2865 | 136.37 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21225 | 110.17 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23077 | 110.17 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29768 | 110.17 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29414 | 110.17 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3424 | 110.17 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31518 | 110.17 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29414 | 110.17 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20474 | 110.17 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3424 | 110.17 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29385 | 110.17 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25907 | 161.38 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25546 | 161.38 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30404 | 161.38 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27686 | 161.38 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25546 | 161.38 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24602 | 161.38 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30404 | 161.38 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25518 | 161.38 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20346 | 139.66 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22176 | 139.66 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28745 | 139.66 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28385 | 139.66 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33242 | 139.66 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30525 | 139.66 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28385 | 139.66 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21763 | 139.66 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33242 | 139.66 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28357 | 139.66 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20372 | 136.52 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22202 | 136.52 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28771 | 136.52 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28411 | 136.52 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33268 | 136.52 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30551 | 136.52 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28411 | 136.52 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21737 | 136.52 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33268 | 136.52 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28383 | 136.52 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2113 | 128.63 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2284 | 128.63 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28695 | 128.63 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28375 | 128.63 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33589 | 128.63 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31036 | 128.63 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28375 | 128.63 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22561 | 128.63 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33589 | 128.63 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28333 | 128.63 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26484 | 161.6 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26118 | 161.6 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30985 | 161.6 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2827 | 161.6 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26118 | 161.6 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23858 | 161.6 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30985 | 161.6 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2609 | 161.6 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20792 | 140.65 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22622 | 140.65 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29279 | 140.65 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28913 | 140.65 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3378 | 140.65 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31065 | 140.65 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28913 | 140.65 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21063 | 140.65 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3378 | 140.65 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28885 | 140.65 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2081 | 138.03 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2264 | 138.03 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29298 | 138.03 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28931 | 138.03 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33798 | 138.03 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31083 | 138.03 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28931 | 138.03 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21045 | 138.03 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33798 | 138.03 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28904 | 138.03 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21623 | 130.39 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23334 | 130.39 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29285 | 130.39 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28959 | 130.39 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34182 | 130.39 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31632 | 130.39 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28959 | 130.39 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.218 | 130.39 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34182 | 130.39 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28918 | 130.39 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21498 | 114.74 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2333 | 114.74 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30005 | 114.74 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29652 | 114.74 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34479 | 114.74 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31764 | 114.74 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29652 | 114.74 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20362 | 114.74 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34479 | 114.74 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29623 | 114.74 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20376 | 136.74 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22218 | 136.74 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28884 | 136.74 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28518 | 136.74 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33384 | 136.74 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30666 | 136.74 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28518 | 136.74 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21389 | 136.74 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33384 | 136.74 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2849 | 136.74 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21082 | 110.5 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22925 | 110.5 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2961 | 110.5 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29256 | 110.5 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34083 | 110.5 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31364 | 110.5 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29256 | 110.5 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20688 | 110.5 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34083 | 110.5 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29228 | 110.5 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20376 | 136.7 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22218 | 136.7 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28884 | 136.7 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28518 | 136.7 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33384 | 136.7 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30666 | 136.7 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28518 | 136.7 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21389 | 136.7 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33384 | 136.7 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2849 | 136.7 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21082 | 110.51 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22925 | 110.51 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2961 | 110.51 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29257 | 110.51 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34083 | 110.51 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31364 | 110.51 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29257 | 110.51 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20688 | 110.51 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34083 | 110.51 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29228 | 110.51 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25882 | 161.07 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25522 | 161.07 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30379 | 161.07 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27661 | 161.07 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25522 | 161.07 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24651 | 161.07 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30379 | 161.07 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25494 | 161.07 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20352 | 135.82 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2218 | 135.82 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2874 | 135.82 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2838 | 135.82 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33236 | 135.82 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30519 | 135.82 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2838 | 135.82 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21793 | 135.82 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33236 | 135.82 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28352 | 135.82 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2111 | 127.9 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22819 | 127.9 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28662 | 127.9 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28343 | 127.9 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33557 | 127.9 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31003 | 127.9 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28343 | 127.9 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22618 | 127.9 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33557 | 127.9 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28301 | 127.9 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26238 | 159.41 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2587 | 159.41 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3074 | 159.41 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28022 | 159.41 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2587 | 159.41 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23999 | 159.41 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3074 | 159.41 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25843 | 159.41 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20535 | 135.53 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22376 | 135.53 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29065 | 135.53 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28697 | 135.53 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33566 | 135.53 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30849 | 135.53 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28697 | 135.53 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21172 | 135.53 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33566 | 135.53 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2867 | 135.53 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21294 | 127.42 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23021 | 127.42 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2902 | 127.42 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28691 | 127.42 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33914 | 127.42 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31365 | 127.42 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28691 | 127.42 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21936 | 127.42 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33914 | 127.42 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28651 | 127.42 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26238 | 159.41 | P42:345:OKGE:SB_JOCO7313
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2587 | 159.41 | P42:345:OKGE:SB_JOCO7313
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3074 | 159.41 | P42:345:OKGE:SB_JOCO7313
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28022 | 159.41 | P42:345:OKGE:SB_JOCO7313
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2587 | 159.41 | P42:345:OKGE:SB_JOCO7313
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23999 | 159.41 | P42:345:OKGE:SB_JOCO7313
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3074 | 159.41 | P42:345:OKGE:SB_JOCO7313
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25843 | 159.41 | P42:345:OKGE:SB_JOCO7313
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26238 | 159.56 | P42:345:OKGE:SB_JOCO7383
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2587 | 159.56 | P42:345:OKGE:SB_JOCO7383
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3074 | 159.56 | P42:345:OKGE:SB_JOCO7383
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28022 | 159.56 | P42:345:OKGE:SB_JOCO7383
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2587 | 159.56 | P42:345:OKGE:SB_JOCO7383
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23999 | 159.56 | P42:345:OKGE:SB_JOCO7383
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3074 | 159.56 | P42:345:OKGE:SB_JOCO7383
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25843 | 159.56 | P42:345:OKGE:SB_JOCO7383
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26484 | 160.3 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26118 | 160.3 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30985 | 160.3 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2827 | 160.3 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26118 | 160.3 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23858 | 160.3 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30985 | 160.3 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2609 | 160.3 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20792 | 140.98 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22622 | 140.98 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29279 | 140.98 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28913 | 140.98 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3378 | 140.98 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31065 | 140.98 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28913 | 140.98 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21063 | 140.98 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3378 | 140.98 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28885 | 140.98 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2081 | 138.1 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2264 | 138.1 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29298 | 138.1 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28931 | 138.1 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33798 | 138.1 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31083 | 138.1 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28931 | 138.1 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21045 | 138.1 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33798 | 138.1 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28904 | 138.1 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21623 | 130.43 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23334 | 130.43 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29285 | 130.43 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28959 | 130.43 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34182 | 130.43 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31632 | 130.43 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28959 | 130.43 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.218 | 130.43 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34182 | 130.43 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28918 | 130.43 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21498 | 115.07 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2333 | 115.07 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30005 | 115.07 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29652 | 115.07 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34479 | 115.07 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31764 | 115.07 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29652 | 115.07 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20362 | 115.07 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34479 | 115.07 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29623 | 115.07 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26484 | 161.48 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26118 | 161.48 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30985 | 161.48 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2827 | 161.48 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26118 | 161.48 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23858 | 161.48 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30985 | 161.48 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2609 | 161.48 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20792 | 140.17 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22622 | 140.17 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29279 | 140.17 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28913 | 140.17 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3378 | 140.17 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31065 | 140.17 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28913 | 140.17 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21063 | 140.17 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3378 | 140.17 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28885 | 140.17 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2081 | 137.24 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2264 | 137.24 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29298 | 137.24 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28931 | 137.24 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33798 | 137.24 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31083 | 137.24 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28931 | 137.24 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21045 | 137.24 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33798 | 137.24 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28904 | 137.24 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21623 | 129.49 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23334 | 129.49 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29285 | 129.49 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28959 | 129.49 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34182 | 129.49 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31632 | 129.49 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28959 | 129.49 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.218 | 129.49 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34182 | 129.49 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28918 | 129.49 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21498 | 114.27 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2333 | 114.27 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30005 | 114.27 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29652 | 114.27 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34479 | 114.27 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31764 | 114.27 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29652 | 114.27 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20362 | 114.27 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34479 | 114.27 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29623 | 114.27 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20402 | 136.42 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22249 | 136.42 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28949 | 136.42 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2858 | 136.42 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3345 | 136.42 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30731 | 136.42 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2858 | 136.42 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21238 | 136.42 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3345 | 136.42 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28553 | 136.42 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20432 | 133.42 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22278 | 133.42 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28979 | 133.42 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2861 | 133.42 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3348 | 133.42 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30761 | 133.42 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2861 | 133.42 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21208 | 133.42 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3348 | 133.42 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28583 | 133.42 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21178 | 125.2 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22913 | 125.2 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2893 | 125.2 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.286 | 125.2 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33822 | 125.2 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31272 | 125.2 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.286 | 125.2 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21971 | 125.2 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33822 | 125.2 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2856 | 125.2 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21097 | 110.62 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22945 | 110.62 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29664 | 110.62 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29308 | 110.62 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34138 | 110.62 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31418 | 110.62 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29308 | 110.62 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20548 | 110.62 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34138 | 110.62 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2928 | 110.62 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26239 | 159.39 | P42:345:OKGE:SB_NOST7383
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25871 | 159.39 | P42:345:OKGE:SB_NOST7383
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3074 | 159.39 | P42:345:OKGE:SB_NOST7383
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28021 | 159.39 | P42:345:OKGE:SB_NOST7383
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25871 | 159.39 | P42:345:OKGE:SB_NOST7383
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23963 | 159.39 | P42:345:OKGE:SB_NOST7383
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3074 | 159.39 | P42:345:OKGE:SB_NOST7383
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25844 | 159.39 | P42:345:OKGE:SB_NOST7383
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26217 | 155.7 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25848 | 155.7 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30718 | 155.7 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27998 | 155.7 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25848 | 155.7 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23969 | 155.7 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30718 | 155.7 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25821 | 155.7 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20379 | 136.62 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22226 | 136.62 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28926 | 136.62 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28558 | 136.62 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33427 | 136.62 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30708 | 136.62 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28558 | 136.62 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21259 | 136.62 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33427 | 136.62 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28531 | 136.62 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21077 | 110.56 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22926 | 110.56 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29645 | 110.56 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29289 | 110.56 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34119 | 110.56 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31399 | 110.56 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29289 | 110.56 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20565 | 110.56 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34119 | 110.56 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29261 | 110.56 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20379 | 137.13 | P42:345:OKGE:SB_RARD7311
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22226 | 137.13 | P42:345:OKGE:SB_RARD7311
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28926 | 137.13 | P42:345:OKGE:SB_RARD7311
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28558 | 137.13 | P42:345:OKGE:SB_RARD7311
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33427 | 137.13 | P42:345:OKGE:SB_RARD7311
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30708 | 137.13 | P42:345:OKGE:SB_RARD7311
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28558 | 137.13 | P42:345:OKGE:SB_RARD7311
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21259 | 137.13 | P42:345:OKGE:SB_RARD7311
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33427 | 137.13 | P42:345:OKGE:SB_RARD7311
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2853 | 137.13 | P42:345:OKGE:SB_RARD7311
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20379 | 137.36 | P42:345:OKGE:SB_RARD7393
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22226 | 137.36 | P42:345:OKGE:SB_RARD7393
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28926 | 137.36 | P42:345:OKGE:SB_RARD7393
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28558 | 137.36 | P42:345:OKGE:SB_RARD7393
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33427 | 137.36 | P42:345:OKGE:SB_RARD7393
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30708 | 137.36 | P42:345:OKGE:SB_RARD7393
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28558 | 137.36 | P42:345:OKGE:SB_RARD7393
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21259 | 137.36 | P42:345:OKGE:SB_RARD7393
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33427 | 137.36 | P42:345:OKGE:SB_RARD7393
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28531 | 137.36 | P42:345:OKGE:SB_RARD7393
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26183 | 156.15 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25814 | 156.15 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30684 | 156.15 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27964 | 156.15 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25814 | 156.15 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24005 | 156.15 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30684 | 156.15 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25787 | 156.15 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20373 | 136.89 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2222 | 136.89 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28919 | 136.89 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28551 | 136.89 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33421 | 136.89 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30701 | 136.89 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28551 | 136.89 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21268 | 136.89 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33421 | 136.89 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28524 | 136.89 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21074 | 110.75 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22923 | 110.75 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2964 | 110.75 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29285 | 110.75 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34115 | 110.75 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31395 | 110.75 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29285 | 110.75 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20572 | 110.75 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34115 | 110.75 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29257 | 110.75 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26182 | 157.34 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25814 | 157.34 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30683 | 157.34 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27964 | 157.34 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25814 | 157.34 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24006 | 157.34 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30683 | 157.34 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25787 | 157.34 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20368 | 137.36 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22215 | 137.36 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28914 | 137.36 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28545 | 137.36 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33415 | 137.36 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30695 | 137.36 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28545 | 137.36 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21275 | 137.36 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33415 | 137.36 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28518 | 137.36 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21068 | 111.24 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22917 | 111.24 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29634 | 111.24 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29279 | 111.24 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34108 | 111.24 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31388 | 111.24 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29279 | 111.24 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20579 | 111.24 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34108 | 111.24 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2925 | 111.24 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20075 | 135.76 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21902 | 135.76 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2845 | 135.76 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2809 | 135.76 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32946 | 135.76 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30228 | 135.76 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2809 | 135.76 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22111 | 135.76 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32946 | 135.76 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28062 | 135.76 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20102 | 133.15 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2193 | 133.15 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28477 | 133.15 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28118 | 133.15 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32973 | 133.15 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30256 | 133.15 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28118 | 133.15 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22083 | 133.15 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32973 | 133.15 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2809 | 133.15 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20843 | 125.03 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22551 | 125.03 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28384 | 125.03 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28065 | 125.03 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33279 | 125.03 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30724 | 125.03 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28065 | 125.03 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22917 | 125.03 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33279 | 125.03 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28023 | 125.03 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20801 | 108.94 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2263 | 108.94 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29196 | 108.94 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28849 | 108.94 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33665 | 108.94 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30947 | 108.94 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28849 | 108.94 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2139 | 108.94 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33665 | 108.94 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2882 | 108.94 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25908 | 150.87 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25544 | 150.87 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30407 | 150.87 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2769 | 150.87 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25544 | 150.87 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24481 | 150.87 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30407 | 150.87 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25516 | 150.87 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20071 | 133.49 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21905 | 133.49 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28531 | 133.49 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28167 | 133.49 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3303 | 133.49 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30314 | 133.49 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28167 | 133.49 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21857 | 133.49 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3303 | 133.49 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28139 | 133.49 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.201 | 128.93 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21934 | 128.93 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2856 | 128.93 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28195 | 128.93 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33059 | 128.93 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30342 | 128.93 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28195 | 128.93 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21829 | 128.93 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33059 | 128.93 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28168 | 128.93 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20837 | 120.32 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22554 | 120.32 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28478 | 120.32 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28154 | 120.32 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33373 | 120.32 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30821 | 120.32 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28154 | 120.32 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2264 | 120.32 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33373 | 120.32 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28113 | 120.32 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20766 | 107.65 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22602 | 107.65 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29246 | 107.65 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28895 | 107.65 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33718 | 107.65 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31001 | 107.65 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28895 | 107.65 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21168 | 107.65 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33718 | 107.65 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28866 | 107.65 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26233 | 159.51 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25865 | 159.51 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30734 | 159.51 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28017 | 159.51 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25865 | 159.51 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24 | 159.51 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30734 | 159.51 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25838 | 159.51 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20524 | 135.6 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22366 | 135.6 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29056 | 135.6 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28688 | 135.6 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33557 | 135.6 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3084 | 135.6 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28688 | 135.6 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21177 | 135.6 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33557 | 135.6 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28661 | 135.6 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21282 | 127.5 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2301 | 127.5 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29011 | 127.5 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28682 | 127.5 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33905 | 127.5 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31355 | 127.5 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28682 | 127.5 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21942 | 127.5 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33905 | 127.5 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28641 | 127.5 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26282 | 159.51 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25917 | 159.51 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30781 | 159.51 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28062 | 159.51 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25917 | 159.51 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24011 | 159.51 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30781 | 159.51 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25889 | 159.51 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20571 | 139.73 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22414 | 139.73 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29067 | 139.73 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28701 | 139.73 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33566 | 139.73 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30847 | 139.73 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28701 | 139.73 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21226 | 139.73 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33566 | 139.73 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28674 | 139.73 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.206 | 136.2 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22443 | 136.2 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29096 | 136.2 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2873 | 136.2 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33595 | 136.2 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30876 | 136.2 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2873 | 136.2 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21197 | 136.2 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33595 | 136.2 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28703 | 136.2 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21361 | 128.2 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23091 | 128.2 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29052 | 128.2 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28725 | 128.2 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33944 | 128.2 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31392 | 128.2 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28725 | 128.2 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21963 | 128.2 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33944 | 128.2 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28685 | 128.2 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21278 | 113.23 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23124 | 113.23 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29794 | 113.23 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29442 | 113.23 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34267 | 113.23 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31547 | 113.23 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29442 | 113.23 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20524 | 113.23 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34267 | 113.23 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29413 | 113.23 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20582 | 135.38 | P42:345:OKGE:SB_TAGA7386
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22426 | 135.38 | P42:345:OKGE:SB_TAGA7386
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29085 | 135.38 | P42:345:OKGE:SB_TAGA7386
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28719 | 135.38 | P42:345:OKGE:SB_TAGA7386
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33585 | 135.38 | P42:345:OKGE:SB_TAGA7386
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30866 | 135.38 | P42:345:OKGE:SB_TAGA7386
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28719 | 135.38 | P42:345:OKGE:SB_TAGA7386
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 135.38 | P42:345:OKGE:SB_TAGA7386
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33585 | 135.38 | P42:345:OKGE:SB_TAGA7386
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28692 | 135.38 | P42:345:OKGE:SB_TAGA7386
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21341 | 127.22 | P42:345:OKGE:SB_TAGA7386
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23072 | 127.22 | P42:345:OKGE:SB_TAGA7386
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29041 | 127.22 | P42:345:OKGE:SB_TAGA7386
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28714 | 127.22 | P42:345:OKGE:SB_TAGA7386
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33933 | 127.22 | P42:345:OKGE:SB_TAGA7386
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31382 | 127.22 | P42:345:OKGE:SB_TAGA7386
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28714 | 127.22 | P42:345:OKGE:SB_TAGA7386
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21957 | 127.22 | P42:345:OKGE:SB_TAGA7386
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33933 | 127.22 | P42:345:OKGE:SB_TAGA7386
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28674 | 127.22 | P42:345:OKGE:SB_TAGA7386
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26277 | 159.65 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25911 | 159.65 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30776 | 159.65 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28057 | 159.65 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25911 | 159.65 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24006 | 159.65 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30776 | 159.65 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25883 | 159.65 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20561 | 139.53 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22404 | 139.53 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29062 | 139.53 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28696 | 139.53 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33561 | 139.53 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30842 | 139.53 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28696 | 139.53 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21221 | 139.53 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33561 | 139.53 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28669 | 139.53 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20591 | 136.07 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22435 | 136.07 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29092 | 136.07 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28726 | 136.07 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33592 | 136.07 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30872 | 136.07 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28726 | 136.07 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21191 | 136.07 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33592 | 136.07 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28699 | 136.07 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21351 | 127.99 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23081 | 127.99 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29048 | 127.99 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28721 | 127.99 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3394 | 127.99 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31389 | 127.99 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28721 | 127.99 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21956 | 127.99 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3394 | 127.99 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2868 | 127.99 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21268 | 113.13 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23113 | 113.13 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29789 | 113.13 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29436 | 113.13 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34262 | 113.13 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31542 | 113.13 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29436 | 113.13 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20518 | 113.13 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34262 | 113.13 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29407 | 113.13 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26277 | 159.66 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25911 | 159.66 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30776 | 159.66 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28057 | 159.66 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25911 | 159.66 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24006 | 159.66 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30776 | 159.66 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25883 | 159.66 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20561 | 139.56 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22404 | 139.56 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29062 | 139.56 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28696 | 139.56 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33561 | 139.56 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30842 | 139.56 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28696 | 139.56 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21221 | 139.56 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33561 | 139.56 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28669 | 139.56 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20591 | 136.11 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22434 | 136.11 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29092 | 136.11 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28726 | 136.11 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33592 | 136.11 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30872 | 136.11 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28726 | 136.11 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21191 | 136.11 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33592 | 136.11 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28699 | 136.11 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21351 | 128 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23081 | 128 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29048 | 128 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28721 | 128 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3394 | 128 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31389 | 128 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28721 | 128 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21956 | 128 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3394 | 128 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2868 | 128 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21268 | 113.1 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23113 | 113.1 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29789 | 113.1 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29436 | 113.1 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34262 | 113.1 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31542 | 113.1 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29436 | 113.1 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20518 | 113.1 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34262 | 113.1 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29407 | 113.1 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26511 | 169.45 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26148 | 169.45 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31008 | 169.45 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28284 | 169.45 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26148 | 169.45 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23809 | 169.45 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31008 | 169.45 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26121 | 169.45 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20984 | 145.78 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22834 | 145.78 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29449 | 145.78 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29086 | 145.78 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33945 | 145.78 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31222 | 145.78 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29086 | 145.78 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20871 | 145.78 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33945 | 145.78 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29058 | 145.78 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2102 | 142.44 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2287 | 142.44 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29485 | 142.44 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29122 | 142.44 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33981 | 142.44 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31258 | 142.44 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29122 | 142.44 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20835 | 142.44 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33981 | 142.44 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29094 | 142.44 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21777 | 134.31 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23514 | 134.31 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29442 | 134.31 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29119 | 134.31 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34331 | 134.31 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31777 | 134.31 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29119 | 134.31 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21595 | 134.31 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34331 | 134.31 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29078 | 134.31 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21001 | 169.94 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27193 | 169.94 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26861 | 169.94 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31666 | 169.94 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28914 | 169.94 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26861 | 169.94 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2371 | 169.94 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31666 | 169.94 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26829 | 169.94 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22303 | 148.61 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.242 | 148.61 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30392 | 148.61 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3006 | 148.61 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34864 | 148.61 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32112 | 148.61 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3006 | 148.61 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20511 | 148.61 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34864 | 148.61 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30028 | 148.61 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22303 | 147.15 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24201 | 147.15 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30392 | 147.15 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30061 | 147.15 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34865 | 147.15 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32113 | 147.15 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30061 | 147.15 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20511 | 147.15 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34865 | 147.15 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30029 | 147.15 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23083 | 139.14 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24871 | 139.14 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30374 | 139.14 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30082 | 139.14 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3524 | 139.14 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32665 | 139.14 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30082 | 139.14 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21262 | 139.14 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3524 | 139.14 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30037 | 139.14 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2305 | 119.14 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24949 | 119.14 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31156 | 119.14 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30837 | 119.14 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35605 | 119.14 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32853 | 119.14 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30837 | 119.14 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35605 | 119.14 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30803 | 119.14 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20424 | 137.49 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22271 | 137.49 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2898 | 137.49 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2861 | 137.49 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33481 | 137.49 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30762 | 137.49 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2861 | 137.49 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2119 | 137.49 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33481 | 137.49 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28583 | 137.49 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20462 | 133.67 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22309 | 133.67 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29017 | 133.67 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28648 | 133.67 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33519 | 133.67 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30799 | 133.67 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28648 | 133.67 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21152 | 133.67 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33519 | 133.67 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28621 | 133.67 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21209 | 125.49 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22944 | 125.49 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28971 | 125.49 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28641 | 125.49 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33863 | 125.49 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31313 | 125.49 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28641 | 125.49 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21911 | 125.49 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33863 | 125.49 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.286 | 125.49 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21125 | 111.32 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22975 | 111.32 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29701 | 111.32 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29345 | 111.32 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34175 | 111.32 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31456 | 111.32 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29345 | 111.32 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20494 | 111.32 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34175 | 111.32 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29317 | 111.32 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21096 | 113.07 | P42:500:OKGE:SB_FTTH8581
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22945 | 113.07 | P42:500:OKGE:SB_FTTH8581
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29669 | 113.07 | P42:500:OKGE:SB_FTTH8581
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29313 | 113.07 | P42:500:OKGE:SB_FTTH8581
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34143 | 113.07 | P42:500:OKGE:SB_FTTH8581
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31423 | 113.07 | P42:500:OKGE:SB_FTTH8581
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29313 | 113.07 | P42:500:OKGE:SB_FTTH8581
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20531 | 113.07 | P42:500:OKGE:SB_FTTH8581
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34143 | 113.07 | P42:500:OKGE:SB_FTTH8581
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29284 | 113.07 | P42:500:OKGE:SB_FTTH8581
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21097 | 113.14 | P42:500:OKGE:SB_FTTH8583
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22946 | 113.14 | P42:500:OKGE:SB_FTTH8583
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29671 | 113.14 | P42:500:OKGE:SB_FTTH8583
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29315 | 113.14 | P42:500:OKGE:SB_FTTH8583
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34145 | 113.14 | P42:500:OKGE:SB_FTTH8583
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31425 | 113.14 | P42:500:OKGE:SB_FTTH8583
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29315 | 113.14 | P42:500:OKGE:SB_FTTH8583
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20529 | 113.14 | P42:500:OKGE:SB_FTTH8583
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34145 | 113.14 | P42:500:OKGE:SB_FTTH8583
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29286 | 113.14 | P42:500:OKGE:SB_FTTH8583
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21096 | 113.07 | P42:500:OKGE:SB_FTTH8585
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22945 | 113.07 | P42:500:OKGE:SB_FTTH8585
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29669 | 113.07 | P42:500:OKGE:SB_FTTH8585
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29313 | 113.07 | P42:500:OKGE:SB_FTTH8585
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34143 | 113.07 | P42:500:OKGE:SB_FTTH8585
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31423 | 113.07 | P42:500:OKGE:SB_FTTH8585
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29313 | 113.07 | P42:500:OKGE:SB_FTTH8585
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20531 | 113.07 | P42:500:OKGE:SB_FTTH8585
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34143 | 113.07 | P42:500:OKGE:SB_FTTH8585
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29284 | 113.07 | P42:500:OKGE:SB_FTTH8585
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20406 | 137.11 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22254 | 137.11 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2896 | 137.11 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28591 | 137.11 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33461 | 137.11 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30742 | 137.11 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28591 | 137.11 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21215 | 137.11 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33461 | 137.11 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28564 | 137.11 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20441 | 133.41 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22288 | 133.41 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28994 | 133.41 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28625 | 133.41 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33495 | 133.41 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30776 | 133.41 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28625 | 133.41 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2118 | 133.41 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33495 | 133.41 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 133.41 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21188 | 125.2 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22924 | 125.2 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28947 | 125.2 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28617 | 125.2 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3384 | 125.2 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3129 | 125.2 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28617 | 125.2 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21939 | 125.2 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3384 | 125.2 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28577 | 125.2 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21106 | 110.97 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22955 | 110.97 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2968 | 110.97 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29324 | 110.97 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34154 | 110.97 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31434 | 110.97 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29324 | 110.97 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2052 | 110.97 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34154 | 110.97 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29295 | 110.97 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20169 | 202.23 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21803 | 202.23 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28441 | 202.23 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28062 | 202.23 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32968 | 202.23 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30351 | 202.23 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28062 | 202.23 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23285 | 202.23 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32968 | 202.23 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28036 | 202.23 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23623 | 189.5 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25257 | 189.5 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31895 | 189.5 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31516 | 189.5 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36421 | 189.5 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-033 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21299 | 189.5 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33804 | 189.5 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-065 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21299 | 189.5 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31516 | 189.5 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36421 | 189.5 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3149 | 189.5 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23615 | 181.41 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25249 | 181.41 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31888 | 181.41 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31508 | 181.41 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36414 | 181.41 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21291 | 181.41 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33797 | 181.41 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21291 | 181.41 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31508 | 181.41 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36414 | 181.41 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31482 | 181.41 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24828 | 176.36 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26263 | 176.36 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31975 | 176.36 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31645 | 176.36 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36965 | 176.36 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23931 | 176.36 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34442 | 176.36 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23931 | 176.36 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31645 | 176.36 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2069 | 176.36 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36965 | 176.36 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31603 | 176.36 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24425 | 153.12 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26061 | 153.12 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3272 | 153.12 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32355 | 153.12 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.37216 | 153.12 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22093 | 153.12 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34598 | 153.12 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22093 | 153.12 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32355 | 153.12 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.37216 | 153.12 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32327 | 153.12 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.26184 | 159.83 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25815 | 159.83 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30685 | 159.83 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27966 | 159.83 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25815 | 159.83 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23992 | 159.83 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30685 | 159.83 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25788 | 159.83 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2046 | 139.32 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22307 | 139.32 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29012 | 139.32 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28643 | 139.32 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33514 | 139.32 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30794 | 139.32 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28643 | 139.32 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21164 | 139.32 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33514 | 139.32 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28616 | 139.32 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20493 | 135.67 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2234 | 135.67 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29046 | 135.67 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28677 | 135.67 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33547 | 135.67 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30828 | 135.67 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28677 | 135.67 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21131 | 135.67 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33547 | 135.67 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2865 | 135.67 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21245 | 127.53 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22979 | 127.53 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29002 | 127.53 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28672 | 127.53 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33895 | 127.53 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31345 | 127.53 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28672 | 127.53 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21887 | 127.53 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33895 | 127.53 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28632 | 127.53 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21164 | 113.14 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23013 | 113.14 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29736 | 113.14 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29381 | 113.14 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34211 | 113.14 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31491 | 113.14 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29381 | 113.14 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20465 | 113.14 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34211 | 113.14 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29352 | 113.14 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2101 | 172.29 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2778 | 172.29 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27396 | 172.29 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32304 | 172.29 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29658 | 172.29 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27396 | 172.29 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23261 | 172.29 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32304 | 172.29 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.27371 | 172.29 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22506 | 154.45 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24206 | 154.45 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30976 | 154.45 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30592 | 154.45 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35499 | 154.45 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32854 | 154.45 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30592 | 154.45 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20066 | 154.45 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35499 | 154.45 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30567 | 154.45 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22519 | 148.16 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24218 | 148.16 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30988 | 148.16 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30604 | 148.16 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35511 | 148.16 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.32866 | 148.16 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30604 | 148.16 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20053 | 148.16 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.35511 | 148.16 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30579 | 148.16 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23579 | 140.69 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.25108 | 140.69 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31046 | 140.69 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30707 | 140.69 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36009 | 140.69 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33482 | 140.69 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30707 | 140.69 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20842 | 140.69 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36009 | 140.69 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30667 | 140.69 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.23262 | 123.9 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.24963 | 123.9 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31753 | 123.9 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31384 | 123.9 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36247 | 123.9 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33601 | 123.9 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31384 | 123.9 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.36247 | 123.9 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31357 | 123.9 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20421 | 137.53 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22268 | 137.53 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28976 | 137.53 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28607 | 137.53 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33478 | 137.53 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 137.53 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28607 | 137.53 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21193 | 137.53 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33478 | 137.53 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.2858 | 137.53 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20457 | 133.66 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22305 | 133.66 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29013 | 133.66 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28644 | 133.66 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33514 | 133.66 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.30795 | 133.66 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28644 | 133.66 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21157 | 133.66 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33514 | 133.66 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28617 | 133.66 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21205 | 125.32 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22941 | 125.32 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28967 | 125.32 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28637 | 125.32 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33859 | 125.32 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.3131 | 125.32 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28637 | 125.32 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21915 | 125.32 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.33859 | 125.32 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.28597 | 125.32 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.21122 | 111.35 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.35 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29698 | 111.35 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29342 | 111.35 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.35 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 111.35 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29342 | 111.35 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.20497 | 111.35 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.35 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 111.35 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 478 |  | 0.26202 | 183.06 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 478 |  | 0.25833 | 183.06 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 478 |  | 0.30704 | 183.06 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 478 |  | 0.27985 | 183.06 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 478 |  | 0.25833 | 183.06 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 478 |  | 0.23967 | 183.06 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 478 |  | 0.30704 | 183.06 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 478 |  | 0.25806 | 183.06 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 478 |  | 0.20422 | 159.98 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 478 |  | 0.22269 | 159.98 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 478 |  | 0.28977 | 159.98 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 478 |  | 0.28608 | 159.98 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 478 |  | 0.33479 | 159.98 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 478 |  | 0.30759 | 159.98 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 478 |  | 0.28608 | 159.98 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 478 |  | 0.21192 | 159.98 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 478 |  | 0.33479 | 159.98 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 478 |  | 0.28581 | 159.98 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 553 |  | 0.20458 | 134.46 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 553 |  | 0.22306 | 134.46 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 553 |  | 0.29014 | 134.46 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 553 |  | 0.28645 | 134.46 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 553 |  | 0.33516 | 134.46 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 553 |  | 0.30796 | 134.46 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 553 |  | 0.28645 | 134.46 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 553 |  | 0.21156 | 134.46 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 553 |  | 0.33516 | 134.46 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 553 |  | 0.28618 | 134.46 | System Intact
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 478 |  | 0.21123 | 129.74 | System Intact
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 478 |  | 0.22972 | 129.74 | System Intact
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 478 |  | 0.29699 | 129.74 | System Intact
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 478 |  | 0.29343 | 129.74 | System Intact
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 478 |  | 0.34173 | 129.74 | System Intact
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 478 |  | 0.31453 | 129.74 | System Intact
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 478 |  | 0.29343 | 129.74 | System Intact
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 478 |  | 0.20496 | 129.74 | System Intact
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 478 |  | 0.34173 | 129.74 | System Intact
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 478 |  | 0.29314 | 129.74 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 553 |  | 0.21207 | 126.3 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 553 |  | 0.22942 | 126.3 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 553 |  | 0.28968 | 126.3 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 553 |  | 0.28638 | 126.3 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 553 |  | 0.33861 | 126.3 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 553 |  | 0.31311 | 126.3 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 553 |  | 0.28638 | 126.3 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 553 |  | 0.21914 | 126.3 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 553 |  | 0.33861 | 126.3 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 553 |  | 0.28598 | 126.3 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.38 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.38 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.38 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.38 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.38 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.38 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.38 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.38 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.38 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.38 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.33 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.33 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.33 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.33 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.33 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.33 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.33 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.33 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.33 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.33 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.13 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.13 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.13 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.13 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.13 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.13 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.13 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.13 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.13 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.13 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.73 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.73 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.73 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.73 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.73 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.73 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.73 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.73 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.73 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.73 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 129.86 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 129.86 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 129.86 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 129.86 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 129.86 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 129.86 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 129.86 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 129.86 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 129.86 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 129.86 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.97 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.97 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.97 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.97 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.97 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.97 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.97 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.97 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.97 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.97 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.96 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.96 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.96 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.96 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.96 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.96 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.96 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.96 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.96 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.96 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.84 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.84 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.84 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.84 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.84 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.84 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.84 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.84 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.84 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.84 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 128.1 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 128.1 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 128.1 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 128.1 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 128.1 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 128.1 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 128.1 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 128.1 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 128.1 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 128.1 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.96 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.96 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.96 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.96 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.96 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.96 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.96 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.96 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.96 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.96 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 126.49 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 126.49 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 126.49 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.49 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.49 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 126.49 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.49 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 126.49 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.49 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 126.49 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.96 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.96 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.96 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.96 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.96 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.96 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.96 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.96 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.96 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.96 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 126.92 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 126.92 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 126.92 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.92 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.92 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 126.92 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.92 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 126.92 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.92 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 126.92 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.96 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.96 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.96 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.96 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.96 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.96 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.96 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.96 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.96 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.96 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.96 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.96 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.96 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.96 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.96 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.96 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.96 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.96 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.96 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.96 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.95 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.95 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.95 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.95 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.95 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.95 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.95 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.95 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.95 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.95 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20428 | 127.96 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.96 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.96 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28609 | 127.96 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.96 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3076 | 127.96 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28609 | 127.96 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.96 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.96 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28582 | 127.96 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 128.77 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 128.77 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 128.77 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 128.77 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 128.77 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 128.77 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 128.77 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 128.77 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 128.77 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 128.77 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 128.83 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 128.83 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 128.83 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 128.83 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 128.83 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 128.83 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 128.83 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 128.83 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 128.83 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 128.83 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.95 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.95 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.95 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.95 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.95 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.95 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.95 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.95 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.95 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.95 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.95 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.95 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.95 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.95 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.95 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.95 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.95 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.95 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.95 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.95 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.95 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.95 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.95 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.95 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.95 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.95 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.95 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.95 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.95 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.95 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.12 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.12 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.12 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.12 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.12 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.12 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.12 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.12 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.12 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.12 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.85 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.85 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.85 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.85 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.85 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.85 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.85 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.85 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.85 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.85 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.85 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.85 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.85 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.85 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.85 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.85 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.85 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.85 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.85 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.85 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20519 | 128.41 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22485 | 128.41 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28983 | 128.41 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28605 | 128.41 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33504 | 128.41 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30786 | 128.41 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28605 | 128.41 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21191 | 128.41 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33504 | 128.41 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28579 | 128.41 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20431 | 125.94 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22281 | 125.94 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28979 | 125.94 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 125.94 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33482 | 125.94 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30764 | 125.94 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 125.94 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21207 | 125.94 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33482 | 125.94 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 125.94 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20433 | 123.26 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22282 | 123.26 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28979 | 123.26 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28611 | 123.26 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33483 | 123.26 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30765 | 123.26 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28611 | 123.26 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21208 | 123.26 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33483 | 123.26 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 123.26 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 126.88 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 126.88 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 126.88 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.88 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.88 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 126.88 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.88 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 126.88 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.88 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 126.88 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20508 | 129.79 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22428 | 129.79 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29169 | 129.79 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28814 | 129.79 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33694 | 129.79 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30883 | 129.79 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28814 | 129.79 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21181 | 129.79 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33694 | 129.79 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28784 | 129.79 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20508 | 128.42 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22428 | 128.42 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29169 | 128.42 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28814 | 128.42 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33694 | 128.42 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30883 | 128.42 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28814 | 128.42 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21181 | 128.42 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33694 | 128.42 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28784 | 128.42 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20428 | 127.67 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22278 | 127.67 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28979 | 127.67 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28602 | 127.67 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33481 | 127.67 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.67 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28602 | 127.67 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21204 | 127.67 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33481 | 127.67 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28582 | 127.67 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20535 | 128.45 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22383 | 128.45 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29048 | 128.45 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28682 | 128.45 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33548 | 128.45 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30826 | 128.45 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28682 | 128.45 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21184 | 128.45 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33548 | 128.45 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28655 | 128.45 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20498 | 128.23 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22348 | 128.23 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29024 | 128.23 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28657 | 128.23 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33524 | 128.23 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30803 | 128.23 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28657 | 128.23 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21192 | 128.23 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33524 | 128.23 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2863 | 128.23 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20394 | 128.18 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22218 | 128.18 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29566 | 128.18 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2942 | 128.18 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33617 | 128.18 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30891 | 128.18 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2942 | 128.18 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21128 | 128.18 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33617 | 128.18 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29368 | 128.18 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20394 | 128.5 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22218 | 128.5 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29566 | 128.5 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2942 | 128.5 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33617 | 128.5 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30891 | 128.5 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2942 | 128.5 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21128 | 128.5 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33617 | 128.5 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29368 | 128.5 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21077 | 128.55 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22554 | 128.55 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29093 | 128.55 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28722 | 128.55 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33601 | 128.55 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30883 | 128.55 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28722 | 128.55 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21136 | 128.55 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33601 | 128.55 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28695 | 128.55 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20432 | 127.24 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22281 | 127.24 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28976 | 127.24 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28608 | 127.24 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33478 | 127.24 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30758 | 127.24 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28608 | 127.24 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21207 | 127.24 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33478 | 127.24 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28581 | 127.24 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 126.63 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 126.63 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 126.63 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.63 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.63 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 126.63 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.63 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 126.63 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.63 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 126.63 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20456 | 127.95 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22314 | 127.95 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29183 | 127.95 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28804 | 127.95 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33539 | 127.95 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30803 | 127.95 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28804 | 127.95 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21219 | 127.95 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33539 | 127.95 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28781 | 127.95 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.09 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.09 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.09 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.09 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.09 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.09 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.09 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.09 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.09 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.09 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20349 | 127.17 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21934 | 127.17 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29104 | 127.17 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28741 | 127.17 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.336 | 127.17 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30875 | 127.17 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28741 | 127.17 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21148 | 127.17 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.336 | 127.17 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28713 | 127.17 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20436 | 125.56 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22286 | 125.56 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28982 | 125.56 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28613 | 125.56 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33487 | 125.56 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3077 | 125.56 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28613 | 125.56 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21208 | 125.56 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33487 | 125.56 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28586 | 125.56 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20412 | 127.4 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22289 | 127.4 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29014 | 127.4 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28648 | 127.4 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33513 | 127.4 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30791 | 127.4 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28648 | 127.4 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21189 | 127.4 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33513 | 127.4 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2862 | 127.4 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20456 | 127.81 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22324 | 127.81 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29027 | 127.81 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2866 | 127.81 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33543 | 127.81 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30795 | 127.81 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2866 | 127.81 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.81 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33543 | 127.81 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28633 | 127.81 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20444 | 125.73 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22293 | 125.73 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2898 | 125.73 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28612 | 125.73 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3349 | 125.73 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30771 | 125.73 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28612 | 125.73 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21219 | 125.73 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3349 | 125.73 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28584 | 125.73 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20434 | 126.74 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22283 | 126.74 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28979 | 126.74 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28611 | 126.74 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33484 | 126.74 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30767 | 126.74 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28611 | 126.74 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21214 | 126.74 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33484 | 126.74 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28584 | 126.74 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.87 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.87 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28981 | 127.87 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28625 | 127.87 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.87 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3076 | 127.87 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28625 | 127.87 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.87 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.87 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28625 | 127.87 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20444 | 128.68 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22426 | 128.68 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29254 | 128.68 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28919 | 128.68 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33699 | 128.68 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30969 | 128.68 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28919 | 128.68 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21097 | 128.68 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33699 | 128.68 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28888 | 128.68 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20428 | 127.83 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22277 | 127.83 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29001 | 127.83 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28676 | 127.83 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33481 | 127.83 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30762 | 127.83 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28676 | 127.83 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21204 | 127.83 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33481 | 127.83 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28633 | 127.83 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 128.79 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 128.79 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 128.79 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 128.79 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 128.79 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 128.79 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 128.79 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 128.79 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20427 | 127.8 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22277 | 127.8 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29005 | 127.8 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28688 | 127.8 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33482 | 127.8 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30762 | 127.8 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28688 | 127.8 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21204 | 127.8 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33482 | 127.8 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28642 | 127.8 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 126.66 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 126.66 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 126.66 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.66 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.66 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 126.66 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.66 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 126.66 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.66 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 126.66 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 123.84 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 123.84 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 123.84 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 123.84 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 123.84 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 123.84 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 123.84 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 123.84 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 123.84 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 123.84 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20498 | 128.23 | P12:115:SPS-AEPW:KIRBY3:SHAM3WT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22347 | 128.23 | P12:115:SPS-AEPW:KIRBY3:SHAM3WT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29024 | 128.23 | P12:115:SPS-AEPW:KIRBY3:SHAM3WT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28657 | 128.23 | P12:115:SPS-AEPW:KIRBY3:SHAM3WT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33524 | 128.23 | P12:115:SPS-AEPW:KIRBY3:SHAM3WT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30803 | 128.23 | P12:115:SPS-AEPW:KIRBY3:SHAM3WT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28657 | 128.23 | P12:115:SPS-AEPW:KIRBY3:SHAM3WT
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21192 | 128.23 | P12:115:SPS-AEPW:KIRBY3:SHAM3WT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33524 | 128.23 | P12:115:SPS-AEPW:KIRBY3:SHAM3WT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28629 | 128.23 | P12:115:SPS-AEPW:KIRBY3:SHAM3WT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20418 | 127.13 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22267 | 127.13 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28957 | 127.13 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28589 | 127.13 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33459 | 127.13 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30739 | 127.13 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28589 | 127.13 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2125 | 127.13 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33459 | 127.13 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28562 | 127.13 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20552 | 129.31 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22401 | 129.31 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29066 | 129.31 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28699 | 129.31 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33566 | 129.31 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30844 | 129.31 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28699 | 129.31 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21168 | 129.31 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33566 | 129.31 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28672 | 129.31 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21818 | 137.88 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2365 | 137.88 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29898 | 137.88 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29561 | 137.88 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.34375 | 137.88 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31629 | 137.88 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29561 | 137.88 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20935 | 137.88 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.34375 | 137.88 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2953 | 137.88 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21818 | 134.84 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2365 | 134.84 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29898 | 134.84 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29561 | 134.84 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.34375 | 134.84 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31629 | 134.84 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29561 | 134.84 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20935 | 134.84 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.34375 | 134.84 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2953 | 134.84 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20258 | 130.01 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22092 | 130.01 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29127 | 130.01 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28705 | 130.01 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3378 | 130.01 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30992 | 130.01 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28705 | 130.01 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21115 | 130.01 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3378 | 130.01 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28684 | 130.01 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20403 | 127.03 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22253 | 127.03 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28948 | 127.03 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2858 | 127.03 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3345 | 127.03 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3073 | 127.03 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2858 | 127.03 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21244 | 127.03 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3345 | 127.03 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28553 | 127.03 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20924 | 132.66 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2275 | 132.66 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29381 | 132.66 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29015 | 132.66 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33882 | 132.66 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3117 | 132.66 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29015 | 132.66 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21062 | 132.66 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33882 | 132.66 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28988 | 132.66 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.23603 | 175.07 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2524 | 175.07 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31871 | 175.07 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31492 | 175.07 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.36397 | 175.07 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-033 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21277 | 175.07 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3378 | 175.07 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-065 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21277 | 175.07 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31492 | 175.07 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.36397 | 175.07 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31466 | 175.07 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20408 | 126.52 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22258 | 126.52 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28951 | 126.52 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28582 | 126.52 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33452 | 126.52 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30733 | 126.52 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28582 | 126.52 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21247 | 126.52 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33452 | 126.52 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28555 | 126.52 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20151 | 124.16 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21991 | 124.16 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28628 | 124.16 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28263 | 124.16 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33128 | 124.16 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3041 | 124.16 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28263 | 124.16 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21723 | 124.16 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33128 | 124.16 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28235 | 124.16 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20924 | 133.87 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2275 | 133.87 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29381 | 133.87 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29015 | 133.87 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33882 | 133.87 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3117 | 133.87 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29015 | 133.87 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21062 | 133.87 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33882 | 133.87 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28988 | 133.87 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.23603 | 143.55 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2524 | 143.55 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31871 | 143.55 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31492 | 143.55 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.36397 | 143.55 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3378 | 143.55 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31492 | 143.55 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.36397 | 143.55 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31466 | 143.55 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20579 | 130.17 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22425 | 130.17 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29069 | 130.17 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28703 | 130.17 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33568 | 130.17 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30849 | 130.17 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28703 | 130.17 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21239 | 130.17 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33568 | 130.17 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28676 | 130.17 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20579 | 130.17 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22425 | 130.17 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29069 | 130.17 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28703 | 130.17 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33568 | 130.17 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30848 | 130.17 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28703 | 130.17 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21239 | 130.17 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33568 | 130.17 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28676 | 130.17 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20396 | 126.43 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22241 | 126.43 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28902 | 126.43 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28535 | 126.43 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33402 | 126.43 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30683 | 126.43 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28535 | 126.43 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21377 | 126.43 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33402 | 126.43 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28508 | 126.43 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20396 | 126.43 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22241 | 126.43 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28902 | 126.43 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28535 | 126.43 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33402 | 126.43 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30683 | 126.43 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28535 | 126.43 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21377 | 126.43 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33402 | 126.43 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28508 | 126.43 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20826 | 131.92 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22657 | 131.92 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29301 | 131.92 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28935 | 131.92 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33802 | 131.92 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31087 | 131.92 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28935 | 131.92 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21072 | 131.92 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33802 | 131.92 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28908 | 131.92 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20559 | 129.25 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22406 | 129.25 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29057 | 129.25 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28691 | 129.25 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33557 | 129.25 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30837 | 129.25 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28691 | 129.25 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21234 | 129.25 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33557 | 129.25 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28664 | 129.25 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2056 | 129.26 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22406 | 129.26 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29057 | 129.26 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28691 | 129.26 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33557 | 129.26 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30837 | 129.26 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28691 | 129.26 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21234 | 129.26 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33557 | 129.26 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28664 | 129.26 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20189 | 126.04 | P12:345:OKGE:BKRBKR349
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22027 | 126.04 | P12:345:OKGE:BKRBKR349
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28626 | 126.04 | P12:345:OKGE:BKRBKR349
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28263 | 126.04 | P12:345:OKGE:BKRBKR349
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33124 | 126.04 | P12:345:OKGE:BKRBKR349
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30405 | 126.04 | P12:345:OKGE:BKRBKR349
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28263 | 126.04 | P12:345:OKGE:BKRBKR349
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21801 | 126.04 | P12:345:OKGE:BKRBKR349
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33124 | 126.04 | P12:345:OKGE:BKRBKR349
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28235 | 126.04 | P12:345:OKGE:BKRBKR349
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20385 | 127.08 | P12:345:OKGE:BKRBKR357_2
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22234 | 127.08 | P12:345:OKGE:BKRBKR357_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28926 | 127.08 | P12:345:OKGE:BKRBKR357_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28558 | 127.08 | P12:345:OKGE:BKRBKR357_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33428 | 127.08 | P12:345:OKGE:BKRBKR357_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30708 | 127.08 | P12:345:OKGE:BKRBKR357_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28558 | 127.08 | P12:345:OKGE:BKRBKR357_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21273 | 127.08 | P12:345:OKGE:BKRBKR357_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33428 | 127.08 | P12:345:OKGE:BKRBKR357_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28531 | 127.08 | P12:345:OKGE:BKRBKR357_2
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22496 | 142.12 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.24197 | 142.12 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30959 | 142.12 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30575 | 142.12 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.35483 | 142.12 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.32837 | 142.12 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30575 | 142.12 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20097 | 142.12 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.35483 | 142.12 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3055 | 142.12 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20529 | 129.13 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22378 | 129.13 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29069 | 129.13 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28701 | 129.13 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3357 | 129.13 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30851 | 129.13 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28701 | 129.13 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21137 | 129.13 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3357 | 129.13 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28673 | 129.13 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20529 | 129.13 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22378 | 129.13 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29069 | 129.13 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28701 | 129.13 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3357 | 129.13 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30851 | 129.13 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28701 | 129.13 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21137 | 129.13 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3357 | 129.13 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28673 | 129.13 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 125.45 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 125.45 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 125.45 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 125.45 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 125.45 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 125.45 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 125.45 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 125.45 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 125.45 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 125.45 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 125.65 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 125.65 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 125.65 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 125.65 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 125.65 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 125.65 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 125.65 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 125.65 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 125.65 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 125.65 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20408 | 126.52 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22258 | 126.52 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28951 | 126.52 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28582 | 126.52 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33452 | 126.52 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30733 | 126.52 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28582 | 126.52 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21247 | 126.52 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33452 | 126.52 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28555 | 126.52 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20151 | 124.16 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21991 | 124.16 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28628 | 124.16 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28263 | 124.16 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33128 | 124.16 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3041 | 124.16 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28263 | 124.16 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21723 | 124.16 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33128 | 124.16 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28235 | 124.16 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20924 | 133.87 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2275 | 133.87 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29381 | 133.87 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29015 | 133.87 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33882 | 133.87 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3117 | 133.87 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29015 | 133.87 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21062 | 133.87 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33882 | 133.87 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28988 | 133.87 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22496 | 142.15 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.24197 | 142.15 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30959 | 142.15 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30575 | 142.15 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.35483 | 142.15 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.32837 | 142.15 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30575 | 142.15 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20097 | 142.15 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.35483 | 142.15 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3055 | 142.15 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20504 | 129.22 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22354 | 129.22 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29042 | 129.22 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28674 | 129.22 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33544 | 129.22 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30824 | 129.22 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28674 | 129.22 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21165 | 129.22 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33544 | 129.22 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28647 | 129.22 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20504 | 129.22 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22354 | 129.22 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29042 | 129.22 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28674 | 129.22 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33544 | 129.22 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30824 | 129.22 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28674 | 129.22 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21165 | 129.22 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33544 | 129.22 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28647 | 129.22 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20978 | 132.27 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2283 | 132.27 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29437 | 132.27 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29075 | 132.27 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33934 | 132.27 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3121 | 132.27 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29075 | 132.27 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20895 | 132.27 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33934 | 132.27 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29047 | 132.27 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.25624 | 136.14 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.27211 | 136.14 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.35957 | 136.14 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.35442 | 136.14 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.37989 | 136.14 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.36735 | 136.14 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.35442 | 136.14 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28553 | 136.14 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.37989 | 136.14 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.35482 | 136.14 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20SP | GEN-2017-104 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29638 | 136.14 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2053 | 128.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1)
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22381 | 128.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29048 | 128.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28682 | 128.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33548 | 128.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30827 | 128.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28682 | 128.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21185 | 128.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33548 | 128.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28654 | 128.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1)
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20573 | 129.13 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22423 | 129.13 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29107 | 129.13 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28739 | 129.13 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33608 | 129.13 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30888 | 129.13 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28739 | 129.13 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21103 | 129.13 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33608 | 129.13 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28712 | 129.13 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20537 | 128.96 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22387 | 128.96 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29075 | 128.96 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28707 | 128.96 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33576 | 128.96 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30856 | 128.96 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28707 | 128.96 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21128 | 128.96 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33576 | 128.96 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2868 | 128.96 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20536 | 129.58 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22387 | 129.58 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29053 | 129.58 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28686 | 129.58 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33553 | 129.58 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30831 | 129.58 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28686 | 129.58 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21183 | 129.58 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33553 | 129.58 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28659 | 129.58 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20583 | 129.07 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22433 | 129.07 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29117 | 129.07 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28749 | 129.07 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33618 | 129.07 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30898 | 129.07 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28749 | 129.07 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21093 | 129.07 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33618 | 129.07 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28722 | 129.07 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.13 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.13 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.13 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.13 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.13 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.13 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.13 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.13 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.13 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.13 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.72 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.72 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.72 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.72 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.72 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.72 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.72 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.72 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.72 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.72 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20552 | 129.29 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22401 | 129.29 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29066 | 129.29 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28699 | 129.29 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33566 | 129.29 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30844 | 129.29 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28699 | 129.29 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21168 | 129.29 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33566 | 129.29 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28672 | 129.29 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 128.1 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 128.1 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 128.1 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 128.1 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 128.1 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 128.1 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 128.1 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 128.1 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 128.1 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 128.1 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.95 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.95 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.95 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.95 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.95 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.95 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.95 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.95 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.95 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.95 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.96 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.96 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.96 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.96 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.96 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.96 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.96 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.96 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.96 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.96 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.95 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.95 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.95 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.95 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.95 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.95 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.95 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.95 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.95 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.95 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.96 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.96 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.96 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.96 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.96 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.96 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.96 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.96 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.96 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.96 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 126.99 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 126.99 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 126.99 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.99 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.99 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 126.99 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.99 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 126.99 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.99 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 126.99 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.96 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.96 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.96 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.96 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.96 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.96 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.96 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.96 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.96 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.96 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.95 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.95 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.95 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.95 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.95 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.95 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.95 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.95 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.95 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.95 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 126.55 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 126.55 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 126.55 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.55 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.55 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 126.55 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.55 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 126.55 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.55 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 126.55 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.96 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.96 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.96 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.96 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.96 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.96 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.96 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.96 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.96 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.96 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.95 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.95 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.95 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.95 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.95 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.95 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.95 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.95 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.95 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.95 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.95 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.95 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.95 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.95 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.95 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.95 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.95 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.95 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.95 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.95 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.95 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.95 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.95 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.95 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.95 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.95 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.95 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.95 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.95 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.95 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.95 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.95 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.95 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.95 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.95 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.95 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.95 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.95 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.95 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.95 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.25624 | 136.15 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.27211 | 136.15 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.35957 | 136.15 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.35442 | 136.15 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.37989 | 136.15 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.36735 | 136.15 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.35442 | 136.15 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28553 | 136.15 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.37989 | 136.15 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.35482 | 136.15 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-104 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29638 | 136.15 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20413 | 126.86 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22263 | 126.86 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2896 | 126.86 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28591 | 126.86 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33462 | 126.86 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30742 | 126.86 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28591 | 126.86 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21228 | 126.86 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33462 | 126.86 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28564 | 126.86 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20413 | 126.89 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22263 | 126.89 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2896 | 126.89 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28591 | 126.89 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33462 | 126.89 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30742 | 126.89 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28591 | 126.89 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21228 | 126.89 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33462 | 126.89 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28564 | 126.89 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20413 | 126.86 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22263 | 126.86 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2896 | 126.86 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28591 | 126.86 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33462 | 126.86 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30742 | 126.86 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28591 | 126.86 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21228 | 126.86 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33462 | 126.86 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28564 | 126.86 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20402 | 127.08 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22252 | 127.08 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28947 | 127.08 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28578 | 127.08 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33448 | 127.08 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30729 | 127.08 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28578 | 127.08 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21246 | 127.08 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33448 | 127.08 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28551 | 127.08 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20402 | 127.08 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22252 | 127.08 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28947 | 127.08 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28578 | 127.08 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33448 | 127.08 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30729 | 127.08 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28578 | 127.08 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21246 | 127.08 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33448 | 127.08 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28551 | 127.08 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20402 | 127.08 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22252 | 127.08 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28947 | 127.08 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28578 | 127.08 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33448 | 127.08 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30729 | 127.08 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28578 | 127.08 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21246 | 127.08 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33448 | 127.08 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28551 | 127.08 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20936 | 133 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22761 | 133 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29392 | 133 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29026 | 133 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33893 | 133 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31181 | 133 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29026 | 133 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21057 | 133 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33893 | 133 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28999 | 133 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.23604 | 175.03 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.25241 | 175.03 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31872 | 175.03 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31493 | 175.03 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.36398 | 175.03 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-033 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21278 | 175.03 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33781 | 175.03 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-065 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21278 | 175.03 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31493 | 175.03 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.36398 | 175.03 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31467 | 175.03 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.23719 | 175.5 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.25352 | 175.5 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31952 | 175.5 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31575 | 175.5 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.36476 | 175.5 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-033 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21372 | 175.5 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33859 | 175.5 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-065 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21372 | 175.5 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31575 | 175.5 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.36476 | 175.5 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31548 | 175.5 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20403 | 127.03 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22253 | 127.03 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28948 | 127.03 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2858 | 127.03 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3345 | 127.03 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3073 | 127.03 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2858 | 127.03 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21244 | 127.03 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3345 | 127.03 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28553 | 127.03 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.23603 | 143.55 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2524 | 143.55 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31871 | 143.55 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31492 | 143.55 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.36397 | 143.55 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3378 | 143.55 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31492 | 143.55 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.36397 | 143.55 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31466 | 143.55 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.23603 | 142.95 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2524 | 142.95 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31871 | 142.95 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31492 | 142.95 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.36397 | 142.95 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3378 | 142.95 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31492 | 142.95 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.36397 | 142.95 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31466 | 142.95 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20246 | 126.46 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22094 | 126.46 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28775 | 126.46 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28408 | 126.46 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33276 | 126.46 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30557 | 126.46 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28408 | 126.46 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21451 | 126.46 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33276 | 126.46 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28381 | 126.46 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20363 | 126.69 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22203 | 126.69 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28862 | 126.69 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28495 | 126.69 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33363 | 126.69 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30646 | 126.69 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28495 | 126.69 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21446 | 126.69 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33363 | 126.69 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28468 | 126.69 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20177 | 124.37 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22014 | 124.37 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28646 | 124.37 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28281 | 124.37 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33146 | 124.37 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30429 | 124.37 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28281 | 124.37 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21728 | 124.37 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33146 | 124.37 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28253 | 124.37 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20151 | 124.16 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21991 | 124.16 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28628 | 124.16 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28263 | 124.16 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33128 | 124.16 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3041 | 124.16 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28263 | 124.16 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21723 | 124.16 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33128 | 124.16 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28235 | 124.16 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20924 | 132.84 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2275 | 132.84 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29381 | 132.84 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29015 | 132.84 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33882 | 132.84 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3117 | 132.84 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29015 | 132.84 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21062 | 132.84 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33882 | 132.84 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28988 | 132.84 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20924 | 132.84 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2275 | 132.84 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29381 | 132.84 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29015 | 132.84 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33882 | 132.84 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3117 | 132.84 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29015 | 132.84 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21062 | 132.84 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33882 | 132.84 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28988 | 132.84 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20924 | 132.8 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2275 | 132.8 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29381 | 132.8 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29015 | 132.8 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33882 | 132.8 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3117 | 132.8 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29015 | 132.8 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21062 | 132.8 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33882 | 132.8 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28988 | 132.8 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20467 | 128.99 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22317 | 128.99 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29014 | 128.99 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28645 | 128.99 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33516 | 128.99 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30796 | 128.99 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28645 | 128.99 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21176 | 128.99 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33516 | 128.99 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28618 | 128.99 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.98 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.98 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.98 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28609 | 127.98 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.98 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3076 | 127.98 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28609 | 127.98 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.98 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.98 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28582 | 127.98 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.96 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.96 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.96 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.96 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.96 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.96 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.96 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.96 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.96 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.96 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 126.55 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 126.55 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 126.55 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.55 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.55 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 126.55 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.55 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 126.55 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.55 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 126.55 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.95 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.95 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.95 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.95 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.95 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.95 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.95 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.95 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.95 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.95 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.95 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.95 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.95 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.95 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.95 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.95 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.95 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.95 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.95 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.95 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.95 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.95 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.95 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.95 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.95 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.95 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.95 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.95 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.95 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.95 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.95 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.95 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.95 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.95 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.95 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.95 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.95 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.95 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.95 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.95 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2053 | 129.04 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22381 | 129.04 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29048 | 129.04 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28682 | 129.04 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33548 | 129.04 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30827 | 129.04 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28682 | 129.04 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21185 | 129.04 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33548 | 129.04 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28654 | 129.04 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2053 | 128.67 | P23:345:SUNC:HLC_BRK182
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22381 | 128.67 | P23:345:SUNC:HLC_BRK182
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29048 | 128.67 | P23:345:SUNC:HLC_BRK182
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28682 | 128.67 | P23:345:SUNC:HLC_BRK182
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33548 | 128.67 | P23:345:SUNC:HLC_BRK182
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30827 | 128.67 | P23:345:SUNC:HLC_BRK182
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28682 | 128.67 | P23:345:SUNC:HLC_BRK182
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21185 | 128.67 | P23:345:SUNC:HLC_BRK182
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33548 | 128.67 | P23:345:SUNC:HLC_BRK182
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28654 | 128.67 | P23:345:SUNC:HLC_BRK182
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20965 | 132.23 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22817 | 132.23 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29422 | 132.23 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2906 | 132.23 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33919 | 132.23 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31195 | 132.23 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2906 | 132.23 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20913 | 132.23 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33919 | 132.23 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29032 | 132.23 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21004 | 132.45 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22856 | 132.45 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29462 | 132.45 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29099 | 132.45 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33958 | 132.45 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31234 | 132.45 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29099 | 132.45 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20874 | 132.45 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33958 | 132.45 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29071 | 132.45 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20545 | 128.97 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22396 | 128.97 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29083 | 128.97 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28715 | 128.97 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33584 | 128.97 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30864 | 128.97 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28715 | 128.97 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21121 | 128.97 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33584 | 128.97 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28688 | 128.97 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20573 | 129.13 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22423 | 129.13 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29107 | 129.13 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28739 | 129.13 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33608 | 129.13 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30888 | 129.13 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28739 | 129.13 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21103 | 129.13 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33608 | 129.13 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28712 | 129.13 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20583 | 129.07 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22433 | 129.07 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29117 | 129.07 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28749 | 129.07 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33618 | 129.07 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30898 | 129.07 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28749 | 129.07 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21093 | 129.07 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33618 | 129.07 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28722 | 129.07 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20573 | 129.13 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22423 | 129.13 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29107 | 129.13 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28739 | 129.13 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33608 | 129.13 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30888 | 129.13 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28739 | 129.13 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21103 | 129.13 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33608 | 129.13 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28712 | 129.13 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20583 | 129.07 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22433 | 129.07 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29117 | 129.07 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28749 | 129.07 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33618 | 129.07 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30898 | 129.07 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28749 | 129.07 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21093 | 129.07 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33618 | 129.07 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28722 | 129.07 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20579 | 129.24 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2243 | 129.24 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29113 | 129.24 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28745 | 129.24 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33614 | 129.24 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30894 | 129.24 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28745 | 129.24 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21098 | 129.24 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33614 | 129.24 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28718 | 129.24 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20579 | 129.22 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2243 | 129.22 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29113 | 129.22 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28745 | 129.22 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33614 | 129.22 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30894 | 129.22 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28745 | 129.22 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21098 | 129.22 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33614 | 129.22 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28718 | 129.22 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20579 | 129.25 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2243 | 129.25 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29113 | 129.25 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28745 | 129.25 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33614 | 129.25 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30894 | 129.25 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28745 | 129.25 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21098 | 129.25 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33614 | 129.25 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28718 | 129.25 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20529 | 129.41 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2238 | 129.41 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29047 | 129.41 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28681 | 129.41 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33547 | 129.41 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30826 | 129.41 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28681 | 129.41 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21186 | 129.41 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33547 | 129.41 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28654 | 129.41 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20514 | 129.4 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22363 | 129.4 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2905 | 129.4 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28682 | 129.4 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33552 | 129.4 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30832 | 129.4 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28682 | 129.4 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2116 | 129.4 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33552 | 129.4 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28655 | 129.4 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20514 | 129.4 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22363 | 129.4 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2905 | 129.4 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28682 | 129.4 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33552 | 129.4 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30832 | 129.4 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28682 | 129.4 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2116 | 129.4 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33552 | 129.4 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28655 | 129.4 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.85 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.85 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.85 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.85 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.85 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.85 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.85 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.85 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.85 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.85 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.85 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.85 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.85 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.85 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.85 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.85 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.85 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.85 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.85 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.85 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2043 | 127.85 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2228 | 127.85 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28979 | 127.85 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28611 | 127.85 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33481 | 127.85 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30762 | 127.85 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28611 | 127.85 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21204 | 127.85 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33481 | 127.85 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28584 | 127.85 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.97 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.97 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.97 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.97 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.97 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.97 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.97 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.97 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.97 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.97 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 126.99 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 126.99 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 126.99 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.99 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.99 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 126.99 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.99 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 126.99 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.99 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28582 | 126.99 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.96 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.96 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.96 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.96 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.96 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.96 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.96 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.96 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.96 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.96 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.95 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.95 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.95 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.95 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.95 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.95 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.95 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.95 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.95 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.95 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20417 | 126.57 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22267 | 126.57 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28965 | 126.57 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28596 | 126.57 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33467 | 126.57 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30747 | 126.57 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28596 | 126.57 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21221 | 126.57 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33467 | 126.57 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28569 | 126.57 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20416 | 126.47 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22266 | 126.47 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28964 | 126.47 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28595 | 126.47 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33466 | 126.47 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30746 | 126.47 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28595 | 126.47 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21222 | 126.47 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33466 | 126.47 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28568 | 126.47 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20411 | 127.93 | P41:345:OKGE:SB_SEOL7382
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22259 | 127.93 | P41:345:OKGE:SB_SEOL7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28937 | 127.93 | P41:345:OKGE:SB_SEOL7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2857 | 127.93 | P41:345:OKGE:SB_SEOL7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33438 | 127.93 | P41:345:OKGE:SB_SEOL7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30719 | 127.93 | P41:345:OKGE:SB_SEOL7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2857 | 127.93 | P41:345:OKGE:SB_SEOL7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21297 | 127.93 | P41:345:OKGE:SB_SEOL7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33438 | 127.93 | P41:345:OKGE:SB_SEOL7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28543 | 127.93 | P41:345:OKGE:SB_SEOL7382
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20396 | 127.38 | P41:345:OKGE:SB_SEOL7383
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22241 | 127.38 | P41:345:OKGE:SB_SEOL7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28902 | 127.38 | P41:345:OKGE:SB_SEOL7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28535 | 127.38 | P41:345:OKGE:SB_SEOL7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33402 | 127.38 | P41:345:OKGE:SB_SEOL7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30683 | 127.38 | P41:345:OKGE:SB_SEOL7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28535 | 127.38 | P41:345:OKGE:SB_SEOL7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21377 | 127.38 | P41:345:OKGE:SB_SEOL7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33402 | 127.38 | P41:345:OKGE:SB_SEOL7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28508 | 127.38 | P41:345:OKGE:SB_SEOL7383
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20413 | 126.89 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22263 | 126.89 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2896 | 126.89 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28591 | 126.89 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33462 | 126.89 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30742 | 126.89 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28591 | 126.89 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21228 | 126.89 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33462 | 126.89 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28564 | 126.89 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20413 | 126.86 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22263 | 126.86 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2896 | 126.86 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28591 | 126.86 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33462 | 126.86 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30742 | 126.86 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28591 | 126.86 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21228 | 126.86 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33462 | 126.86 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28564 | 126.86 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20402 | 127.08 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22252 | 127.08 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28947 | 127.08 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28578 | 127.08 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33448 | 127.08 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30729 | 127.08 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28578 | 127.08 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21246 | 127.08 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33448 | 127.08 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28551 | 127.08 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20402 | 127.08 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22252 | 127.08 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28947 | 127.08 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28578 | 127.08 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33448 | 127.08 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30729 | 127.08 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28578 | 127.08 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21246 | 127.08 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33448 | 127.08 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28551 | 127.08 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20402 | 127.08 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22252 | 127.08 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28947 | 127.08 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28578 | 127.08 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33448 | 127.08 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30729 | 127.08 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28578 | 127.08 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21246 | 127.08 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33448 | 127.08 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28551 | 127.08 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20936 | 133 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22761 | 133 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29392 | 133 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29026 | 133 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33893 | 133 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31181 | 133 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29026 | 133 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21057 | 133 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33893 | 133 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28999 | 133 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.23719 | 175.5 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.25352 | 175.5 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31952 | 175.5 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31575 | 175.5 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.36476 | 175.5 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-033 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21372 | 175.5 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33859 | 175.5 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-065 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21372 | 175.5 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31575 | 175.5 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.36476 | 175.5 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31548 | 175.5 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20403 | 127.03 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22253 | 127.03 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28948 | 127.03 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2858 | 127.03 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3345 | 127.03 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3073 | 127.03 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2858 | 127.03 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21244 | 127.03 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3345 | 127.03 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28553 | 127.03 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.23603 | 143.55 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2524 | 143.55 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31871 | 143.55 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31492 | 143.55 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.36397 | 143.55 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3378 | 143.55 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31492 | 143.55 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.36397 | 143.55 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31466 | 143.55 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.23603 | 142.95 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2524 | 142.95 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31871 | 142.95 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31492 | 142.95 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.36397 | 142.95 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3378 | 142.95 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31492 | 142.95 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.36397 | 142.95 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31466 | 142.95 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20246 | 126.46 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22094 | 126.46 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28775 | 126.46 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28408 | 126.46 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33276 | 126.46 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30557 | 126.46 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28408 | 126.46 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21451 | 126.46 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33276 | 126.46 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28381 | 126.46 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20363 | 126.69 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22203 | 126.69 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28862 | 126.69 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28495 | 126.69 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33363 | 126.69 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30646 | 126.69 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28495 | 126.69 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21446 | 126.69 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33363 | 126.69 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28468 | 126.69 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20177 | 124.37 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22014 | 124.37 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28646 | 124.37 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28281 | 124.37 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33146 | 124.37 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30429 | 124.37 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28281 | 124.37 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21728 | 124.37 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33146 | 124.37 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28253 | 124.37 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20151 | 124.16 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21991 | 124.16 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28628 | 124.16 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28263 | 124.16 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33128 | 124.16 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3041 | 124.16 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28263 | 124.16 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21723 | 124.16 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33128 | 124.16 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28235 | 124.16 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20924 | 132.84 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2275 | 132.84 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29381 | 132.84 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29015 | 132.84 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33882 | 132.84 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3117 | 132.84 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29015 | 132.84 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21062 | 132.84 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33882 | 132.84 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28988 | 132.84 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20924 | 132.84 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2275 | 132.84 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29381 | 132.84 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29015 | 132.84 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33882 | 132.84 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3117 | 132.84 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29015 | 132.84 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21062 | 132.84 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33882 | 132.84 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28988 | 132.84 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20924 | 132.8 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2275 | 132.8 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29381 | 132.8 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29015 | 132.8 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33882 | 132.8 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3117 | 132.8 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29015 | 132.8 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21062 | 132.8 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33882 | 132.8 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28988 | 132.8 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.34 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.34 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28979 | 127.34 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.34 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33481 | 127.34 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.34 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.34 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21204 | 127.34 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33481 | 127.34 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.34 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20593 | 129.18 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22444 | 129.18 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29127 | 129.18 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2876 | 129.18 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33628 | 129.18 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30908 | 129.18 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2876 | 129.18 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21084 | 129.18 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33628 | 129.18 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28732 | 129.18 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20448 | 128.8 | P42:345:NPPD:BKR-SW-3308
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22298 | 128.8 | P42:345:NPPD:BKR-SW-3308
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28995 | 128.8 | P42:345:NPPD:BKR-SW-3308
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28627 | 128.8 | P42:345:NPPD:BKR-SW-3308
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33497 | 128.8 | P42:345:NPPD:BKR-SW-3308
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30777 | 128.8 | P42:345:NPPD:BKR-SW-3308
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28627 | 128.8 | P42:345:NPPD:BKR-SW-3308
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21192 | 128.8 | P42:345:NPPD:BKR-SW-3308
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33497 | 128.8 | P42:345:NPPD:BKR-SW-3308
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.286 | 128.8 | P42:345:NPPD:BKR-SW-3308
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2019 | 126.02 | P42:345:OKGE:SB_ARIA7381
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22028 | 126.02 | P42:345:OKGE:SB_ARIA7381
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28627 | 126.02 | P42:345:OKGE:SB_ARIA7381
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28264 | 126.02 | P42:345:OKGE:SB_ARIA7381
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33125 | 126.02 | P42:345:OKGE:SB_ARIA7381
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30406 | 126.02 | P42:345:OKGE:SB_ARIA7381
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28264 | 126.02 | P42:345:OKGE:SB_ARIA7381
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.218 | 126.02 | P42:345:OKGE:SB_ARIA7381
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33125 | 126.02 | P42:345:OKGE:SB_ARIA7381
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28236 | 126.02 | P42:345:OKGE:SB_ARIA7381
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22331 | 146.14 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.24224 | 146.14 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30243 | 146.14 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29924 | 146.14 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.34706 | 146.14 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31941 | 146.14 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29924 | 146.14 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20858 | 146.14 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.34706 | 146.14 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2989 | 146.14 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22496 | 142.15 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.24197 | 142.15 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30959 | 142.15 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30575 | 142.15 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.35483 | 142.15 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.32837 | 142.15 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30575 | 142.15 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20097 | 142.15 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.35483 | 142.15 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3055 | 142.15 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22496 | 142.12 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.24197 | 142.12 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30959 | 142.12 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30575 | 142.12 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.35483 | 142.12 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.32837 | 142.12 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30575 | 142.12 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20097 | 142.12 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.35483 | 142.12 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3055 | 142.12 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22496 | 142.15 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.24197 | 142.15 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30959 | 142.15 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30575 | 142.15 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.35483 | 142.15 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.32837 | 142.15 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30575 | 142.15 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20097 | 142.15 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.35483 | 142.15 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3055 | 142.15 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20527 | 126.34 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22379 | 126.34 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29044 | 126.34 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28677 | 126.34 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33543 | 126.34 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30822 | 126.34 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28677 | 126.34 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21187 | 126.34 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33543 | 126.34 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2865 | 126.34 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20527 | 126.15 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2238 | 126.15 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29044 | 126.15 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28678 | 126.15 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33544 | 126.15 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30822 | 126.15 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28678 | 126.15 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21187 | 126.15 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33544 | 126.15 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2865 | 126.15 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20826 | 131.06 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22657 | 131.06 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29301 | 131.06 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28935 | 131.06 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33802 | 131.06 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31087 | 131.06 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28935 | 131.06 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21072 | 131.06 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33802 | 131.06 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28908 | 131.06 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20391 | 126.13 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22236 | 126.13 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28894 | 126.13 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28528 | 126.13 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33394 | 126.13 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30675 | 126.13 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28528 | 126.13 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21391 | 126.13 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33394 | 126.13 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.285 | 126.13 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20391 | 126.09 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22236 | 126.09 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28894 | 126.09 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28528 | 126.09 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33394 | 126.09 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30675 | 126.09 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28528 | 126.09 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21391 | 126.09 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33394 | 126.09 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.285 | 126.09 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20826 | 131.38 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22657 | 131.38 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29301 | 131.38 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28935 | 131.38 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33802 | 131.38 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31087 | 131.38 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28935 | 131.38 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21072 | 131.38 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33802 | 131.38 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28908 | 131.38 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20826 | 130.55 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22657 | 130.55 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29301 | 130.55 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28935 | 130.55 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33802 | 130.55 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31087 | 130.55 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28935 | 130.55 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21072 | 130.55 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33802 | 130.55 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28908 | 130.55 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20405 | 126.24 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22255 | 126.24 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28946 | 126.24 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28578 | 126.24 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33448 | 126.24 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30728 | 126.24 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28578 | 126.24 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21254 | 126.24 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33448 | 126.24 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28551 | 126.24 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20385 | 126.37 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22234 | 126.37 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28926 | 126.37 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28558 | 126.37 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33428 | 126.37 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30708 | 126.37 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28558 | 126.37 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21273 | 126.37 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33428 | 126.37 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28531 | 126.37 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20385 | 126.87 | P42:345:OKGE:SB_RARD7311
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22234 | 126.87 | P42:345:OKGE:SB_RARD7311
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28926 | 126.87 | P42:345:OKGE:SB_RARD7311
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28558 | 126.87 | P42:345:OKGE:SB_RARD7311
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33428 | 126.87 | P42:345:OKGE:SB_RARD7311
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30708 | 126.87 | P42:345:OKGE:SB_RARD7311
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28558 | 126.87 | P42:345:OKGE:SB_RARD7311
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21273 | 126.87 | P42:345:OKGE:SB_RARD7311
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33428 | 126.87 | P42:345:OKGE:SB_RARD7311
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28531 | 126.87 | P42:345:OKGE:SB_RARD7311
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20385 | 127.08 | P42:345:OKGE:SB_RARD7393
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22234 | 127.08 | P42:345:OKGE:SB_RARD7393
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28926 | 127.08 | P42:345:OKGE:SB_RARD7393
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28558 | 127.08 | P42:345:OKGE:SB_RARD7393
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33428 | 127.08 | P42:345:OKGE:SB_RARD7393
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30708 | 127.08 | P42:345:OKGE:SB_RARD7393
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28558 | 127.08 | P42:345:OKGE:SB_RARD7393
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21273 | 127.08 | P42:345:OKGE:SB_RARD7393
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33428 | 127.08 | P42:345:OKGE:SB_RARD7393
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28531 | 127.08 | P42:345:OKGE:SB_RARD7393
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20381 | 126.56 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22231 | 126.56 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28922 | 126.56 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28553 | 126.56 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33423 | 126.56 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30703 | 126.56 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28553 | 126.56 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21279 | 126.56 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33423 | 126.56 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28526 | 126.56 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20376 | 127.02 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22226 | 127.02 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28916 | 127.02 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28547 | 127.02 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33417 | 127.02 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30697 | 127.02 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28547 | 127.02 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21286 | 127.02 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33417 | 127.02 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2852 | 127.02 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2012 | 123.88 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2195 | 123.88 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28489 | 123.88 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2813 | 123.88 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.32985 | 123.88 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30268 | 123.88 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2813 | 123.88 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22085 | 123.88 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.32985 | 123.88 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28102 | 123.88 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20088 | 123.04 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21925 | 123.04 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28542 | 123.04 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28178 | 123.04 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33041 | 123.04 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30324 | 123.04 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28178 | 123.04 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21861 | 123.04 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33041 | 123.04 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2815 | 123.04 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20579 | 129.39 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22425 | 129.39 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29069 | 129.39 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28703 | 129.39 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33568 | 129.39 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30849 | 129.39 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28703 | 129.39 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21239 | 129.39 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33568 | 129.39 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28676 | 129.39 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2038 | 127.14 | P42:345:OKGE:SB_WONG7383
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2223 | 127.14 | P42:345:OKGE:SB_WONG7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2892 | 127.14 | P42:345:OKGE:SB_WONG7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28552 | 127.14 | P42:345:OKGE:SB_WONG7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33421 | 127.14 | P42:345:OKGE:SB_WONG7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30701 | 127.14 | P42:345:OKGE:SB_WONG7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28552 | 127.14 | P42:345:OKGE:SB_WONG7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21283 | 127.14 | P42:345:OKGE:SB_WONG7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33421 | 127.14 | P42:345:OKGE:SB_WONG7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28524 | 127.14 | P42:345:OKGE:SB_WONG7383
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20568 | 129.27 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22415 | 129.27 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29064 | 129.27 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28698 | 129.27 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33563 | 129.27 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30844 | 129.27 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28698 | 129.27 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21233 | 129.27 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33563 | 129.27 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28671 | 129.27 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20568 | 129.28 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22415 | 129.28 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29064 | 129.28 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28698 | 129.28 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33563 | 129.28 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30844 | 129.28 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28698 | 129.28 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21233 | 129.28 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33563 | 129.28 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28671 | 129.28 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20978 | 135.61 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2283 | 135.61 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29437 | 135.61 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29075 | 135.61 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33934 | 135.61 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3121 | 135.61 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29075 | 135.61 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20895 | 135.61 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33934 | 135.61 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29047 | 135.61 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22283 | 139.28 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.24183 | 139.28 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30366 | 139.28 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30035 | 139.28 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.34839 | 139.28 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.32087 | 139.28 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30035 | 139.28 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20552 | 139.28 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.34839 | 139.28 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30003 | 139.28 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20431 | 127.21 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22281 | 127.21 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2898 | 127.21 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28611 | 127.21 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33482 | 127.21 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30762 | 127.21 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28611 | 127.21 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21203 | 127.21 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33482 | 127.21 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28584 | 127.21 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20413 | 126.86 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22263 | 126.86 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.2896 | 126.86 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28591 | 126.86 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33462 | 126.86 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30742 | 126.86 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28591 | 126.86 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21228 | 126.86 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33462 | 126.86 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28564 | 126.86 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.23604 | 175.03 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.25241 | 175.03 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31872 | 175.03 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31493 | 175.03 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.36398 | 175.03 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-033 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21278 | 175.03 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33781 | 175.03 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-065 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21278 | 175.03 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31493 | 175.03 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.36398 | 175.03 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.31467 | 175.03 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20467 | 128.99 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22317 | 128.99 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.29014 | 128.99 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28645 | 128.99 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33516 | 128.99 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30796 | 128.99 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28645 | 128.99 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21176 | 128.99 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33516 | 128.99 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28618 | 128.99 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22496 | 142.15 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.24197 | 142.15 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30959 | 142.15 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30575 | 142.15 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.35483 | 142.15 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.32837 | 142.15 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.30575 | 142.15 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20097 | 142.15 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.35483 | 142.15 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3055 | 142.15 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.20428 | 127.12 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.22278 | 127.12 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.12 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28609 | 127.12 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33479 | 127.12 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.3076 | 127.12 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28609 | 127.12 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.12 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.33479 | 127.12 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 |  | 553 | 0.28582 | 127.12 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 | 478 |  | 0.20429 | 148.08 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 | 478 |  | 0.22279 | 148.08 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 | 478 |  | 0.28978 | 148.08 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 | 478 |  | 0.2861 | 148.08 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 | 478 |  | 0.3348 | 148.08 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 | 478 |  | 0.30761 | 148.08 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 | 478 |  | 0.2861 | 148.08 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 | 478 |  | 0.21205 | 148.08 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 | 478 |  | 0.3348 | 148.08 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 | 478 |  | 0.28583 | 148.08 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998088 TOLK2 230 2 |  | 553 | 0.21079 | 100.51 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998088 TOLK2 230 2 |  | 553 | 0.21079 | 100.51 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525531 TOLK 6 230 998088 TOLK2 230 2 | 478 |  | 0.06831 | 101.35 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-172 | 'FROM -> TO' | 525531 TOLK 6 230 998088 TOLK2 230 2 | 478 |  | 0.09467 | 101.35 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998088 TOLK2 230 2 | 478 |  | 0.17368 | 101.35 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998088 TOLK2 230 2 | 478 |  | 0.16977 | 101.35 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998088 TOLK2 230 2 | 478 |  | 0.20698 | 101.35 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998088 TOLK2 230 2 | 478 |  | 0.1825 | 101.35 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998088 TOLK2 230 2 | 478 |  | 0.16977 | 101.35 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998088 TOLK2 230 2 | 478 |  | 0.07567 | 101.35 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998088 TOLK2 230 2 | 478 |  | 0.20698 | 101.35 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998088 TOLK2 230 2 | 478 |  | 0.16975 | 101.35 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.22066 | 108.7 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21633 | 108.7 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26567 | 108.7 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.23257 | 108.7 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21633 | 108.7 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26567 | 108.7 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21615 | 108.7 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.22066 | 107.34 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21633 | 107.34 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26567 | 107.34 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.23257 | 107.34 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21633 | 107.34 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26567 | 107.34 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21615 | 107.34 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.2177 | 106.26 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21297 | 106.26 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26239 | 106.26 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.23045 | 106.26 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21297 | 106.26 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26239 | 106.26 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21301 | 106.26 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.22387 | 107.01 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.22169 | 107.01 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26384 | 107.01 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.23184 | 107.01 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.22169 | 107.01 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26384 | 107.01 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.22128 | 107.01 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21961 | 108.06 | P12:115:SPS:V08.1.TUCO.HALECTR
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21539 | 108.06 | P12:115:SPS:V08.1.TUCO.HALECTR
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26397 | 108.06 | P12:115:SPS:V08.1.TUCO.HALECTR
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.2317 | 108.06 | P12:115:SPS:V08.1.TUCO.HALECTR
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21539 | 108.06 | P12:115:SPS:V08.1.TUCO.HALECTR
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26397 | 108.06 | P12:115:SPS:V08.1.TUCO.HALECTR
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21521 | 108.06 | P12:115:SPS:V08.1.TUCO.HALECTR
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.22017 | 107.53 | P12:115:SPS:V09.1.HALECTR.PLANTX
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21594 | 107.53 | P12:115:SPS:V09.1.HALECTR.PLANTX
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26444 | 107.53 | P12:115:SPS:V09.1.HALECTR.PLANTX
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.2323 | 107.53 | P12:115:SPS:V09.1.HALECTR.PLANTX
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21594 | 107.53 | P12:115:SPS:V09.1.HALECTR.PLANTX
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26444 | 107.53 | P12:115:SPS:V09.1.HALECTR.PLANTX
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21577 | 107.53 | P12:115:SPS:V09.1.HALECTR.PLANTX
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21837 | 106.24 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21388 | 106.24 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26324 | 106.24 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.23097 | 106.24 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21388 | 106.24 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26324 | 106.24 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21373 | 106.24 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.22027 | 107.02 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21605 | 107.02 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26443 | 107.02 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.2324 | 107.02 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21605 | 107.02 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26443 | 107.02 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21588 | 107.02 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21767 | 107.52 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26238 | 107.52 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.23044 | 107.52 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26238 | 107.52 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21301 | 107.52 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21802 | 106.42 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21417 | 106.42 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.2624 | 106.42 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.23046 | 106.42 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21417 | 106.42 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.2624 | 106.42 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21379 | 106.42 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.22163 | 114.88 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21731 | 114.88 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26617 | 114.88 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.23401 | 114.88 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21731 | 114.88 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26617 | 114.88 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21714 | 114.88 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.22163 | 112.8 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21731 | 112.8 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26617 | 112.8 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.23401 | 112.8 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21731 | 112.8 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26617 | 112.8 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21714 | 112.8 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.22002 | 108.64 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21483 | 108.64 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26663 | 108.64 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.23385 | 108.64 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21483 | 108.64 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26663 | 108.64 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21476 | 108.64 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21599 | 104 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21149 | 104 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26067 | 104 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.2287 | 104 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21149 | 104 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26067 | 104 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21135 | 104 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21675 | 105.02 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21223 | 105.02 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26144 | 105.02 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.22949 | 105.02 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21223 | 105.02 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26144 | 105.02 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21209 | 105.02 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21797 | 107.46 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21345 | 107.46 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26267 | 107.46 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.23073 | 107.46 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21345 | 107.46 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26267 | 107.46 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21331 | 107.46 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21783 | 107.5 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21332 | 107.5 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26252 | 107.5 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.23057 | 107.5 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21332 | 107.5 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26252 | 107.5 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21318 | 107.5 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21783 | 107.5 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21332 | 107.5 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26252 | 107.5 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.23057 | 107.5 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21332 | 107.5 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26252 | 107.5 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21318 | 107.5 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21492 | 104.97 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21045 | 104.97 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.25958 | 104.97 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.22758 | 104.97 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21045 | 104.97 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.25958 | 104.97 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.2103 | 104.97 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21767 | 105.35 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21315 | 105.35 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26238 | 105.35 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.23044 | 105.35 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21315 | 105.35 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26238 | 105.35 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21301 | 105.35 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21767 | 105.27 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21315 | 105.27 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26238 | 105.27 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.23044 | 105.27 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21315 | 105.27 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26238 | 105.27 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21301 | 105.27 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21675 | 105.02 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21223 | 105.02 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26144 | 105.02 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.22949 | 105.02 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21223 | 105.02 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26144 | 105.02 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21209 | 105.02 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21797 | 107.46 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21345 | 107.46 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26267 | 107.46 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.23073 | 107.46 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21345 | 107.46 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26267 | 107.46 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21331 | 107.46 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21967 | 108.34 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21518 | 108.34 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26434 | 108.34 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.23237 | 108.34 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21518 | 108.34 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26434 | 108.34 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21504 | 108.34 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.23797 | 111.06 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.23246 | 111.06 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26916 | 111.06 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.24366 | 111.06 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.23246 | 111.06 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26916 | 111.06 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.23272 | 111.06 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21804 | 106.98 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21353 | 106.98 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26273 | 106.98 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.23078 | 106.98 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21353 | 106.98 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26273 | 106.98 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21339 | 106.98 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.23797 | 111.09 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.23246 | 111.09 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26916 | 111.09 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.24366 | 111.09 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.23246 | 111.09 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26916 | 111.09 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.23272 | 111.09 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21599 | 103.99 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21149 | 103.99 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26067 | 103.99 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.2287 | 103.99 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21149 | 103.99 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26067 | 103.99 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21135 | 103.99 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21612 | 104.46 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21163 | 104.46 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26079 | 104.46 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.22881 | 104.46 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21163 | 104.46 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26079 | 104.46 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21148 | 104.46 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21599 | 104 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21149 | 104 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26067 | 104 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.2287 | 104 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21149 | 104 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26067 | 104 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21135 | 104 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21704 | 105.47 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21252 | 105.47 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26174 | 105.47 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.22979 | 105.47 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21252 | 105.47 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26174 | 105.47 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21238 | 105.47 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21746 | 105.68 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21294 | 105.68 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26216 | 105.68 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.23021 | 105.68 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21294 | 105.68 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26216 | 105.68 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.2128 | 105.68 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.2168 | 104.98 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21228 | 104.98 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26149 | 104.98 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.22955 | 104.98 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21228 | 104.98 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26149 | 104.98 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21214 | 104.98 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21675 | 105.02 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21223 | 105.02 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26144 | 105.02 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.22949 | 105.02 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21223 | 105.02 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26144 | 105.02 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21209 | 105.02 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21797 | 107.33 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21345 | 107.33 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26267 | 107.33 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.23073 | 107.33 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21345 | 107.33 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26267 | 107.33 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21331 | 107.33 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21797 | 107.34 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21345 | 107.34 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26267 | 107.34 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.23073 | 107.34 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21345 | 107.34 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26267 | 107.34 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21331 | 107.34 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21797 | 107.37 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21345 | 107.37 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26267 | 107.37 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.23073 | 107.37 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21345 | 107.37 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26267 | 107.37 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21331 | 107.37 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21741 | 105.74 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21289 | 105.74 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26211 | 105.74 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.23017 | 105.74 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21289 | 105.74 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26211 | 105.74 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21275 | 105.74 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.2196 | 108.26 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21511 | 108.26 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26427 | 108.26 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.23229 | 108.26 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21511 | 108.26 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26427 | 108.26 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21497 | 108.26 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21976 | 108.41 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21527 | 108.41 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26443 | 108.41 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.23245 | 108.41 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21527 | 108.41 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26443 | 108.41 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21513 | 108.41 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21612 | 104.46 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21163 | 104.46 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26079 | 104.46 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.22881 | 104.46 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21163 | 104.46 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26079 | 104.46 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21148 | 104.46 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21599 | 104 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21149 | 104 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26067 | 104 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.2287 | 104 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21149 | 104 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26067 | 104 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21135 | 104 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21704 | 105.47 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21252 | 105.47 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26174 | 105.47 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.22979 | 105.47 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21252 | 105.47 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26174 | 105.47 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21238 | 105.47 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21746 | 105.68 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21294 | 105.68 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26216 | 105.68 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.23021 | 105.68 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21294 | 105.68 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26216 | 105.68 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.2128 | 105.68 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.2168 | 104.98 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21228 | 104.98 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26149 | 104.98 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.22955 | 104.98 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21228 | 104.98 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26149 | 104.98 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21214 | 104.98 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21675 | 105.02 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21223 | 105.02 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26144 | 105.02 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.22949 | 105.02 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21223 | 105.02 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26144 | 105.02 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21209 | 105.02 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21797 | 107.33 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21345 | 107.33 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26267 | 107.33 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.23073 | 107.33 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21345 | 107.33 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26267 | 107.33 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21331 | 107.33 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21797 | 107.34 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21345 | 107.34 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26267 | 107.34 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.23073 | 107.34 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21345 | 107.34 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26267 | 107.34 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21331 | 107.34 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21797 | 107.37 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21345 | 107.37 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26267 | 107.37 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.23073 | 107.37 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21345 | 107.37 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26267 | 107.37 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21331 | 107.37 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21741 | 105.74 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21289 | 105.74 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26211 | 105.74 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.23017 | 105.74 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21289 | 105.74 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26211 | 105.74 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21275 | 105.74 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.2243 | 125.63 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.22012 | 125.63 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26872 | 125.63 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.23638 | 125.63 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.22012 | 125.63 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26872 | 125.63 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21994 | 125.63 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21079 | 100.51 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21079 | 100.51 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21492 | 104.97 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21045 | 104.97 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.25958 | 104.97 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.22758 | 104.97 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21045 | 104.97 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.25958 | 104.97 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.2103 | 104.97 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21492 | 104.97 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21045 | 104.97 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.25958 | 104.97 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.22758 | 104.97 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21045 | 104.97 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.25958 | 104.97 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.2103 | 104.97 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21576 | 105.42 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21126 | 105.42 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26044 | 105.42 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.22848 | 105.42 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21126 | 105.42 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26044 | 105.42 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21112 | 105.42 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21653 | 104.66 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21202 | 104.66 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26122 | 104.66 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.22927 | 104.66 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21202 | 104.66 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26122 | 104.66 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21188 | 104.66 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21967 | 112.78 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21518 | 112.78 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26434 | 112.78 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.23237 | 112.78 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21518 | 112.78 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26434 | 112.78 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21504 | 112.78 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.22475 | 118.58 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.22047 | 118.58 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26926 | 118.58 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.23704 | 118.58 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.22047 | 118.58 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26926 | 118.58 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.2203 | 118.58 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21599 | 103.99 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21149 | 103.99 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26067 | 103.99 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.2287 | 103.99 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21149 | 103.99 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.26067 | 103.99 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 |  | 553 | 0.21135 | 103.99 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 | 478 |  | 0.21767 | 123.2 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 | 478 |  | 0.21315 | 123.2 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 | 478 |  | 0.26238 | 123.2 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 | 478 |  | 0.23044 | 123.2 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 | 478 |  | 0.21315 | 123.2 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 | 478 |  | 0.16605 | 123.2 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 | 478 |  | 0.26238 | 123.2 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 | 478 |  | 0.21301 | 123.2 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 | 478 |  | 0.20698 | 101.35 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-078 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 | 478 |  | 0.07567 | 101.35 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 | 478 |  | 0.20698 | 101.35 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.20168 | 116.26 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.21802 | 116.26 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.28441 | 116.26 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.28062 | 116.26 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.32967 | 116.26 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.3035 | 116.26 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.28062 | 116.26 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.23285 | 116.26 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.32967 | 116.26 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.28036 | 116.26 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.23622 | 111.49 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.25255 | 111.49 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31894 | 111.49 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31515 | 111.49 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.36421 | 111.49 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-033 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.21298 | 111.49 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.33804 | 111.49 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-065 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.21298 | 111.49 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31515 | 111.49 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.36421 | 111.49 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31489 | 111.49 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.23603 | 101.96 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.2524 | 101.96 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31871 | 101.96 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31492 | 101.96 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.36397 | 101.96 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-033 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.21277 | 101.96 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.3378 | 101.96 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-065 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.21277 | 101.96 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31492 | 101.96 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.36397 | 101.96 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31466 | 101.96 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.23614 | 101.16 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.25248 | 101.16 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.31887 | 101.16 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.31508 | 101.16 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.36413 | 101.16 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.21291 | 101.16 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.33796 | 101.16 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.21291 | 101.16 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.31508 | 101.16 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.36413 | 101.16 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.31482 | 101.16 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.20168 | 100.96 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.21802 | 100.96 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.28441 | 100.96 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.28062 | 100.96 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.32967 | 100.96 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.3035 | 100.96 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.28062 | 100.96 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.23285 | 100.96 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.32967 | 100.96 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.28036 | 100.96 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.20276 | 104.85 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.21862 | 104.85 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.30617 | 104.85 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.30101 | 104.85 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.3265 | 104.85 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31396 | 104.85 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.30101 | 104.85 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.33869 | 104.85 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.3265 | 104.85 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.30142 | 104.85 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24L | GEN-2017-104 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.24294 | 104.85 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.20276 | 104.85 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.21862 | 104.85 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.30617 | 104.85 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.30101 | 104.85 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.3265 | 104.85 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31396 | 104.85 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.30101 | 104.85 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.33869 | 104.85 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.3265 | 104.85 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.30142 | 104.85 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-104 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.24294 | 104.85 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.20169 | 116.27 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.21803 | 116.27 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.28441 | 116.27 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.28062 | 116.27 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.32968 | 116.27 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.30351 | 116.27 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.28062 | 116.27 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.23285 | 116.27 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.32968 | 116.27 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.28036 | 116.27 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.23623 | 111.49 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.25257 | 111.49 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31895 | 111.49 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31516 | 111.49 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.36421 | 111.49 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-033 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.21299 | 111.49 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.33804 | 111.49 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-065 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.21299 | 111.49 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31516 | 111.49 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.36421 | 111.49 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.3149 | 111.49 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.23604 | 101.95 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.25241 | 101.95 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31872 | 101.95 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31493 | 101.95 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.36398 | 101.95 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-033 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.21278 | 101.95 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.33781 | 101.95 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-065 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.21278 | 101.95 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31493 | 101.95 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.36398 | 101.95 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31467 | 101.95 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.23615 | 101.12 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.25249 | 101.12 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.31888 | 101.12 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.31508 | 101.12 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.36414 | 101.12 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.21291 | 101.12 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.33797 | 101.12 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.21291 | 101.12 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.31508 | 101.12 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.36414 | 101.12 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.31482 | 101.12 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.20225 | 117.64 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.21856 | 117.64 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.28464 | 117.64 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.28087 | 117.64 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.32989 | 117.64 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.30372 | 117.64 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.28087 | 117.64 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.23325 | 117.64 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.32989 | 117.64 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.28061 | 117.64 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.23732 | 111.77 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.25363 | 111.77 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31971 | 111.77 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31594 | 111.77 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.36496 | 111.77 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-033 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.21388 | 111.77 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.33878 | 111.77 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-065 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.21388 | 111.77 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31594 | 111.77 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.36496 | 111.77 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31568 | 111.77 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.23719 | 102.22 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.25352 | 102.22 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31952 | 102.22 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31575 | 102.22 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.36476 | 102.22 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-033 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.21372 | 102.22 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.33859 | 102.22 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-065 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.21372 | 102.22 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31575 | 102.22 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.36476 | 102.22 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31548 | 102.22 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.23717 | 102.19 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.25348 | 102.19 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.31956 | 102.19 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.31579 | 102.19 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.36481 | 102.19 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.21374 | 102.19 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.33864 | 102.19 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.21374 | 102.19 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.31579 | 102.19 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.36481 | 102.19 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.31553 | 102.19 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.20168 | 100.96 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.21802 | 100.96 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.28441 | 100.96 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.28062 | 100.96 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.32967 | 100.96 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.3035 | 100.96 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.28062 | 100.96 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.23285 | 100.96 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.32967 | 100.96 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.28036 | 100.96 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.20168 | 100.56 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.21802 | 100.56 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.28441 | 100.56 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.28062 | 100.56 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.32967 | 100.56 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.3035 | 100.56 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.28062 | 100.56 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.23285 | 100.56 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.32967 | 100.56 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.28036 | 100.56 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.20225 | 117.64 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.21856 | 117.64 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.28464 | 117.64 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.28087 | 117.64 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.32989 | 117.64 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.30372 | 117.64 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.28087 | 117.64 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.23325 | 117.64 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.32989 | 117.64 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.28061 | 117.64 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.23732 | 111.77 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.25363 | 111.77 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31971 | 111.77 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31594 | 111.77 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.36496 | 111.77 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-033 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.21388 | 111.77 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.33878 | 111.77 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-065 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.21388 | 111.77 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31594 | 111.77 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.36496 | 111.77 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31568 | 111.77 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.23719 | 102.22 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.25352 | 102.22 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31952 | 102.22 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31575 | 102.22 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.36476 | 102.22 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-033 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.21372 | 102.22 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.33859 | 102.22 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-065 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.21372 | 102.22 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31575 | 102.22 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.36476 | 102.22 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31548 | 102.22 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.23717 | 102.19 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.25348 | 102.19 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.31956 | 102.19 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.31579 | 102.19 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.36481 | 102.19 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.21374 | 102.19 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.33864 | 102.19 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.21374 | 102.19 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.31579 | 102.19 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.36481 | 102.19 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.31553 | 102.19 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.20168 | 100.96 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.21802 | 100.96 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.28441 | 100.96 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.28062 | 100.96 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.32967 | 100.96 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.3035 | 100.96 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.28062 | 100.96 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.23285 | 100.96 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.32967 | 100.96 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.28036 | 100.96 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.20168 | 100.56 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.21802 | 100.56 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.28441 | 100.56 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.28062 | 100.56 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.32967 | 100.56 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.3035 | 100.56 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.28062 | 100.56 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.23285 | 100.56 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.32967 | 100.56 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.28036 | 100.56 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.21076 | 104.94 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.27105 | 104.94 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.26786 | 104.94 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31568 | 104.94 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.28803 | 104.94 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.26786 | 104.94 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.23978 | 104.94 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31568 | 104.94 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.26752 | 104.94 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.20169 | 116.27 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.21803 | 116.27 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.28441 | 116.27 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.28062 | 116.27 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.32968 | 116.27 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.30351 | 116.27 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.28062 | 116.27 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.23285 | 116.27 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.32968 | 116.27 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.28036 | 116.27 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.23623 | 111.49 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.25257 | 111.49 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31895 | 111.49 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31516 | 111.49 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.36421 | 111.49 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-033 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.21299 | 111.49 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.33804 | 111.49 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-065 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.21299 | 111.49 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31516 | 111.49 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.36421 | 111.49 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.3149 | 111.49 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.23604 | 101.95 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.25241 | 101.95 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31872 | 101.95 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31493 | 101.95 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.36398 | 101.95 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-033 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.21278 | 101.95 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.33781 | 101.95 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-065 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.21278 | 101.95 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31493 | 101.95 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.36398 | 101.95 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 956 | 0.31467 | 101.95 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.23615 | 101.12 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.25249 | 101.12 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.31888 | 101.12 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.31508 | 101.12 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.36414 | 101.12 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.21291 | 101.12 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.33797 | 101.12 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.21291 | 101.12 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.31508 | 101.12 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.36414 | 101.12 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 |  | 987.2 | 0.31482 | 101.12 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.2 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.2 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.2 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.2 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.2 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.2 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.2 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.2 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.2 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.2 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 131.89 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 131.89 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 131.89 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 131.89 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 131.89 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 131.89 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 131.89 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 131.89 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 131.89 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 131.89 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.38 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.38 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.38 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.38 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.38 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.38 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.38 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.38 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.38 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.38 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 111.4 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.4 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 111.4 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.4 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.4 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 111.4 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.4 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 111.4 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.4 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 111.4 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.16 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.16 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.16 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.16 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.16 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.16 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.16 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.16 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.16 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.16 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 131.84 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 131.84 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 131.84 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 131.84 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 131.84 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 131.84 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 131.84 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 131.84 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 131.84 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 131.84 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.26 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.26 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.26 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.26 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.26 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.26 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.26 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.26 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.26 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.26 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 111.37 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.37 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 111.37 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.37 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.37 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 111.37 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.37 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 111.37 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.37 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 111.37 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 135.89 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 135.89 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 135.89 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 135.89 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 135.89 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 135.89 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 135.89 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 135.89 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 135.89 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 135.89 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 111.13 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.13 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 111.13 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.13 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.13 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 111.13 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.13 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 111.13 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.13 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 111.13 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.44 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.44 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.44 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.44 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.44 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.44 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.44 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.44 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.44 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.44 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 132.12 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 132.12 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 132.12 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.12 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.12 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 132.12 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.12 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 132.12 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.12 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 132.12 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.62 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.62 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.62 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.62 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.62 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.62 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.62 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.62 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.62 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.62 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 111.63 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.63 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 111.63 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.63 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.63 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 111.63 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.63 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 111.63 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.63 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 111.63 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 133.82 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 133.82 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 133.82 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 133.82 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 133.82 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 133.82 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 133.82 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 133.82 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 133.82 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 133.82 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.08 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 126.08 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 126.08 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.08 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.08 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 126.08 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 126.08 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 126.08 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 126.08 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 126.08 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 114 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 114 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 114 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 114 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 114 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 114 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 114 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 114 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 114 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 114 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.68 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.68 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.68 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.68 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.68 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.68 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.68 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.68 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.68 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.68 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 132.38 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 132.38 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 132.38 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.38 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.38 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 132.38 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.38 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 132.38 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.38 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 132.38 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.89 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.89 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.89 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.89 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.89 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.89 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.89 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.89 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.89 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.89 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.89 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.89 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.89 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.89 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.89 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.89 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.89 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.89 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.89 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.89 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.56 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.56 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.56 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.56 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.56 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.56 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.56 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.56 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.56 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.56 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 132.26 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 132.26 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 132.26 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.26 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.26 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 132.26 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.26 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 132.26 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.26 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 132.26 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.83 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.83 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.83 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.83 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.83 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.83 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.83 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.83 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.83 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.83 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 132.45 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 132.45 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 132.45 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.45 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.45 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 132.45 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.45 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 132.45 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.45 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 132.45 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 125.04 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 125.04 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 125.04 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 125.04 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 125.04 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 125.04 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 125.04 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 125.04 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 125.04 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 125.04 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 112 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 112 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 112 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 112 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 112 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 112 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.67 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.67 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.67 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.67 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.67 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.67 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.67 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.67 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.67 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.67 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 132.38 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 132.38 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 132.38 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.38 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.38 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 132.38 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.38 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 132.38 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.38 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 132.38 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.87 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.87 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.87 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.87 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.87 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.87 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.87 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.87 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.87 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.87 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 135.23 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 135.23 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 135.23 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 135.23 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 135.23 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 135.23 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 135.23 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 135.23 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 135.23 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 135.23 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 130.87 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 130.87 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 130.87 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 130.87 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 130.87 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 130.87 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 130.87 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 130.87 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 130.87 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 130.87 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 123.34 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 123.34 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 123.34 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 123.34 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 123.34 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 123.34 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 123.34 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 123.34 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 123.34 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 123.34 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.89 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.89 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.89 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.89 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.89 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.89 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.89 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.89 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.89 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.89 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 123.79 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 123.79 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 123.79 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 123.79 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 123.79 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 123.79 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 123.79 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 123.79 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 123.79 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 123.79 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26202 | 153.97 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 153.97 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 153.97 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27985 | 153.97 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 153.97 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23967 | 153.97 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 153.97 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25806 | 153.97 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.67 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.67 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.67 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.67 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.67 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.67 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.67 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.67 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.67 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.67 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 132.38 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 132.38 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 132.38 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.38 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.38 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 132.38 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.38 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 132.38 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.38 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 132.38 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.87 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.87 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.87 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.87 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.87 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.87 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.87 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.87 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.87 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.87 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.89 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.89 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.89 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.89 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.89 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.89 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.89 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.89 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.89 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.89 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.88 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.88 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.88 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.88 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.88 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.88 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.88 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.88 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.88 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.88 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21206 | 124.89 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.89 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.89 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.89 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3386 | 124.89 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3131 | 124.89 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.89 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.89 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3386 | 124.89 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.89 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 135.05 | P11:345:OKGE:BKRBKR_GSU05
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 135.05 | P11:345:OKGE:BKRBKR_GSU05
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 135.05 | P11:345:OKGE:BKRBKR_GSU05
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 135.05 | P11:345:OKGE:BKRBKR_GSU05
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 135.05 | P11:345:OKGE:BKRBKR_GSU05
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 135.05 | P11:345:OKGE:BKRBKR_GSU05
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 135.05 | P11:345:OKGE:BKRBKR_GSU05
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 135.05 | P11:345:OKGE:BKRBKR_GSU05
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 135.05 | P11:345:OKGE:BKRBKR_GSU05
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 135.05 | P11:345:OKGE:BKRBKR_GSU05
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 135.05 | P11:345:OKGE:BKRBKR_GSU06
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 135.05 | P11:345:OKGE:BKRBKR_GSU06
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 135.05 | P11:345:OKGE:BKRBKR_GSU06
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 135.05 | P11:345:OKGE:BKRBKR_GSU06
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 135.05 | P11:345:OKGE:BKRBKR_GSU06
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 135.05 | P11:345:OKGE:BKRBKR_GSU06
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 135.05 | P11:345:OKGE:BKRBKR_GSU06
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 135.05 | P11:345:OKGE:BKRBKR_GSU06
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 135.05 | P11:345:OKGE:BKRBKR_GSU06
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 135.05 | P11:345:OKGE:BKRBKR_GSU06
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 137.18 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 137.18 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 137.18 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 137.18 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 137.18 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 137.18 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 137.18 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 137.18 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 137.18 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 137.18 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 112.98 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 112.98 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 112.98 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.98 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.98 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 112.98 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.98 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 112.98 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.98 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 112.98 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 137.18 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 137.18 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 137.18 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 137.18 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 137.18 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 137.18 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 137.18 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 137.18 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 137.18 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 137.18 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 113.12 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 113.12 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 113.12 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 113.12 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 113.12 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 113.12 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 113.12 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 113.12 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 113.12 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 113.12 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 135.04 | P11:345:OKGE:BKRBKR_GSU22
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 135.04 | P11:345:OKGE:BKRBKR_GSU22
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 135.04 | P11:345:OKGE:BKRBKR_GSU22
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 135.04 | P11:345:OKGE:BKRBKR_GSU22
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 135.04 | P11:345:OKGE:BKRBKR_GSU22
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 135.04 | P11:345:OKGE:BKRBKR_GSU22
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 135.04 | P11:345:OKGE:BKRBKR_GSU22
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 135.04 | P11:345:OKGE:BKRBKR_GSU22
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 135.04 | P11:345:OKGE:BKRBKR_GSU22
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 135.04 | P11:345:OKGE:BKRBKR_GSU22
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.67 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.67 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.67 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.67 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.67 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.67 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.67 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.67 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.67 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.67 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 132.37 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 132.37 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 132.37 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.37 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.37 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 132.37 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.37 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 132.37 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.37 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 132.37 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.88 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.88 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.88 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.88 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.88 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.88 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.88 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.88 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.88 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.88 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 111.92 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.92 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 111.92 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.92 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.92 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 111.92 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.92 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 111.92 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.92 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 111.92 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.67 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.67 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.67 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.67 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.67 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.67 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.67 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.67 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.67 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.67 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 132.37 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 132.37 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 132.37 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.37 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.37 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 132.37 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.37 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 132.37 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.37 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 132.37 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.88 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.88 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.88 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.88 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.88 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.88 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.88 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.88 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.88 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.88 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 111.92 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.92 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 111.92 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.92 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.92 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 111.92 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.92 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 111.92 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.92 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 111.92 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.67 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.67 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.67 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.67 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.67 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.67 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.67 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.67 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.67 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.67 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 132.37 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 132.37 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 132.37 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.37 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.37 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 132.37 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.37 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 132.37 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.37 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 132.37 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.88 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.88 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.88 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.88 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.88 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.88 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.88 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.88 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.88 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.88 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 111.94 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.94 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 111.94 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.94 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.94 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 111.94 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.94 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 111.94 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.94 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 111.94 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 135.97 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 135.97 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 135.97 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 135.97 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 135.97 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 135.97 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 135.97 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 135.97 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 135.97 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 135.97 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 131.62 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 131.62 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 131.62 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 131.62 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 131.62 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 131.62 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 131.62 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 131.62 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 131.62 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 131.62 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 123.97 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 123.97 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 123.97 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 123.97 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 123.97 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 123.97 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 123.97 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 123.97 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 123.97 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 123.97 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 111.15 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.15 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 111.15 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.15 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.15 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 111.15 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.15 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 111.15 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.15 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 111.15 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.56 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.56 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.56 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.56 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.56 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.56 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.56 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.56 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.56 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.56 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 132.26 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 132.26 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 132.26 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.26 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.26 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 132.26 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.26 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 132.26 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.26 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 132.26 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.77 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.77 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.77 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.77 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.77 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.77 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.77 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.77 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.77 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.77 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.57 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.57 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.57 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.57 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.57 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.57 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.57 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.57 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.57 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.57 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 132.27 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 132.27 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 132.27 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.27 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.27 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 132.27 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.27 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 132.27 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.27 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 132.27 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.77 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.77 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.77 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.77 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.77 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.77 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.77 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.77 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.77 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.77 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26202 | 154.85 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 154.85 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 154.85 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27985 | 154.85 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 154.85 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23967 | 154.85 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 154.85 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25806 | 154.85 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 132.56 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 132.56 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 132.56 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.56 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.56 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 132.56 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.56 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 132.56 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.56 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 132.56 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 125.07 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 125.07 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 125.07 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 125.07 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 125.07 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 125.07 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 125.07 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 125.07 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 125.07 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 125.07 | P11:345:WERE:WOLFU1_GEN::
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26207 | 155.19 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25828 | 155.19 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30728 | 155.19 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2801 | 155.19 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25828 | 155.19 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23953 | 155.19 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30728 | 155.19 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25802 | 155.19 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20512 | 137.1 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22475 | 137.1 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28982 | 137.1 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28603 | 137.1 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33503 | 137.1 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30785 | 137.1 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28603 | 137.1 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21179 | 137.1 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33503 | 137.1 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28577 | 137.1 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20549 | 132.88 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22512 | 132.88 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2902 | 132.88 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28641 | 132.88 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33541 | 132.88 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30822 | 132.88 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28641 | 132.88 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21141 | 132.88 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33541 | 132.88 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28615 | 132.88 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21305 | 125.38 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23165 | 125.38 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28974 | 125.38 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28633 | 125.38 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33888 | 125.38 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31339 | 125.38 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28633 | 125.38 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21899 | 125.38 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33888 | 125.38 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28594 | 125.38 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21214 | 112.42 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23179 | 112.42 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29703 | 112.42 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29338 | 112.42 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34198 | 112.42 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31479 | 112.42 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29338 | 112.42 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20482 | 112.42 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34198 | 112.42 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2931 | 112.42 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20424 | 134.36 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22271 | 134.36 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28978 | 134.36 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 134.36 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33481 | 134.36 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30763 | 134.36 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 134.36 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21195 | 134.36 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33481 | 134.36 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 134.36 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20461 | 130.21 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22308 | 130.21 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29015 | 130.21 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 130.21 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33518 | 130.21 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.308 | 130.21 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 130.21 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21158 | 130.21 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33518 | 130.21 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 130.21 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21126 | 109.59 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22975 | 109.59 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 109.59 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 109.59 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34175 | 109.59 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31457 | 109.59 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 109.59 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20499 | 109.59 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34175 | 109.59 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29315 | 109.59 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26208 | 153.89 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25839 | 153.89 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30712 | 153.89 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27994 | 153.89 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25839 | 153.89 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23966 | 153.89 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30712 | 153.89 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25812 | 153.89 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20426 | 131.85 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22273 | 131.85 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28978 | 131.85 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28609 | 131.85 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33482 | 131.85 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30764 | 131.85 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28609 | 131.85 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21196 | 131.85 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33482 | 131.85 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28582 | 131.85 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20463 | 127.85 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2231 | 127.85 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29016 | 127.85 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28647 | 127.85 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3352 | 127.85 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30802 | 127.85 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28647 | 127.85 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21158 | 127.85 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3352 | 127.85 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2862 | 127.85 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21217 | 120.73 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22952 | 120.73 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28971 | 120.73 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28641 | 120.73 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3387 | 120.73 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31325 | 120.73 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28641 | 120.73 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21922 | 120.73 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3387 | 120.73 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28601 | 120.73 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21127 | 106.61 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22976 | 106.61 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 106.61 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29344 | 106.61 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34176 | 106.61 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31458 | 106.61 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29344 | 106.61 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20499 | 106.61 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34176 | 106.61 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29315 | 106.61 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 135.66 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 135.66 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 135.66 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 135.66 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 135.66 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 135.66 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 135.66 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 135.66 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 135.66 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 135.66 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 110.89 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 110.89 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 110.89 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 110.89 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 110.89 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 110.89 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 110.89 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 110.89 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 110.89 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 110.89 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20131 | 136.95 | P12:115:SPS:T28A.1.LAMTON.PLANTX
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21904 | 136.95 | P12:115:SPS:T28A.1.LAMTON.PLANTX
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29138 | 136.95 | P12:115:SPS:T28A.1.LAMTON.PLANTX
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28789 | 136.95 | P12:115:SPS:T28A.1.LAMTON.PLANTX
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33607 | 136.95 | P12:115:SPS:T28A.1.LAMTON.PLANTX
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30875 | 136.95 | P12:115:SPS:T28A.1.LAMTON.PLANTX
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28789 | 136.95 | P12:115:SPS:T28A.1.LAMTON.PLANTX
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2114 | 136.95 | P12:115:SPS:T28A.1.LAMTON.PLANTX
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33607 | 136.95 | P12:115:SPS:T28A.1.LAMTON.PLANTX
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2876 | 136.95 | P12:115:SPS:T28A.1.LAMTON.PLANTX
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20832 | 112.1 | P12:115:SPS:T28A.1.LAMTON.PLANTX
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22607 | 112.1 | P12:115:SPS:T28A.1.LAMTON.PLANTX
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29857 | 112.1 | P12:115:SPS:T28A.1.LAMTON.PLANTX
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29519 | 112.1 | P12:115:SPS:T28A.1.LAMTON.PLANTX
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34304 | 112.1 | P12:115:SPS:T28A.1.LAMTON.PLANTX
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31572 | 112.1 | P12:115:SPS:T28A.1.LAMTON.PLANTX
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29519 | 112.1 | P12:115:SPS:T28A.1.LAMTON.PLANTX
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20441 | 112.1 | P12:115:SPS:T28A.1.LAMTON.PLANTX
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34304 | 112.1 | P12:115:SPS:T28A.1.LAMTON.PLANTX
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29488 | 112.1 | P12:115:SPS:T28A.1.LAMTON.PLANTX
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20502 | 138.26 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22419 | 138.26 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29168 | 138.26 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28813 | 138.26 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33693 | 138.26 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30882 | 138.26 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28813 | 138.26 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21168 | 138.26 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33693 | 138.26 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28783 | 138.26 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20548 | 133.44 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22465 | 133.44 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29214 | 133.44 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28859 | 133.44 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33739 | 133.44 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30928 | 133.44 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28859 | 133.44 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21122 | 133.44 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33739 | 133.44 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28829 | 133.44 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 113.97 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23126 | 113.97 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29923 | 113.97 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29604 | 113.97 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34373 | 113.97 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31564 | 113.97 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29604 | 113.97 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20476 | 113.97 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34373 | 113.97 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2957 | 113.97 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 112.46 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23126 | 112.46 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29923 | 112.46 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29604 | 112.46 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34373 | 112.46 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31564 | 112.46 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29604 | 112.46 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20476 | 112.46 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34373 | 112.46 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2957 | 112.46 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2047 | 131.51 | P12:115:SPS:T35.1.TERRY.YOAKUM
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22316 | 131.51 | P12:115:SPS:T35.1.TERRY.YOAKUM
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 131.51 | P12:115:SPS:T35.1.TERRY.YOAKUM
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28646 | 131.51 | P12:115:SPS:T35.1.TERRY.YOAKUM
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33518 | 131.51 | P12:115:SPS:T35.1.TERRY.YOAKUM
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30789 | 131.51 | P12:115:SPS:T35.1.TERRY.YOAKUM
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28646 | 131.51 | P12:115:SPS:T35.1.TERRY.YOAKUM
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21161 | 131.51 | P12:115:SPS:T35.1.TERRY.YOAKUM
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33518 | 131.51 | P12:115:SPS:T35.1.TERRY.YOAKUM
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 131.51 | P12:115:SPS:T35.1.TERRY.YOAKUM
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21135 | 110.61 | P12:115:SPS:T35.1.TERRY.YOAKUM
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22982 | 110.61 | P12:115:SPS:T35.1.TERRY.YOAKUM
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 110.61 | P12:115:SPS:T35.1.TERRY.YOAKUM
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29344 | 110.61 | P12:115:SPS:T35.1.TERRY.YOAKUM
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34175 | 110.61 | P12:115:SPS:T35.1.TERRY.YOAKUM
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31446 | 110.61 | P12:115:SPS:T35.1.TERRY.YOAKUM
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29344 | 110.61 | P12:115:SPS:T35.1.TERRY.YOAKUM
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20502 | 110.61 | P12:115:SPS:T35.1.TERRY.YOAKUM
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34175 | 110.61 | P12:115:SPS:T35.1.TERRY.YOAKUM
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29315 | 110.61 | P12:115:SPS:T35.1.TERRY.YOAKUM
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20421 | 136.38 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22268 | 136.38 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28978 | 136.38 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.286 | 136.38 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.38 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3076 | 136.38 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.286 | 136.38 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.38 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.38 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.38 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 132.08 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22305 | 132.08 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29015 | 132.08 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28637 | 132.08 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.08 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30797 | 132.08 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28637 | 132.08 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21155 | 132.08 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.08 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 132.08 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.59 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.59 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.59 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.59 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.59 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.59 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.59 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.59 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.59 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.59 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 111.61 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.61 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.297 | 111.61 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29337 | 111.61 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.61 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31454 | 111.61 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29337 | 111.61 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 111.61 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.61 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 111.61 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26251 | 155.54 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25885 | 155.54 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30751 | 155.54 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2803 | 155.54 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25885 | 155.54 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23968 | 155.54 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30751 | 155.54 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25857 | 155.54 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20531 | 137 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22376 | 137 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2905 | 137 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28683 | 137 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33549 | 137 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30828 | 137 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28683 | 137 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2117 | 137 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33549 | 137 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28656 | 137 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20565 | 132.84 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2241 | 132.84 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29084 | 132.84 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28718 | 132.84 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33584 | 132.84 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30862 | 132.84 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28718 | 132.84 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21135 | 132.84 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33584 | 132.84 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2869 | 132.84 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21315 | 125.48 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23047 | 125.48 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29039 | 125.48 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28711 | 125.48 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33929 | 125.48 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31378 | 125.48 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28711 | 125.48 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21895 | 125.48 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33929 | 125.48 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2867 | 125.48 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21236 | 112.1 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23082 | 112.1 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29774 | 112.1 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29421 | 112.1 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34247 | 112.1 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31525 | 112.1 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29421 | 112.1 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2047 | 112.1 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34247 | 112.1 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29392 | 112.1 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20493 | 136.85 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22339 | 136.85 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29024 | 136.85 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28657 | 136.85 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33524 | 136.85 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30804 | 136.85 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28657 | 136.85 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21179 | 136.85 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33524 | 136.85 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2863 | 136.85 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20386 | 136.93 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22207 | 136.93 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29565 | 136.93 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29419 | 136.93 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33615 | 136.93 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3089 | 136.93 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29419 | 136.93 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21116 | 136.93 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33615 | 136.93 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29366 | 136.93 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20426 | 132.47 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22247 | 132.47 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29605 | 132.47 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29459 | 132.47 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33655 | 132.47 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3093 | 132.47 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29459 | 132.47 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21076 | 132.47 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33655 | 132.47 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29406 | 132.47 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21173 | 124.98 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22886 | 124.98 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29522 | 124.98 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29399 | 124.98 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33993 | 124.98 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3144 | 124.98 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29399 | 124.98 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21833 | 124.98 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33993 | 124.98 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29336 | 124.98 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21087 | 112.18 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22909 | 112.18 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30283 | 112.18 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30148 | 112.18 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34312 | 112.18 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31586 | 112.18 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30148 | 112.18 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20418 | 112.18 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34312 | 112.18 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30094 | 112.18 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26792 | 155.49 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26647 | 155.49 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30843 | 155.49 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28118 | 155.49 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26647 | 155.49 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23888 | 155.49 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30843 | 155.49 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26594 | 155.49 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20386 | 137.24 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22207 | 137.24 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29565 | 137.24 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29419 | 137.24 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33615 | 137.24 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3089 | 137.24 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29419 | 137.24 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21116 | 137.24 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33615 | 137.24 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29366 | 137.24 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20426 | 132.72 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22247 | 132.72 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29605 | 132.72 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29459 | 132.72 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33655 | 132.72 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3093 | 132.72 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29459 | 132.72 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21076 | 132.72 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33655 | 132.72 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29406 | 132.72 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21173 | 125.2 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22886 | 125.2 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29522 | 125.2 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29399 | 125.2 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33993 | 125.2 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3144 | 125.2 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29399 | 125.2 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21833 | 125.2 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33993 | 125.2 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29336 | 125.2 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21087 | 112.59 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22909 | 112.59 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30283 | 112.59 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30148 | 112.59 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34312 | 112.59 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31586 | 112.59 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30148 | 112.59 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20418 | 112.59 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34312 | 112.59 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30094 | 112.59 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26319 | 155.42 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25947 | 155.42 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30827 | 155.42 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28109 | 155.42 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25947 | 155.42 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23897 | 155.42 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30827 | 155.42 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25921 | 155.42 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21069 | 137.5 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22543 | 137.5 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29091 | 137.5 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2872 | 137.5 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33599 | 137.5 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30881 | 137.5 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2872 | 137.5 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21125 | 137.5 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33599 | 137.5 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28693 | 137.5 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21772 | 112.61 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23248 | 112.61 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29814 | 112.61 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29455 | 112.61 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34295 | 112.61 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31576 | 112.61 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29455 | 112.61 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20427 | 112.61 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34295 | 112.61 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29427 | 112.61 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20425 | 136 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22271 | 136 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28975 | 136 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28606 | 136 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33477 | 136 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30756 | 136 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28606 | 136 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21194 | 136 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33477 | 136 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28579 | 136 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21127 | 111.17 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22974 | 111.17 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29696 | 111.17 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29341 | 111.17 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34171 | 111.17 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3145 | 111.17 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29341 | 111.17 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20498 | 111.17 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34171 | 111.17 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29312 | 111.17 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 111.32 | P12:115:SPS:T83.1.SP-FKFD.ALLEN
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.32 | P12:115:SPS:T83.1.SP-FKFD.ALLEN
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29698 | 111.32 | P12:115:SPS:T83.1.SP-FKFD.ALLEN
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29342 | 111.32 | P12:115:SPS:T83.1.SP-FKFD.ALLEN
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.32 | P12:115:SPS:T83.1.SP-FKFD.ALLEN
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 111.32 | P12:115:SPS:T83.1.SP-FKFD.ALLEN
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29342 | 111.32 | P12:115:SPS:T83.1.SP-FKFD.ALLEN
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 111.32 | P12:115:SPS:T83.1.SP-FKFD.ALLEN
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.32 | P12:115:SPS:T83.1.SP-FKFD.ALLEN
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 111.32 | P12:115:SPS:T83.1.SP-FKFD.ALLEN
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 110.26 | P12:115:SPS:T86.1.AMASTH.SPGDRW
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 110.26 | P12:115:SPS:T86.1.AMASTH.SPGDRW
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 110.26 | P12:115:SPS:T86.1.AMASTH.SPGDRW
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 110.26 | P12:115:SPS:T86.1.AMASTH.SPGDRW
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 110.26 | P12:115:SPS:T86.1.AMASTH.SPGDRW
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 110.26 | P12:115:SPS:T86.1.AMASTH.SPGDRW
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 110.26 | P12:115:SPS:T86.1.AMASTH.SPGDRW
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 110.26 | P12:115:SPS:T86.1.AMASTH.SPGDRW
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 110.26 | P12:115:SPS:T86.1.AMASTH.SPGDRW
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 110.26 | P12:115:SPS:T86.1.AMASTH.SPGDRW
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 135.31 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 135.31 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 135.31 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 135.31 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 135.31 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 135.31 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 135.31 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 135.31 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 135.31 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 135.31 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 110.22 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 110.22 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 110.22 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 110.22 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 110.22 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 110.22 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 110.22 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 110.22 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 110.22 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 110.22 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26417 | 155.59 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26037 | 155.59 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30773 | 155.59 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28036 | 155.59 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26037 | 155.59 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23972 | 155.59 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30773 | 155.59 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26014 | 155.59 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20449 | 136.61 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22304 | 136.61 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29182 | 136.61 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28802 | 136.61 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33538 | 136.61 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30802 | 136.61 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28802 | 136.61 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 136.61 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33538 | 136.61 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28779 | 136.61 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20488 | 132.46 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22343 | 132.46 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29221 | 132.46 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28841 | 132.46 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33577 | 132.46 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30841 | 132.46 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28841 | 132.46 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21168 | 132.46 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33577 | 132.46 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28818 | 132.46 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21249 | 125.02 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22991 | 125.02 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29201 | 125.02 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28858 | 125.02 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33931 | 125.02 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31361 | 125.02 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28858 | 125.02 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2194 | 125.02 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33931 | 125.02 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28823 | 125.02 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2115 | 111.66 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23007 | 111.66 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29902 | 111.66 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29534 | 111.66 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34232 | 111.66 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31496 | 111.66 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29534 | 111.66 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20511 | 111.66 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34232 | 111.66 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2951 | 111.66 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 135.83 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 135.83 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 135.83 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 135.83 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 135.83 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 135.83 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 135.83 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 135.83 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 135.83 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 135.83 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 110.98 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 110.98 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 110.98 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 110.98 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 110.98 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 110.98 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 110.98 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 110.98 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 110.98 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 110.98 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20342 | 135.88 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21924 | 135.88 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29104 | 135.88 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2874 | 135.88 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33599 | 135.88 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30875 | 135.88 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2874 | 135.88 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21135 | 135.88 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33599 | 135.88 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28713 | 135.88 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21045 | 110.91 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22628 | 110.91 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29824 | 110.91 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29471 | 110.91 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34297 | 110.91 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31572 | 110.91 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29471 | 110.91 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20436 | 110.91 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34297 | 110.91 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29442 | 110.91 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2621 | 154.87 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25841 | 154.87 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30716 | 154.87 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27998 | 154.87 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25841 | 154.87 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23966 | 154.87 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30716 | 154.87 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25814 | 154.87 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20429 | 133.98 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22277 | 133.98 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28981 | 133.98 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28612 | 133.98 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33486 | 133.98 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30768 | 133.98 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28612 | 133.98 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21196 | 133.98 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33486 | 133.98 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28585 | 133.98 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20467 | 129.87 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22314 | 129.87 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29018 | 129.87 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28649 | 129.87 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33524 | 129.87 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30806 | 129.87 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28649 | 129.87 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21158 | 129.87 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33524 | 129.87 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28622 | 129.87 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21226 | 123.04 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22961 | 123.04 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 123.04 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28648 | 123.04 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33879 | 123.04 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31335 | 123.04 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28648 | 123.04 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21922 | 123.04 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33879 | 123.04 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28607 | 123.04 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2113 | 108.79 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22979 | 108.79 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29702 | 108.79 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29346 | 108.79 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3418 | 108.79 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31462 | 108.79 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29346 | 108.79 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.205 | 108.79 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3418 | 108.79 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29318 | 108.79 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20404 | 136.11 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22279 | 136.11 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29012 | 136.11 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28646 | 136.11 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33511 | 136.11 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30789 | 136.11 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28646 | 136.11 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21177 | 136.11 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33511 | 136.11 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 136.11 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20442 | 131.88 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22317 | 131.88 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2905 | 131.88 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28684 | 131.88 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33549 | 131.88 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30828 | 131.88 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28684 | 131.88 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21139 | 131.88 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33549 | 131.88 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28656 | 131.88 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21106 | 111.1 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22982 | 111.1 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29734 | 111.1 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2938 | 111.1 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34205 | 111.1 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31483 | 111.1 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2938 | 111.1 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20481 | 111.1 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34205 | 111.1 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29351 | 111.1 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26264 | 155.45 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25897 | 155.45 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3078 | 155.45 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28032 | 155.45 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25897 | 155.45 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23954 | 155.45 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3078 | 155.45 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25869 | 155.45 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20449 | 136.6 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22315 | 136.6 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29025 | 136.6 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28659 | 136.6 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33541 | 136.6 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30793 | 136.6 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28659 | 136.6 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21193 | 136.6 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33541 | 136.6 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28631 | 136.6 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20489 | 132.41 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22354 | 132.41 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29065 | 132.41 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28698 | 132.41 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33581 | 132.41 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30833 | 132.41 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28698 | 132.41 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21153 | 132.41 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33581 | 132.41 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28671 | 132.41 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21243 | 124.78 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22994 | 124.78 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 124.78 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28687 | 124.78 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33923 | 124.78 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31339 | 124.78 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28687 | 124.78 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21917 | 124.78 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33923 | 124.78 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28646 | 124.78 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21151 | 111.92 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23018 | 111.92 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29751 | 111.92 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29401 | 111.92 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34234 | 111.92 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31486 | 111.92 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29401 | 111.92 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20497 | 111.92 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34234 | 111.92 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29371 | 111.92 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26214 | 154.49 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25846 | 154.49 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30724 | 154.49 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28006 | 154.49 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25846 | 154.49 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2397 | 154.49 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30724 | 154.49 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25819 | 154.49 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20437 | 133.85 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22283 | 133.85 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28979 | 133.85 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2861 | 133.85 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33489 | 133.85 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3077 | 133.85 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2861 | 133.85 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21206 | 133.85 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33489 | 133.85 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28583 | 133.85 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20476 | 129.6 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22322 | 129.6 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29018 | 129.6 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28649 | 129.6 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33528 | 129.6 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30809 | 129.6 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28649 | 129.6 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21167 | 129.6 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33528 | 129.6 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28622 | 129.6 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21243 | 123.13 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22974 | 123.13 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28967 | 123.13 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28639 | 123.13 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33881 | 123.13 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31336 | 123.13 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28639 | 123.13 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21952 | 123.13 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33881 | 123.13 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 123.13 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21138 | 108.52 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22986 | 108.52 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.297 | 108.52 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29346 | 108.52 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34183 | 108.52 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31464 | 108.52 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29346 | 108.52 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2051 | 108.52 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34183 | 108.52 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29317 | 108.52 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20427 | 135.57 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22273 | 135.57 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28978 | 135.57 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28609 | 135.57 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33482 | 135.57 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30766 | 135.57 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28609 | 135.57 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21202 | 135.57 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33482 | 135.57 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28582 | 135.57 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20462 | 131.16 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22309 | 131.16 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29013 | 131.16 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28644 | 131.16 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33517 | 131.16 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30801 | 131.16 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28644 | 131.16 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21167 | 131.16 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33517 | 131.16 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28617 | 131.16 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21129 | 110.43 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22978 | 110.43 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29701 | 110.43 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29345 | 110.43 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34178 | 110.43 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31461 | 110.43 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29345 | 110.43 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20505 | 110.43 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34178 | 110.43 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29316 | 110.43 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.59 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.59 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2898 | 136.59 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28624 | 136.59 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.59 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.59 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28624 | 136.59 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21193 | 136.59 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.59 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28624 | 136.59 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20459 | 132.26 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 132.26 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29017 | 132.26 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28661 | 132.26 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33515 | 132.26 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 132.26 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28661 | 132.26 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 132.26 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33515 | 132.26 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2866 | 132.26 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.77 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.77 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28973 | 124.77 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28661 | 124.77 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3386 | 124.77 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.77 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28661 | 124.77 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.77 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3386 | 124.77 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28661 | 124.77 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 111.82 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.82 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29702 | 111.82 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29359 | 111.82 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.82 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 111.82 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29359 | 111.82 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 111.82 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.82 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29359 | 111.82 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26488 | 155.79 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26152 | 155.79 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30932 | 155.79 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28202 | 155.79 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26152 | 155.79 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2385 | 155.79 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30932 | 155.79 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26121 | 155.79 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20436 | 137.56 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22415 | 137.56 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29252 | 137.56 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28916 | 137.56 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33696 | 137.56 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30966 | 137.56 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28916 | 137.56 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21086 | 137.56 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33696 | 137.56 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28885 | 137.56 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20479 | 133 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22458 | 133 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29295 | 133 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28959 | 133 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33739 | 133 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31009 | 133 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28959 | 133 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21043 | 133 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33739 | 133 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28928 | 133 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21226 | 125.34 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23094 | 125.34 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29253 | 125.34 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28955 | 125.34 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34087 | 125.34 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3153 | 125.34 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28955 | 125.34 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21796 | 125.34 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34087 | 125.34 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28911 | 125.34 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21138 | 112.86 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23119 | 112.86 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29973 | 112.86 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2965 | 112.86 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34392 | 112.86 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31662 | 112.86 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2965 | 112.86 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20388 | 112.86 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34392 | 112.86 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29618 | 112.86 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20421 | 136.55 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22268 | 136.55 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29 | 136.55 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28675 | 136.55 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3348 | 136.55 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30761 | 136.55 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28675 | 136.55 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.55 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3348 | 136.55 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28632 | 136.55 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20457 | 132.23 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22304 | 132.23 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29036 | 132.23 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28711 | 132.23 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33517 | 132.23 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30797 | 132.23 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28711 | 132.23 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21155 | 132.23 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33517 | 132.23 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28669 | 132.23 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21206 | 124.75 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22941 | 124.75 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28987 | 124.75 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28694 | 124.75 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33862 | 124.75 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31312 | 124.75 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28694 | 124.75 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21913 | 124.75 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33862 | 124.75 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28641 | 124.75 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21122 | 111.81 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22971 | 111.81 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2972 | 111.81 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29407 | 111.81 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34174 | 111.81 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31454 | 111.81 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29407 | 111.81 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20495 | 111.81 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34174 | 111.81 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29363 | 111.81 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26202 | 151.8 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 151.8 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27985 | 151.8 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23967 | 151.8 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 151.8 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25806 | 151.8 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 137.45 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 137.45 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 137.45 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 137.45 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 137.45 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 137.45 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 137.45 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 137.45 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 133.25 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 133.25 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 133.25 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 133.25 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 133.25 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 133.25 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 133.25 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 133.25 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 125.76 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 125.76 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 125.76 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 125.76 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 125.76 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 125.76 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 125.76 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 125.76 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 112.58 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 112.58 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 112.58 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.58 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 112.58 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 112.58 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.58 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 112.58 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.58 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.58 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2898 | 136.58 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28624 | 136.58 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.58 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.58 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28624 | 136.58 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21193 | 136.58 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.58 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28479 | 136.58 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20459 | 132.26 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 132.26 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29017 | 132.26 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28661 | 132.26 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33515 | 132.26 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 132.26 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28661 | 132.26 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 132.26 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33515 | 132.26 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28516 | 132.26 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 111.85 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.85 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29702 | 111.85 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29359 | 111.85 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.85 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 111.85 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29359 | 111.85 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 111.85 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.85 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29206 | 111.85 | P12:115:SPS:W64.1.PLSTHL.FE-CLV
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2042 | 136.52 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22267 | 136.52 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29004 | 136.52 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28687 | 136.52 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3348 | 136.52 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30761 | 136.52 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28687 | 136.52 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.52 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3348 | 136.52 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28641 | 136.52 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20457 | 132.29 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22304 | 132.29 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2904 | 132.29 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28723 | 132.29 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33517 | 132.29 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30798 | 132.29 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28723 | 132.29 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21155 | 132.29 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33517 | 132.29 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28678 | 132.29 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21205 | 124.77 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2294 | 124.77 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2899 | 124.77 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28704 | 124.77 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33862 | 124.77 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31312 | 124.77 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28704 | 124.77 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21913 | 124.77 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33862 | 124.77 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28648 | 124.77 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21122 | 111.78 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22971 | 111.78 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29724 | 111.78 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29418 | 111.78 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34174 | 111.78 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31455 | 111.78 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29418 | 111.78 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20495 | 111.78 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34174 | 111.78 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29372 | 111.78 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26202 | 154.79 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 154.79 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 154.79 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27985 | 154.79 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 154.79 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23967 | 154.79 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 154.79 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25806 | 154.79 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 135.24 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 135.24 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 135.24 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 135.24 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 135.24 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 135.24 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 135.24 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 135.24 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 135.24 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 135.24 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 131.12 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 131.12 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 131.12 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 131.12 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 131.12 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 131.12 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 131.12 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 131.12 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 131.12 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 131.12 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 123.73 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 123.73 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 123.73 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 123.73 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 123.73 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 123.73 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 123.73 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 123.73 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 123.73 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 123.73 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 110.29 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 110.29 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 110.29 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 110.29 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 110.29 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 110.29 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 110.29 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 110.29 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 110.29 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 110.29 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26202 | 153.32 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 153.32 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 153.32 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27985 | 153.32 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 153.32 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23967 | 153.32 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 153.32 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25806 | 153.32 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 132.54 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 132.54 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 132.54 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 132.54 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 132.54 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 132.54 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 132.54 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 132.54 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 132.54 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 132.54 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 128.26 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 128.26 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 128.26 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 128.26 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 128.26 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 128.26 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 128.26 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 128.26 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 128.26 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 128.26 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 107.6 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 107.6 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 107.6 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 107.6 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 107.6 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 107.6 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 107.6 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 107.6 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 107.6 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 107.6 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 133.65 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 133.65 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 133.65 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 133.65 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 133.65 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 133.65 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 133.65 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 133.65 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 133.65 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 133.65 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 129.44 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 129.44 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 129.44 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 129.44 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 129.44 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 129.44 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 129.44 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 129.44 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 129.44 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 129.44 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 106.17 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 106.17 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 106.17 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 106.17 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 106.17 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 106.17 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 106.17 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 106.17 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 106.17 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 106.17 | P12:115:SPS:W79.1.RDRNR.BATLX
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20493 | 136.85 | P12:115:SPS-AEPW:KIRBY3:SHAM3WT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22339 | 136.85 | P12:115:SPS-AEPW:KIRBY3:SHAM3WT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29024 | 136.85 | P12:115:SPS-AEPW:KIRBY3:SHAM3WT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28657 | 136.85 | P12:115:SPS-AEPW:KIRBY3:SHAM3WT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33524 | 136.85 | P12:115:SPS-AEPW:KIRBY3:SHAM3WT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30804 | 136.85 | P12:115:SPS-AEPW:KIRBY3:SHAM3WT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28657 | 136.85 | P12:115:SPS-AEPW:KIRBY3:SHAM3WT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21179 | 136.85 | P12:115:SPS-AEPW:KIRBY3:SHAM3WT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33524 | 136.85 | P12:115:SPS-AEPW:KIRBY3:SHAM3WT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2863 | 136.85 | P12:115:SPS-AEPW:KIRBY3:SHAM3WT
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26202 | 152.78 | P12:138:OKGE:BKRBKR347
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 152.78 | P12:138:OKGE:BKRBKR347
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 152.78 | P12:138:OKGE:BKRBKR347
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27985 | 152.78 | P12:138:OKGE:BKRBKR347
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 152.78 | P12:138:OKGE:BKRBKR347
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23967 | 152.78 | P12:138:OKGE:BKRBKR347
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 152.78 | P12:138:OKGE:BKRBKR347
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25806 | 152.78 | P12:138:OKGE:BKRBKR347
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2041 | 135.94 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22256 | 135.94 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28954 | 135.94 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28585 | 135.94 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33455 | 135.94 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30736 | 135.94 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28585 | 135.94 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21243 | 135.94 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33455 | 135.94 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28558 | 135.94 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21113 | 111.24 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2296 | 111.24 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29676 | 111.24 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29321 | 111.24 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34151 | 111.24 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31431 | 111.24 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29321 | 111.24 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20545 | 111.24 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34151 | 111.24 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29293 | 111.24 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20548 | 137.89 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22393 | 137.89 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29067 | 137.89 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.287 | 137.89 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33567 | 137.89 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30845 | 137.89 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.287 | 137.89 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21154 | 137.89 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33567 | 137.89 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28673 | 137.89 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20583 | 133.61 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22428 | 133.61 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29102 | 133.61 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28735 | 133.61 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33601 | 133.61 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3088 | 133.61 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28735 | 133.61 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21119 | 133.61 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33601 | 133.61 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28708 | 133.61 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21332 | 126.13 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23065 | 126.13 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29056 | 126.13 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28729 | 126.13 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33947 | 126.13 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31396 | 126.13 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28729 | 126.13 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21878 | 126.13 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33947 | 126.13 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28688 | 126.13 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21252 | 113.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.231 | 113.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29791 | 113.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29438 | 113.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34264 | 113.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31543 | 113.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29438 | 113.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20454 | 113.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34264 | 113.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29409 | 113.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26202 | 153.5 | P12:230:AEPW:SWEETWT6:BUFFCK6
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 153.5 | P12:230:AEPW:SWEETWT6:BUFFCK6
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 153.5 | P12:230:AEPW:SWEETWT6:BUFFCK6
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27985 | 153.5 | P12:230:AEPW:SWEETWT6:BUFFCK6
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 153.5 | P12:230:AEPW:SWEETWT6:BUFFCK6
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23967 | 153.5 | P12:230:AEPW:SWEETWT6:BUFFCK6
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 153.5 | P12:230:AEPW:SWEETWT6:BUFFCK6
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25806 | 153.5 | P12:230:AEPW:SWEETWT6:BUFFCK6
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20558 | 167.71 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26813 | 167.71 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26476 | 167.71 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3129 | 167.71 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28545 | 167.71 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26476 | 167.71 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24009 | 167.71 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3129 | 167.71 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26445 | 167.71 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21834 | 145.23 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23664 | 145.23 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29919 | 145.23 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29582 | 145.23 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34396 | 145.23 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31651 | 145.23 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29582 | 145.23 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20903 | 145.23 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34396 | 145.23 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29551 | 145.23 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21834 | 143.07 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23664 | 143.07 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29919 | 143.07 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29582 | 143.07 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34395 | 143.07 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3165 | 143.07 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29582 | 143.07 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20903 | 143.07 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34395 | 143.07 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2955 | 143.07 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22608 | 135.91 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24325 | 135.91 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29888 | 135.91 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29591 | 135.91 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34759 | 135.91 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32189 | 135.91 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29591 | 135.91 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21664 | 135.91 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34759 | 135.91 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29546 | 135.91 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22578 | 118.29 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2441 | 118.29 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30681 | 118.29 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30356 | 118.29 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35133 | 118.29 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32388 | 118.29 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30356 | 118.29 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20163 | 118.29 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35133 | 118.29 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30323 | 118.29 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20558 | 163.91 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26813 | 163.91 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26476 | 163.91 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3129 | 163.91 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28545 | 163.91 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26476 | 163.91 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24009 | 163.91 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3129 | 163.91 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26445 | 163.91 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21834 | 142.5 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23664 | 142.5 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29919 | 142.5 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29582 | 142.5 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34396 | 142.5 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31651 | 142.5 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29582 | 142.5 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20903 | 142.5 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34396 | 142.5 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29551 | 142.5 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21834 | 140.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23664 | 140.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29919 | 140.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29582 | 140.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34395 | 140.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3165 | 140.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29582 | 140.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20903 | 140.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34395 | 140.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2955 | 140.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22608 | 133.05 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24325 | 133.05 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29888 | 133.05 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29591 | 133.05 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34759 | 133.05 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32189 | 133.05 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29591 | 133.05 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21664 | 133.05 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34759 | 133.05 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29546 | 133.05 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22578 | 115.57 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2441 | 115.57 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30681 | 115.57 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30356 | 115.57 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35133 | 115.57 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32388 | 115.57 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30356 | 115.57 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20163 | 115.57 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35133 | 115.57 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30323 | 115.57 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2025 | 138.73 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22081 | 138.73 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29124 | 138.73 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28702 | 138.73 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33777 | 138.73 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30989 | 138.73 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28702 | 138.73 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21105 | 138.73 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33777 | 138.73 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2868 | 138.73 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20293 | 133.62 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22125 | 133.62 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29168 | 133.62 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28746 | 133.62 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33821 | 133.62 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31032 | 133.62 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28746 | 133.62 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21061 | 133.62 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33821 | 133.62 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28724 | 133.62 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21046 | 125.83 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22765 | 125.83 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29114 | 125.83 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28733 | 125.83 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34151 | 125.83 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3153 | 125.83 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28733 | 125.83 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2182 | 125.83 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34151 | 125.83 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28698 | 125.83 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20942 | 114.5 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2277 | 114.5 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29743 | 114.5 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29289 | 114.5 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34456 | 114.5 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31674 | 114.5 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29289 | 114.5 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20414 | 114.5 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34456 | 114.5 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29271 | 114.5 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20397 | 135.77 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22244 | 135.77 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28948 | 135.77 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28579 | 135.77 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33449 | 135.77 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3073 | 135.77 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28579 | 135.77 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21231 | 135.77 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33449 | 135.77 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28552 | 135.77 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26431 | 163.14 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26065 | 163.14 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30932 | 163.14 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2822 | 163.14 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26065 | 163.14 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2399 | 163.14 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30932 | 163.14 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26037 | 163.14 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20899 | 141.46 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22724 | 141.46 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29365 | 141.46 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28999 | 141.46 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33866 | 141.46 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31154 | 141.46 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28999 | 141.46 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21055 | 141.46 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33866 | 141.46 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28972 | 141.46 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20918 | 139.05 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22742 | 139.05 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29384 | 139.05 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29018 | 139.05 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33885 | 139.05 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31173 | 139.05 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29018 | 139.05 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21036 | 139.05 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33885 | 139.05 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28991 | 139.05 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21728 | 132.26 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23431 | 132.26 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29359 | 132.26 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29034 | 132.26 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34259 | 132.26 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31709 | 132.26 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29034 | 132.26 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21805 | 132.26 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34259 | 132.26 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28993 | 132.26 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2162 | 116.33 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23446 | 116.33 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30106 | 116.33 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29753 | 116.33 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3458 | 116.33 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31867 | 116.33 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29753 | 116.33 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2034 | 116.33 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3458 | 116.33 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29724 | 116.33 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20168 | 192.66 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21802 | 192.66 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28441 | 192.66 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28062 | 192.66 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32967 | 192.66 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3035 | 192.66 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28062 | 192.66 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23285 | 192.66 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32967 | 192.66 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28036 | 192.66 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23622 | 183.86 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25255 | 183.86 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31894 | 183.86 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31515 | 183.86 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36421 | 183.86 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-033 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21298 | 183.86 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33804 | 183.86 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-065 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21298 | 183.86 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31515 | 183.86 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36421 | 183.86 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31489 | 183.86 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23614 | 176.08 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25248 | 176.08 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31887 | 176.08 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31508 | 176.08 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36413 | 176.08 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21291 | 176.08 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33796 | 176.08 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21291 | 176.08 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31508 | 176.08 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36413 | 176.08 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31482 | 176.08 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24826 | 172.49 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26262 | 172.49 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31975 | 172.49 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31644 | 172.49 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36965 | 172.49 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2393 | 172.49 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34442 | 172.49 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2393 | 172.49 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31644 | 172.49 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2069 | 172.49 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36965 | 172.49 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31603 | 172.49 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24423 | 151.79 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26059 | 151.79 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32719 | 151.79 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32354 | 151.79 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.37215 | 151.79 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22092 | 151.79 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34597 | 151.79 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22092 | 151.79 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32354 | 151.79 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.37215 | 151.79 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32327 | 151.79 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26143 | 152.74 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25775 | 152.74 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30645 | 152.74 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27925 | 152.74 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25775 | 152.74 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24054 | 152.74 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30645 | 152.74 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25748 | 152.74 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20322 | 135.8 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22168 | 135.8 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28865 | 135.8 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28496 | 135.8 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33366 | 135.8 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30647 | 135.8 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28496 | 135.8 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21333 | 135.8 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33366 | 135.8 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28469 | 135.8 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20357 | 130.69 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22203 | 130.69 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.289 | 130.69 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28532 | 130.69 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33402 | 130.69 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30683 | 130.69 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28532 | 130.69 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21297 | 130.69 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33402 | 130.69 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28505 | 130.69 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.211 | 123.09 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22834 | 123.09 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28847 | 123.09 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28517 | 123.09 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33739 | 123.09 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31189 | 123.09 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28517 | 123.09 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22065 | 123.09 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33739 | 123.09 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28477 | 123.09 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 111.81 | P12:345:AEPW:R.S.S.-7:COGENT7
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.81 | P12:345:AEPW:R.S.S.-7:COGENT7
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 111.81 | P12:345:AEPW:R.S.S.-7:COGENT7
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.81 | P12:345:AEPW:R.S.S.-7:COGENT7
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.81 | P12:345:AEPW:R.S.S.-7:COGENT7
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 111.81 | P12:345:AEPW:R.S.S.-7:COGENT7
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.81 | P12:345:AEPW:R.S.S.-7:COGENT7
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 111.81 | P12:345:AEPW:R.S.S.-7:COGENT7
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.81 | P12:345:AEPW:R.S.S.-7:COGENT7
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 111.81 | P12:345:AEPW:R.S.S.-7:COGENT7
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26191 | 155.64 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25822 | 155.64 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30693 | 155.64 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27973 | 155.64 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25822 | 155.64 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23982 | 155.64 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30693 | 155.64 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25795 | 155.64 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20404 | 135.21 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22251 | 135.21 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28952 | 135.21 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28584 | 135.21 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33454 | 135.21 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30734 | 135.21 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28584 | 135.21 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21232 | 135.21 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33454 | 135.21 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28557 | 135.21 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20435 | 131.52 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22282 | 131.52 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28984 | 131.52 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28615 | 131.52 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33485 | 131.52 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30766 | 131.52 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28615 | 131.52 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.212 | 131.52 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33485 | 131.52 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28588 | 131.52 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21182 | 123.99 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22917 | 123.99 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28935 | 123.99 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28606 | 123.99 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33828 | 123.99 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31278 | 123.99 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28606 | 123.99 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21962 | 123.99 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33828 | 123.99 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28565 | 123.99 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.211 | 110.73 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22949 | 110.73 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29669 | 110.73 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29313 | 110.73 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34143 | 110.73 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31423 | 110.73 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29313 | 110.73 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20541 | 110.73 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34143 | 110.73 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29285 | 110.73 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25967 | 149.02 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25601 | 149.02 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30467 | 149.02 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27749 | 149.02 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25601 | 149.02 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24369 | 149.02 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30467 | 149.02 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25574 | 149.02 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20125 | 133.48 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21962 | 133.48 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 133.48 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28242 | 133.48 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33108 | 133.48 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3039 | 133.48 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28242 | 133.48 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21728 | 133.48 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33108 | 133.48 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28215 | 133.48 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20169 | 127.83 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22006 | 127.83 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28652 | 127.83 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28287 | 127.83 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33152 | 127.83 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30435 | 127.83 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28287 | 127.83 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21684 | 127.83 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33152 | 127.83 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28259 | 127.83 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20906 | 119.99 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22627 | 119.99 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28576 | 119.99 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2825 | 119.99 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3347 | 119.99 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30919 | 119.99 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2825 | 119.99 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22486 | 119.99 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3347 | 119.99 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28209 | 119.99 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20832 | 108.36 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22671 | 108.36 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29336 | 108.36 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28983 | 108.36 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33808 | 108.36 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31091 | 108.36 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28983 | 108.36 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21026 | 108.36 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33808 | 108.36 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28954 | 108.36 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26431 | 162.9 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26065 | 162.9 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30932 | 162.9 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2822 | 162.9 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26065 | 162.9 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2399 | 162.9 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30932 | 162.9 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26037 | 162.9 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20899 | 142.59 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22724 | 142.59 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29365 | 142.59 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28999 | 142.59 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33866 | 142.59 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31154 | 142.59 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28999 | 142.59 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21055 | 142.59 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33866 | 142.59 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28972 | 142.59 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20918 | 140.18 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22742 | 140.18 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29384 | 140.18 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29018 | 140.18 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33885 | 140.18 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31173 | 140.18 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29018 | 140.18 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21036 | 140.18 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33885 | 140.18 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28991 | 140.18 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21728 | 133.55 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23431 | 133.55 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29359 | 133.55 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29034 | 133.55 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34259 | 133.55 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31709 | 133.55 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29034 | 133.55 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21805 | 133.55 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34259 | 133.55 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28993 | 133.55 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2162 | 117.52 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23446 | 117.52 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30106 | 117.52 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29753 | 117.52 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3458 | 117.52 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31867 | 117.52 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29753 | 117.52 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2034 | 117.52 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3458 | 117.52 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29724 | 117.52 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20168 | 172.31 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21802 | 172.31 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28441 | 172.31 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28062 | 172.31 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32967 | 172.31 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3035 | 172.31 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28062 | 172.31 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23285 | 172.31 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32967 | 172.31 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28036 | 172.31 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23622 | 154.37 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25255 | 154.37 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31894 | 154.37 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31515 | 154.37 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36421 | 154.37 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33804 | 154.37 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31515 | 154.37 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36421 | 154.37 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31489 | 154.37 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23614 | 147.47 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25248 | 147.47 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31887 | 147.47 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31508 | 147.47 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36413 | 147.47 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33796 | 147.47 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31508 | 147.47 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36413 | 147.47 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31482 | 147.47 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24826 | 140.83 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26262 | 140.83 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31975 | 140.83 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31644 | 140.83 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36965 | 140.83 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34442 | 140.83 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31644 | 140.83 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2069 | 140.83 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36965 | 140.83 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31603 | 140.83 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24423 | 122.24 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26059 | 122.24 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32719 | 122.24 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32354 | 122.24 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.37215 | 122.24 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34597 | 122.24 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32354 | 122.24 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.37215 | 122.24 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32327 | 122.24 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26191 | 155.64 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25822 | 155.64 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30693 | 155.64 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27973 | 155.64 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25822 | 155.64 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23982 | 155.64 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30693 | 155.64 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25795 | 155.64 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26282 | 158.61 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25917 | 158.61 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30781 | 158.61 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28062 | 158.61 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25917 | 158.61 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24011 | 158.61 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30781 | 158.61 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25889 | 158.61 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20571 | 138.83 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22414 | 138.83 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29067 | 138.83 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28701 | 138.83 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33566 | 138.83 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30847 | 138.83 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28701 | 138.83 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21226 | 138.83 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33566 | 138.83 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28674 | 138.83 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.206 | 134.69 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22443 | 134.69 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29096 | 134.69 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2873 | 134.69 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33595 | 134.69 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30876 | 134.69 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2873 | 134.69 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21197 | 134.69 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33595 | 134.69 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28703 | 134.69 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21361 | 127.4 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23091 | 127.4 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29052 | 127.4 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28725 | 127.4 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33944 | 127.4 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31392 | 127.4 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28725 | 127.4 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21963 | 127.4 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33944 | 127.4 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28685 | 127.4 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21278 | 113.78 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23124 | 113.78 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29794 | 113.78 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29442 | 113.78 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34267 | 113.78 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31547 | 113.78 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29442 | 113.78 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20524 | 113.78 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34267 | 113.78 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29413 | 113.78 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26282 | 158.61 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25916 | 158.61 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30781 | 158.61 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28062 | 158.61 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25916 | 158.61 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24011 | 158.61 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30781 | 158.61 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25889 | 158.61 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20571 | 138.83 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22414 | 138.83 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29067 | 138.83 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28701 | 138.83 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33566 | 138.83 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30847 | 138.83 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28701 | 138.83 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21226 | 138.83 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33566 | 138.83 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28674 | 138.83 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.206 | 134.69 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22443 | 134.69 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29096 | 134.69 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2873 | 134.69 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33595 | 134.69 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30876 | 134.69 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2873 | 134.69 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21197 | 134.69 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33595 | 134.69 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28703 | 134.69 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21361 | 127.4 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2309 | 127.4 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29052 | 127.4 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28725 | 127.4 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33944 | 127.4 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31392 | 127.4 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28725 | 127.4 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21963 | 127.4 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33944 | 127.4 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28685 | 127.4 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21278 | 113.78 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23123 | 113.78 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29794 | 113.78 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29442 | 113.78 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34267 | 113.78 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31547 | 113.78 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29442 | 113.78 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20524 | 113.78 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34267 | 113.78 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29413 | 113.78 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2624 | 155.82 | P12:345:OKGE:BKBK443NEW3
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25871 | 155.82 | P12:345:OKGE:BKBK443NEW3
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30741 | 155.82 | P12:345:OKGE:BKBK443NEW3
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28021 | 155.82 | P12:345:OKGE:BKBK443NEW3
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25871 | 155.82 | P12:345:OKGE:BKBK443NEW3
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23962 | 155.82 | P12:345:OKGE:BKBK443NEW3
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30741 | 155.82 | P12:345:OKGE:BKBK443NEW3
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25844 | 155.82 | P12:345:OKGE:BKBK443NEW3
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26266 | 155.77 | P12:345:OKGE:BKRBKR143
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25897 | 155.77 | P12:345:OKGE:BKRBKR143
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30767 | 155.77 | P12:345:OKGE:BKRBKR143
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28047 | 155.77 | P12:345:OKGE:BKRBKR143
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25897 | 155.77 | P12:345:OKGE:BKRBKR143
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23944 | 155.77 | P12:345:OKGE:BKRBKR143
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30767 | 155.77 | P12:345:OKGE:BKRBKR143
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2587 | 155.77 | P12:345:OKGE:BKRBKR143
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25915 | 157.45 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25554 | 157.45 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30412 | 157.45 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27695 | 157.45 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25554 | 157.45 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24584 | 157.45 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30412 | 157.45 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25526 | 157.45 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20345 | 137.53 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22175 | 137.53 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28749 | 137.53 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28388 | 137.53 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33245 | 137.53 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30528 | 137.53 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28388 | 137.53 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21751 | 137.53 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33245 | 137.53 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2836 | 137.53 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20371 | 134.02 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22201 | 134.02 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28775 | 134.02 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28414 | 134.02 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33271 | 134.02 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30554 | 134.02 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28414 | 134.02 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21725 | 134.02 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33271 | 134.02 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28385 | 134.02 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21128 | 126.81 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2284 | 126.81 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28699 | 126.81 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28378 | 126.81 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33593 | 126.81 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3104 | 126.81 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28378 | 126.81 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22547 | 126.81 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33593 | 126.81 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28337 | 126.81 | P12:345:OKGE:BKRBKR150
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20382 | 135.49 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22224 | 135.49 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28893 | 135.49 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28526 | 135.49 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33393 | 135.49 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30675 | 135.49 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28526 | 135.49 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21373 | 135.49 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33393 | 135.49 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28499 | 135.49 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21087 | 110.59 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22931 | 110.59 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29619 | 110.59 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29265 | 110.59 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34092 | 110.59 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31373 | 110.59 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29265 | 110.59 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20672 | 110.59 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34092 | 110.59 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29236 | 110.59 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20382 | 135.49 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22224 | 135.49 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28893 | 135.49 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28526 | 135.49 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33393 | 135.49 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30675 | 135.49 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28526 | 135.49 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21373 | 135.49 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33393 | 135.49 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28499 | 135.49 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21087 | 110.59 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22931 | 110.59 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29619 | 110.59 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29265 | 110.59 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34092 | 110.59 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31373 | 110.59 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29265 | 110.59 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20672 | 110.59 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34092 | 110.59 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29236 | 110.59 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26231 | 155.8 | P12:345:OKGE:BKRBKR21
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25863 | 155.8 | P12:345:OKGE:BKRBKR21
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30732 | 155.8 | P12:345:OKGE:BKRBKR21
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28015 | 155.8 | P12:345:OKGE:BKRBKR21
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25863 | 155.8 | P12:345:OKGE:BKRBKR21
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23996 | 155.8 | P12:345:OKGE:BKRBKR21
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30732 | 155.8 | P12:345:OKGE:BKRBKR21
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25836 | 155.8 | P12:345:OKGE:BKRBKR21
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21277 | 125.9 | P12:345:OKGE:BKRBKR21
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23005 | 125.9 | P12:345:OKGE:BKRBKR21
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29009 | 125.9 | P12:345:OKGE:BKRBKR21
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2868 | 125.9 | P12:345:OKGE:BKRBKR21
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33903 | 125.9 | P12:345:OKGE:BKRBKR21
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31353 | 125.9 | P12:345:OKGE:BKRBKR21
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2868 | 125.9 | P12:345:OKGE:BKRBKR21
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21936 | 125.9 | P12:345:OKGE:BKRBKR21
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33903 | 125.9 | P12:345:OKGE:BKRBKR21
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28639 | 125.9 | P12:345:OKGE:BKRBKR21
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26484 | 159.05 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26118 | 159.05 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30985 | 159.05 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2827 | 159.05 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26118 | 159.05 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23858 | 159.05 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30985 | 159.05 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2609 | 159.05 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20792 | 139.74 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22622 | 139.74 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29279 | 139.74 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28913 | 139.74 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3378 | 139.74 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31065 | 139.74 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28913 | 139.74 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21063 | 139.74 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3378 | 139.74 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28885 | 139.74 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2081 | 136.36 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2264 | 136.36 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29298 | 136.36 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28931 | 136.36 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33798 | 136.36 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31083 | 136.36 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28931 | 136.36 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21045 | 136.36 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33798 | 136.36 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28904 | 136.36 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21623 | 129.44 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23334 | 129.44 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29285 | 129.44 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28959 | 129.44 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34182 | 129.44 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31632 | 129.44 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28959 | 129.44 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.218 | 129.44 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34182 | 129.44 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28918 | 129.44 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21498 | 115.31 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2333 | 115.31 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30005 | 115.31 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29652 | 115.31 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34479 | 115.31 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31764 | 115.31 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29652 | 115.31 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20362 | 115.31 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34479 | 115.31 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29623 | 115.31 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26272 | 156.11 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25906 | 156.11 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30771 | 156.11 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28052 | 156.11 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25906 | 156.11 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24005 | 156.11 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30771 | 156.11 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25878 | 156.11 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20551 | 137.9 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22395 | 137.9 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29055 | 137.9 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28689 | 137.9 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33555 | 137.9 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30835 | 137.9 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28689 | 137.9 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21222 | 137.9 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33555 | 137.9 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28662 | 137.9 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20581 | 133.94 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22425 | 133.94 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29085 | 133.94 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28719 | 133.94 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33585 | 133.94 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30865 | 133.94 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28719 | 133.94 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 133.94 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33585 | 133.94 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28692 | 133.94 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21341 | 126.54 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23071 | 126.54 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29041 | 126.54 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28714 | 126.54 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33933 | 126.54 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31382 | 126.54 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28714 | 126.54 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21957 | 126.54 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33933 | 126.54 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28673 | 126.54 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26272 | 156.12 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25906 | 156.12 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30772 | 156.12 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28052 | 156.12 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25906 | 156.12 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24006 | 156.12 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30772 | 156.12 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25878 | 156.12 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20552 | 137.9 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22396 | 137.9 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29055 | 137.9 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28689 | 137.9 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33555 | 137.9 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30836 | 137.9 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28689 | 137.9 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21222 | 137.9 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33555 | 137.9 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28662 | 137.9 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20582 | 133.95 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22426 | 133.95 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29085 | 133.95 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28719 | 133.95 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33585 | 133.95 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30866 | 133.95 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28719 | 133.95 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 133.95 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33585 | 133.95 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28692 | 133.95 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21341 | 126.55 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23072 | 126.55 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29041 | 126.55 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28714 | 126.55 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33933 | 126.55 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31382 | 126.55 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28714 | 126.55 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21957 | 126.55 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33933 | 126.55 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28674 | 126.55 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21258 | 112.87 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23104 | 112.87 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29782 | 112.87 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29429 | 112.87 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34255 | 112.87 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31535 | 112.87 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29429 | 112.87 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2052 | 112.87 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34255 | 112.87 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.294 | 112.87 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20874 | 110.61 | P12:345:OKGE:BKRBKR349
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22711 | 110.61 | P12:345:OKGE:BKRBKR349
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29337 | 110.61 | P12:345:OKGE:BKRBKR349
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28987 | 110.61 | P12:345:OKGE:BKRBKR349
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33809 | 110.61 | P12:345:OKGE:BKRBKR349
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3109 | 110.61 | P12:345:OKGE:BKRBKR349
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28987 | 110.61 | P12:345:OKGE:BKRBKR349
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21099 | 110.61 | P12:345:OKGE:BKRBKR349
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33809 | 110.61 | P12:345:OKGE:BKRBKR349
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28958 | 110.61 | P12:345:OKGE:BKRBKR349
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20379 | 135.8 | P12:345:OKGE:BKRBKR357_2
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22226 | 135.8 | P12:345:OKGE:BKRBKR357_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28926 | 135.8 | P12:345:OKGE:BKRBKR357_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28558 | 135.8 | P12:345:OKGE:BKRBKR357_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33427 | 135.8 | P12:345:OKGE:BKRBKR357_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30708 | 135.8 | P12:345:OKGE:BKRBKR357_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28558 | 135.8 | P12:345:OKGE:BKRBKR357_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21259 | 135.8 | P12:345:OKGE:BKRBKR357_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33427 | 135.8 | P12:345:OKGE:BKRBKR357_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28531 | 135.8 | P12:345:OKGE:BKRBKR357_2
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26249 | 155.61 | P12:345:OKGE:BKRBKR4193
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25882 | 155.61 | P12:345:OKGE:BKRBKR4193
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30749 | 155.61 | P12:345:OKGE:BKRBKR4193
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28027 | 155.61 | P12:345:OKGE:BKRBKR4193
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25882 | 155.61 | P12:345:OKGE:BKRBKR4193
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23968 | 155.61 | P12:345:OKGE:BKRBKR4193
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30749 | 155.61 | P12:345:OKGE:BKRBKR4193
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25855 | 155.61 | P12:345:OKGE:BKRBKR4193
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26249 | 155.61 | P12:345:OKGE:BKRBKR4194
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25883 | 155.61 | P12:345:OKGE:BKRBKR4194
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30749 | 155.61 | P12:345:OKGE:BKRBKR4194
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28027 | 155.61 | P12:345:OKGE:BKRBKR4194
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25883 | 155.61 | P12:345:OKGE:BKRBKR4194
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23968 | 155.61 | P12:345:OKGE:BKRBKR4194
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30749 | 155.61 | P12:345:OKGE:BKRBKR4194
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25855 | 155.61 | P12:345:OKGE:BKRBKR4194
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2101 | 167.65 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2778 | 167.65 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27396 | 167.65 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32304 | 167.65 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29658 | 167.65 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27396 | 167.65 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23261 | 167.65 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32304 | 167.65 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27371 | 167.65 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22506 | 152.05 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24206 | 152.05 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30976 | 152.05 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30592 | 152.05 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35499 | 152.05 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32854 | 152.05 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30592 | 152.05 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20066 | 152.05 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35499 | 152.05 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30567 | 152.05 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22519 | 145.29 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24218 | 145.29 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30988 | 145.29 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30604 | 145.29 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35511 | 145.29 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32866 | 145.29 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30604 | 145.29 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20053 | 145.29 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35511 | 145.29 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30579 | 145.29 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23579 | 138.59 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25108 | 138.59 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31046 | 138.59 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30707 | 138.59 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36009 | 138.59 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33482 | 138.59 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30707 | 138.59 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20842 | 138.59 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36009 | 138.59 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30667 | 138.59 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23262 | 123.4 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24963 | 123.4 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31753 | 123.4 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31384 | 123.4 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36247 | 123.4 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33601 | 123.4 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31384 | 123.4 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36247 | 123.4 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31357 | 123.4 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26267 | 156.03 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25899 | 156.03 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30769 | 156.03 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28049 | 156.03 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25899 | 156.03 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23925 | 156.03 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30769 | 156.03 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25872 | 156.03 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20524 | 137.77 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2237 | 137.77 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2907 | 137.77 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28701 | 137.77 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33571 | 137.77 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30852 | 137.77 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28701 | 137.77 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21122 | 137.77 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33571 | 137.77 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28674 | 137.77 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21313 | 125.89 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23046 | 125.89 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29062 | 125.89 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28733 | 125.89 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33955 | 125.89 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31405 | 125.89 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28733 | 125.89 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21844 | 125.89 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33955 | 125.89 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28692 | 125.89 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26267 | 156.03 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25899 | 156.03 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30769 | 156.03 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28049 | 156.03 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25899 | 156.03 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23925 | 156.03 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30769 | 156.03 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25872 | 156.03 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20524 | 137.77 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2237 | 137.77 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2907 | 137.77 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28701 | 137.77 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33571 | 137.77 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30852 | 137.77 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28701 | 137.77 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21122 | 137.77 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33571 | 137.77 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28674 | 137.77 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21313 | 125.89 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23046 | 125.89 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29062 | 125.89 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28733 | 125.89 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33955 | 125.89 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31405 | 125.89 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28733 | 125.89 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21844 | 125.89 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33955 | 125.89 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28692 | 125.89 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26202 | 148.83 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 148.83 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 148.83 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27985 | 148.83 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 148.83 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23967 | 148.83 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 148.83 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25806 | 148.83 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 134.3 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 134.3 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 134.3 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 134.3 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 134.3 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 134.3 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 134.3 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 134.3 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 134.3 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 134.3 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 109.58 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 109.58 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 109.58 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 109.58 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 109.58 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 109.58 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 109.58 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 109.58 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 109.58 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 109.58 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26202 | 149.77 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 149.77 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 149.77 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27985 | 149.77 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 149.77 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23967 | 149.77 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 149.77 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25806 | 149.77 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 134.49 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 134.49 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 134.49 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 134.49 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 134.49 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 134.49 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 134.49 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 134.49 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 134.49 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 134.49 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 130.62 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 130.62 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 130.62 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 130.62 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 130.62 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 130.62 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 130.62 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 130.62 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 130.62 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 130.62 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 123.07 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 123.07 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 123.07 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 123.07 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 123.07 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 123.07 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 123.07 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 123.07 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 123.07 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 123.07 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 109.78 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 109.78 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 109.78 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 109.78 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 109.78 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 109.78 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 109.78 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 109.78 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 109.78 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 109.78 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26202 | 151.98 | P12:345:OKGE:BKRBKR608
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 151.98 | P12:345:OKGE:BKRBKR608
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 151.98 | P12:345:OKGE:BKRBKR608
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27985 | 151.98 | P12:345:OKGE:BKRBKR608
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 151.98 | P12:345:OKGE:BKRBKR608
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23967 | 151.98 | P12:345:OKGE:BKRBKR608
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 151.98 | P12:345:OKGE:BKRBKR608
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25806 | 151.98 | P12:345:OKGE:BKRBKR608
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20404 | 135.21 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22251 | 135.21 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28952 | 135.21 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28584 | 135.21 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33454 | 135.21 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30734 | 135.21 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28584 | 135.21 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21232 | 135.21 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33454 | 135.21 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28557 | 135.21 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20435 | 131.52 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22282 | 131.52 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28984 | 131.52 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28615 | 131.52 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33485 | 131.52 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30766 | 131.52 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28615 | 131.52 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.212 | 131.52 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33485 | 131.52 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28588 | 131.52 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21182 | 123.99 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22917 | 123.99 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28935 | 123.99 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28606 | 123.99 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33828 | 123.99 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31278 | 123.99 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28606 | 123.99 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21962 | 123.99 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33828 | 123.99 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28565 | 123.99 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.211 | 110.73 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22949 | 110.73 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29669 | 110.73 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29313 | 110.73 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34143 | 110.73 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31423 | 110.73 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29313 | 110.73 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20541 | 110.73 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34143 | 110.73 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29285 | 110.73 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25967 | 149.02 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25601 | 149.02 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30467 | 149.02 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27749 | 149.02 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25601 | 149.02 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24369 | 149.02 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30467 | 149.02 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25574 | 149.02 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20125 | 133.48 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21962 | 133.48 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 133.48 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28242 | 133.48 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33108 | 133.48 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3039 | 133.48 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28242 | 133.48 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21728 | 133.48 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33108 | 133.48 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28215 | 133.48 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20169 | 127.83 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22006 | 127.83 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28652 | 127.83 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28287 | 127.83 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33152 | 127.83 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30435 | 127.83 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28287 | 127.83 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21684 | 127.83 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33152 | 127.83 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28259 | 127.83 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20906 | 119.99 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22627 | 119.99 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28576 | 119.99 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2825 | 119.99 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3347 | 119.99 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30919 | 119.99 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2825 | 119.99 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22486 | 119.99 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3347 | 119.99 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28209 | 119.99 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20832 | 108.36 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22671 | 108.36 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29336 | 108.36 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28983 | 108.36 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33808 | 108.36 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31091 | 108.36 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28983 | 108.36 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21026 | 108.36 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33808 | 108.36 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28954 | 108.36 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26431 | 162.9 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26065 | 162.9 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30932 | 162.9 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2822 | 162.9 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26065 | 162.9 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2399 | 162.9 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30932 | 162.9 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26037 | 162.9 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20899 | 142.59 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22724 | 142.59 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29365 | 142.59 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28999 | 142.59 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33866 | 142.59 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31154 | 142.59 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28999 | 142.59 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21055 | 142.59 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33866 | 142.59 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28972 | 142.59 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20918 | 140.18 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22742 | 140.18 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29384 | 140.18 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29018 | 140.18 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33885 | 140.18 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31173 | 140.18 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29018 | 140.18 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21036 | 140.18 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33885 | 140.18 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28991 | 140.18 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21728 | 133.55 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23431 | 133.55 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29359 | 133.55 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29034 | 133.55 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34259 | 133.55 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31709 | 133.55 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29034 | 133.55 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21805 | 133.55 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34259 | 133.55 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28993 | 133.55 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2162 | 117.52 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23446 | 117.52 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30106 | 117.52 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29753 | 117.52 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3458 | 117.52 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31867 | 117.52 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29753 | 117.52 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2034 | 117.52 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3458 | 117.52 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29724 | 117.52 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26258 | 155.74 | P12:345:OKGE-ITC:BKRBKR502_1
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25889 | 155.74 | P12:345:OKGE-ITC:BKRBKR502_1
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 155.74 | P12:345:OKGE-ITC:BKRBKR502_1
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2804 | 155.74 | P12:345:OKGE-ITC:BKRBKR502_1
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25889 | 155.74 | P12:345:OKGE-ITC:BKRBKR502_1
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23929 | 155.74 | P12:345:OKGE-ITC:BKRBKR502_1
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 155.74 | P12:345:OKGE-ITC:BKRBKR502_1
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25862 | 155.74 | P12:345:OKGE-ITC:BKRBKR502_1
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26258 | 155.74 | P12:345:OKGE-ITC:BKRBKR503_1
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25889 | 155.74 | P12:345:OKGE-ITC:BKRBKR503_1
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 155.74 | P12:345:OKGE-ITC:BKRBKR503_1
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2804 | 155.74 | P12:345:OKGE-ITC:BKRBKR503_1
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25889 | 155.74 | P12:345:OKGE-ITC:BKRBKR503_1
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23929 | 155.74 | P12:345:OKGE-ITC:BKRBKR503_1
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 155.74 | P12:345:OKGE-ITC:BKRBKR503_1
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25862 | 155.74 | P12:345:OKGE-ITC:BKRBKR503_1
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2101 | 167.65 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2778 | 167.65 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27396 | 167.65 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32304 | 167.65 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29658 | 167.65 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27396 | 167.65 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23261 | 167.65 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32304 | 167.65 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27371 | 167.65 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22506 | 152.07 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24206 | 152.07 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30976 | 152.07 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30592 | 152.07 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35499 | 152.07 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32854 | 152.07 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30592 | 152.07 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20066 | 152.07 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35499 | 152.07 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30567 | 152.07 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22519 | 145.33 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24218 | 145.33 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30988 | 145.33 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30604 | 145.33 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35511 | 145.33 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32866 | 145.33 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30604 | 145.33 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20053 | 145.33 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35511 | 145.33 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30579 | 145.33 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23579 | 138.62 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25108 | 138.62 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31046 | 138.62 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30707 | 138.62 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36009 | 138.62 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33482 | 138.62 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30707 | 138.62 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20842 | 138.62 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36009 | 138.62 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30667 | 138.62 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23262 | 123.43 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24963 | 123.43 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31753 | 123.43 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31384 | 123.43 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36247 | 123.43 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33601 | 123.43 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31384 | 123.43 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36247 | 123.43 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31357 | 123.43 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26245 | 156.1 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25877 | 156.1 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30747 | 156.1 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28027 | 156.1 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25877 | 156.1 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23948 | 156.1 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30747 | 156.1 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2585 | 156.1 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20498 | 137.76 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22344 | 137.76 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29042 | 137.76 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28673 | 137.76 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33543 | 137.76 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30823 | 137.76 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28673 | 137.76 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21152 | 137.76 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33543 | 137.76 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28646 | 137.76 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20531 | 133.51 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22378 | 133.51 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29075 | 133.51 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28707 | 133.51 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33576 | 133.51 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30857 | 133.51 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28707 | 133.51 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21118 | 133.51 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33576 | 133.51 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2868 | 133.51 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21285 | 126.11 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23019 | 126.11 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29032 | 126.11 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28703 | 126.11 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33925 | 126.11 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31375 | 126.11 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28703 | 126.11 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21875 | 126.11 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33925 | 126.11 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28663 | 126.11 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21201 | 113 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23049 | 113 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29764 | 113 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29409 | 113 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34239 | 113 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31519 | 113 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29409 | 113 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20454 | 113 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34239 | 113 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29381 | 113 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26245 | 156.1 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25877 | 156.1 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30747 | 156.1 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28027 | 156.1 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25877 | 156.1 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23948 | 156.1 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30747 | 156.1 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2585 | 156.1 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20498 | 137.76 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22344 | 137.76 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29042 | 137.76 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28673 | 137.76 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33543 | 137.76 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30823 | 137.76 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28673 | 137.76 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21152 | 137.76 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33543 | 137.76 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28646 | 137.76 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20531 | 133.51 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22378 | 133.51 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29075 | 133.51 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28707 | 133.51 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33576 | 133.51 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30857 | 133.51 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28707 | 133.51 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21118 | 133.51 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33576 | 133.51 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2868 | 133.51 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21285 | 126.11 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23019 | 126.11 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29032 | 126.11 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28703 | 126.11 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33925 | 126.11 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31375 | 126.11 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28703 | 126.11 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21875 | 126.11 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33925 | 126.11 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28663 | 126.11 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21201 | 113 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23049 | 113 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29764 | 113 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29409 | 113 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34239 | 113 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31519 | 113 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29409 | 113 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20454 | 113 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34239 | 113 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29381 | 113 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26258 | 155.74 | P12:345:PWT:THIS-DGRS_345_1::FUTURE
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25889 | 155.74 | P12:345:PWT:THIS-DGRS_345_1::FUTURE
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 155.74 | P12:345:PWT:THIS-DGRS_345_1::FUTURE
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2804 | 155.74 | P12:345:PWT:THIS-DGRS_345_1::FUTURE
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25889 | 155.74 | P12:345:PWT:THIS-DGRS_345_1::FUTURE
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23929 | 155.74 | P12:345:PWT:THIS-DGRS_345_1::FUTURE
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 155.74 | P12:345:PWT:THIS-DGRS_345_1::FUTURE
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25862 | 155.74 | P12:345:PWT:THIS-DGRS_345_1::FUTURE
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26258 | 155.74 | P12:345:PWT:THIS-DGRS_345_2::FUTURE
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25889 | 155.74 | P12:345:PWT:THIS-DGRS_345_2::FUTURE
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 155.74 | P12:345:PWT:THIS-DGRS_345_2::FUTURE
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2804 | 155.74 | P12:345:PWT:THIS-DGRS_345_2::FUTURE
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25889 | 155.74 | P12:345:PWT:THIS-DGRS_345_2::FUTURE
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23929 | 155.74 | P12:345:PWT:THIS-DGRS_345_2::FUTURE
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 155.74 | P12:345:PWT:THIS-DGRS_345_2::FUTURE
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25862 | 155.74 | P12:345:PWT:THIS-DGRS_345_2::FUTURE
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26511 | 161.46 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26148 | 161.46 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31008 | 161.46 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28284 | 161.46 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26148 | 161.46 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23809 | 161.46 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31008 | 161.46 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26121 | 161.46 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20984 | 140.57 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22834 | 140.57 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29449 | 140.57 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29086 | 140.57 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33945 | 140.57 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31222 | 140.57 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29086 | 140.57 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20871 | 140.57 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33945 | 140.57 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29058 | 140.57 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2102 | 134.98 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2287 | 134.98 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29485 | 134.98 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29122 | 134.98 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33981 | 134.98 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31258 | 134.98 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29122 | 134.98 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20835 | 134.98 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33981 | 134.98 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29094 | 134.98 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21777 | 127.69 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23514 | 127.69 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29442 | 127.69 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29119 | 127.69 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34331 | 127.69 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31777 | 127.69 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29119 | 127.69 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21595 | 127.69 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34331 | 127.69 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29078 | 127.69 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21698 | 116.65 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23549 | 116.65 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30182 | 116.65 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29832 | 116.65 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34652 | 116.65 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31928 | 116.65 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29832 | 116.65 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20163 | 116.65 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34652 | 116.65 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29803 | 116.65 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20276 | 179.09 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21862 | 179.09 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30617 | 179.09 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30101 | 179.09 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3265 | 179.09 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31396 | 179.09 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30101 | 179.09 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33869 | 179.09 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3265 | 179.09 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30142 | 179.09 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24L | GEN-2017-104 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24294 | 179.09 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25304 | 147.43 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26889 | 147.43 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35645 | 147.43 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35129 | 147.43 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.37678 | 147.43 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36423 | 147.43 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35129 | 147.43 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28842 | 147.43 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.37678 | 147.43 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3517 | 147.43 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24WP | GEN-2017-104 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29322 | 147.43 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25398 | 146.53 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27178 | 146.53 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36788 | 146.53 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36229 | 146.53 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.38487 | 146.53 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.37692 | 146.53 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36229 | 146.53 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28586 | 146.53 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.38487 | 146.53 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36282 | 146.53 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 19WP | GEN-2017-104 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33702 | 146.53 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25621 | 146.46 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27206 | 146.46 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35962 | 146.46 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35446 | 146.46 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.37994 | 146.46 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3674 | 146.46 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35446 | 146.46 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28525 | 146.46 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.37994 | 146.46 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35486 | 146.46 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 24SP | GEN-2017-104 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29638 | 146.46 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21306 | 125.74 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1)
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23042 | 125.74 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29035 | 125.74 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28707 | 125.74 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33926 | 125.74 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31374 | 125.74 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28707 | 125.74 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21899 | 125.74 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33926 | 125.74 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28666 | 125.74 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26283 | 157.3 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25915 | 157.3 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30784 | 157.3 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28064 | 157.3 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25915 | 157.3 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23915 | 157.3 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30784 | 157.3 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25888 | 157.3 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26262 | 156.49 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25894 | 156.49 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30763 | 156.49 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28044 | 156.49 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25894 | 156.49 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23928 | 156.49 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30763 | 156.49 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25867 | 156.49 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26271 | 156.19 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25904 | 156.19 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30771 | 156.19 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2805 | 156.19 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25904 | 156.19 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2395 | 156.19 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30771 | 156.19 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25877 | 156.19 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21312 | 126.43 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23048 | 126.43 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29039 | 126.43 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28711 | 126.43 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3393 | 126.43 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31378 | 126.43 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28711 | 126.43 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21898 | 126.43 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3393 | 126.43 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28671 | 126.43 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26287 | 157.15 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25919 | 157.15 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30788 | 157.15 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28068 | 157.15 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25919 | 157.15 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23911 | 157.15 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30788 | 157.15 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25892 | 157.15 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21097 | 112.91 | P12:500:EES-EAI:ARK_NU:FTSMTH:1
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22947 | 112.91 | P12:500:EES-EAI:ARK_NU:FTSMTH:1
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29671 | 112.91 | P12:500:EES-EAI:ARK_NU:FTSMTH:1
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29315 | 112.91 | P12:500:EES-EAI:ARK_NU:FTSMTH:1
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34145 | 112.91 | P12:500:EES-EAI:ARK_NU:FTSMTH:1
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31425 | 112.91 | P12:500:EES-EAI:ARK_NU:FTSMTH:1
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29315 | 112.91 | P12:500:EES-EAI:ARK_NU:FTSMTH:1
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20529 | 112.91 | P12:500:EES-EAI:ARK_NU:FTSMTH:1
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34145 | 112.91 | P12:500:EES-EAI:ARK_NU:FTSMTH:1
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29286 | 112.91 | P12:500:EES-EAI:ARK_NU:FTSMTH:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21188 | 123.86 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22924 | 123.86 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28947 | 123.86 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28617 | 123.86 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3384 | 123.86 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3129 | 123.86 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28617 | 123.86 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21939 | 123.86 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3384 | 123.86 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28577 | 123.86 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21182 | 123.99 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22917 | 123.99 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28935 | 123.99 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28606 | 123.99 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33828 | 123.99 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31278 | 123.99 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28606 | 123.99 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21962 | 123.99 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33828 | 123.99 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28565 | 123.99 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 125.04 | P12:HV:EES::TURK 4%:1(1)
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 125.04 | P12:HV:EES::TURK 4%:1(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 125.04 | P12:HV:EES::TURK 4%:1(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 125.04 | P12:HV:EES::TURK 4%:1(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 125.04 | P12:HV:EES::TURK 4%:1(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 125.04 | P12:HV:EES::TURK 4%:1(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 125.04 | P12:HV:EES::TURK 4%:1(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 125.04 | P12:HV:EES::TURK 4%:1(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 125.04 | P12:HV:EES::TURK 4%:1(1)
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 125.04 | P12:HV:EES::TURK 4%:1(1)
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 135.89 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 135.89 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 135.89 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 135.89 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 135.89 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 135.89 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 135.89 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 135.89 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 135.89 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 135.89 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.42 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.42 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.42 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.42 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.42 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.42 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.42 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.42 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.42 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.42 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.6 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.6 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.6 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.6 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.6 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.6 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.6 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.6 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.6 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.6 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20548 | 137.89 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22393 | 137.89 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29067 | 137.89 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.287 | 137.89 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33567 | 137.89 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30845 | 137.89 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.287 | 137.89 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21154 | 137.89 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33567 | 137.89 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28673 | 137.89 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20583 | 133.61 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22428 | 133.61 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29102 | 133.61 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28735 | 133.61 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33601 | 133.61 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3088 | 133.61 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28735 | 133.61 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21119 | 133.61 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33601 | 133.61 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28708 | 133.61 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21332 | 126.12 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23065 | 126.12 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29056 | 126.12 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28729 | 126.12 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33947 | 126.12 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31396 | 126.12 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28729 | 126.12 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21878 | 126.12 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33947 | 126.12 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28688 | 126.12 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21252 | 113.01 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.231 | 113.01 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29791 | 113.01 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29438 | 113.01 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34264 | 113.01 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31543 | 113.01 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29438 | 113.01 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20454 | 113.01 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34264 | 113.01 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29409 | 113.01 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.83 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.83 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.83 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.83 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.83 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.83 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.83 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.83 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.83 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.83 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 132.45 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 132.45 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 132.45 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.45 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.45 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 132.45 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.45 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 132.45 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.45 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 132.45 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 125.04 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 125.04 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 125.04 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 125.04 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 125.04 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 125.04 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 125.04 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 125.04 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 125.04 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 125.04 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 112.01 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 112.01 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 112.01 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.01 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.01 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 112.01 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 112.01 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 112.01 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 112.01 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 112.01 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20398 | 135.8 | P13:138-345:OKGE:BKRBKR_3W034
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22243 | 135.8 | P13:138-345:OKGE:BKRBKR_3W034
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28941 | 135.8 | P13:138-345:OKGE:BKRBKR_3W034
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28572 | 135.8 | P13:138-345:OKGE:BKRBKR_3W034
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33442 | 135.8 | P13:138-345:OKGE:BKRBKR_3W034
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30723 | 135.8 | P13:138-345:OKGE:BKRBKR_3W034
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28572 | 135.8 | P13:138-345:OKGE:BKRBKR_3W034
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21257 | 135.8 | P13:138-345:OKGE:BKRBKR_3W034
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33442 | 135.8 | P13:138-345:OKGE:BKRBKR_3W034
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28545 | 135.8 | P13:138-345:OKGE:BKRBKR_3W034
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20393 | 135.77 | P13:138-345:OKGE:BKRBKR_3W035
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22238 | 135.77 | P13:138-345:OKGE:BKRBKR_3W035
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28934 | 135.77 | P13:138-345:OKGE:BKRBKR_3W035
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28565 | 135.77 | P13:138-345:OKGE:BKRBKR_3W035
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33435 | 135.77 | P13:138-345:OKGE:BKRBKR_3W035
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30716 | 135.77 | P13:138-345:OKGE:BKRBKR_3W035
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28565 | 135.77 | P13:138-345:OKGE:BKRBKR_3W035
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2127 | 135.77 | P13:138-345:OKGE:BKRBKR_3W035
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33435 | 135.77 | P13:138-345:OKGE:BKRBKR_3W035
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28538 | 135.77 | P13:138-345:OKGE:BKRBKR_3W035
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.67 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.67 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.67 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.67 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.67 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.67 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.67 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.67 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.67 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.67 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 132.37 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 132.37 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 132.37 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.37 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.37 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 132.37 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.37 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 132.37 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.37 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 132.37 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.88 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.88 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.88 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.88 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.88 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.88 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.88 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.88 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.88 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.88 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 111.92 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.92 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 111.92 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.92 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.92 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 111.92 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.92 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 111.92 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.92 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 111.92 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26202 | 154.68 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 154.68 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 154.68 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27985 | 154.68 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 154.68 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23967 | 154.68 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 154.68 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25806 | 154.68 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.88 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.88 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.88 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.88 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.88 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.88 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.88 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.88 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.88 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.88 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.67 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.67 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.67 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.67 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.67 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.67 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.67 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.67 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.67 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.67 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 132.37 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 132.37 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 132.37 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.37 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.37 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 132.37 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.37 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 132.37 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.37 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 132.37 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.87 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.87 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.87 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.87 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.87 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.87 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.87 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.87 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.87 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.87 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 111.92 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.92 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 111.92 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.92 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.92 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 111.92 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.92 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 111.92 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.92 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 111.92 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.89 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.89 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.89 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.89 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.89 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.89 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.89 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.89 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.89 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.89 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26202 | 153.92 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 153.92 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 153.92 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27985 | 153.92 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 153.92 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23967 | 153.92 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 153.92 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25806 | 153.92 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 123.86 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 123.86 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 123.86 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 123.86 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 123.86 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 123.86 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 123.86 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 123.86 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 123.86 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 123.86 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26202 | 154.6 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 154.6 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 154.6 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27985 | 154.6 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 154.6 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23967 | 154.6 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 154.6 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25806 | 154.6 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.88 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.88 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.88 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.88 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.88 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.88 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.88 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.88 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.88 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.88 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.69 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.69 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.69 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.69 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.69 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.69 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.69 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.69 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.69 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.69 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.88 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.88 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.88 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.88 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.88 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.88 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.88 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.88 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.88 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.88 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.67 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.67 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.67 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.67 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.67 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.67 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.67 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.67 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.67 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.67 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 132.38 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 132.38 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 132.38 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.38 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.38 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 132.38 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.38 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 132.38 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.38 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 132.38 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.87 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.87 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.87 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.87 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.87 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.87 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.87 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.87 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.87 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.87 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 135.29 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 135.29 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 135.29 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 135.29 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 135.29 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 135.29 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 135.29 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 135.29 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 135.29 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 135.29 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 130.93 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 130.93 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 130.93 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 130.93 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 130.93 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 130.93 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 130.93 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 130.93 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 130.93 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 130.93 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 123.41 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 123.41 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 123.41 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 123.41 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 123.41 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 123.41 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 123.41 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 123.41 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 123.41 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 123.41 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26202 | 153.97 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 153.97 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 153.97 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27985 | 153.97 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 153.97 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23967 | 153.97 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 153.97 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25806 | 153.97 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.67 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.67 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.67 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.67 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.67 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.67 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.67 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.67 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.67 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.67 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 132.38 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 132.38 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 132.38 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.38 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.38 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 132.38 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.38 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 132.38 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.38 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 132.38 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.87 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.87 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.87 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.87 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.87 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.87 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.87 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.87 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.87 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.87 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.67 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.67 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.67 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.67 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.67 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.67 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.67 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.67 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.67 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.67 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 132.37 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 132.37 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 132.37 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.37 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.37 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 132.37 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.37 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 132.37 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.37 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 132.37 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.88 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.88 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.88 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.88 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.88 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.88 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.88 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.88 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.88 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.88 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 111.92 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.92 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 111.92 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.92 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.92 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 111.92 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.92 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 111.92 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.92 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 111.92 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.67 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.67 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.67 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.67 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.67 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.67 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.67 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.67 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.67 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.67 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 132.37 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 132.37 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 132.37 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.37 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.37 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 132.37 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.37 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 132.37 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.37 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 132.37 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.88 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.88 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.88 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.88 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.88 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.88 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.88 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.88 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.88 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.88 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 111.92 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.92 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 111.92 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.92 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.92 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 111.92 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.92 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 111.92 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.92 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 111.92 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.67 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.67 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.67 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.67 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.67 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.67 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.67 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.67 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.67 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.67 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 132.37 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 132.37 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 132.37 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.37 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.37 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 132.37 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.37 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 132.37 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.37 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 132.37 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.87 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.87 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.87 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.87 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.87 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.87 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.87 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.87 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.87 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.87 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 111.92 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.92 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 111.92 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.92 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.92 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 111.92 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.92 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 111.92 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.92 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 111.92 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.67 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.67 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.67 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.67 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.67 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.67 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.67 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.67 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.67 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.67 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 132.37 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 132.37 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 132.37 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.37 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.37 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 132.37 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.37 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 132.37 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.37 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 132.37 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.88 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.88 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.88 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.88 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.88 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.88 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.88 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.88 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.88 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.88 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 111.94 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.94 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 111.94 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.94 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.94 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 111.94 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.94 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 111.94 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.94 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 111.94 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20276 | 179.09 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21862 | 179.09 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30617 | 179.09 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30101 | 179.09 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3265 | 179.09 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31396 | 179.09 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30101 | 179.09 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33869 | 179.09 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3265 | 179.09 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30142 | 179.09 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-104 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24294 | 179.09 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25304 | 147.44 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26889 | 147.44 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35645 | 147.44 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35129 | 147.44 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.37678 | 147.44 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36423 | 147.44 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35129 | 147.44 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28842 | 147.44 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.37678 | 147.44 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3517 | 147.44 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-104 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29322 | 147.44 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25398 | 146.53 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27178 | 146.53 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36788 | 146.53 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36229 | 146.53 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.38487 | 146.53 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.37692 | 146.53 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36229 | 146.53 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28586 | 146.53 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.38487 | 146.53 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36282 | 146.53 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-104 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33702 | 146.53 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25621 | 146.46 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27206 | 146.46 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35962 | 146.46 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35446 | 146.46 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.37994 | 146.46 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3674 | 146.46 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35446 | 146.46 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28525 | 146.46 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.37994 | 146.46 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35486 | 146.46 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-104 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29638 | 146.46 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20406 | 135.56 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22254 | 135.56 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2896 | 135.56 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28591 | 135.56 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33461 | 135.56 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30742 | 135.56 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28591 | 135.56 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21215 | 135.56 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33461 | 135.56 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28564 | 135.56 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20441 | 131.37 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22288 | 131.37 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28994 | 131.37 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28625 | 131.37 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33495 | 131.37 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30776 | 131.37 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28625 | 131.37 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2118 | 131.37 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33495 | 131.37 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 131.37 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21188 | 123.86 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22924 | 123.86 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28947 | 123.86 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28617 | 123.86 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3384 | 123.86 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3129 | 123.86 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28617 | 123.86 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21939 | 123.86 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3384 | 123.86 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28577 | 123.86 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21106 | 110.79 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22955 | 110.79 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2968 | 110.79 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29324 | 110.79 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34154 | 110.79 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31434 | 110.79 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29324 | 110.79 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2052 | 110.79 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34154 | 110.79 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29295 | 110.79 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20406 | 135.58 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22254 | 135.58 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2896 | 135.58 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28591 | 135.58 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33461 | 135.58 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30742 | 135.58 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28591 | 135.58 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21215 | 135.58 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33461 | 135.58 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28564 | 135.58 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20441 | 131.39 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22288 | 131.39 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28994 | 131.39 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28625 | 131.39 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33495 | 131.39 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30776 | 131.39 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28625 | 131.39 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2118 | 131.39 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33495 | 131.39 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 131.39 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21188 | 123.88 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22924 | 123.88 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28947 | 123.88 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28617 | 123.88 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3384 | 123.88 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3129 | 123.88 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28617 | 123.88 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21939 | 123.88 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3384 | 123.88 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28577 | 123.88 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21106 | 110.83 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22955 | 110.83 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2968 | 110.83 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29324 | 110.83 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34154 | 110.83 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31434 | 110.83 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29324 | 110.83 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2052 | 110.83 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34154 | 110.83 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29295 | 110.83 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20406 | 135.56 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22254 | 135.56 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2896 | 135.56 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28591 | 135.56 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33461 | 135.56 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30742 | 135.56 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28591 | 135.56 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21215 | 135.56 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33461 | 135.56 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28564 | 135.56 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20441 | 131.38 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22288 | 131.38 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28994 | 131.38 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28625 | 131.38 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33495 | 131.38 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30776 | 131.38 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28625 | 131.38 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2118 | 131.38 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33495 | 131.38 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 131.38 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21188 | 123.86 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22924 | 123.86 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28947 | 123.86 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28617 | 123.86 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3384 | 123.86 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3129 | 123.86 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28617 | 123.86 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21939 | 123.86 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3384 | 123.86 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28577 | 123.86 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21106 | 110.79 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22955 | 110.79 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2968 | 110.79 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29324 | 110.79 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34154 | 110.79 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31434 | 110.79 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29324 | 110.79 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2052 | 110.79 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34154 | 110.79 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29295 | 110.79 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20396 | 135.82 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22243 | 135.82 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28947 | 135.82 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28578 | 135.82 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33448 | 135.82 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30729 | 135.82 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28578 | 135.82 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21233 | 135.82 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33448 | 135.82 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28551 | 135.82 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20396 | 135.82 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22243 | 135.82 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28947 | 135.82 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28578 | 135.82 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33448 | 135.82 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30729 | 135.82 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28578 | 135.82 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21233 | 135.82 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33448 | 135.82 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28551 | 135.82 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20396 | 135.81 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22243 | 135.81 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28947 | 135.81 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28578 | 135.81 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33448 | 135.81 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30729 | 135.81 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28578 | 135.81 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21233 | 135.81 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33448 | 135.81 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28551 | 135.81 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26439 | 163.4 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26073 | 163.4 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3094 | 163.4 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28228 | 163.4 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26073 | 163.4 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23988 | 163.4 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3094 | 163.4 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26045 | 163.4 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20912 | 141.85 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22735 | 141.85 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29377 | 141.85 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29011 | 141.85 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33878 | 141.85 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31166 | 141.85 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29011 | 141.85 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2105 | 141.85 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33878 | 141.85 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28983 | 141.85 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20931 | 139.34 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22754 | 139.34 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29396 | 139.34 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2903 | 139.34 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33897 | 139.34 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31185 | 139.34 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2903 | 139.34 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21031 | 139.34 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33897 | 139.34 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29002 | 139.34 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21741 | 132.55 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23443 | 132.55 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2937 | 132.55 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29045 | 132.55 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3427 | 132.55 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31721 | 132.55 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29045 | 132.55 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.218 | 132.55 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3427 | 132.55 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29004 | 132.55 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21633 | 116.62 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23458 | 116.62 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30118 | 116.62 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29765 | 116.62 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34592 | 116.62 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3188 | 116.62 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29765 | 116.62 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20334 | 116.62 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34592 | 116.62 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29736 | 116.62 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20169 | 192.67 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21803 | 192.67 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28441 | 192.67 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28062 | 192.67 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32968 | 192.67 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30351 | 192.67 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28062 | 192.67 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23285 | 192.67 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32968 | 192.67 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28036 | 192.67 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23623 | 183.84 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25257 | 183.84 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31895 | 183.84 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31516 | 183.84 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36421 | 183.84 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-033 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21299 | 183.84 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33804 | 183.84 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-065 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21299 | 183.84 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31516 | 183.84 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36421 | 183.84 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3149 | 183.84 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23615 | 176.01 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25249 | 176.01 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31888 | 176.01 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31508 | 176.01 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36414 | 176.01 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21291 | 176.01 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33797 | 176.01 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21291 | 176.01 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31508 | 176.01 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36414 | 176.01 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31482 | 176.01 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24828 | 172.02 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26263 | 172.02 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31975 | 172.02 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31645 | 172.02 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36965 | 172.02 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23931 | 172.02 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34442 | 172.02 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23931 | 172.02 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31645 | 172.02 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2069 | 172.02 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36965 | 172.02 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31603 | 172.02 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24425 | 151.75 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26061 | 151.75 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3272 | 151.75 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32355 | 151.75 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.37216 | 151.75 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22093 | 151.75 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34598 | 151.75 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22093 | 151.75 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32355 | 151.75 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.37216 | 151.75 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32327 | 151.75 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20225 | 194 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21856 | 194 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28464 | 194 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28087 | 194 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32989 | 194 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30372 | 194 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28087 | 194 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23325 | 194 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32989 | 194 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28061 | 194 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23732 | 184.23 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25363 | 184.23 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31971 | 184.23 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31594 | 184.23 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36496 | 184.23 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-033 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21388 | 184.23 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33878 | 184.23 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-065 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21388 | 184.23 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31594 | 184.23 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36496 | 184.23 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31568 | 184.23 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23717 | 177.45 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25348 | 177.45 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31956 | 177.45 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31579 | 177.45 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36481 | 177.45 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21374 | 177.45 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33864 | 177.45 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21374 | 177.45 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31579 | 177.45 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36481 | 177.45 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31553 | 177.45 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24943 | 173.69 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26375 | 173.69 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32051 | 173.69 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31723 | 173.69 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3704 | 173.69 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24031 | 173.69 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34516 | 173.69 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24031 | 173.69 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31723 | 173.69 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20684 | 173.69 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3704 | 173.69 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31681 | 173.69 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24539 | 152.64 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26172 | 152.64 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32801 | 152.64 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32438 | 152.64 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.37295 | 152.64 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22188 | 152.64 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34677 | 152.64 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22188 | 152.64 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32438 | 152.64 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.37295 | 152.64 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3241 | 152.64 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20397 | 135.77 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22244 | 135.77 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28948 | 135.77 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28579 | 135.77 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33449 | 135.77 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3073 | 135.77 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28579 | 135.77 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21231 | 135.77 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33449 | 135.77 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28552 | 135.77 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20168 | 172.31 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21802 | 172.31 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28441 | 172.31 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28062 | 172.31 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32967 | 172.31 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3035 | 172.31 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28062 | 172.31 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23285 | 172.31 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32967 | 172.31 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28036 | 172.31 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23622 | 154.37 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25255 | 154.37 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31894 | 154.37 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31515 | 154.37 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36421 | 154.37 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33804 | 154.37 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31515 | 154.37 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36421 | 154.37 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31489 | 154.37 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23614 | 147.47 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25248 | 147.47 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31887 | 147.47 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31508 | 147.47 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36413 | 147.47 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33796 | 147.47 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31508 | 147.47 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36413 | 147.47 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31482 | 147.47 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24826 | 140.83 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26262 | 140.83 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31975 | 140.83 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31644 | 140.83 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36965 | 140.83 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34442 | 140.83 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31644 | 140.83 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2069 | 140.83 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36965 | 140.83 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31603 | 140.83 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24423 | 122.24 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26059 | 122.24 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32719 | 122.24 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32354 | 122.24 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.37215 | 122.24 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34597 | 122.24 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32354 | 122.24 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.37215 | 122.24 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32327 | 122.24 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20168 | 171.7 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21802 | 171.7 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28441 | 171.7 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28062 | 171.7 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32967 | 171.7 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3035 | 171.7 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28062 | 171.7 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23285 | 171.7 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32967 | 171.7 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28036 | 171.7 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23622 | 153.93 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25255 | 153.93 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31894 | 153.93 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31515 | 153.93 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36421 | 153.93 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33804 | 153.93 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31515 | 153.93 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36421 | 153.93 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31489 | 153.93 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23614 | 146.97 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25248 | 146.97 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31887 | 146.97 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31508 | 146.97 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36413 | 146.97 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33796 | 146.97 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31508 | 146.97 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36413 | 146.97 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31482 | 146.97 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24826 | 140.54 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26262 | 140.54 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31975 | 140.54 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31644 | 140.54 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36965 | 140.54 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34442 | 140.54 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31644 | 140.54 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2069 | 140.54 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36965 | 140.54 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31603 | 140.54 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24423 | 121.68 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26059 | 121.68 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32719 | 121.68 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32354 | 121.68 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.37215 | 121.68 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34597 | 121.68 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32354 | 121.68 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.37215 | 121.68 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32327 | 121.68 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26076 | 151.53 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25708 | 151.53 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30577 | 151.53 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27857 | 151.53 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25708 | 151.53 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24137 | 151.53 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30577 | 151.53 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25681 | 151.53 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20231 | 135.31 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22076 | 135.31 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28766 | 135.31 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28398 | 135.31 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33267 | 135.31 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30548 | 135.31 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28398 | 135.31 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21447 | 135.31 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33267 | 135.31 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28371 | 135.31 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20274 | 129.81 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2212 | 129.81 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28809 | 129.81 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28441 | 129.81 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3331 | 129.81 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30591 | 129.81 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28441 | 129.81 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21404 | 129.81 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3331 | 129.81 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28414 | 129.81 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21013 | 122.21 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22746 | 122.21 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2875 | 122.21 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28421 | 122.21 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33643 | 122.21 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31092 | 122.21 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28421 | 122.21 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22178 | 122.21 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33643 | 122.21 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28381 | 122.21 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20933 | 110.51 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2278 | 110.51 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29488 | 110.51 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29133 | 110.51 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33961 | 110.51 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31242 | 110.51 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29133 | 110.51 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2075 | 110.51 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33961 | 110.51 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29104 | 110.51 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26147 | 152.65 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2578 | 152.65 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30647 | 152.65 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2793 | 152.65 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2578 | 152.65 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24146 | 152.65 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30647 | 152.65 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25752 | 152.65 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20357 | 134.97 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22195 | 134.97 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28863 | 134.97 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28496 | 134.97 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33364 | 134.97 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30647 | 134.97 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28496 | 134.97 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2143 | 134.97 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33364 | 134.97 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28469 | 134.97 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2038 | 130.28 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22218 | 130.28 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28886 | 130.28 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28519 | 130.28 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33387 | 130.28 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3067 | 130.28 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28519 | 130.28 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21407 | 130.28 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33387 | 130.28 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28492 | 130.28 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21132 | 122.52 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22855 | 122.52 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28828 | 122.52 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.285 | 122.52 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33722 | 122.52 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31172 | 122.52 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.285 | 122.52 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22189 | 122.52 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33722 | 122.52 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2846 | 122.52 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21051 | 110.52 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22891 | 110.52 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29577 | 110.52 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29223 | 110.52 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34051 | 110.52 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31333 | 110.52 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29223 | 110.52 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20741 | 110.52 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34051 | 110.52 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29195 | 110.52 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25992 | 149.07 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25626 | 149.07 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30491 | 149.07 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27774 | 149.07 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25626 | 149.07 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24367 | 149.07 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30491 | 149.07 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25599 | 149.07 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20156 | 133.29 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21991 | 133.29 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28632 | 133.29 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28266 | 133.29 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33131 | 133.29 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30414 | 133.29 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28266 | 133.29 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21727 | 133.29 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33131 | 133.29 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28239 | 133.29 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20192 | 127.63 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22027 | 127.63 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28667 | 127.63 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28302 | 127.63 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33167 | 127.63 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3045 | 127.63 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28302 | 127.63 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21691 | 127.63 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33167 | 127.63 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28275 | 127.63 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20933 | 119.8 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22651 | 119.8 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28591 | 119.8 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28266 | 119.8 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33486 | 119.8 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30935 | 119.8 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28266 | 119.8 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22495 | 119.8 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33486 | 119.8 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28225 | 119.8 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20858 | 108.4 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22695 | 108.4 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29354 | 108.4 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29002 | 108.4 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33826 | 108.4 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31109 | 108.4 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29002 | 108.4 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2103 | 108.4 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33826 | 108.4 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28973 | 108.4 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25967 | 149.02 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25601 | 149.02 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30467 | 149.02 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27749 | 149.02 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25601 | 149.02 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24369 | 149.02 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30467 | 149.02 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25574 | 149.02 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20125 | 133.48 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21962 | 133.48 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 133.48 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28242 | 133.48 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33108 | 133.48 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3039 | 133.48 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28242 | 133.48 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21728 | 133.48 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33108 | 133.48 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28215 | 133.48 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20169 | 127.83 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22006 | 127.83 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28652 | 127.83 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28287 | 127.83 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33152 | 127.83 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30435 | 127.83 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28287 | 127.83 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21684 | 127.83 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33152 | 127.83 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28259 | 127.83 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20906 | 119.99 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22627 | 119.99 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28576 | 119.99 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2825 | 119.99 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3347 | 119.99 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30919 | 119.99 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2825 | 119.99 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22486 | 119.99 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3347 | 119.99 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28209 | 119.99 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20832 | 108.36 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22671 | 108.36 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29336 | 108.36 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28983 | 108.36 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33808 | 108.36 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31091 | 108.36 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28983 | 108.36 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21026 | 108.36 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33808 | 108.36 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28954 | 108.36 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26431 | 163.12 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26065 | 163.12 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30932 | 163.12 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2822 | 163.12 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26065 | 163.12 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2399 | 163.12 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30932 | 163.12 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26037 | 163.12 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20899 | 141.62 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22724 | 141.62 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29365 | 141.62 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28999 | 141.62 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33866 | 141.62 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31154 | 141.62 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28999 | 141.62 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21055 | 141.62 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33866 | 141.62 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28972 | 141.62 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20918 | 139.21 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22742 | 139.21 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29384 | 139.21 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29018 | 139.21 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33885 | 139.21 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31173 | 139.21 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29018 | 139.21 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21036 | 139.21 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33885 | 139.21 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28991 | 139.21 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21728 | 132.44 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23431 | 132.44 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29359 | 132.44 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29034 | 132.44 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34259 | 132.44 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31709 | 132.44 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29034 | 132.44 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21805 | 132.44 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34259 | 132.44 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28993 | 132.44 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2162 | 116.5 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23446 | 116.5 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30106 | 116.5 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29753 | 116.5 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3458 | 116.5 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31867 | 116.5 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29753 | 116.5 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2034 | 116.5 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3458 | 116.5 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29724 | 116.5 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26431 | 163.13 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26065 | 163.13 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30932 | 163.13 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2822 | 163.13 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26065 | 163.13 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2399 | 163.13 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30932 | 163.13 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26037 | 163.13 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20899 | 141.62 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22724 | 141.62 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29365 | 141.62 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28999 | 141.62 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33866 | 141.62 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31154 | 141.62 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28999 | 141.62 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21055 | 141.62 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33866 | 141.62 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28972 | 141.62 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20918 | 139.22 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22742 | 139.22 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29384 | 139.22 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29018 | 139.22 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33885 | 139.22 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31173 | 139.22 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29018 | 139.22 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21036 | 139.22 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33885 | 139.22 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28991 | 139.22 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21728 | 132.44 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23431 | 132.44 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29359 | 132.44 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29034 | 132.44 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34259 | 132.44 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31709 | 132.44 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29034 | 132.44 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21805 | 132.44 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34259 | 132.44 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28993 | 132.44 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2162 | 116.51 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23446 | 116.51 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30106 | 116.51 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29753 | 116.51 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3458 | 116.51 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31867 | 116.51 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29753 | 116.51 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2034 | 116.51 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3458 | 116.51 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29724 | 116.51 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26431 | 163.01 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26065 | 163.01 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30932 | 163.01 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2822 | 163.01 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26065 | 163.01 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2399 | 163.01 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30932 | 163.01 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26037 | 163.01 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20899 | 141.58 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22724 | 141.58 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29365 | 141.58 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28999 | 141.58 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33866 | 141.58 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31154 | 141.58 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28999 | 141.58 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21055 | 141.58 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33866 | 141.58 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28972 | 141.58 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20918 | 139.15 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22742 | 139.15 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29384 | 139.15 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29018 | 139.15 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33885 | 139.15 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31173 | 139.15 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29018 | 139.15 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21036 | 139.15 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33885 | 139.15 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28991 | 139.15 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21728 | 132.4 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23431 | 132.4 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29359 | 132.4 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29034 | 132.4 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34259 | 132.4 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31709 | 132.4 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29034 | 132.4 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21805 | 132.4 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34259 | 132.4 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28993 | 132.4 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2162 | 116.47 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23446 | 116.47 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30106 | 116.47 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29753 | 116.47 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3458 | 116.47 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31867 | 116.47 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29753 | 116.47 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2034 | 116.47 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3458 | 116.47 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29724 | 116.47 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26143 | 152.72 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25775 | 152.72 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30644 | 152.72 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27925 | 152.72 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25775 | 152.72 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24054 | 152.72 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30644 | 152.72 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25748 | 152.72 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20322 | 135.81 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22167 | 135.81 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28865 | 135.81 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28496 | 135.81 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33366 | 135.81 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30647 | 135.81 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28496 | 135.81 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21333 | 135.81 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33366 | 135.81 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28469 | 135.81 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20357 | 130.69 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22203 | 130.69 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.289 | 130.69 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28532 | 130.69 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33402 | 130.69 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30682 | 130.69 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28532 | 130.69 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21297 | 130.69 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33402 | 130.69 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28505 | 130.69 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.211 | 123.1 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22833 | 123.1 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28847 | 123.1 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28517 | 123.1 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33739 | 123.1 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31189 | 123.1 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28517 | 123.1 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22065 | 123.1 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33739 | 123.1 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28477 | 123.1 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26138 | 152.54 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2577 | 152.54 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30639 | 152.54 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2792 | 152.54 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2577 | 152.54 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2406 | 152.54 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30639 | 152.54 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25742 | 152.54 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20313 | 135.76 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22159 | 135.76 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28856 | 135.76 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28487 | 135.76 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33357 | 135.76 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30638 | 135.76 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28487 | 135.76 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21342 | 135.76 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33357 | 135.76 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2846 | 135.76 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20349 | 130.62 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22195 | 130.62 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28892 | 130.62 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28524 | 130.62 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33393 | 130.62 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30674 | 130.62 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28524 | 130.62 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21306 | 130.62 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33393 | 130.62 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28496 | 130.62 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21092 | 122.93 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22825 | 122.93 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28838 | 122.93 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28509 | 122.93 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33731 | 122.93 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31181 | 122.93 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28509 | 122.93 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22074 | 122.93 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33731 | 122.93 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28469 | 122.93 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26184 | 156.23 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25815 | 156.23 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30685 | 156.23 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27966 | 156.23 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25815 | 156.23 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23992 | 156.23 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30685 | 156.23 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25788 | 156.23 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2046 | 137.68 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22307 | 137.68 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29012 | 137.68 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28643 | 137.68 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33514 | 137.68 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30794 | 137.68 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28643 | 137.68 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21164 | 137.68 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33514 | 137.68 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28616 | 137.68 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20493 | 133.53 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2234 | 133.53 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29046 | 133.53 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28677 | 133.53 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33547 | 133.53 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30828 | 133.53 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28677 | 133.53 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21131 | 133.53 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33547 | 133.53 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2865 | 133.53 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21245 | 126.09 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22979 | 126.09 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29002 | 126.09 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28672 | 126.09 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33895 | 126.09 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31345 | 126.09 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28672 | 126.09 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21887 | 126.09 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33895 | 126.09 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28632 | 126.09 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21164 | 112.91 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23013 | 112.91 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29736 | 112.91 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29381 | 112.91 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34211 | 112.91 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31491 | 112.91 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29381 | 112.91 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20465 | 112.91 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34211 | 112.91 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29352 | 112.91 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26191 | 155.64 | P23:345:GRDA:CLEVLND CB13280
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25822 | 155.64 | P23:345:GRDA:CLEVLND CB13280
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30693 | 155.64 | P23:345:GRDA:CLEVLND CB13280
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27973 | 155.64 | P23:345:GRDA:CLEVLND CB13280
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25822 | 155.64 | P23:345:GRDA:CLEVLND CB13280
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23982 | 155.64 | P23:345:GRDA:CLEVLND CB13280
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30693 | 155.64 | P23:345:GRDA:CLEVLND CB13280
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25795 | 155.64 | P23:345:GRDA:CLEVLND CB13280
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26202 | 153.97 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 153.97 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 153.97 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27985 | 153.97 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 153.97 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23967 | 153.97 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 153.97 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25806 | 153.97 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20421 | 136.69 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.69 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.69 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.69 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.69 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.69 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.69 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21193 | 136.69 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.69 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.69 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 132.39 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 132.39 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 132.39 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.39 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33515 | 132.39 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 132.39 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.39 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 132.39 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33515 | 132.39 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 132.39 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21206 | 124.89 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.89 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.89 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.89 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3386 | 124.89 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.89 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.89 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.89 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3386 | 124.89 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.89 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 111.94 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.94 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29698 | 111.94 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29342 | 111.94 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.94 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 111.94 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29342 | 111.94 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 111.94 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.94 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 111.94 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.68 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.68 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.68 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.68 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.68 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.68 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.68 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.68 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.68 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.68 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 132.38 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 132.38 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 132.38 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.38 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.38 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 132.38 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.38 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 132.38 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.38 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 132.38 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.87 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.87 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.87 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.87 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.87 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.87 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.87 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.87 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.87 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.87 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 111.93 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.93 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 111.93 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.93 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.93 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 111.93 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.93 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 111.93 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.93 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 111.93 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20419 | 137.14 | P23:345:MEC:LOUISA 964
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22267 | 137.14 | P23:345:MEC:LOUISA 964
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28975 | 137.14 | P23:345:MEC:LOUISA 964
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28606 | 137.14 | P23:345:MEC:LOUISA 964
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33476 | 137.14 | P23:345:MEC:LOUISA 964
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30757 | 137.14 | P23:345:MEC:LOUISA 964
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28606 | 137.14 | P23:345:MEC:LOUISA 964
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21195 | 137.14 | P23:345:MEC:LOUISA 964
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33476 | 137.14 | P23:345:MEC:LOUISA 964
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28579 | 137.14 | P23:345:MEC:LOUISA 964
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21121 | 112.41 | P23:345:MEC:LOUISA 964
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2297 | 112.41 | P23:345:MEC:LOUISA 964
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29696 | 112.41 | P23:345:MEC:LOUISA 964
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2934 | 112.41 | P23:345:MEC:LOUISA 964
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34171 | 112.41 | P23:345:MEC:LOUISA 964
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31451 | 112.41 | P23:345:MEC:LOUISA 964
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2934 | 112.41 | P23:345:MEC:LOUISA 964
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20499 | 112.41 | P23:345:MEC:LOUISA 964
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34171 | 112.41 | P23:345:MEC:LOUISA 964
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29312 | 112.41 | P23:345:MEC:LOUISA 964
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.68 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.68 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.68 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.68 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.68 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.68 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.68 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.68 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.68 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.68 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.89 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.89 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.89 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.89 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.89 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.89 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.89 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.89 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.89 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.89 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 111.93 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.93 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 111.93 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.93 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.93 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 111.93 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.93 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 111.93 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.93 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 111.93 | P23:345:MEC:RAUN 0180
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 135.29 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 135.29 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 135.29 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 135.29 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 135.29 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 135.29 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 135.29 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 135.29 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 135.29 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 135.29 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 130.94 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 130.94 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 130.94 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 130.94 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 130.94 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 130.94 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 130.94 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 130.94 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 130.94 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 130.94 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 123.41 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 123.41 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 123.41 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 123.41 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 123.41 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 123.41 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 123.41 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 123.41 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 123.41 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 123.41 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 110.49 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 110.49 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 110.49 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 110.49 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 110.49 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 110.49 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 110.49 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 110.49 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 110.49 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 110.49 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.67 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.67 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.67 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.67 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.67 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.67 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.67 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.67 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.67 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.67 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 132.37 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 132.37 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 132.37 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.37 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.37 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 132.37 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.37 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 132.37 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.37 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 132.37 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.88 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.88 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.88 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.88 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.88 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.88 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.88 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.88 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.88 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.88 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 111.92 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.92 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 111.92 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.92 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.92 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 111.92 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.92 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 111.92 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.92 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 111.92 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.67 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.67 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.67 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.67 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.67 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.67 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.67 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.67 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.67 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.67 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 132.37 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 132.37 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 132.37 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.37 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.37 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 132.37 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.37 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 132.37 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.37 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 132.37 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.88 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.88 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.88 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.88 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.88 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.88 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.88 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.88 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.88 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.88 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 111.92 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.92 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 111.92 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.92 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.92 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 111.92 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.92 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 111.92 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.92 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 111.92 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.67 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.67 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.67 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.67 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.67 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.67 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.67 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.67 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.67 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.67 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 132.37 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 132.37 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 132.37 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.37 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.37 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 132.37 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.37 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 132.37 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.37 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 132.37 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.87 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.87 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.87 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.87 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.87 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.87 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.87 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.87 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.87 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.87 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 111.92 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.92 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 111.92 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.92 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.92 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 111.92 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.92 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 111.92 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.92 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 111.92 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.67 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.67 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.67 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.67 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.67 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.67 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.67 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.67 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.67 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.67 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 132.37 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 132.37 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 132.37 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.37 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.37 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 132.37 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.37 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 132.37 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.37 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 132.37 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.88 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.88 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.88 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.88 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.88 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.88 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.88 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.88 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.88 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.88 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 111.94 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.94 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 111.94 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.94 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.94 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 111.94 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.94 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 111.94 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.94 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 111.94 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21306 | 125.75 | P23:345:SUNC:BU_BRK488
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23042 | 125.75 | P23:345:SUNC:BU_BRK488
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29035 | 125.75 | P23:345:SUNC:BU_BRK488
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28707 | 125.75 | P23:345:SUNC:BU_BRK488
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33926 | 125.75 | P23:345:SUNC:BU_BRK488
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31374 | 125.75 | P23:345:SUNC:BU_BRK488
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28707 | 125.75 | P23:345:SUNC:BU_BRK488
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21899 | 125.75 | P23:345:SUNC:BU_BRK488
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33926 | 125.75 | P23:345:SUNC:BU_BRK488
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28666 | 125.75 | P23:345:SUNC:BU_BRK488
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20522 | 137.59 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22371 | 137.59 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29047 | 137.59 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2868 | 137.59 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33547 | 137.59 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30826 | 137.59 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2868 | 137.59 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21172 | 137.59 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33547 | 137.59 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28653 | 137.59 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21306 | 125.96 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23042 | 125.96 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29035 | 125.96 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28707 | 125.96 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33926 | 125.96 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31374 | 125.96 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28707 | 125.96 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21899 | 125.96 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33926 | 125.96 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28666 | 125.96 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21305 | 125.73 | P23:345:SUNC:HLC_BRK182
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23042 | 125.73 | P23:345:SUNC:HLC_BRK182
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29034 | 125.73 | P23:345:SUNC:HLC_BRK182
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28706 | 125.73 | P23:345:SUNC:HLC_BRK182
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33925 | 125.73 | P23:345:SUNC:HLC_BRK182
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31374 | 125.73 | P23:345:SUNC:HLC_BRK182
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28706 | 125.73 | P23:345:SUNC:HLC_BRK182
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21899 | 125.73 | P23:345:SUNC:HLC_BRK182
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33925 | 125.73 | P23:345:SUNC:HLC_BRK182
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28666 | 125.73 | P23:345:SUNC:HLC_BRK182
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26507 | 161.38 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26145 | 161.38 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31004 | 161.38 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2828 | 161.38 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26145 | 161.38 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23815 | 161.38 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31004 | 161.38 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26117 | 161.38 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20971 | 140.53 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2282 | 140.53 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29434 | 140.53 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29071 | 140.53 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3393 | 140.53 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31206 | 140.53 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29071 | 140.53 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20888 | 140.53 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3393 | 140.53 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29043 | 140.53 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21761 | 127.74 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23498 | 127.74 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29425 | 127.74 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29102 | 127.74 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34314 | 127.74 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3176 | 127.74 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29102 | 127.74 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21614 | 127.74 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34314 | 127.74 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29061 | 127.74 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26525 | 162.07 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26163 | 162.07 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31022 | 162.07 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28298 | 162.07 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26163 | 162.07 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23798 | 162.07 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31022 | 162.07 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26135 | 162.07 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21012 | 140.95 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22862 | 140.95 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29475 | 140.95 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29112 | 140.95 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33972 | 140.95 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31248 | 140.95 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29112 | 140.95 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20848 | 140.95 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33972 | 140.95 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29085 | 140.95 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21049 | 135.11 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22899 | 135.11 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29512 | 135.11 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29149 | 135.11 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34008 | 135.11 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31285 | 135.11 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29149 | 135.11 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20811 | 135.11 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34008 | 135.11 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29122 | 135.11 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21804 | 127.77 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23541 | 127.77 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29468 | 127.77 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29145 | 127.77 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34357 | 127.77 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31803 | 127.77 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29145 | 127.77 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21572 | 127.77 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34357 | 127.77 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29104 | 127.77 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21726 | 117.02 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23577 | 117.02 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30208 | 117.02 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29859 | 117.02 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34678 | 117.02 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31954 | 117.02 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29859 | 117.02 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20139 | 117.02 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34678 | 117.02 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29829 | 117.02 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26266 | 156.74 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25898 | 156.74 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30767 | 156.74 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28047 | 156.74 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25898 | 156.74 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23925 | 156.74 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30767 | 156.74 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25871 | 156.74 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20545 | 137.69 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22393 | 137.69 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29088 | 137.69 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2872 | 137.69 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33589 | 137.69 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30869 | 137.69 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2872 | 137.69 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21103 | 137.69 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33589 | 137.69 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28693 | 137.69 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21249 | 113.05 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23098 | 113.05 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29812 | 113.05 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29457 | 113.05 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34286 | 113.05 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31565 | 113.05 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29457 | 113.05 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20405 | 113.05 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34286 | 113.05 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29428 | 113.05 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26283 | 157.31 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25915 | 157.31 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30784 | 157.31 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28064 | 157.31 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25915 | 157.31 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23915 | 157.31 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30784 | 157.31 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25888 | 157.31 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20574 | 137.88 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22422 | 137.88 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29114 | 137.88 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28746 | 137.88 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33614 | 137.88 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30894 | 137.88 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28746 | 137.88 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21084 | 137.88 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33614 | 137.88 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28718 | 137.88 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21278 | 113.26 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23127 | 113.26 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29837 | 113.26 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29482 | 113.26 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34311 | 113.26 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3159 | 113.26 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29482 | 113.26 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20386 | 113.26 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34311 | 113.26 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29454 | 113.26 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26287 | 157.12 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25919 | 157.12 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30788 | 157.12 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28068 | 157.12 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25919 | 157.12 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23911 | 157.12 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30788 | 157.12 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25892 | 157.12 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20585 | 137.82 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22433 | 137.82 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29125 | 137.82 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28757 | 137.82 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33626 | 137.82 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30906 | 137.82 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28757 | 137.82 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21073 | 137.82 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33626 | 137.82 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2873 | 137.82 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21288 | 113.17 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23138 | 113.17 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29848 | 113.17 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29493 | 113.17 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34322 | 113.17 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31601 | 113.17 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29493 | 113.17 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20375 | 113.17 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34322 | 113.17 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29464 | 113.17 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26283 | 157.3 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25915 | 157.3 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30784 | 157.3 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28064 | 157.3 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25915 | 157.3 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23915 | 157.3 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30784 | 157.3 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25888 | 157.3 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20574 | 137.88 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22422 | 137.88 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29114 | 137.88 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28746 | 137.88 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33614 | 137.88 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30894 | 137.88 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28746 | 137.88 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21084 | 137.88 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33614 | 137.88 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28718 | 137.88 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21278 | 113.26 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23127 | 113.26 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29837 | 113.26 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29482 | 113.26 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34311 | 113.26 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3159 | 113.26 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29482 | 113.26 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20386 | 113.26 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34311 | 113.26 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29454 | 113.26 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26287 | 157.15 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25919 | 157.15 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30788 | 157.15 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28068 | 157.15 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25919 | 157.15 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23911 | 157.15 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30788 | 157.15 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25892 | 157.15 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20585 | 137.82 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22433 | 137.82 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29125 | 137.82 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28757 | 137.82 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33626 | 137.82 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30906 | 137.82 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28757 | 137.82 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21073 | 137.82 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33626 | 137.82 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2873 | 137.82 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21288 | 113.17 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23138 | 113.17 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29848 | 113.17 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29493 | 113.17 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34322 | 113.17 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31601 | 113.17 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29493 | 113.17 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20375 | 113.17 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34322 | 113.17 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29464 | 113.17 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26286 | 157.45 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25918 | 157.45 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30787 | 157.45 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28067 | 157.45 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25918 | 157.45 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23913 | 157.45 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30787 | 157.45 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25891 | 157.45 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20581 | 137.97 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22429 | 137.97 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2912 | 137.97 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28752 | 137.97 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3362 | 137.97 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.309 | 137.97 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28752 | 137.97 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21079 | 137.97 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3362 | 137.97 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28725 | 137.97 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26286 | 157.36 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25918 | 157.36 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30787 | 157.36 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28067 | 157.36 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25918 | 157.36 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23913 | 157.36 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30787 | 157.36 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25891 | 157.36 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20581 | 137.96 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22429 | 137.96 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2912 | 137.96 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28752 | 137.96 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3362 | 137.96 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.309 | 137.96 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28752 | 137.96 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21079 | 137.96 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3362 | 137.96 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28725 | 137.96 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26286 | 157.47 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25918 | 157.47 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30787 | 157.47 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28067 | 157.47 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25918 | 157.47 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23913 | 157.47 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30787 | 157.47 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25891 | 157.47 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20581 | 137.97 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22429 | 137.97 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2912 | 137.97 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28752 | 137.97 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3362 | 137.97 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.309 | 137.97 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28752 | 137.97 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21079 | 137.97 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3362 | 137.97 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28725 | 137.97 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2627 | 155.88 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25903 | 155.88 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3077 | 155.88 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28049 | 155.88 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25903 | 155.88 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23949 | 155.88 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3077 | 155.88 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25876 | 155.88 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20522 | 137.87 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2237 | 137.87 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29046 | 137.87 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28679 | 137.87 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33546 | 137.87 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30825 | 137.87 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28679 | 137.87 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21173 | 137.87 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33546 | 137.87 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28652 | 137.87 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21305 | 126.17 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23041 | 126.17 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29034 | 126.17 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28706 | 126.17 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33925 | 126.17 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31374 | 126.17 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28706 | 126.17 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.219 | 126.17 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33925 | 126.17 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28665 | 126.17 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26251 | 156.24 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25882 | 156.24 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30752 | 156.24 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28032 | 156.24 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25882 | 156.24 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23946 | 156.24 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30752 | 156.24 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25855 | 156.24 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20507 | 137.93 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22354 | 137.93 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2905 | 137.93 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28681 | 137.93 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33551 | 137.93 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30831 | 137.93 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28681 | 137.93 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21147 | 137.93 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33551 | 137.93 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28654 | 137.93 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2054 | 133.68 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22387 | 133.68 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29083 | 133.68 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28714 | 133.68 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33584 | 133.68 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30864 | 133.68 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28714 | 133.68 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21114 | 133.68 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33584 | 133.68 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28687 | 133.68 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21295 | 126.3 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23029 | 126.3 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29041 | 126.3 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28711 | 126.3 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33933 | 126.3 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31383 | 126.3 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28711 | 126.3 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2187 | 126.3 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33933 | 126.3 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28671 | 126.3 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2121 | 113.17 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23059 | 113.17 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29773 | 113.17 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29418 | 113.17 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34247 | 113.17 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31527 | 113.17 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29418 | 113.17 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20449 | 113.17 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34247 | 113.17 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29389 | 113.17 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26251 | 156.24 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25882 | 156.24 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30752 | 156.24 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28032 | 156.24 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25882 | 156.24 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23946 | 156.24 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30752 | 156.24 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25855 | 156.24 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20507 | 137.93 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22354 | 137.93 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2905 | 137.93 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28681 | 137.93 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33551 | 137.93 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30831 | 137.93 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28681 | 137.93 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21147 | 137.93 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33551 | 137.93 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28654 | 137.93 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2054 | 133.68 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22387 | 133.68 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29083 | 133.68 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28714 | 133.68 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33584 | 133.68 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30864 | 133.68 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28714 | 133.68 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21114 | 133.68 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33584 | 133.68 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28687 | 133.68 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21295 | 126.3 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23029 | 126.3 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29041 | 126.3 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28711 | 126.3 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33933 | 126.3 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31383 | 126.3 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28711 | 126.3 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2187 | 126.3 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33933 | 126.3 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28671 | 126.3 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2121 | 113.17 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23059 | 113.17 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29773 | 113.17 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29418 | 113.17 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34247 | 113.17 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31527 | 113.17 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29418 | 113.17 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20449 | 113.17 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34247 | 113.17 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29389 | 113.17 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.57 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.57 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.57 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.57 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.57 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.57 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.57 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.57 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.57 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.57 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 132.26 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 132.26 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 132.26 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.26 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.26 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 132.26 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.26 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 132.26 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.26 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 132.26 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.77 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.77 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.77 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.77 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.77 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.77 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.77 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.77 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.77 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.77 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 111.81 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.81 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 111.81 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.81 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.81 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 111.81 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.81 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 111.81 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.81 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 111.81 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.56 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.56 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.56 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.56 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.56 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.56 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.56 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.56 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.56 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.56 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20458 | 132.27 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 132.27 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 132.27 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.27 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.27 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 132.27 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.27 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 132.27 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.27 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 132.27 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.77 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.77 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.77 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.77 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.77 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.77 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.77 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.77 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.77 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.77 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 111.83 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.83 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 111.83 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.83 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.83 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 111.83 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.83 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 111.83 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.83 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 111.83 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20423 | 136.56 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2227 | 136.56 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28978 | 136.56 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28609 | 136.56 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3348 | 136.56 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3076 | 136.56 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28609 | 136.56 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.56 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3348 | 136.56 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28582 | 136.56 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2046 | 132.26 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22307 | 132.26 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29015 | 132.26 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28646 | 132.26 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33517 | 132.26 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30797 | 132.26 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28646 | 132.26 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21154 | 132.26 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33517 | 132.26 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28619 | 132.26 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21208 | 124.77 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22943 | 124.77 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28969 | 124.77 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28639 | 124.77 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33862 | 124.77 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31312 | 124.77 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28639 | 124.77 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21912 | 124.77 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33862 | 124.77 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28599 | 124.77 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21124 | 111.82 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22973 | 111.82 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.297 | 111.82 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29344 | 111.82 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34174 | 111.82 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31454 | 111.82 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29344 | 111.82 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20495 | 111.82 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34174 | 111.82 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29315 | 111.82 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21249 | 125.81 | P23:345:WERE:WICH_345-50::
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22983 | 125.81 | P23:345:WERE:WICH_345-50::
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28999 | 125.81 | P23:345:WERE:WICH_345-50::
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2867 | 125.81 | P23:345:WERE:WICH_345-50::
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33892 | 125.81 | P23:345:WERE:WICH_345-50::
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31342 | 125.81 | P23:345:WERE:WICH_345-50::
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2867 | 125.81 | P23:345:WERE:WICH_345-50::
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21903 | 125.81 | P23:345:WERE:WICH_345-50::
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33892 | 125.81 | P23:345:WERE:WICH_345-50::
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2863 | 125.81 | P23:345:WERE:WICH_345-50::
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26203 | 154.94 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25834 | 154.94 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 154.94 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27985 | 154.94 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25834 | 154.94 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23967 | 154.94 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 154.94 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25807 | 154.94 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2046 | 132.59 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22307 | 132.59 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29015 | 132.59 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28646 | 132.59 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33517 | 132.59 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30798 | 132.59 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28646 | 132.59 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21154 | 132.59 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33517 | 132.59 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28619 | 132.59 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21208 | 125.1 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22943 | 125.1 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2897 | 125.1 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28639 | 125.1 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33862 | 125.1 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31312 | 125.1 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28639 | 125.1 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21912 | 125.1 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33862 | 125.1 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28599 | 125.1 | P23:345:WERE:WOLF_345-50::
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26202 | 154.89 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 154.89 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 154.89 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27985 | 154.89 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 154.89 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23968 | 154.89 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 154.89 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25806 | 154.89 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20459 | 132.64 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 132.64 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 132.64 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.64 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.64 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 132.64 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 132.64 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21156 | 132.64 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 132.64 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 132.64 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 125.15 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 125.15 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 125.15 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 125.15 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 125.15 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 125.15 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 125.15 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 125.15 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 125.15 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 125.15 | P23:345:WERE:WOLF_345-60::
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.69 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.69 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.69 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.69 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.69 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.69 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.69 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.69 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.69 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.69 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21206 | 124.9 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.9 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.9 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.9 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.9 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.9 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.9 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.9 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.9 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.9 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26202 | 153.92 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 153.92 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 153.92 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27984 | 153.92 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 153.92 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23967 | 153.92 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 153.92 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25806 | 153.92 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 135.73 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 135.73 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 135.73 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 135.73 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 135.73 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 135.73 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 135.73 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 135.73 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 135.73 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 135.73 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21206 | 123.85 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 123.85 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 123.85 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 123.85 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3386 | 123.85 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 123.85 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 123.85 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 123.85 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3386 | 123.85 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 123.85 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26202 | 154.6 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 154.6 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 154.6 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27985 | 154.6 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 154.6 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23967 | 154.6 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 154.6 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25806 | 154.6 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.68 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.68 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.68 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.68 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.68 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.68 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.68 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.68 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.68 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.68 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21206 | 124.89 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.89 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.89 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.89 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.89 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.89 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.89 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.89 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.89 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.89 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26202 | 154.66 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 154.66 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 154.66 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27984 | 154.66 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25833 | 154.66 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23967 | 154.66 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30704 | 154.66 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25806 | 154.66 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.66 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.66 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.66 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.66 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.66 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 136.66 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.66 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.66 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.66 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.66 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21206 | 124.87 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.87 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28968 | 124.87 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.87 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3386 | 124.87 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.87 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.87 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21914 | 124.87 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3386 | 124.87 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.87 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21097 | 112.91 | P23:500:EES-EAI:ARK_NU:B5106
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22947 | 112.91 | P23:500:EES-EAI:ARK_NU:B5106
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29671 | 112.91 | P23:500:EES-EAI:ARK_NU:B5106
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29315 | 112.91 | P23:500:EES-EAI:ARK_NU:B5106
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34145 | 112.91 | P23:500:EES-EAI:ARK_NU:B5106
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31425 | 112.91 | P23:500:EES-EAI:ARK_NU:B5106
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29315 | 112.91 | P23:500:EES-EAI:ARK_NU:B5106
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20529 | 112.91 | P23:500:EES-EAI:ARK_NU:B5106
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34145 | 112.91 | P23:500:EES-EAI:ARK_NU:B5106
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29286 | 112.91 | P23:500:EES-EAI:ARK_NU:B5106
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20409 | 135.52 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22257 | 135.52 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28963 | 135.52 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28594 | 135.52 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33465 | 135.52 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30746 | 135.52 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28594 | 135.52 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21209 | 135.52 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33465 | 135.52 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28567 | 135.52 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20444 | 131.47 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22292 | 131.47 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28998 | 131.47 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28629 | 131.47 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.335 | 131.47 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3078 | 131.47 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28629 | 131.47 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21174 | 131.47 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.335 | 131.47 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28602 | 131.47 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 123.87 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22928 | 123.87 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28952 | 123.87 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28622 | 123.87 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33845 | 123.87 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31295 | 123.87 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28622 | 123.87 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21932 | 123.87 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33845 | 123.87 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28582 | 123.87 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21111 | 110.82 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2296 | 110.82 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29685 | 110.82 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29329 | 110.82 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34159 | 110.82 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31439 | 110.82 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29329 | 110.82 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20513 | 110.82 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34159 | 110.82 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29301 | 110.82 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20409 | 135.43 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22256 | 135.43 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28963 | 135.43 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28594 | 135.43 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33464 | 135.43 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30745 | 135.43 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28594 | 135.43 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2121 | 135.43 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33464 | 135.43 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28567 | 135.43 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20443 | 131.38 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22291 | 131.38 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28997 | 131.38 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28628 | 131.38 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33499 | 131.38 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30779 | 131.38 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28628 | 131.38 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21175 | 131.38 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33499 | 131.38 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28601 | 131.38 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21191 | 123.78 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22927 | 123.78 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28951 | 123.78 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28621 | 123.78 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33844 | 123.78 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31294 | 123.78 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28621 | 123.78 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21934 | 123.78 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33844 | 123.78 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 123.78 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2111 | 110.74 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22959 | 110.74 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29684 | 110.74 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29328 | 110.74 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34158 | 110.74 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31439 | 110.74 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29328 | 110.74 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20514 | 110.74 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34158 | 110.74 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.293 | 110.74 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 135.05 | P41:345:OKGE:SB_MUGE7384
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 135.05 | P41:345:OKGE:SB_MUGE7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 135.05 | P41:345:OKGE:SB_MUGE7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 135.05 | P41:345:OKGE:SB_MUGE7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 135.05 | P41:345:OKGE:SB_MUGE7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 135.05 | P41:345:OKGE:SB_MUGE7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 135.05 | P41:345:OKGE:SB_MUGE7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 135.05 | P41:345:OKGE:SB_MUGE7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 135.05 | P41:345:OKGE:SB_MUGE7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 135.05 | P41:345:OKGE:SB_MUGE7384
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20393 | 134.71 | P41:345:OKGE:SB_MUGE7385
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2224 | 134.71 | P41:345:OKGE:SB_MUGE7385
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28946 | 134.71 | P41:345:OKGE:SB_MUGE7385
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28577 | 134.71 | P41:345:OKGE:SB_MUGE7385
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33447 | 134.71 | P41:345:OKGE:SB_MUGE7385
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30728 | 134.71 | P41:345:OKGE:SB_MUGE7385
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28577 | 134.71 | P41:345:OKGE:SB_MUGE7385
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21229 | 134.71 | P41:345:OKGE:SB_MUGE7385
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33447 | 134.71 | P41:345:OKGE:SB_MUGE7385
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2855 | 134.71 | P41:345:OKGE:SB_MUGE7385
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21104 | 112.2 | P41:345:OKGE:SB_SEOL7382
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2295 | 112.2 | P41:345:OKGE:SB_SEOL7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29656 | 112.2 | P41:345:OKGE:SB_SEOL7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29301 | 112.2 | P41:345:OKGE:SB_SEOL7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3413 | 112.2 | P41:345:OKGE:SB_SEOL7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3141 | 112.2 | P41:345:OKGE:SB_SEOL7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29301 | 112.2 | P41:345:OKGE:SB_SEOL7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20591 | 112.2 | P41:345:OKGE:SB_SEOL7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3413 | 112.2 | P41:345:OKGE:SB_SEOL7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29272 | 112.2 | P41:345:OKGE:SB_SEOL7382
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21087 | 111.95 | P41:345:OKGE:SB_SEOL7383
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22931 | 111.95 | P41:345:OKGE:SB_SEOL7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29619 | 111.95 | P41:345:OKGE:SB_SEOL7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29265 | 111.95 | P41:345:OKGE:SB_SEOL7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34092 | 111.95 | P41:345:OKGE:SB_SEOL7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31373 | 111.95 | P41:345:OKGE:SB_SEOL7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29265 | 111.95 | P41:345:OKGE:SB_SEOL7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20672 | 111.95 | P41:345:OKGE:SB_SEOL7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34092 | 111.95 | P41:345:OKGE:SB_SEOL7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29236 | 111.95 | P41:345:OKGE:SB_SEOL7383
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20406 | 135.58 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22254 | 135.58 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2896 | 135.58 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28591 | 135.58 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33461 | 135.58 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30742 | 135.58 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28591 | 135.58 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21215 | 135.58 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33461 | 135.58 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28564 | 135.58 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20441 | 131.39 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22288 | 131.39 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28994 | 131.39 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28625 | 131.39 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33495 | 131.39 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30776 | 131.39 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28625 | 131.39 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2118 | 131.39 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33495 | 131.39 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 131.39 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21188 | 123.88 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22924 | 123.88 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28947 | 123.88 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28617 | 123.88 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3384 | 123.88 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3129 | 123.88 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28617 | 123.88 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21939 | 123.88 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3384 | 123.88 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28577 | 123.88 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21106 | 110.83 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22955 | 110.83 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2968 | 110.83 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29324 | 110.83 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34154 | 110.83 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31434 | 110.83 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29324 | 110.83 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2052 | 110.83 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34154 | 110.83 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29295 | 110.83 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20406 | 135.56 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22254 | 135.56 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2896 | 135.56 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28591 | 135.56 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33461 | 135.56 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30742 | 135.56 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28591 | 135.56 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21215 | 135.56 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33461 | 135.56 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28564 | 135.56 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20441 | 131.38 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22288 | 131.38 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28994 | 131.38 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28625 | 131.38 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33495 | 131.38 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30776 | 131.38 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28625 | 131.38 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2118 | 131.38 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33495 | 131.38 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 131.38 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21188 | 123.86 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22924 | 123.86 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28947 | 123.86 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28617 | 123.86 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3384 | 123.86 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3129 | 123.86 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28617 | 123.86 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21939 | 123.86 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3384 | 123.86 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28577 | 123.86 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21106 | 110.79 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22955 | 110.79 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2968 | 110.79 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29324 | 110.79 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34154 | 110.79 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31434 | 110.79 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29324 | 110.79 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2052 | 110.79 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34154 | 110.79 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29295 | 110.79 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20396 | 135.82 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22243 | 135.82 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28947 | 135.82 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28578 | 135.82 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33448 | 135.82 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30729 | 135.82 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28578 | 135.82 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21233 | 135.82 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33448 | 135.82 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28551 | 135.82 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20396 | 135.82 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22243 | 135.82 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28947 | 135.82 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28578 | 135.82 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33448 | 135.82 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30729 | 135.82 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28578 | 135.82 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21233 | 135.82 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33448 | 135.82 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28551 | 135.82 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20396 | 135.81 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22243 | 135.81 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28947 | 135.81 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28578 | 135.81 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33448 | 135.81 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30729 | 135.81 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28578 | 135.81 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21233 | 135.81 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33448 | 135.81 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28551 | 135.81 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26439 | 163.4 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26073 | 163.4 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3094 | 163.4 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28228 | 163.4 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26073 | 163.4 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23988 | 163.4 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3094 | 163.4 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26045 | 163.4 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20912 | 141.85 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22735 | 141.85 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29377 | 141.85 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29011 | 141.85 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33878 | 141.85 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31166 | 141.85 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29011 | 141.85 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2105 | 141.85 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33878 | 141.85 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28983 | 141.85 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20931 | 139.34 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22754 | 139.34 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29396 | 139.34 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2903 | 139.34 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33897 | 139.34 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31185 | 139.34 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2903 | 139.34 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21031 | 139.34 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33897 | 139.34 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29002 | 139.34 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21741 | 132.55 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23443 | 132.55 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2937 | 132.55 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29045 | 132.55 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3427 | 132.55 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31721 | 132.55 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29045 | 132.55 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.218 | 132.55 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3427 | 132.55 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29004 | 132.55 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21633 | 116.62 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23458 | 116.62 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30118 | 116.62 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29765 | 116.62 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34592 | 116.62 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3188 | 116.62 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29765 | 116.62 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20334 | 116.62 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34592 | 116.62 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29736 | 116.62 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20225 | 194 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21856 | 194 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28464 | 194 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28087 | 194 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32989 | 194 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30372 | 194 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28087 | 194 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23325 | 194 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32989 | 194 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28061 | 194 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23732 | 184.23 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25363 | 184.23 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31971 | 184.23 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31594 | 184.23 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36496 | 184.23 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-033 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21388 | 184.23 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33878 | 184.23 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-065 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21388 | 184.23 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31594 | 184.23 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36496 | 184.23 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31568 | 184.23 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23717 | 177.45 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25348 | 177.45 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31956 | 177.45 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31579 | 177.45 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36481 | 177.45 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21374 | 177.45 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33864 | 177.45 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21374 | 177.45 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31579 | 177.45 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36481 | 177.45 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31553 | 177.45 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24943 | 173.69 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26375 | 173.69 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32051 | 173.69 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31723 | 173.69 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3704 | 173.69 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24031 | 173.69 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34516 | 173.69 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24031 | 173.69 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31723 | 173.69 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20684 | 173.69 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3704 | 173.69 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31681 | 173.69 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24539 | 152.64 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26172 | 152.64 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32801 | 152.64 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32438 | 152.64 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.37295 | 152.64 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22188 | 152.64 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34677 | 152.64 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22188 | 152.64 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32438 | 152.64 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.37295 | 152.64 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3241 | 152.64 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20397 | 135.77 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22244 | 135.77 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28948 | 135.77 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28579 | 135.77 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33449 | 135.77 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3073 | 135.77 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28579 | 135.77 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21231 | 135.77 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33449 | 135.77 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28552 | 135.77 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20168 | 172.31 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21802 | 172.31 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28441 | 172.31 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28062 | 172.31 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32967 | 172.31 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3035 | 172.31 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28062 | 172.31 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23285 | 172.31 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32967 | 172.31 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28036 | 172.31 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23622 | 154.37 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25255 | 154.37 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31894 | 154.37 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31515 | 154.37 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36421 | 154.37 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33804 | 154.37 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31515 | 154.37 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36421 | 154.37 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31489 | 154.37 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23614 | 147.47 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25248 | 147.47 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31887 | 147.47 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31508 | 147.47 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36413 | 147.47 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33796 | 147.47 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31508 | 147.47 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36413 | 147.47 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31482 | 147.47 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24826 | 140.83 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26262 | 140.83 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31975 | 140.83 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31644 | 140.83 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36965 | 140.83 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34442 | 140.83 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31644 | 140.83 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2069 | 140.83 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36965 | 140.83 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31603 | 140.83 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24423 | 122.24 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26059 | 122.24 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32719 | 122.24 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32354 | 122.24 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.37215 | 122.24 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34597 | 122.24 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32354 | 122.24 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.37215 | 122.24 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32327 | 122.24 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20168 | 171.7 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21802 | 171.7 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28441 | 171.7 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28062 | 171.7 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32967 | 171.7 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3035 | 171.7 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28062 | 171.7 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23285 | 171.7 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32967 | 171.7 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28036 | 171.7 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23622 | 153.93 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25255 | 153.93 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31894 | 153.93 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31515 | 153.93 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36421 | 153.93 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33804 | 153.93 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31515 | 153.93 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36421 | 153.93 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31489 | 153.93 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23614 | 146.97 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25248 | 146.97 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31887 | 146.97 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31508 | 146.97 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36413 | 146.97 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33796 | 146.97 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31508 | 146.97 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36413 | 146.97 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31482 | 146.97 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24826 | 140.54 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26262 | 140.54 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31975 | 140.54 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31644 | 140.54 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36965 | 140.54 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34442 | 140.54 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31644 | 140.54 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2069 | 140.54 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36965 | 140.54 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31603 | 140.54 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24423 | 121.68 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26059 | 121.68 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32719 | 121.68 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32354 | 121.68 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.37215 | 121.68 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34597 | 121.68 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32354 | 121.68 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.37215 | 121.68 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32327 | 121.68 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26076 | 151.53 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25708 | 151.53 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30577 | 151.53 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27857 | 151.53 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25708 | 151.53 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24137 | 151.53 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30577 | 151.53 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25681 | 151.53 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20231 | 135.31 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22076 | 135.31 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28766 | 135.31 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28398 | 135.31 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33267 | 135.31 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30548 | 135.31 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28398 | 135.31 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21447 | 135.31 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33267 | 135.31 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28371 | 135.31 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20274 | 129.81 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2212 | 129.81 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28809 | 129.81 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28441 | 129.81 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3331 | 129.81 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30591 | 129.81 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28441 | 129.81 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21404 | 129.81 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3331 | 129.81 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28414 | 129.81 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21013 | 122.21 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22746 | 122.21 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2875 | 122.21 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28421 | 122.21 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33643 | 122.21 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31092 | 122.21 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28421 | 122.21 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22178 | 122.21 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33643 | 122.21 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28381 | 122.21 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20933 | 110.51 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2278 | 110.51 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29488 | 110.51 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29133 | 110.51 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33961 | 110.51 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31242 | 110.51 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29133 | 110.51 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2075 | 110.51 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33961 | 110.51 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29104 | 110.51 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26147 | 152.65 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2578 | 152.65 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30647 | 152.65 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2793 | 152.65 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2578 | 152.65 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24146 | 152.65 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30647 | 152.65 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25752 | 152.65 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20357 | 134.97 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22195 | 134.97 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28863 | 134.97 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28496 | 134.97 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33364 | 134.97 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30647 | 134.97 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28496 | 134.97 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2143 | 134.97 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33364 | 134.97 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28469 | 134.97 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2038 | 130.28 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22218 | 130.28 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28886 | 130.28 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28519 | 130.28 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33387 | 130.28 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3067 | 130.28 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28519 | 130.28 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21407 | 130.28 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33387 | 130.28 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28492 | 130.28 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21132 | 122.52 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22855 | 122.52 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28828 | 122.52 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.285 | 122.52 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33722 | 122.52 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31172 | 122.52 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.285 | 122.52 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22189 | 122.52 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33722 | 122.52 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2846 | 122.52 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21051 | 110.52 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22891 | 110.52 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29577 | 110.52 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29223 | 110.52 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34051 | 110.52 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31333 | 110.52 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29223 | 110.52 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20741 | 110.52 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34051 | 110.52 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29195 | 110.52 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25992 | 149.07 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25626 | 149.07 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30491 | 149.07 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27774 | 149.07 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25626 | 149.07 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24367 | 149.07 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30491 | 149.07 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25599 | 149.07 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20156 | 133.29 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21991 | 133.29 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28632 | 133.29 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28266 | 133.29 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33131 | 133.29 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30414 | 133.29 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28266 | 133.29 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21727 | 133.29 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33131 | 133.29 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28239 | 133.29 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20192 | 127.63 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22027 | 127.63 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28667 | 127.63 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28302 | 127.63 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33167 | 127.63 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3045 | 127.63 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28302 | 127.63 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21691 | 127.63 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33167 | 127.63 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28275 | 127.63 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20933 | 119.8 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22651 | 119.8 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28591 | 119.8 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28266 | 119.8 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33486 | 119.8 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30935 | 119.8 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28266 | 119.8 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22495 | 119.8 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33486 | 119.8 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28225 | 119.8 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20858 | 108.4 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22695 | 108.4 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29354 | 108.4 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29002 | 108.4 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33826 | 108.4 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31109 | 108.4 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29002 | 108.4 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2103 | 108.4 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33826 | 108.4 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28973 | 108.4 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25967 | 149.02 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25601 | 149.02 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30467 | 149.02 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27749 | 149.02 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25601 | 149.02 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24369 | 149.02 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30467 | 149.02 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25574 | 149.02 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20125 | 133.48 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21962 | 133.48 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 133.48 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28242 | 133.48 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33108 | 133.48 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3039 | 133.48 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28242 | 133.48 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21728 | 133.48 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33108 | 133.48 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28215 | 133.48 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20169 | 127.83 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22006 | 127.83 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28652 | 127.83 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28287 | 127.83 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33152 | 127.83 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30435 | 127.83 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28287 | 127.83 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21684 | 127.83 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33152 | 127.83 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28259 | 127.83 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20906 | 119.99 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22627 | 119.99 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28576 | 119.99 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2825 | 119.99 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3347 | 119.99 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30919 | 119.99 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2825 | 119.99 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22486 | 119.99 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3347 | 119.99 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28209 | 119.99 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20832 | 108.36 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22671 | 108.36 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29336 | 108.36 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28983 | 108.36 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33808 | 108.36 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31091 | 108.36 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28983 | 108.36 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21026 | 108.36 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33808 | 108.36 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28954 | 108.36 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26431 | 163.12 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26065 | 163.12 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30932 | 163.12 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2822 | 163.12 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26065 | 163.12 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2399 | 163.12 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30932 | 163.12 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26037 | 163.12 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20899 | 141.62 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22724 | 141.62 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29365 | 141.62 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28999 | 141.62 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33866 | 141.62 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31154 | 141.62 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28999 | 141.62 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21055 | 141.62 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33866 | 141.62 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28972 | 141.62 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20918 | 139.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22742 | 139.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29384 | 139.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29018 | 139.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33885 | 139.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31173 | 139.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29018 | 139.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21036 | 139.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33885 | 139.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28991 | 139.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21728 | 132.44 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23431 | 132.44 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29359 | 132.44 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29034 | 132.44 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34259 | 132.44 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31709 | 132.44 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29034 | 132.44 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21805 | 132.44 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34259 | 132.44 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28993 | 132.44 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2162 | 116.5 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23446 | 116.5 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30106 | 116.5 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29753 | 116.5 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3458 | 116.5 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31867 | 116.5 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29753 | 116.5 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2034 | 116.5 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3458 | 116.5 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29724 | 116.5 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26431 | 163.13 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26065 | 163.13 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30932 | 163.13 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2822 | 163.13 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26065 | 163.13 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2399 | 163.13 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30932 | 163.13 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26037 | 163.13 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20899 | 141.62 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22724 | 141.62 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29365 | 141.62 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28999 | 141.62 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33866 | 141.62 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31154 | 141.62 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28999 | 141.62 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21055 | 141.62 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33866 | 141.62 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28972 | 141.62 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20918 | 139.22 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22742 | 139.22 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29384 | 139.22 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29018 | 139.22 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33885 | 139.22 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31173 | 139.22 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29018 | 139.22 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21036 | 139.22 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33885 | 139.22 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28991 | 139.22 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21728 | 132.44 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23431 | 132.44 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29359 | 132.44 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29034 | 132.44 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34259 | 132.44 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31709 | 132.44 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29034 | 132.44 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21805 | 132.44 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34259 | 132.44 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28993 | 132.44 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2162 | 116.51 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23446 | 116.51 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30106 | 116.51 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29753 | 116.51 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3458 | 116.51 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31867 | 116.51 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29753 | 116.51 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2034 | 116.51 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3458 | 116.51 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29724 | 116.51 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26431 | 163.01 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26065 | 163.01 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30932 | 163.01 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2822 | 163.01 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26065 | 163.01 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2399 | 163.01 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30932 | 163.01 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26037 | 163.01 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20899 | 141.58 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22724 | 141.58 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29365 | 141.58 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28999 | 141.58 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33866 | 141.58 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31154 | 141.58 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28999 | 141.58 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21055 | 141.58 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33866 | 141.58 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28972 | 141.58 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20918 | 139.15 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22742 | 139.15 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29384 | 139.15 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29018 | 139.15 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33885 | 139.15 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31173 | 139.15 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29018 | 139.15 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21036 | 139.15 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33885 | 139.15 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28991 | 139.15 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21728 | 132.4 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23431 | 132.4 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29359 | 132.4 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29034 | 132.4 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34259 | 132.4 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31709 | 132.4 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29034 | 132.4 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21805 | 132.4 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34259 | 132.4 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28993 | 132.4 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2162 | 116.47 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23446 | 116.47 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30106 | 116.47 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29753 | 116.47 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3458 | 116.47 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31867 | 116.47 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29753 | 116.47 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2034 | 116.47 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3458 | 116.47 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29724 | 116.47 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26143 | 152.72 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25775 | 152.72 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30644 | 152.72 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27925 | 152.72 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25775 | 152.72 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24054 | 152.72 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30644 | 152.72 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25748 | 152.72 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20322 | 135.81 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22167 | 135.81 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28865 | 135.81 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28496 | 135.81 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33366 | 135.81 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30647 | 135.81 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28496 | 135.81 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21333 | 135.81 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33366 | 135.81 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28469 | 135.81 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20357 | 130.69 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22203 | 130.69 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.289 | 130.69 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28532 | 130.69 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33402 | 130.69 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30682 | 130.69 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28532 | 130.69 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21297 | 130.69 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33402 | 130.69 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28505 | 130.69 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.211 | 123.1 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22833 | 123.1 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28847 | 123.1 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28517 | 123.1 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33739 | 123.1 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31189 | 123.1 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28517 | 123.1 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22065 | 123.1 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33739 | 123.1 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28477 | 123.1 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26138 | 152.54 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2577 | 152.54 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30639 | 152.54 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2792 | 152.54 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2577 | 152.54 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2406 | 152.54 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30639 | 152.54 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25742 | 152.54 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20313 | 135.76 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22159 | 135.76 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28856 | 135.76 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28487 | 135.76 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33357 | 135.76 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30638 | 135.76 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28487 | 135.76 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21342 | 135.76 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33357 | 135.76 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2846 | 135.76 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20349 | 130.62 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22195 | 130.62 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28892 | 130.62 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28524 | 130.62 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33393 | 130.62 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30674 | 130.62 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28524 | 130.62 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21306 | 130.62 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33393 | 130.62 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28496 | 130.62 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21092 | 122.93 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22825 | 122.93 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28838 | 122.93 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28509 | 122.93 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33731 | 122.93 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31181 | 122.93 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28509 | 122.93 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22074 | 122.93 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33731 | 122.93 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28469 | 122.93 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26191 | 155.64 | P42:345:GRDA:CLEVLND CB13280
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25822 | 155.64 | P42:345:GRDA:CLEVLND CB13280
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30693 | 155.64 | P42:345:GRDA:CLEVLND CB13280
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27973 | 155.64 | P42:345:GRDA:CLEVLND CB13280
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25822 | 155.64 | P42:345:GRDA:CLEVLND CB13280
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23982 | 155.64 | P42:345:GRDA:CLEVLND CB13280
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30693 | 155.64 | P42:345:GRDA:CLEVLND CB13280
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25795 | 155.64 | P42:345:GRDA:CLEVLND CB13280
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20422 | 136.16 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22269 | 136.16 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28977 | 136.16 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.16 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.16 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3076 | 136.16 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28608 | 136.16 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 136.16 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33479 | 136.16 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28581 | 136.16 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20459 | 131.84 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22306 | 131.84 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29014 | 131.84 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 131.84 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 131.84 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30796 | 131.84 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28645 | 131.84 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21155 | 131.84 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33516 | 131.84 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28618 | 131.84 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21207 | 124.26 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22942 | 124.26 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28969 | 124.26 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.26 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.26 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31311 | 124.26 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28638 | 124.26 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21913 | 124.26 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33861 | 124.26 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 124.26 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21123 | 111.36 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.36 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29699 | 111.36 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.36 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.36 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31454 | 111.36 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29343 | 111.36 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20496 | 111.36 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.36 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 111.36 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26293 | 157.33 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25925 | 157.33 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30794 | 157.33 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28074 | 157.33 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25925 | 157.33 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23906 | 157.33 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30794 | 157.33 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25898 | 157.33 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20597 | 137.93 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22445 | 137.93 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29136 | 137.93 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28768 | 137.93 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33637 | 137.93 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30917 | 137.93 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28768 | 137.93 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21063 | 137.93 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33637 | 137.93 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28741 | 137.93 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21301 | 113.29 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2315 | 113.29 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29859 | 113.29 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29505 | 113.29 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34333 | 113.29 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31613 | 113.29 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29505 | 113.29 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20364 | 113.29 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34333 | 113.29 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29476 | 113.29 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21226 | 125.71 | P42:345:NPPD:BKR-SW-3308
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22962 | 125.71 | P42:345:NPPD:BKR-SW-3308
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28985 | 125.71 | P42:345:NPPD:BKR-SW-3308
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28655 | 125.71 | P42:345:NPPD:BKR-SW-3308
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33877 | 125.71 | P42:345:NPPD:BKR-SW-3308
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31328 | 125.71 | P42:345:NPPD:BKR-SW-3308
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28655 | 125.71 | P42:345:NPPD:BKR-SW-3308
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21902 | 125.71 | P42:345:NPPD:BKR-SW-3308
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33877 | 125.71 | P42:345:NPPD:BKR-SW-3308
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28615 | 125.71 | P42:345:NPPD:BKR-SW-3308
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20875 | 110.59 | P42:345:OKGE:SB_ARIA7381
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22712 | 110.59 | P42:345:OKGE:SB_ARIA7381
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29338 | 110.59 | P42:345:OKGE:SB_ARIA7381
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28988 | 110.59 | P42:345:OKGE:SB_ARIA7381
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33809 | 110.59 | P42:345:OKGE:SB_ARIA7381
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31091 | 110.59 | P42:345:OKGE:SB_ARIA7381
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28988 | 110.59 | P42:345:OKGE:SB_ARIA7381
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21098 | 110.59 | P42:345:OKGE:SB_ARIA7381
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33809 | 110.59 | P42:345:OKGE:SB_ARIA7381
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28959 | 110.59 | P42:345:OKGE:SB_ARIA7381
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26265 | 155.77 | P42:345:OKGE:SB_ARIA7382
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25897 | 155.77 | P42:345:OKGE:SB_ARIA7382
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30766 | 155.77 | P42:345:OKGE:SB_ARIA7382
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28047 | 155.77 | P42:345:OKGE:SB_ARIA7382
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25897 | 155.77 | P42:345:OKGE:SB_ARIA7382
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23945 | 155.77 | P42:345:OKGE:SB_ARIA7382
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30766 | 155.77 | P42:345:OKGE:SB_ARIA7382
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2587 | 155.77 | P42:345:OKGE:SB_ARIA7382
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21076 | 178.5 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27105 | 178.5 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26786 | 178.5 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31568 | 178.5 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28803 | 178.5 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26786 | 178.5 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23978 | 178.5 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31568 | 178.5 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26752 | 178.5 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22342 | 151.93 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24232 | 151.93 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30262 | 151.93 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29943 | 151.93 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34725 | 151.93 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3196 | 151.93 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29943 | 151.93 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2082 | 151.93 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34725 | 151.93 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29909 | 151.93 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22317 | 150.01 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24207 | 150.01 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30237 | 150.01 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29918 | 150.01 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.347 | 150.01 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31935 | 150.01 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29918 | 150.01 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20846 | 150.01 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.347 | 150.01 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29884 | 150.01 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23102 | 143.62 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24885 | 143.62 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30232 | 143.62 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29951 | 143.62 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35086 | 143.62 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32503 | 143.62 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29951 | 143.62 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21588 | 143.62 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35086 | 143.62 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29904 | 143.62 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23094 | 124.41 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24986 | 124.41 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31032 | 124.41 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30724 | 124.41 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35471 | 124.41 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32706 | 124.41 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30724 | 124.41 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20072 | 124.41 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35471 | 124.41 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30688 | 124.41 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26249 | 155.61 | P42:345:OKGE:SB_BAER7318
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25882 | 155.61 | P42:345:OKGE:SB_BAER7318
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30749 | 155.61 | P42:345:OKGE:SB_BAER7318
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28027 | 155.61 | P42:345:OKGE:SB_BAER7318
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25882 | 155.61 | P42:345:OKGE:SB_BAER7318
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23968 | 155.61 | P42:345:OKGE:SB_BAER7318
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30749 | 155.61 | P42:345:OKGE:SB_BAER7318
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25855 | 155.61 | P42:345:OKGE:SB_BAER7318
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26249 | 155.65 | P42:345:OKGE:SB_BAER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25883 | 155.65 | P42:345:OKGE:SB_BAER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30749 | 155.65 | P42:345:OKGE:SB_BAER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28027 | 155.65 | P42:345:OKGE:SB_BAER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25883 | 155.65 | P42:345:OKGE:SB_BAER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23968 | 155.65 | P42:345:OKGE:SB_BAER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30749 | 155.65 | P42:345:OKGE:SB_BAER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25855 | 155.65 | P42:345:OKGE:SB_BAER7384
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2101 | 167.65 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2778 | 167.65 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27396 | 167.65 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32304 | 167.65 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29658 | 167.65 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27396 | 167.65 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23261 | 167.65 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32304 | 167.65 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27371 | 167.65 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22506 | 152.07 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24206 | 152.07 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30976 | 152.07 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30592 | 152.07 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35499 | 152.07 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32854 | 152.07 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30592 | 152.07 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20066 | 152.07 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35499 | 152.07 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30567 | 152.07 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22519 | 145.33 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24218 | 145.33 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30988 | 145.33 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30604 | 145.33 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35511 | 145.33 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32866 | 145.33 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30604 | 145.33 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20053 | 145.33 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35511 | 145.33 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30579 | 145.33 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23579 | 138.62 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25108 | 138.62 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31046 | 138.62 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30707 | 138.62 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36009 | 138.62 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33482 | 138.62 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30707 | 138.62 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20842 | 138.62 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36009 | 138.62 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30667 | 138.62 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23262 | 123.43 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24963 | 123.43 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31753 | 123.43 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31384 | 123.43 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36247 | 123.43 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33601 | 123.43 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31384 | 123.43 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36247 | 123.43 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31357 | 123.43 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2101 | 167.65 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2778 | 167.65 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27396 | 167.65 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32304 | 167.65 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29658 | 167.65 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27396 | 167.65 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23261 | 167.65 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32304 | 167.65 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27371 | 167.65 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22506 | 152.05 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24206 | 152.05 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30976 | 152.05 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30592 | 152.05 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35499 | 152.05 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32854 | 152.05 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30592 | 152.05 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20066 | 152.05 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35499 | 152.05 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30567 | 152.05 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22519 | 145.29 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24218 | 145.29 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30988 | 145.29 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30604 | 145.29 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35511 | 145.29 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32866 | 145.29 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30604 | 145.29 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20053 | 145.29 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35511 | 145.29 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30579 | 145.29 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23579 | 138.59 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25108 | 138.59 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31046 | 138.59 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30707 | 138.59 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36009 | 138.59 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33482 | 138.59 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30707 | 138.59 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20842 | 138.59 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36009 | 138.59 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30667 | 138.59 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23262 | 123.4 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24963 | 123.4 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31753 | 123.4 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31384 | 123.4 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36247 | 123.4 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33601 | 123.4 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31384 | 123.4 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36247 | 123.4 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31357 | 123.4 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2101 | 167.61 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2778 | 167.61 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27396 | 167.61 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32304 | 167.61 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29658 | 167.61 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27396 | 167.61 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23261 | 167.61 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32304 | 167.61 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27371 | 167.61 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22506 | 152.08 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24206 | 152.08 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30976 | 152.08 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30592 | 152.08 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35499 | 152.08 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32854 | 152.08 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30592 | 152.08 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20066 | 152.08 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35499 | 152.08 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30567 | 152.08 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22519 | 145.33 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24218 | 145.33 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30988 | 145.33 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30604 | 145.33 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35511 | 145.33 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32866 | 145.33 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30604 | 145.33 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20053 | 145.33 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35511 | 145.33 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30579 | 145.33 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23579 | 138.63 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25108 | 138.63 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31046 | 138.63 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30707 | 138.63 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36009 | 138.63 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33482 | 138.63 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30707 | 138.63 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20842 | 138.63 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36009 | 138.63 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30667 | 138.63 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23262 | 123.45 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24963 | 123.45 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31753 | 123.45 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31384 | 123.45 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36247 | 123.45 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33601 | 123.45 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31384 | 123.45 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36247 | 123.45 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31357 | 123.45 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26249 | 150.56 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25882 | 150.56 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30749 | 150.56 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28027 | 150.56 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25882 | 150.56 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23968 | 150.56 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30749 | 150.56 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25855 | 150.56 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20521 | 135.06 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2237 | 135.06 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29044 | 135.06 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28677 | 135.06 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33543 | 135.06 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30821 | 135.06 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28677 | 135.06 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21173 | 135.06 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33543 | 135.06 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2865 | 135.06 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21225 | 110.21 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23076 | 110.21 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29768 | 110.21 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29414 | 110.21 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3424 | 110.21 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31518 | 110.21 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29414 | 110.21 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20474 | 110.21 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3424 | 110.21 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29385 | 110.21 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26249 | 149.5 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25883 | 149.5 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30749 | 149.5 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28027 | 149.5 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25883 | 149.5 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23968 | 149.5 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30749 | 149.5 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25855 | 149.5 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20521 | 134.86 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22371 | 134.86 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29044 | 134.86 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28677 | 134.86 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33543 | 134.86 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30822 | 134.86 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28677 | 134.86 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21173 | 134.86 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33543 | 134.86 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2865 | 134.86 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21225 | 110.01 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23077 | 110.01 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29768 | 110.01 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29414 | 110.01 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3424 | 110.01 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31518 | 110.01 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29414 | 110.01 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20474 | 110.01 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3424 | 110.01 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29385 | 110.01 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25907 | 157.66 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25546 | 157.66 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30404 | 157.66 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27686 | 157.66 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25546 | 157.66 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24602 | 157.66 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30404 | 157.66 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25518 | 157.66 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20346 | 138 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22176 | 138 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28745 | 138 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28385 | 138 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33242 | 138 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30525 | 138 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28385 | 138 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21763 | 138 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33242 | 138 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28357 | 138 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20372 | 134.34 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22202 | 134.34 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28771 | 134.34 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28411 | 134.34 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33268 | 134.34 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30551 | 134.34 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28411 | 134.34 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21737 | 134.34 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33268 | 134.34 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28383 | 134.34 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2113 | 127.14 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2284 | 127.14 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28695 | 127.14 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28375 | 127.14 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33589 | 127.14 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31036 | 127.14 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28375 | 127.14 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22561 | 127.14 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33589 | 127.14 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28333 | 127.14 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26484 | 157.86 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26118 | 157.86 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30985 | 157.86 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2827 | 157.86 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26118 | 157.86 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23858 | 157.86 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30985 | 157.86 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2609 | 157.86 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20792 | 138.95 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22622 | 138.95 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29279 | 138.95 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28913 | 138.95 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3378 | 138.95 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31065 | 138.95 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28913 | 138.95 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21063 | 138.95 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3378 | 138.95 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28885 | 138.95 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2081 | 135.77 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2264 | 135.77 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29298 | 135.77 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28931 | 135.77 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33798 | 135.77 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31083 | 135.77 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28931 | 135.77 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21045 | 135.77 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33798 | 135.77 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28904 | 135.77 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21623 | 128.81 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23334 | 128.81 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29285 | 128.81 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28959 | 128.81 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34182 | 128.81 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31632 | 128.81 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28959 | 128.81 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.218 | 128.81 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34182 | 128.81 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28918 | 128.81 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21498 | 114.47 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2333 | 114.47 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30005 | 114.47 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29652 | 114.47 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34479 | 114.47 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31764 | 114.47 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29652 | 114.47 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20362 | 114.47 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34479 | 114.47 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29623 | 114.47 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20376 | 135.21 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22218 | 135.21 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28884 | 135.21 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28518 | 135.21 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33384 | 135.21 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30666 | 135.21 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28518 | 135.21 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21389 | 135.21 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33384 | 135.21 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2849 | 135.21 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21082 | 110.33 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22925 | 110.33 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2961 | 110.33 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29256 | 110.33 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34083 | 110.33 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31364 | 110.33 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29256 | 110.33 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20688 | 110.33 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34083 | 110.33 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29228 | 110.33 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20376 | 135.17 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22218 | 135.17 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28884 | 135.17 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28518 | 135.17 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33384 | 135.17 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30666 | 135.17 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28518 | 135.17 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21389 | 135.17 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33384 | 135.17 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2849 | 135.17 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21082 | 110.36 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22925 | 110.36 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2961 | 110.36 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29257 | 110.36 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34083 | 110.36 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31364 | 110.36 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29257 | 110.36 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20688 | 110.36 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34083 | 110.36 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29228 | 110.36 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25882 | 157.38 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25522 | 157.38 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30379 | 157.38 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27661 | 157.38 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25522 | 157.38 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24651 | 157.38 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30379 | 157.38 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25494 | 157.38 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20352 | 133.67 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2218 | 133.67 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2874 | 133.67 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2838 | 133.67 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33236 | 133.67 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30519 | 133.67 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2838 | 133.67 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21793 | 133.67 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33236 | 133.67 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28352 | 133.67 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2111 | 126.45 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22819 | 126.45 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28662 | 126.45 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28343 | 126.45 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33557 | 126.45 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31003 | 126.45 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28343 | 126.45 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22618 | 126.45 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33557 | 126.45 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28301 | 126.45 | P42:345:OKGE:SB_DRER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26238 | 155.84 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2587 | 155.84 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3074 | 155.84 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28022 | 155.84 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2587 | 155.84 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23999 | 155.84 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3074 | 155.84 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25843 | 155.84 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20535 | 133.39 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22376 | 133.39 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29065 | 133.39 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28697 | 133.39 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33566 | 133.39 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30849 | 133.39 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28697 | 133.39 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21172 | 133.39 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33566 | 133.39 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2867 | 133.39 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21294 | 125.98 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23021 | 125.98 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2902 | 125.98 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28691 | 125.98 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33914 | 125.98 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31365 | 125.98 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28691 | 125.98 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21936 | 125.98 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33914 | 125.98 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28651 | 125.98 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26238 | 155.84 | P42:345:OKGE:SB_JOCO7313
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2587 | 155.84 | P42:345:OKGE:SB_JOCO7313
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3074 | 155.84 | P42:345:OKGE:SB_JOCO7313
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28022 | 155.84 | P42:345:OKGE:SB_JOCO7313
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2587 | 155.84 | P42:345:OKGE:SB_JOCO7313
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23999 | 155.84 | P42:345:OKGE:SB_JOCO7313
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3074 | 155.84 | P42:345:OKGE:SB_JOCO7313
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25843 | 155.84 | P42:345:OKGE:SB_JOCO7313
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26238 | 155.99 | P42:345:OKGE:SB_JOCO7383
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2587 | 155.99 | P42:345:OKGE:SB_JOCO7383
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3074 | 155.99 | P42:345:OKGE:SB_JOCO7383
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28022 | 155.99 | P42:345:OKGE:SB_JOCO7383
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2587 | 155.99 | P42:345:OKGE:SB_JOCO7383
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23999 | 155.99 | P42:345:OKGE:SB_JOCO7383
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3074 | 155.99 | P42:345:OKGE:SB_JOCO7383
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25843 | 155.99 | P42:345:OKGE:SB_JOCO7383
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26484 | 156.67 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26118 | 156.67 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30985 | 156.67 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2827 | 156.67 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26118 | 156.67 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23858 | 156.67 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30985 | 156.67 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2609 | 156.67 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20792 | 139.26 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22622 | 139.26 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29279 | 139.26 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28913 | 139.26 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3378 | 139.26 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31065 | 139.26 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28913 | 139.26 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21063 | 139.26 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3378 | 139.26 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28885 | 139.26 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2081 | 135.84 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2264 | 135.84 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29298 | 135.84 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28931 | 135.84 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33798 | 135.84 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31083 | 135.84 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28931 | 135.84 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21045 | 135.84 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33798 | 135.84 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28904 | 135.84 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21623 | 128.86 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23334 | 128.86 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29285 | 128.86 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28959 | 128.86 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34182 | 128.86 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31632 | 128.86 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28959 | 128.86 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.218 | 128.86 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34182 | 128.86 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28918 | 128.86 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21498 | 114.79 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2333 | 114.79 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30005 | 114.79 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29652 | 114.79 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34479 | 114.79 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31764 | 114.79 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29652 | 114.79 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20362 | 114.79 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34479 | 114.79 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29623 | 114.79 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26484 | 157.76 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26118 | 157.76 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30985 | 157.76 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2827 | 157.76 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26118 | 157.76 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23858 | 157.76 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30985 | 157.76 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2609 | 157.76 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20792 | 138.49 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22622 | 138.49 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29279 | 138.49 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28913 | 138.49 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3378 | 138.49 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31065 | 138.49 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28913 | 138.49 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21063 | 138.49 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3378 | 138.49 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28885 | 138.49 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2081 | 135.02 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2264 | 135.02 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29298 | 135.02 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28931 | 135.02 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33798 | 135.02 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31083 | 135.02 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28931 | 135.02 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21045 | 135.02 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33798 | 135.02 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28904 | 135.02 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21623 | 127.96 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23334 | 127.96 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29285 | 127.96 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28959 | 127.96 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34182 | 127.96 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31632 | 127.96 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28959 | 127.96 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.218 | 127.96 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34182 | 127.96 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28918 | 127.96 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21498 | 114.01 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2333 | 114.01 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30005 | 114.01 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29652 | 114.01 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34479 | 114.01 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31764 | 114.01 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29652 | 114.01 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20362 | 114.01 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34479 | 114.01 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29623 | 114.01 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20402 | 134.9 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22249 | 134.9 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28949 | 134.9 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2858 | 134.9 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3345 | 134.9 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30731 | 134.9 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2858 | 134.9 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21238 | 134.9 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3345 | 134.9 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28553 | 134.9 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20432 | 131.39 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22278 | 131.39 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28979 | 131.39 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2861 | 131.39 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3348 | 131.39 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30761 | 131.39 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2861 | 131.39 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21208 | 131.39 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3348 | 131.39 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28583 | 131.39 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21178 | 123.86 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22913 | 123.86 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2893 | 123.86 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.286 | 123.86 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33822 | 123.86 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31272 | 123.86 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.286 | 123.86 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21971 | 123.86 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33822 | 123.86 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2856 | 123.86 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21097 | 110.5 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22945 | 110.5 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29664 | 110.5 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29308 | 110.5 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34138 | 110.5 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31418 | 110.5 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29308 | 110.5 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20548 | 110.5 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34138 | 110.5 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2928 | 110.5 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26239 | 155.83 | P42:345:OKGE:SB_NOST7383
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25871 | 155.83 | P42:345:OKGE:SB_NOST7383
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3074 | 155.83 | P42:345:OKGE:SB_NOST7383
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28021 | 155.83 | P42:345:OKGE:SB_NOST7383
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25871 | 155.83 | P42:345:OKGE:SB_NOST7383
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23963 | 155.83 | P42:345:OKGE:SB_NOST7383
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3074 | 155.83 | P42:345:OKGE:SB_NOST7383
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25844 | 155.83 | P42:345:OKGE:SB_NOST7383
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26217 | 152.42 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25848 | 152.42 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30718 | 152.42 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27998 | 152.42 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25848 | 152.42 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23969 | 152.42 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30718 | 152.42 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25821 | 152.42 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20379 | 135.1 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22226 | 135.1 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28926 | 135.1 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28558 | 135.1 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33427 | 135.1 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30708 | 135.1 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28558 | 135.1 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21259 | 135.1 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33427 | 135.1 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28531 | 135.1 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21077 | 110.38 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22926 | 110.38 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29645 | 110.38 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29289 | 110.38 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34119 | 110.38 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31399 | 110.38 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29289 | 110.38 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20565 | 110.38 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34119 | 110.38 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29261 | 110.38 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20379 | 135.59 | P42:345:OKGE:SB_RARD7311
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22226 | 135.59 | P42:345:OKGE:SB_RARD7311
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28926 | 135.59 | P42:345:OKGE:SB_RARD7311
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28558 | 135.59 | P42:345:OKGE:SB_RARD7311
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33427 | 135.59 | P42:345:OKGE:SB_RARD7311
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30708 | 135.59 | P42:345:OKGE:SB_RARD7311
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28558 | 135.59 | P42:345:OKGE:SB_RARD7311
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21259 | 135.59 | P42:345:OKGE:SB_RARD7311
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33427 | 135.59 | P42:345:OKGE:SB_RARD7311
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28531 | 135.59 | P42:345:OKGE:SB_RARD7311
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20379 | 135.8 | P42:345:OKGE:SB_RARD7393
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22226 | 135.8 | P42:345:OKGE:SB_RARD7393
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28926 | 135.8 | P42:345:OKGE:SB_RARD7393
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28558 | 135.8 | P42:345:OKGE:SB_RARD7393
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33427 | 135.8 | P42:345:OKGE:SB_RARD7393
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30708 | 135.8 | P42:345:OKGE:SB_RARD7393
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28558 | 135.8 | P42:345:OKGE:SB_RARD7393
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21259 | 135.8 | P42:345:OKGE:SB_RARD7393
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33427 | 135.8 | P42:345:OKGE:SB_RARD7393
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28531 | 135.8 | P42:345:OKGE:SB_RARD7393
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26183 | 152.83 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25814 | 152.83 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30684 | 152.83 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27964 | 152.83 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25814 | 152.83 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24005 | 152.83 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30684 | 152.83 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25787 | 152.83 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20373 | 135.36 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2222 | 135.36 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28919 | 135.36 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28551 | 135.36 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33421 | 135.36 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30701 | 135.36 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28551 | 135.36 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21268 | 135.36 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33421 | 135.36 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28524 | 135.36 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21074 | 110.57 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22923 | 110.57 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2964 | 110.57 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29285 | 110.57 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34115 | 110.57 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31395 | 110.57 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29285 | 110.57 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20572 | 110.57 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34115 | 110.57 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29257 | 110.57 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26182 | 153.93 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25814 | 153.93 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30683 | 153.93 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27964 | 153.93 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25814 | 153.93 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24006 | 153.93 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30683 | 153.93 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25787 | 153.93 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20368 | 135.81 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22215 | 135.81 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28914 | 135.81 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28545 | 135.81 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33415 | 135.81 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30695 | 135.81 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28545 | 135.81 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21275 | 135.81 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33415 | 135.81 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28518 | 135.81 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21068 | 111.05 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22917 | 111.05 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29634 | 111.05 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29279 | 111.05 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34108 | 111.05 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31388 | 111.05 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29279 | 111.05 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20579 | 111.05 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34108 | 111.05 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2925 | 111.05 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20075 | 134.27 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21902 | 134.27 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2845 | 134.27 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2809 | 134.27 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32946 | 134.27 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30228 | 134.27 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2809 | 134.27 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22111 | 134.27 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32946 | 134.27 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28062 | 134.27 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20102 | 131.13 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2193 | 131.13 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28477 | 131.13 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28118 | 131.13 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32973 | 131.13 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30256 | 131.13 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28118 | 131.13 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22083 | 131.13 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32973 | 131.13 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2809 | 131.13 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20843 | 123.7 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22551 | 123.7 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28384 | 123.7 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28065 | 123.7 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33279 | 123.7 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30724 | 123.7 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28065 | 123.7 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22917 | 123.7 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33279 | 123.7 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28023 | 123.7 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20801 | 108.83 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2263 | 108.83 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29196 | 108.83 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28849 | 108.83 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33665 | 108.83 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30947 | 108.83 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28849 | 108.83 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2139 | 108.83 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33665 | 108.83 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2882 | 108.83 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25908 | 147.92 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25544 | 147.92 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30407 | 147.92 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2769 | 147.92 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25544 | 147.92 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24481 | 147.92 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30407 | 147.92 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25516 | 147.92 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20071 | 132.1 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21905 | 132.1 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28531 | 132.1 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28167 | 132.1 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3303 | 132.1 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30314 | 132.1 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28167 | 132.1 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21857 | 132.1 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3303 | 132.1 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28139 | 132.1 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.201 | 127.1 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21934 | 127.1 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2856 | 127.1 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28195 | 127.1 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33059 | 127.1 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30342 | 127.1 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28195 | 127.1 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21829 | 127.1 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33059 | 127.1 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28168 | 127.1 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20837 | 119.17 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22554 | 119.17 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28478 | 119.17 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28154 | 119.17 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33373 | 119.17 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30821 | 119.17 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28154 | 119.17 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2264 | 119.17 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33373 | 119.17 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28113 | 119.17 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20766 | 107.53 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22602 | 107.53 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29246 | 107.53 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28895 | 107.53 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33718 | 107.53 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31001 | 107.53 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28895 | 107.53 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21168 | 107.53 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33718 | 107.53 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28866 | 107.53 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26233 | 155.94 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25865 | 155.94 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30734 | 155.94 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28017 | 155.94 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25865 | 155.94 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24 | 155.94 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30734 | 155.94 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25838 | 155.94 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20524 | 133.46 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22366 | 133.46 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29056 | 133.46 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28688 | 133.46 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33557 | 133.46 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3084 | 133.46 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28688 | 133.46 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21177 | 133.46 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33557 | 133.46 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28661 | 133.46 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21282 | 126.06 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2301 | 126.06 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29011 | 126.06 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28682 | 126.06 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33905 | 126.06 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31355 | 126.06 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28682 | 126.06 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21942 | 126.06 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33905 | 126.06 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28641 | 126.06 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26282 | 155.94 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25917 | 155.94 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30781 | 155.94 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28062 | 155.94 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25917 | 155.94 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24011 | 155.94 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30781 | 155.94 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25889 | 155.94 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20571 | 138.07 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22414 | 138.07 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29067 | 138.07 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28701 | 138.07 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33566 | 138.07 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30847 | 138.07 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28701 | 138.07 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21226 | 138.07 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33566 | 138.07 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28674 | 138.07 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.206 | 134.03 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22443 | 134.03 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29096 | 134.03 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2873 | 134.03 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33595 | 134.03 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30876 | 134.03 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2873 | 134.03 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21197 | 134.03 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33595 | 134.03 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28703 | 134.03 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21361 | 126.73 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23091 | 126.73 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29052 | 126.73 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28725 | 126.73 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33944 | 126.73 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31392 | 126.73 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28725 | 126.73 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21963 | 126.73 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33944 | 126.73 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28685 | 126.73 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21278 | 112.99 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23124 | 112.99 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29794 | 112.99 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29442 | 112.99 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34267 | 112.99 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31547 | 112.99 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29442 | 112.99 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20524 | 112.99 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34267 | 112.99 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29413 | 112.99 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20582 | 133.25 | P42:345:OKGE:SB_TAGA7386
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22426 | 133.25 | P42:345:OKGE:SB_TAGA7386
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29085 | 133.25 | P42:345:OKGE:SB_TAGA7386
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28719 | 133.25 | P42:345:OKGE:SB_TAGA7386
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33585 | 133.25 | P42:345:OKGE:SB_TAGA7386
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30866 | 133.25 | P42:345:OKGE:SB_TAGA7386
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28719 | 133.25 | P42:345:OKGE:SB_TAGA7386
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21192 | 133.25 | P42:345:OKGE:SB_TAGA7386
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33585 | 133.25 | P42:345:OKGE:SB_TAGA7386
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28692 | 133.25 | P42:345:OKGE:SB_TAGA7386
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21341 | 125.8 | P42:345:OKGE:SB_TAGA7386
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23072 | 125.8 | P42:345:OKGE:SB_TAGA7386
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29041 | 125.8 | P42:345:OKGE:SB_TAGA7386
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28714 | 125.8 | P42:345:OKGE:SB_TAGA7386
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33933 | 125.8 | P42:345:OKGE:SB_TAGA7386
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31382 | 125.8 | P42:345:OKGE:SB_TAGA7386
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28714 | 125.8 | P42:345:OKGE:SB_TAGA7386
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21957 | 125.8 | P42:345:OKGE:SB_TAGA7386
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33933 | 125.8 | P42:345:OKGE:SB_TAGA7386
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28674 | 125.8 | P42:345:OKGE:SB_TAGA7386
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26277 | 156.07 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25911 | 156.07 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30776 | 156.07 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28057 | 156.07 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25911 | 156.07 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24006 | 156.07 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30776 | 156.07 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25883 | 156.07 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20561 | 137.88 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22404 | 137.88 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29062 | 137.88 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28696 | 137.88 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33561 | 137.88 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30842 | 137.88 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28696 | 137.88 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21221 | 137.88 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33561 | 137.88 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28669 | 137.88 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20591 | 133.91 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22435 | 133.91 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29092 | 133.91 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28726 | 133.91 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33592 | 133.91 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30872 | 133.91 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28726 | 133.91 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21191 | 133.91 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33592 | 133.91 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28699 | 133.91 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21351 | 126.53 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23081 | 126.53 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29048 | 126.53 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28721 | 126.53 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3394 | 126.53 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31389 | 126.53 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28721 | 126.53 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21956 | 126.53 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3394 | 126.53 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2868 | 126.53 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21268 | 112.89 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23113 | 112.89 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29789 | 112.89 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29436 | 112.89 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34262 | 112.89 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31542 | 112.89 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29436 | 112.89 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20518 | 112.89 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34262 | 112.89 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29407 | 112.89 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26277 | 156.08 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25911 | 156.08 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30776 | 156.08 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28057 | 156.08 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25911 | 156.08 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24006 | 156.08 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30776 | 156.08 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25883 | 156.08 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20561 | 137.91 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22404 | 137.91 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29062 | 137.91 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28696 | 137.91 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33561 | 137.91 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30842 | 137.91 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28696 | 137.91 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21221 | 137.91 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33561 | 137.91 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28669 | 137.91 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20591 | 133.95 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22434 | 133.95 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29092 | 133.95 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28726 | 133.95 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33592 | 133.95 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30872 | 133.95 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28726 | 133.95 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21191 | 133.95 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33592 | 133.95 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28699 | 133.95 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21351 | 126.54 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23081 | 126.54 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29048 | 126.54 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28721 | 126.54 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3394 | 126.54 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31389 | 126.54 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28721 | 126.54 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21956 | 126.54 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3394 | 126.54 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2868 | 126.54 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21268 | 112.87 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23113 | 112.87 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29789 | 112.87 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29436 | 112.87 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34262 | 112.87 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31542 | 112.87 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29436 | 112.87 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20518 | 112.87 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34262 | 112.87 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29407 | 112.87 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26511 | 165.08 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26148 | 165.08 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31008 | 165.08 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28284 | 165.08 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26148 | 165.08 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23809 | 165.08 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31008 | 165.08 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26121 | 165.08 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20984 | 143.85 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22834 | 143.85 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29449 | 143.85 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29086 | 143.85 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33945 | 143.85 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31222 | 143.85 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29086 | 143.85 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20871 | 143.85 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33945 | 143.85 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29058 | 143.85 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2102 | 139.95 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2287 | 139.95 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29485 | 139.95 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29122 | 139.95 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33981 | 139.95 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31258 | 139.95 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29122 | 139.95 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20835 | 139.95 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33981 | 139.95 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29094 | 139.95 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21777 | 132.55 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23514 | 132.55 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29442 | 132.55 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29119 | 132.55 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34331 | 132.55 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31777 | 132.55 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29119 | 132.55 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21595 | 132.55 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34331 | 132.55 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29078 | 132.55 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21001 | 165.54 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27193 | 165.54 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26861 | 165.54 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31666 | 165.54 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28914 | 165.54 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26861 | 165.54 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2371 | 165.54 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31666 | 165.54 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26829 | 165.54 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22303 | 146.52 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.242 | 146.52 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30392 | 146.52 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3006 | 146.52 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34864 | 146.52 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32112 | 146.52 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3006 | 146.52 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20511 | 146.52 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34864 | 146.52 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30028 | 146.52 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22303 | 144.42 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24201 | 144.42 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30392 | 144.42 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30061 | 144.42 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34865 | 144.42 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32113 | 144.42 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30061 | 144.42 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20511 | 144.42 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34865 | 144.42 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30029 | 144.42 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23083 | 137.13 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24871 | 137.13 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30374 | 137.13 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30082 | 137.13 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3524 | 137.13 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32665 | 137.13 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30082 | 137.13 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21262 | 137.13 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3524 | 137.13 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30037 | 137.13 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2305 | 118.77 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24949 | 118.77 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31156 | 118.77 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30837 | 118.77 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35605 | 118.77 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32853 | 118.77 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30837 | 118.77 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35605 | 118.77 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30803 | 118.77 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20424 | 135.93 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22271 | 135.93 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2898 | 135.93 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2861 | 135.93 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33481 | 135.93 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30762 | 135.93 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2861 | 135.93 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2119 | 135.93 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33481 | 135.93 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28583 | 135.93 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20462 | 131.63 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22309 | 131.63 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29017 | 131.63 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28648 | 131.63 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33519 | 131.63 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30799 | 131.63 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28648 | 131.63 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21152 | 131.63 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33519 | 131.63 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28621 | 131.63 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21209 | 124.14 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22944 | 124.14 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28971 | 124.14 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28641 | 124.14 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33863 | 124.14 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31313 | 124.14 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28641 | 124.14 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21911 | 124.14 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33863 | 124.14 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.286 | 124.14 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21125 | 111.12 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22975 | 111.12 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29701 | 111.12 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29345 | 111.12 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34175 | 111.12 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31456 | 111.12 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29345 | 111.12 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20494 | 111.12 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34175 | 111.12 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29317 | 111.12 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21096 | 112.84 | P42:500:OKGE:SB_FTTH8581
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22945 | 112.84 | P42:500:OKGE:SB_FTTH8581
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29669 | 112.84 | P42:500:OKGE:SB_FTTH8581
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29313 | 112.84 | P42:500:OKGE:SB_FTTH8581
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34143 | 112.84 | P42:500:OKGE:SB_FTTH8581
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31423 | 112.84 | P42:500:OKGE:SB_FTTH8581
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29313 | 112.84 | P42:500:OKGE:SB_FTTH8581
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20531 | 112.84 | P42:500:OKGE:SB_FTTH8581
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34143 | 112.84 | P42:500:OKGE:SB_FTTH8581
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29284 | 112.84 | P42:500:OKGE:SB_FTTH8581
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21097 | 112.9 | P42:500:OKGE:SB_FTTH8583
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22946 | 112.9 | P42:500:OKGE:SB_FTTH8583
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29671 | 112.9 | P42:500:OKGE:SB_FTTH8583
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29315 | 112.9 | P42:500:OKGE:SB_FTTH8583
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34145 | 112.9 | P42:500:OKGE:SB_FTTH8583
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31425 | 112.9 | P42:500:OKGE:SB_FTTH8583
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29315 | 112.9 | P42:500:OKGE:SB_FTTH8583
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20529 | 112.9 | P42:500:OKGE:SB_FTTH8583
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34145 | 112.9 | P42:500:OKGE:SB_FTTH8583
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29286 | 112.9 | P42:500:OKGE:SB_FTTH8583
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21096 | 112.84 | P42:500:OKGE:SB_FTTH8585
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22945 | 112.84 | P42:500:OKGE:SB_FTTH8585
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29669 | 112.84 | P42:500:OKGE:SB_FTTH8585
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29313 | 112.84 | P42:500:OKGE:SB_FTTH8585
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34143 | 112.84 | P42:500:OKGE:SB_FTTH8585
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31423 | 112.84 | P42:500:OKGE:SB_FTTH8585
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29313 | 112.84 | P42:500:OKGE:SB_FTTH8585
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20531 | 112.84 | P42:500:OKGE:SB_FTTH8585
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34143 | 112.84 | P42:500:OKGE:SB_FTTH8585
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29284 | 112.84 | P42:500:OKGE:SB_FTTH8585
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20406 | 135.56 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22254 | 135.56 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2896 | 135.56 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28591 | 135.56 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33461 | 135.56 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30742 | 135.56 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28591 | 135.56 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21215 | 135.56 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33461 | 135.56 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28564 | 135.56 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20441 | 131.37 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22288 | 131.37 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28994 | 131.37 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28625 | 131.37 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33495 | 131.37 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30776 | 131.37 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28625 | 131.37 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2118 | 131.37 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33495 | 131.37 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28598 | 131.37 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21188 | 123.86 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22924 | 123.86 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28947 | 123.86 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28617 | 123.86 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3384 | 123.86 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3129 | 123.86 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28617 | 123.86 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21939 | 123.86 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3384 | 123.86 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28577 | 123.86 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21106 | 110.79 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22955 | 110.79 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2968 | 110.79 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29324 | 110.79 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34154 | 110.79 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31434 | 110.79 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29324 | 110.79 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2052 | 110.79 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34154 | 110.79 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29295 | 110.79 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20169 | 192.67 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21803 | 192.67 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28441 | 192.67 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28062 | 192.67 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32968 | 192.67 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30351 | 192.67 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28062 | 192.67 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23285 | 192.67 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32968 | 192.67 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28036 | 192.67 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23623 | 183.84 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25257 | 183.84 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31895 | 183.84 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31516 | 183.84 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36421 | 183.84 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-033 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21299 | 183.84 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33804 | 183.84 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-065 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21299 | 183.84 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31516 | 183.84 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36421 | 183.84 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3149 | 183.84 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23615 | 176.01 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25249 | 176.01 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31888 | 176.01 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31508 | 176.01 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36414 | 176.01 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21291 | 176.01 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33797 | 176.01 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21291 | 176.01 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31508 | 176.01 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36414 | 176.01 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31482 | 176.01 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24828 | 172.02 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26263 | 172.02 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31975 | 172.02 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31645 | 172.02 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36965 | 172.02 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23931 | 172.02 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34442 | 172.02 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23931 | 172.02 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31645 | 172.02 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2069 | 172.02 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36965 | 172.02 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31603 | 172.02 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24425 | 151.75 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26061 | 151.75 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3272 | 151.75 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32355 | 151.75 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.37216 | 151.75 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22093 | 151.75 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34598 | 151.75 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22093 | 151.75 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32355 | 151.75 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.37216 | 151.75 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32327 | 151.75 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26184 | 156.23 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25815 | 156.23 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30685 | 156.23 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27966 | 156.23 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25815 | 156.23 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23992 | 156.23 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30685 | 156.23 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25788 | 156.23 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2046 | 137.68 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22307 | 137.68 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29012 | 137.68 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28643 | 137.68 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33514 | 137.68 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30794 | 137.68 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28643 | 137.68 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21164 | 137.68 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33514 | 137.68 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28616 | 137.68 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20493 | 133.53 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2234 | 133.53 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29046 | 133.53 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28677 | 133.53 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33547 | 133.53 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30828 | 133.53 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28677 | 133.53 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21131 | 133.53 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33547 | 133.53 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2865 | 133.53 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21245 | 126.09 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22979 | 126.09 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29002 | 126.09 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28672 | 126.09 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33895 | 126.09 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31345 | 126.09 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28672 | 126.09 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21887 | 126.09 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33895 | 126.09 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28632 | 126.09 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21164 | 112.91 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23013 | 112.91 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29736 | 112.91 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29381 | 112.91 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34211 | 112.91 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31491 | 112.91 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29381 | 112.91 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20465 | 112.91 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34211 | 112.91 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29352 | 112.91 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2101 | 167.62 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2778 | 167.62 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27396 | 167.62 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32304 | 167.62 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29658 | 167.62 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27396 | 167.62 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23261 | 167.62 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32304 | 167.62 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27371 | 167.62 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22506 | 152.07 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24206 | 152.07 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30976 | 152.07 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30592 | 152.07 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35499 | 152.07 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32854 | 152.07 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30592 | 152.07 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20066 | 152.07 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35499 | 152.07 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30567 | 152.07 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22519 | 145.33 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24218 | 145.33 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30988 | 145.33 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30604 | 145.33 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35511 | 145.33 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32866 | 145.33 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30604 | 145.33 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20053 | 145.33 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35511 | 145.33 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30579 | 145.33 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23579 | 138.59 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25108 | 138.59 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31046 | 138.59 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30707 | 138.59 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36009 | 138.59 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33482 | 138.59 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30707 | 138.59 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20842 | 138.59 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36009 | 138.59 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30667 | 138.59 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23262 | 123.43 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24963 | 123.43 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31753 | 123.43 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31384 | 123.43 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36247 | 123.43 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33601 | 123.43 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31384 | 123.43 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36247 | 123.43 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31357 | 123.43 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20421 | 135.97 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22268 | 135.97 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28976 | 135.97 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28607 | 135.97 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33478 | 135.97 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 135.97 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28607 | 135.97 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21193 | 135.97 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33478 | 135.97 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2858 | 135.97 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20457 | 131.62 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22305 | 131.62 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29013 | 131.62 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28644 | 131.62 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33514 | 131.62 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30795 | 131.62 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28644 | 131.62 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21157 | 131.62 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33514 | 131.62 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28617 | 131.62 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21205 | 123.97 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22941 | 123.97 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28967 | 123.97 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28637 | 123.97 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33859 | 123.97 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3131 | 123.97 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28637 | 123.97 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21915 | 123.97 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33859 | 123.97 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28597 | 123.97 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21122 | 111.15 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.15 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29698 | 111.15 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29342 | 111.15 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.15 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 111.15 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29342 | 111.15 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20497 | 111.15 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.15 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 111.15 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.26202 | 179.04 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.25833 | 179.04 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.30704 | 179.04 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.27985 | 179.04 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.25833 | 179.04 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.23967 | 179.04 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.30704 | 179.04 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.25806 | 179.04 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.20422 | 158.13 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.22269 | 158.13 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.28977 | 158.13 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.28608 | 158.13 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.33479 | 158.13 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.30759 | 158.13 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.28608 | 158.13 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.21192 | 158.13 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.33479 | 158.13 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.28581 | 158.13 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 553 |  | 0.20458 | 132.37 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 553 |  | 0.22306 | 132.37 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 553 |  | 0.29014 | 132.37 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 553 |  | 0.28645 | 132.37 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 553 |  | 0.33516 | 132.37 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 553 |  | 0.30796 | 132.37 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 553 |  | 0.28645 | 132.37 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 553 |  | 0.21156 | 132.37 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 553 |  | 0.33516 | 132.37 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 553 |  | 0.28618 | 132.37 | System Intact
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.21123 | 129.49 | System Intact
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.22972 | 129.49 | System Intact
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.29699 | 129.49 | System Intact
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.29343 | 129.49 | System Intact
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.34173 | 129.49 | System Intact
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.31453 | 129.49 | System Intact
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.29343 | 129.49 | System Intact
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.20496 | 129.49 | System Intact
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.34173 | 129.49 | System Intact
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.29314 | 129.49 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 553 |  | 0.21207 | 124.92 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 553 |  | 0.22942 | 124.92 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 553 |  | 0.28968 | 124.92 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 553 |  | 0.28638 | 124.92 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 553 |  | 0.33861 | 124.92 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 553 |  | 0.31311 | 124.92 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 553 |  | 0.28638 | 124.92 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 553 |  | 0.21914 | 124.92 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 553 |  | 0.33861 | 124.92 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 553 |  | 0.28598 | 124.92 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 126.65 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 126.65 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 126.65 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.65 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.65 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 126.65 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.65 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 126.65 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.65 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 126.65 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 126.61 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 126.61 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 126.61 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.61 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.61 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 126.61 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.61 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 126.61 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.61 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 126.61 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 126.41 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 126.41 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 126.41 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.41 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.41 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 126.41 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.41 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 126.41 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.41 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 126.41 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 126.99 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 126.99 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 126.99 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.99 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.99 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 126.99 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.99 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 126.99 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.99 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 126.99 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 129.03 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 129.03 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 129.03 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 129.03 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 129.03 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 129.03 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 129.03 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 129.03 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 129.03 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 129.03 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.22 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.22 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.22 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.22 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.22 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.22 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.22 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.22 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.22 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.22 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.21 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.21 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.21 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.21 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.21 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.21 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.21 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.21 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.21 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.21 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.09 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.09 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.09 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.09 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.09 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.09 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.09 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.09 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.09 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.09 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.34 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.34 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.34 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.34 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.34 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.34 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.34 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.34 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.34 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.34 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.21 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.21 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.21 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.21 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.21 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.21 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.21 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.21 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.21 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.21 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 125.79 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 125.79 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 125.79 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 125.79 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 125.79 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 125.79 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 125.79 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 125.79 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 125.79 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 125.79 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.21 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.21 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.21 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.21 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.21 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.21 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.21 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.21 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.21 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.21 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 126.21 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 126.21 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 126.21 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.21 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.21 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 126.21 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.21 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 126.21 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.21 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 126.21 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.21 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.21 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.21 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.21 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.21 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.21 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.21 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.21 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.21 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.21 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.21 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.21 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.21 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.21 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.21 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.21 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.21 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.21 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.21 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.21 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.2 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.2 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.2 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.2 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.2 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.2 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.2 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.2 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20428 | 127.2 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.2 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.2 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28609 | 127.2 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3076 | 127.2 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28609 | 127.2 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.2 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28582 | 127.2 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.99 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.99 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.99 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.99 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.99 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.99 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.99 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.99 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.99 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.99 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 128.04 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 128.04 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 128.04 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 128.04 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 128.04 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 128.04 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 128.04 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 128.04 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 128.04 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 128.04 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.2 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.2 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.2 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.2 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.2 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.2 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.2 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.2 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.2 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.2 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.2 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.2 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.2 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.2 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.2 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.2 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.2 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.2 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.2 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.2 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.2 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.2 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.2 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.2 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 126.4 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 126.4 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 126.4 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.4 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.4 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 126.4 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.4 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 126.4 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.4 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 126.4 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.1 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.1 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.1 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.1 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.1 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.1 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.1 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.1 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.1 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.1 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.1 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.1 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.1 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.1 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.1 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.1 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.1 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.1 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.1 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.1 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20519 | 127.63 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22485 | 127.63 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28983 | 127.63 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28605 | 127.63 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33504 | 127.63 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30786 | 127.63 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28605 | 127.63 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21191 | 127.63 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33504 | 127.63 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28579 | 127.63 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20431 | 125.25 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22281 | 125.25 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28979 | 125.25 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 125.25 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33482 | 125.25 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30764 | 125.25 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 125.25 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21207 | 125.25 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33482 | 125.25 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 125.25 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20433 | 122.64 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22282 | 122.64 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28979 | 122.64 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28611 | 122.64 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33483 | 122.64 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30766 | 122.64 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28611 | 122.64 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21208 | 122.64 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33483 | 122.64 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 122.64 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 126.17 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 126.17 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 126.17 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.17 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.17 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 126.17 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.17 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 126.17 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.17 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 126.17 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20508 | 128.97 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22428 | 128.97 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29169 | 128.97 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28814 | 128.97 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33694 | 128.97 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30883 | 128.97 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28814 | 128.97 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21181 | 128.97 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33694 | 128.97 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28784 | 128.97 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20508 | 127.65 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22428 | 127.65 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29169 | 127.65 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28814 | 127.65 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33694 | 127.65 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30883 | 127.65 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28814 | 127.65 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21181 | 127.65 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33694 | 127.65 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28784 | 127.65 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20428 | 126.92 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22278 | 126.92 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28979 | 126.92 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28602 | 126.92 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33481 | 126.92 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 126.92 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28602 | 126.92 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21204 | 126.92 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33481 | 126.92 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28582 | 126.92 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20535 | 127.67 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22383 | 127.67 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29048 | 127.67 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28682 | 127.67 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33548 | 127.67 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30826 | 127.67 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28682 | 127.67 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21184 | 127.67 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33548 | 127.67 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28655 | 127.67 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20498 | 127.46 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22348 | 127.46 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29024 | 127.46 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28657 | 127.46 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33524 | 127.46 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30803 | 127.46 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28657 | 127.46 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21192 | 127.46 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33524 | 127.46 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2863 | 127.46 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20394 | 127.41 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22218 | 127.41 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29566 | 127.41 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2942 | 127.41 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33617 | 127.41 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30891 | 127.41 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2942 | 127.41 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21128 | 127.41 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33617 | 127.41 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29368 | 127.41 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20394 | 127.72 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22218 | 127.72 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29566 | 127.72 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2942 | 127.72 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33617 | 127.72 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30891 | 127.72 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2942 | 127.72 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21128 | 127.72 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33617 | 127.72 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29368 | 127.72 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21077 | 127.77 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22554 | 127.77 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29093 | 127.77 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28722 | 127.77 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33601 | 127.77 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30883 | 127.77 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28722 | 127.77 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21136 | 127.77 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33601 | 127.77 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28695 | 127.77 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20432 | 126.51 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22281 | 126.51 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28976 | 126.51 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28608 | 126.51 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33478 | 126.51 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30758 | 126.51 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28608 | 126.51 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.51 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33478 | 126.51 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28581 | 126.51 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 125.91 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 125.91 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 125.91 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 125.91 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 125.91 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 125.91 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 125.91 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 125.91 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 125.91 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 125.91 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20456 | 127.2 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22314 | 127.2 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29183 | 127.2 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28804 | 127.2 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33539 | 127.2 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30803 | 127.2 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28804 | 127.2 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21219 | 127.2 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33539 | 127.2 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28781 | 127.2 | P12:115:SPS:V26.1.RSWLL.EDDY_N