## Executive Summary
Executive Summary: DISIS-2017-001 Phase Two Stability and Short Circuit Analysis
Pursuant to the Southwest Power Pool (SPP) Open Access Transmission Tariff (OATT), SPP has conducted this Definitive Interconnection System Impact Study (DISIS) for generation interconnection requests received during the DISIS Queue Cluster Window which closed on March 31, 2017. The primary objective of this DISIS is to identify the system constraints, transient instabilities, and over-dutied equipment associated with connecting the generation to the area transmission system. The Impact Study and other subsequent Interconnection Studies are designed to identify required Transmission Owner Interconnection Facilities, Network Upgrades and other Direct Assignment Facilities needed to inject power into the grid at each specific point of interconnection. The study analysis for the generation interconnection requests included in this DISIS are displayed in this workbook. This workbook provides a convenient method to sort and analyze required study data. The DISIS Manual Version 1.2 posted on http://opsportal.spp.org/Studies/Gen contains details about the DISIS process, methodology, definitions, and useful links. Please review the DISIS Manual or contact gistudies@spp.org for more information about the study process. DISIS-2017-001 Phase 2 includes study requests in the following cluster groups within three regions: North: (04 - Northwest Kansas, 09 - Nebraska, 15 - Eastern South Dakota, 16 - Western North Dakota, 17 - Western South Dakota) Central: (01 - Woodward, 03 - Spearville, 08 - North Oklahoma/South Central Kansas,12 - Northwest Arkansas, 13 - Northeast Kansas/Northwest Missouri) South: (02 - Hitchland, 06 - South Texas Panhandle/New Mexico, 07 - Southwestern Oklahoma, 10 - Southeast Oklahoma/Northeast Texas, 14 - South Central Oklahoma) North: CF Power performed analysis. Central: EPE performed analysis. South: S&C performed analysis. NOTE: per SPP Tariff Attachment V; section 8.4.2 DISIS Phase Two will consist of a short circuit analysis and a stability analysis, taking into account the impact on the power flow analysis of any requests withdrawn after the DISIS Phase One. The Short Circuit Ratio tab has been added to the workbook and will be added to the DISIS Manual.
DISIS Manual Version 1.3
https://opsportal.spp.org/documents/studies/DISIS%20Manual.pdf
This DISIS analyzes the impact of interconnecting new generation for total of:
10,398 MW
The minimum cost, including both power flow and stability, of interconnecting all requests included in this DISIS is estimated at:
4653994678.78
Models Used in Study
2018 MDWG
Winter: 2019
Summer: 2021, 2028
Light: 2021
Group 6 Notes:
Stability/Damping Issue: It has been observed that under few contingencies in the BC cases and under several contingencies in the TC cases the system becomes unstable or exhibits no/low damping oscillations participated by all
the synchronous generators in the area with the frequency of around 0.4 Hz to 0.5 Hz.
These instability/damping issues are attributed to two potentional reasons:
1) Low synchronous generation units availability in the 19W and 21L cases leading to weaker system in terms of voltage and reactive power in comparison to 21S and 28S (stability/damping issues were mostly observed in the 19W and 21L cases).
2) Group's export limit especially in 21L TC.
Mitigation option consideration:
Mitigation options were evaluated for a contingency if it caused an stability/damping issue in the TC cases and not in the BC cases; i.e. caused by the addition of study generators.
Mitigation Options Description:
1) ±600 MVAr SVC at Crossroad 765kV: This mitigation option has been observed to provide dynamic reactive power support, help mitigating the instability and enhance oscillations damping.
Note: The size and location of the SVC has not been optimized in this study. However, several potential locations and sizes were tested and per results from these initial tests and feedback from SPP, Crossroad 765kV location and ±600 MVAr size has been selected.
2) G6 Study Gen Scale Down: Although several G6 upgrades have been already implemented in the cases to resolve the power flow issues initally observed in the study, for several contingencies the stability limits for the G6's ties were found to be
below the values in the power flow cases. If the stability/damping issue was not resolved with the Crossroad SVC option described above, the dispatch of the study generators in the G6 was decreased incrementally and uniformly in steps of 10% until
the issue is resolved (Total maximum dispatch of G6 study gens: 2738MW). This reduces the power export from the G6 main tie-lines CRAWFISH765-SEMINOLE765, O.K.U.-7-L.E.S.-7 and CRAWFISH_DR-BORDER (flows 19WTC: 4692MW, 21LTC: 4929MW, 21STC: 3936MW and 28STC: 3557MW).
Note: Initially, second SVC option was also investigated in combination with the Crossroad SVC to resolve some of the stability/damping issues that Crossroad SVC alone could not mitigate. The tested locations includes TUCO345kV, CRAWFISH345kV, OKU345, which
found to improve the system stability/damping for some of the tested contingencies but not all of them; hence, this mitigation option was not used in this study.

## Revision History
Date | Author | Change Description
2021-04-07 | SPP | Posting of DISIS-2017-001 Phase 2 Results
2021-04-28 | SPP | Phase Two Report Workbook has been updated for dynamics model corrections.

## Requests
Gen Number | Gen Model | Region | Group | Queue | Fuel Type | MW Amount | LOIS Amount | Area | POI | Status | Reactive Compensation Requirements (MVAR)
GEN-2016-172 | A1530U1 | South | 06 - South Texas Panhandle/New Mexico | DIS-17-1 | Wind | 116.55 | 0 | SPS | Newhart 115kV | DISIS STAGE | 14.1
GEN-2016-172 | A1530U1 | South | 06 - South Texas Panhandle/New Mexico | DIS-17-1 | Wind | 113.4 | 0 | SPS | Newhart 115kV | DISIS STAGE | 14.1
GEN-2017-004 | CP17093300 | North | 04 - Northwest Kansas | DIS-17-1 | Wind | 201.6 | 201.6 | WERE | Elm Creek - Summit 345kV | DISIS STAGE | 10.61
GEN-2017-027 | CP20065709 | South | 14 - South Central Oklahoma | DIS-17-1 | Wind | 36 | 18 | OKGE | Pooleville-Ratliff (Carter County) 138kV | DISIS STAGE | 7.3 (GEN1,2,3&4)
GEN-2017-027 | CP20065709 | South | 14 - South Central Oklahoma | DIS-17-1 | Wind | 33.6 | 33.6 | OKGE | Pooleville-Ratliff (Carter County) 138kV | DISIS STAGE | 7.3 (GEN1,2,3&4)
GEN-2017-040 | FLX219 | Central | 08 - North Oklahoma/South Central Kansas | DIS-17-1 | Solar | 200 | 200 | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | DISIS STAGE | -5.5
GEN-2017-058 | GELV5G1 | South | 02 - Hitchland | DIS-17-1 | Solar | 135 | 0 | SPS | Hereford Northeast 115kV | DISIS STAGE | 1.4
GEN-2017-080 | GELV5G1 | South | 06 - South Texas Panhandle/New Mexico | DIS-17-1 | Solar | 312 | 0 | SPS | Tolk 230kV | DISIS STAGE | 12.2
GEN-2017-080 | GELV5G1 | South | 06 - South Texas Panhandle/New Mexico | DIS-17-1 | Solar | 213.2 | 0 | SPS | Tolk 230kV | DISIS STAGE | 12.2
GEN-2017-100 | GEPVG | South | 02 - Hitchland | DIS-17-1 | Solar | 102.6 | 0 | SPS | Texas County 115kV | DISIS STAGE | 1
GEN-2017-087 | GEPVG | South | 06 - South Texas Panhandle/New Mexico | DIS-17-1 | Solar | 64 | 0 | SPS | Clovis Interchange 115kV | DISIS STAGE | 1.3
GEN-2017-059 | GEPVG | South | 06 - South Texas Panhandle/New Mexico | DIS-17-1 | Solar | 90 | 0 | SPS | TUCO 230kV | DISIS STAGE | 5.4
GEN-2017-057 | GEPVG | South | 10 - Southeast Oklahoma/Northeast Texas | DIS-17-1 | Solar | 72.5 | 72.5 | AEPW | Hosston 69kV | DISIS STAGE | 0.8
GEN-2017-074 | GEPVG | Central | 08 - North Oklahoma/South Central Kansas | DIS-17-1 | Solar | 72.5 | 72.5 | AEPW | Pryor Junction 138kV sub | DISIS STAGE | -0.7
GEN-2017-073 | GEPVG | Central | 08 - North Oklahoma/South Central Kansas | DIS-17-1 | Solar | 72.5 | 72.5 | GRDA | Dry Gulch 161kV sub | DISIS STAGE | -0.7
GEN-2017-061 | GEPVG | Central | 08 - North Oklahoma/South Central Kansas | DIS-17-1 | Solar | 101.5 | 101.5 | GRDA | GRDA1 to CLARMR 5 161kV line | DISIS STAGE | -1.1
GEN-2017-071 | GEPVG | Central | 08 - North Oklahoma/South Central Kansas | DIS-17-1 | Solar | 124.7 | 124.7 | OKGE | Greenwood 138kV sub | DISIS STAGE | -1.2
GEN-2017-072 | GEPVG | Central | 08 - North Oklahoma/South Central Kansas | DIS-17-1 | Solar | 52.2 | 52.2 | OKGE | Greenwood 138kV sub | DISIS STAGE | -0.5
GEN-2017-092 | GEPVG | Central | 08 - North Oklahoma/South Central Kansas | DIS-17-1 | Solar | 200 | 200 | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | DISIS STAGE | -8.5
GEN-2017-077 | GEPVG | Central | 08 - North Oklahoma/South Central Kansas | DIS-17-1 | Solar | 124.7 | 124.7 | AEPW | Explorer Claremore Tap EXCLART4 | DISIS STAGE | -1.2
GEN-2017-076 | GEPVG | Central | 12 - Northwest Arkansas | DIS-17-1 | Solar | 52.2 | 52.2 | AEPW | Chamber Springs 161kV sub | DISIS STAGE | -0.6
GEN-2016-039 | GEPVG_LV5 | South | 06 - South Texas Panhandle/New Mexico | DIS-17-1 | Solar | 112 | 0 | SPS | Swisher 115kV | DISIS STAGE | 4.2
GEN-2017-013 | GEWTG2 | North | 04 - Northwest Kansas | DIS-17-1 | Wind | 200 | 200 | SUNC | Mingo 345kV | DISIS STAGE | 7.23
GEN-2017-094 | GEWTG2 | North | 15 - Eastern South Dakota | DIS-17-1 | Wind | 200 | 189.6 | WAPA | Fort Thompson-Huron 230kV | DISIS STAGE | 9.3
GEN-2017-047 | GEWTG2 | South | 02 - Hitchland | DIS-17-1 | Wind | 102 | 0 | SPS | Cole 115kV | DISIS STAGE | 1.6
GEN-2017-007 | GEWTG2 | South | 06 - South Texas Panhandle/New Mexico | DIS-17-1 | Wind | 147.5 | 0 | SPS | Pleasant Hill 230kV sub | DISIS STAGE | 25.5
GEN-2017-007 | GEWTG2 | South | 06 - South Texas Panhandle/New Mexico | DIS-17-1 | Wind | 147.5 | 0 | SPS | Pleasant Hill 230kV sub | DISIS STAGE | 25.5
GEN-2017-087 | GEWTG2 | South | 06 - South Texas Panhandle/New Mexico | DIS-17-1 | Solar | 64 | 0 | SPS | Clovis Interchange 115kV | DISIS STAGE | 1.3
GEN-2017-033 | GEWTG2 | South | 06 - South Texas Panhandle/New Mexico | DIS-17-1 | Wind | 100 | 0 | AEPW | Oklaunion 345kV sub | DISIS STAGE | 19.5
GEN-2017-033 | GEWTG2 | South | 06 - South Texas Panhandle/New Mexico | DIS-17-1 | Wind | 100 | 0 | AEPW | Oklaunion 345kV sub | DISIS STAGE | 19.5
GEN-2017-026 | GEWTG2 | South | 06 - South Texas Panhandle/New Mexico | DIS-17-1 | Wind | 112.5 | 0 | SPS | Tolk 230kV | DISIS STAGE | 19.2
GEN-2017-026 | GEWTG2 | South | 06 - South Texas Panhandle/New Mexico | DIS-17-1 | Wind | 122.5 | 0 | SPS | Tolk 230kV | DISIS STAGE | 19.2
GEN-2017-005 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-17-1 | Wind | 195 | 195 | WERE | Marmaton - Litchfield 161kV | DISIS STAGE | -7.6
GEN-2017-031 | GEWTG2/GEWTE2/GEWTT1 | North | 09 - Nebraska | DIS-17-1 | Wind | 100 | 100 | NPPD | Wildhorse - Covalt 115kV | DISIS STAGE | 3.64
GEN-2016-159 | GSCOR1 | North | 09 - Nebraska | DIS-17-1 | Wind | 427.3 | 427.3 | NPPD | Turtle Creek 345kV | DISIS STAGE | 40.01
GEN-2017-039 | GSCOR1 | South | 06 - South Texas Panhandle/New Mexico | DIS-17-1 | Wind | 200.1 | 0 | SPS | Needmore 230kV sub | DISIS STAGE | 7.9
GEN-2017-097 | PE_GEN_700 (replaced to WECC model) | North | 17 - Western South Dakota | DIS-17-1 | Solar | 128 | 128 | WAPA | Underwood 115kV Sub | DISIS STAGE | 1.29
GEN-2017-055 | PEGEN_H1000A | North | 09 - Nebraska | DIS-17-1 | Solar | 228.3 | 288.3 | LES | Wagener 115kV Sub | DISIS STAGE | 2.71
GEN-2016-103 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-17-1 | Wind | 240 | 0 | BEPC-SPP | Fort Thompson-Leland Olds 345kV | DISIS STAGE | 19.88
GEN-2017-048 | REGCAU1 | North | 16 - Western North Dakota | DIS-17-1 | Wind | 300 | 300 | WAPA | Neset 230kV | DISIS STAGE | 30.78
GEN-2017-065 | REGCAU1 | South | 06 - South Texas Panhandle/New Mexico | DIS-17-1 | Solar | 101.25 | 0 | AEPW | Oklaunion 345kV sub | DISIS STAGE | 9.6
GEN-2017-078 | REGCAU1 | South | 06 - South Texas Panhandle/New Mexico | DIS-17-1 | Wind | 110.4 | 0 | SPS | Eddy County-Tolk (Crossroads) 345kV | DISIS STAGE | 25.8
GEN-2017-078 | REGCAU1 | South | 06 - South Texas Panhandle/New Mexico | DIS-17-1 | Wind | 110.4 | 0 | SPS | Eddy County-Tolk (Crossroads) 345kV | DISIS STAGE | 25.8
GEN-2017-104 | REGCAU1 | South | 06 - South Texas Panhandle/New Mexico | DIS-17-1 | Solar | 240 | 0 | SPS | Hobbs 230kV | DISIS STAGE | 2.6
GEN-2017-016 | REGCAU1 | South | 06 - South Texas Panhandle/New Mexico | DIS-17-1 | Solar | 33 | 0 | SPS | Norton 115kV Switching Station | DISIS STAGE | 0.3
GEN-2016-037 | REGCAU1 | South | 07 - Southwestern Oklahoma | DIS-17-1 | Wind | 300 | 300 | AEPW | Chisholm-Gracemont 345kV | DISIS STAGE | 32.1
GEN-2017-036 | REGCAU1 | South | 07 - Southwestern Oklahoma | DIS-17-1 | Solar | 100 | 100 | WFEC | Snyder 138kV | DISIS STAGE | 1.7
GEN-2017-051 | REGCAU1 | South | 07 - Southwestern Oklahoma | DIS-17-1 | Solar | 30 | 30 | OMPA | Tap Lake Creek SW - Russell SW 69kV | DISIS STAGE | 0.4
GEN-2017-023 | REGCAU1 | South | 14 - South Central Oklahoma | DIS-17-1 | Solar | 85 | 85 | WFEC | Hugo Power Plant 138kV Sub | DISIS STAGE | 1
GEN-2017-022 | REGCAU1 | Central | 08 - North Oklahoma/South Central Kansas | DIS-17-1 | Solar | 65 | 65 | WERE | Altoona- NE Parson 138kV | DISIS STAGE | -0.9
ASGI-2012-008 | None | Central | 13 - Northeast Kansas/Northwest Missouri | PQ | Gas | 3.55 |  | WERE | Sheffield 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-008 | None | Central | 13 - Northeast Kansas/Northwest Missouri | PQ | Gas | 3.55 |  | WERE | Sheffield 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-030 | REGCAU1 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-17-1 | Wind | 200 | 200 | KCPL | Eastown - Iatan 345kV | DISIS STAGE | -84.5
GEN-2017-028 | REGCAU1 | Central | 01 - Woodward | DIS-17-1 | Solar | 50 | 50 | WFEC | El Reno SW 138kV switch station | DISIS STAGE | -1
ASGI-2015-004 | GENROU | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-1 | Thermal | 109.364 |  | GRDA | Coffeyville City 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-011 | REGCAU1 | Central | 01 - Woodward | DIS-17-1 | Solar | 151.8 | 151.8 | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | DISIS STAGE | -4.8
GEN-2017-021 | REGCAU1 | Central | 03 - Spearville | DIS-17-1 | Wind | 200 | 200 | SUNC | Post Rock - Spearville 345kV | DISIS STAGE | -9.5
GEN-2017-099 | REGCAU1 | Central | 03 - Spearville | DIS-17-1 | Wind | 150 | 150 | SUNC | Post Rock - Spearville 345kV | DISIS STAGE | -10.5
GEN-2017-032 | REGCAU1 | Central | 03 - Spearville | DIS-17-1 | Wind | 200 | 200 | SWPS | Finney - Lamar 345kV | DISIS STAGE | 0
GEN-2017-052 | REGCAU1 | Central | 03 - Spearville | DIS-17-1 | Solar | 25 | 25 | SUNC | Tap Bear Creek-Johnson Corner 115kV | DISIS STAGE | -0.4
GEN-2017-024 | REGCAU2 | South | 14 - South Central Oklahoma | DIS-17-1 | Solar | 50 | 50 | WFEC | Frogville 138kV sub | DISIS STAGE | 0.6
GEN-2017-065 | SMASC126 | South | 06 - South Texas Panhandle/New Mexico | DIS-17-1 | Solar | 99 | 0 | AEPW | Oklaunion 345kV sub | DISIS STAGE | 9.6
GEN-2017-068 | SMASC126 | Central | 08 - North Oklahoma/South Central Kansas | DIS-17-1 | Solar | 103.5 | 103.5 | WERE | Wichita 345kV | DISIS STAGE | -3.1
ASGI-2015-004 | GENROU | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-1 | Thermal | 109.364 |  | GRDA | Coffeyville City 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-064 | SMASC134 | North | 17 - Western South Dakota | DIS-17-1 | Solar | 110 | 110 | WAPA | Underwood - Wayside 230kV | DISIS STAGE | 6.68
GEN-2017-069 | SMASC139 | South | 06 - South Texas Panhandle/New Mexico | DIS-17-1 | Solar | 28.6 | 0 | SPS | Norton 115kV Switching Station | DISIS STAGE | 0.1
GEN-2017-010 | SWTGU2 | North | 16 - Western North Dakota | DIS-17-1 | Wind | 200.1 | 200.1 | WAPA | Rhame 230kV Sub | DISIS STAGE | 6.91
GEN-2017-075 | SWTGU2 | South | 14 - South Central Oklahoma | DIS-17-1 | Solar | 200 | 200 | OKGE | Hugo-Sunnyside 345kV | DISIS STAGE | 8.9
GEN-2017-009 | VC18084901, VC19024901 | Central | 08 - North Oklahoma/South Central Kansas | DIS-17-1 | Wind | 301 | 301 | WERE | Neosho - Caney River 345kV | DISIS STAGE | -29.1
ASGI-2015-004 | GENSAL | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-1 | Thermal | 109.364 |  | GRDA | Coffeyville City 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2018-001GIA-61 | VWCOR6 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-17-1-PQ | Wind | 238 |  | AECI | Maryville 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2018-001GIA-61 | VWCOR8 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-17-1-PQ | Wind | 242 |  | AECI | Maryville 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2018-001GIA-61 | VWCOR8 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-17-1-PQ | Wind | 242 |  | AECI | Maryville 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-027 | VC20045709 | South | 14 - South Central Oklahoma | DIS-17-1 | Wind | 24.2 | 24.2 | OKGE | Pooleville-Ratliff (Carter County) 138kV | DISIS STAGE | 7.3 (GEN1,2,3&4)
GEN-2017-027 | VC20045709 | South | 14 - South Central Oklahoma | DIS-17-1 | Wind | 42 | 21 | OKGE | Pooleville-Ratliff (Carter County) 138kV | DISIS STAGE | 7.3 (GEN1,2,3&4)
GEN-2017-014 | VWCO81 (replaced to WECC model) | North | 17 - Western South Dakota | DIS-17-1 | Wind | 300 | 0 | WAPA | Underwood - Philip Tap 230kV | DISIS STAGE | 18.09
GEN-2002-004 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | PQ | Wind | 199.5 |  | WERE | Latham 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-004 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | PQ | Wind | 199.5 |  | WERE | Latham 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-085 | VWCOR8 (replaced to WECC model in 21L case) | North | 09 - Nebraska | DIS-17-1 | Wind | 74 | 74 | NPPD | Friend 115kV | DISIS STAGE | 4.95
GEN-2017-008 | WECC model | North | 09 - Nebraska | DIS-17-1 | Solar | 305 | 305 | NPPD | Moore (GEN-2016-096 Tap)-Pauline 345kV | DISIS STAGE | 20.79
NPPDSpringview | GENCLS | North | 09 - Nebraska | DIS-17-1-PQ | Wind | 3 |  | NPPD
SPSChanning | None | South | 06 - South Texas Panhandle/New Mexico | DIS-17-1-PQ | Wind | 4.2 |  | SPS
SPSLeaCounty | None | South | 06 - South Texas Panhandle/New Mexico | DIS-17-1-PQ | Solar | 5.5 |  | SPS
SWPANixaSolar | None | Central | 12 - Northwest Arkansas | DIS-17-1-PQ | Solar | 7.9 |  | SWPA
J748 | REGCAU1 | North | 09 - Nebraska | DIS-17-1-PQ | Wind | 100 |  | MEC
J748 | REGCAU1 | North | 09 - Nebraska | DIS-17-1-PQ | Wind | 100 |  | MEC
GEN-2004-017 | GENROE | Central | 08 - North Oklahoma/South Central Kansas | DIS-14-2 | CT/ST | 259 |  | EMDE | Riverton 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-017 | GENROE | Central | 08 - North Oklahoma/South Central Kansas | DIS-14-2 | CT/ST | 259 |  | EMDE | Riverton 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-012 | SWTGU2 | Central | 03 - Spearville | PQ | Wind | 248.4 |  | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
BEPCAyrshire | WT3G2 | North | 15 - Eastern South Dakota | DIS-17-1-PQ | Wind | 21 |  | BEPC-SPP | Ayershire 69kV
BEPCGerled | WT3G2 | North | 15 - Eastern South Dakota | DIS-17-1-PQ | Wind | 10.5 |  | BEPC-SPP | Gerled Tap 69kV
BEPCHummel | WT3G2 | North | 15 - Eastern South Dakota | DIS-17-1-PQ | Wind | 10.5 |  | BEPC-SPP | Hummel 69kV
J718 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-17-1-PQ | Solar | 49.98 |  | XEL
WAPATitanWind | REGCAU1 | North | 15 - Eastern South Dakota | DIS-17-1-PQ | Wind | 25 |  | WAPA
BEPCNDPW0 | WT3G2 | North | 16 - Western North Dakota | DIS-17-1-PQ | Wind | 7.5 |  | BEPC-SPP | SW Minot 115kV
BEPCNDPW1 | GEWTG2 | North | 16 - Western North Dakota | DIS-17-1-PQ | Wind | 5 |  | BEPC-SPP | ND Prairie Wind 115kV
GEN-2016-177 | GENSAL | South | 06 - South Texas Panhandle/New Mexico | DIS-16-2 | Gas | 20 |  | SPS | XTO-Cornell 115kV station | IA PENDING
GEN-2016-167 | GEPVG | South | 10 - Southeast Oklahoma/Northeast Texas | DIS-16-2 | Solar | 73.5 |  | AEPW | Lieberman - North Benton 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-160 | GEPVG | North | 04 - Northwest Kansas | DIS-16-2 | Battery | 20 |  | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-147 | GEPVG | North | 09 - Nebraska | DIS-16-2 | Solar | 40 |  | NPPD | Sidney 115kV Sub | FACILITY STUDY STAGE
ASGI-2016-010 | GEWTG0501 | South | 02 - Hitchland | DIS-16-2 | Wind | 90 |  | SPS | Powell Corner 115kV
GEN-2016-133 | GEWTG0501 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-2 | Wind | 187.5 |  | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-134 | GEWTG0501 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-2 | Wind | 187.5 |  | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-137 | GEWTG0501 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-2 | Wind | 187.5 |  | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-138 | GEWTG0501 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-2 | Wind | 187.5 |  | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-139 | GEWTG0501 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-2 | Wind | 100 |  | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-141 | GEWTG0501 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-2 | Wind | 350 |  | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-142 | GEWTG0501 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-2 | Wind | 350 |  | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-145 | GEWTG0501 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-2 | Wind | 175 |  | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-146 | GEWTG0501 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-2 | Wind | 175 |  | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-102 | GEWTG2 | South | 14 - South Central Oklahoma | DIS-16-2 | Wind | 132.5 |  | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-102 | GEWTG2 | South | 14 - South Central Oklahoma | DIS-16-2 | Wind | 18.4 |  | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-128 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-2 | Wind | 176 |  | OKGE | Woodring 345kV | FACILITY STUDY STAGE
GEN-2016-162 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-2 | Wind | 252 |  | WERE | Benton 345kV | FACILITY STUDY STAGE
GEN-2016-163 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-2 | Wind | 252 |  | WERE | Benton 345kV | FACILITY STUDY STAGE
GEN-2016-100 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-2 | Wind | 100 |  | OKGE | Spring Creek-Sooner 345kV | FACILITY STUDY STAGE
GEN-2016-101 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-2 | Wind | 195 |  | OKGE | Spring Creek-Sooner 345kV | FACILITY STUDY STAGE
GEN-2016-150 | GEWTG2 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-16-2 | Wind | 302 |  | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-174 | GEWTG2 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-16-2 | Wind | 302 |  | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-088 | GEWTG2 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-16-2 | Wind | 151.2 |  | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-157 | GEWTG2 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-16-2 | Wind | 252 |  | KCPL | West Gardner 345kV | IA PENDING
GEN-2016-158 | GEWTG2 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-16-2 | Wind | 252 |  | KCPL | West Gardner 345kV | IA PENDING
GEN-2016-149 | GEWTG2 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-16-2 | Wind | 302 |  | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-176 | GEWTG2 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-16-2 | Wind | 302 |  | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-131 | GEWTG2 | Central | 01 - Woodward | DIS-16-2 | Wind | 202.5 |  | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-111 | GEWTG2 | North | 04 - Northwest Kansas | DIS-16-2 | Wind | 302 |  | WERE | Reno-(GEN-2016-112 Tap) Summit 345kV | FACILITY STUDY STAGE
GEN-2016-112 | GEWTG2 | North | 04 - Northwest Kansas | DIS-16-2 | Wind | 220 |  | WERE | Reno (GEN-2016-111 Tap)-Summit 345kV | FACILITY STUDY STAGE
GEN-2016-122 | GEWTG2 | North | 04 - Northwest Kansas | DIS-16-2 | Wind | 225 |  | WERE | Reno (GEN-2016-111 Tap)-Summit 345kV | FACILITY STUDY STAGE
GEN-2016-110 | GEWTG2 | North | 09 - Nebraska | DIS-16-2 | Wind | 152 |  | WAPA | Laramie River-Stegall 345kV Line | FACILITY STUDY STAGE
GEN-2016-126 | GSCOR1 | South | 14 - South Central Oklahoma | DIS-16-2 | Wind | 172.5 |  | OKGE | Arbuckle 138kV | IA PENDING
GEN-2016-121 | SMASC126 | South | 06 - South Texas Panhandle/New Mexico | DIS-16-2 | Solar | 110 |  | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-091 | SWTGU1 | South | 07 - Southwestern Oklahoma | DIS-16-2 | Wind | 303.6 |  | AEPW | Gracemont-Lawton East Side 345kV | IA PENDING
GEN-2016-114 | SWTGU2 | North | 04 - Northwest Kansas | DIS-16-2 | Wind | 310 |  | WERE | Reno-(GEN-2016-112 Tap) Summit 345kV | FACILITY STUDY STAGE
GEN-2016-125 | VWCO81 | South | 06 - South Texas Panhandle/New Mexico | DIS-16-2 | Wind | 74 |  | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-123 | VWCO81 | South | 06 - South Texas Panhandle/New Mexico | DIS-16-2 | Wind | 150 |  | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-124 | VWCO81 | South | 06 - South Texas Panhandle/New Mexico | DIS-16-2 | Wind | 150 |  | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-123 | VWCO81 | South | 06 - South Texas Panhandle/New Mexico | DIS-16-2 | Wind | 148 |  | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-095 | VWCO81 | South | 07 - Southwestern Oklahoma | DIS-16-2 | Wind | 200 |  | AEPW | Gracemont-Lawton East Side 345kV | FACILITY STUDY STAGE
GEN-2016-097 | VWCO81 | South | 07 - Southwestern Oklahoma | DIS-16-2 | Wind | 100 |  | AEPW | Tap Southwestern-Fletcher Tap 138kV | FACILITY STUDY STAGE
GEN-2016-153 | VWCO81 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-2 | Wind | 134 |  | WERE | Viola 345kV | FACILITY STUDY STAGE
GEN-2005-012 | WT4E2 | Central | 03 - Spearville | PQ | Wind | 248.4 |  | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-013 | VWCOR4 | Central | 08 - North Oklahoma/South Central Kansas | PQ | Wind | 300.6 |  | WERE | Caney River 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-115 | VWCO81 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-16-2 | Wind | 300 |  | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-118 | VWCO81 | Central | 01 - Woodward | DIS-16-2 | Wind | 288 |  | WFEC | Dover Switchyard 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-074 | VWCO81 | North | 09 - Nebraska | DIS-16-2 | Wind | 200 |  | NPPD | Sweetwater 345kV | FACILITY STUDY STAGE
GEN-2016-106 | VWCO81 | North | 09 - Nebraska | DIS-16-2 | Wind | 400 |  | NPPD | Gerald Gentleman Station 345kV | FACILITY STUDY STAGE
GEN-2016-036 | GEWTG2 | North | 15 - Eastern South Dakota | DIS-16-2 | Wind | 44.6 |  | WAPA | Granite Falls 115kV | FACILITY STUDY STAGE
GEN-2016-087 | GEWTG2 | North | 15 - Eastern South Dakota | DIS-16-2 | Wind | 98.9 |  | WAPA | Bismark-Glenham 230kV line | FACILITY STUDY STAGE
GEN-2016-092 | GEWTG2 | North | 15 - Eastern South Dakota | DIS-16-2 | Wind | 175 |  | WAPA | Fort Thompson-Leland Olds 345kV | FACILITY STUDY STAGE
GEN-2016-130 | GEWTG2 | North | 16 - Western North Dakota | DIS-16-2 | Wind | 202 |  | WAPA | Leland Olds 345kV | FACILITY STUDY STAGE
GEN-2016-151 | WT3G2 | North | 16 - Western North Dakota | DIS-16-2 | Wind | 202 |  | BEPC-SPP | Tande 345kV | IA PENDING
GEN-2016-094 | GEWTG2 | North | 17 - Western South Dakota | DIS-16-2 | Wind | 200 |  | WAPA | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | FACILITY STUDY STAGE
ASGI-2016-011 | GENSAL | South | 14 - South Central Oklahoma | DIS-16-2-PQ | Thermal | 7.4 |  | SWPA | Allen 138kV
ASGI-2016-012 | GENSAL | South | 14 - South Central Oklahoma | DIS-16-2-PQ | Thermal | 32.1 |  | SWPA | Tupelo 138kV
ASGI-2016-012 | GENSAL | South | 14 - South Central Oklahoma | DIS-16-2-PQ | Thermal | 29.63 |  | SWPA | Tupelo 138kV
ASGI-2016-013 | GENSAL | South | 14 - South Central Oklahoma | DIS-16-2-PQ | Thermal | 2.46 |  | WFEC | Ashland 138kV
ASGI-2016-013 | GENSAL | South | 14 - South Central Oklahoma | DIS-16-2-PQ | Thermal | 2.46 |  | WFEC | Ashland 138kV
J541 | REGCAU1 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-16-2-PQ | Wind | 400 |  | AMMO | Zachary-Ottumwa 345kV line
J476 | REGCAU1 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-16-2-PQ | Wind | 246 |  | AMMO | Atchison County to Booneville 345kV Line Tap
J611 | REGCAU1 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-16-2-PQ | Wind | 110 |  | MEC | Clarinda - Merryville 161kV tap
J583 | REGCAU1 | North | 09 - Nebraska | DIS-16-2-PQ | Wind | 200 |  | MEC | Fallow Avenue 345kV . Zip Code 50002
J555 | VWCOR6 | North | 09 - Nebraska | DIS-16-2-PQ | Wind | 140 |  | MEC
J512 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-16-2-PQ | Wind | 20 |  | MP | Nobles - Fenton 115kV line
J512 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-16-2-PQ | Wind | 230 |  | MP | Nobles - Fenton 115kV line
J569 | SWTGU2 | North | 15 - Eastern South Dakota | DIS-16-2-PQ | Wind | 100 |  | XEL | NSP Rock County
J587 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-16-2-PQ | Wind | 100 |  | XEL | J460 on the Brookings-H081 345kV line
J587 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-16-2-PQ | Wind | 100 |  | XEL | J460 on the Brookings-H081 345kV line
J590 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-16-2-PQ | Wind | 45 |  | MEC | Obrien - Kossuth 345kV line
J590 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-16-2-PQ | Wind | 45 |  | MEC | Obrien - Kossuth 345kV line
ASGI-2016-004 | ECODFG | South | 06 - South Texas Panhandle/New Mexico | DIS-16-1 | Wind | 0.4 |  | SPS | Palo Duro 115kV
GEN-2015-041 | GENROE | South | 06 - South Texas Panhandle/New Mexico | DIS-16-1 | CT | 196 |  | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-013 | VWCOR4 | Central | 08 - North Oklahoma/South Central Kansas | PQ | Wind | 300.6 |  | WERE | Caney River 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-021 | VWCOR6 | Central | 03 - Spearville | PQ | Wind | 94 |  | SUNC | Flat Ridge Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-021 | WT4G1 | Central | 03 - Spearville | PQ | Wind | 94 |  | SUNC | Flat Ridge Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-025 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | ICS1 | Wind | 598.4 |  | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-025 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | ICS1 | Wind | 598.4 |  | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-025 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | ICS1 | Wind | 598.4 |  | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-025 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | ICS1 | Wind | 598.4 |  | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-013 | GENROU | Central | 12 - Northwest Arkansas | DIS-16-1 | CT | 60 |  | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-014 | GENROU | Central | 12 - Northwest Arkansas | DIS-16-1 | CT | 60 |  | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2007-044 | GEWTG2 | Central | 01 - Woodward | ICS1 | Wind | 299.2 |  | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-044 | GEWTG2 | Central | 01 - Woodward | ICS1 | Wind | 299.2 |  | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-003 | GENSAL | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-16-1 | Diesel | 12 |  | KCPL | Paola 161kV
GEN-2016-030 | GEPVG | South | 14 - South Central Oklahoma | DIS-16-1 | Solar | 100 |  | OKGE | Brown 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-082 | GEWTG2 | South | 02 - Hitchland | DIS-16-1 | Wind | 200 |  | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-002 | GEWTG2 | South | 06 - South Texas Panhandle/New Mexico | DIS-16-1 | Wind | 2.65 |  | SPS | SP-Yuma 115kV | WITHDRAWN
GEN-2015-036 | GEWTG2 | South | 14 - South Central Oklahoma | DIS-16-1 | Wind | 151.8 |  | OKGE | Johnston County 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-036 | GEWTG2 | South | 14 - South Central Oklahoma | DIS-16-1 | Wind | 137.5 |  | OKGE | Johnston County 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-036 | GEWTG2 | South | 14 - South Central Oklahoma | DIS-16-1 | Wind | 23 |  | OKGE | Johnston County 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2007-062 | GEWTG2 | Central | 01 - Woodward | ICS1 | Wind | 423.6 |  | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-062 | GEWTG2 | Central | 01 - Woodward | ICS1 | Wind | 423.6 |  | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-062 | GSCORE | Central | 01 - Woodward | ICS1 | Wind | 423.6 |  | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-062 | GSCORE | Central | 01 - Woodward | ICS1 | Wind | 423.6 |  | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-073 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-1 | WIND | 220 |  | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA PENDING
GEN-2016-061 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-1 | Wind | 248.16 |  | OKGE | Sooner-Woodring 345kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2007-062 | VWCOR6 | Central | 01 - Woodward | ICS1 | Wind | 423.6 |  | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-062 | VWCOR6 | Central | 01 - Woodward | ICS1 | Wind | 423.6 |  | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-016 | GEWTG2 | Central | 03 - Spearville | DIS-16-1 | Wind | 78.2 |  | MIDW | North Kinsley 115kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-046 | GEWTG2 | Central | 03 - Spearville | DIS-16-1 | Wind | 299 |  | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-089 | GEWTG2 | North | 09 - Nebraska | DIS-16-1 | Wind | 7.5 |  | WAPA | Utica 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-089 | GEWTG2 | North | 09 - Nebraska | DIS-16-1 | Wind | 192.5 |  | WAPA | Utica 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | GEWTG2 | North | 09 - Nebraska | DIS-16-1 | Wind | 250.7 |  | NPPD | Axtell - Post Rock 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-028 | GSCOR1 | South | 14 - South Central Oklahoma | DIS-16-1 | Wind | 100 |  | AEPW | Clayton 138kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-022 | GSCOR1 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-1 | Wind | 151.8 |  | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA PENDING
GEN-2016-031 | GSCOR1 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-1 | Wind | 202.8 |  | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-003 | GSCOR1 | Central | 01 - Woodward | DIS-16-1 | Wind | 248.4 |  | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | DISIS STAGE
GEN-2016-043 | GSCOR1 | North | 09 - Nebraska | DIS-16-1 | Wind | 230 |  | NPPD | Turtle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-013 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | ICS1 | Wind | 300 |  | OKGE | Hunter 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-013 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | ICS1 | Wind | 300 |  | OKGE | Hunter 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-013 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | ICS1 | Wind | 300 |  | OKGE | Hunter 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-013 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | ICS1 | Wind | 300 |  | OKGE | Hunter 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-044 | SWTGU2 | Central | 01 - Woodward | DIS-10-1 | Wind | 227.5 |  | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-044 | SWTGU2 | Central | 01 - Woodward | DIS-10-1 | Wind | 227.5 |  | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-067 | SWTGU1 | North | 04 - Northwest Kansas | DIS-16-1 | Wind | 73.6 |  | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-063 | VWCOR6 | South | 14 - South Central Oklahoma | DIS-16-1 | Wind | 100 |  | OKGE | Hugo-Sunnyside 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-063 | VWCOR6 | South | 14 - South Central Oklahoma | DIS-16-1 | Wind | 100 |  | OKGE | Hugo-Sunnyside 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-032 | VWCOR6 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-1 | Wind | 200 |  | OKGE | Crescent 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-095 | VWCOR6 | Central | 01 - Woodward | DIS-16-1 | Wind | 176 |  | WFEC | Tap Mooreland - Knob Hill 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-021 | VWCOR6 | North | 09 - Nebraska | DIS-16-1 | Wind | 300 |  | NPPD | Turtle Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-075 | VWCOR6 | North | 09 - Nebraska | DIS-16-1 | Wind | 50 |  | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA PENDING
ASGI-2016-004 | WT1G1 | South | 06 - South Texas Panhandle/New Mexico | DIS-16-1 | Wind | 9.6 |  | SPS | Palo Duro 115kV
GEN-2016-017 | GEWTG2 | North | 15 - Eastern South Dakota | DIS-16-1 | Wind | 250.24 |  | WAPA | Fort Thompson-Leland Olds 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-004 | VWCOR6 | North | 16 - Western North Dakota | DIS-16-1 | Wind | 202 |  | WAPA | Basin Electric 230kV | IA FULLY EXECUTED/ON SCHEDULE
J475 | REGCAU1 | North | 09 - Nebraska | DIS-16-1-PQ | Wind | 168 |  | MEC
J475 | REGCAU1 | North | 09 - Nebraska | DIS-16-1-PQ | Wind | 32 |  | MEC
J495 | REGCAU1 | North | 09 - Nebraska | DIS-16-1-PQ | Wind | 100 |  | ALTW | Ledyard-Colby 345kV line
J495 | REGCAU1 | North | 09 - Nebraska | DIS-16-1-PQ | Wind | 100 |  | ALTW | Ledyard-Colby 345kV line
J506 | REGCAU1 | North | 09 - Nebraska | DIS-16-1-PQ | Wind | 99.1 |  | MEC | Raun-Lakefield Jct 345kV line tap (T-19N, R-43W)
J506 | REGCAU1 | North | 09 - Nebraska | DIS-16-1-PQ | Wind | 100.9 |  | MEC | Raun-Lakefield Jct 345kV line tap (T-19N, R-43W)
J524 | REGCAU1 | North | 09 - Nebraska | DIS-16-1-PQ | Solar | 100 |  | MEC | Webster 161kV bus
J527 | REGCAU1 | North | 09 - Nebraska | DIS-16-1-PQ | Wind | 125 |  | MEC | Booneville Cooper 345kV line
J527 | REGCAU1 | North | 09 - Nebraska | DIS-16-1-PQ | Wind | 125 |  | MEC | Booneville Cooper 345kV line
J530 | REGCAU1 | North | 09 - Nebraska | DIS-16-1-PQ | Wind | 125 |  | MEC | Montezuma - Hills 345kV Line
J530 | REGCAU1 | North | 09 - Nebraska | DIS-16-1-PQ | Wind | 125 |  | MEC | Montezuma - Hills 345kV Line
J534 | REGCAU1 | North | 09 - Nebraska | DIS-16-1-PQ | Wind | 125 |  | ALTW | Kossuth - Webster 345kV Line
J534 | REGCAU1 | North | 09 - Nebraska | DIS-16-1-PQ | Wind | 125 |  | ALTW | Kossuth - Webster 345kV Line
J535 | REGCAU1 | North | 09 - Nebraska | DIS-16-1-PQ | Wind | 210 |  | ALTW | J411 - Lehigh 345kV Line
J498 | WT3G2 | North | 09 - Nebraska | DIS-16-1-PQ | Wind | 170 |  | MEC | MEC 345kV Grimes-Lehigh line (18 miles south of Leigh )
J498 | WT3G2 | North | 09 - Nebraska | DIS-16-1-PQ | Wind | 170 |  | MEC | MEC 345kV Grimes-Lehigh line (18 miles south of Leigh )
J499 | WT3G2 | North | 09 - Nebraska | DIS-16-1-PQ | Wind | 170 |  | MEC | MEC 345kV Fallow-Grimes line (18 miles east of Fallow )
J499 | WT3G2 | North | 09 - Nebraska | DIS-16-1-PQ | Wind | 170 |  | MEC | MEC 345kV Fallow-Grimes line (18 miles east of Fallow )
J500 | WT3G2 | North | 09 - Nebraska | DIS-16-1-PQ | Wind | 168 |  | MEC | New at intersection of MEC 345kV Boone-Atchison and MEC 345kV Rolling Hills-Madison County
J500 | WT3G2 | North | 09 - Nebraska | DIS-16-1-PQ | Wind | 166 |  | MEC | New at intersection of MEC 345kV Boone-Atchison and MEC 345kV Rolling Hills-Madison County
J500 | WT3G2 | North | 09 - Nebraska | DIS-16-1-PQ | Wind | 166 |  | MEC | New at intersection of MEC 345kV Boone-Atchison and MEC 345kV Rolling Hills-Madison County
J432 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-16-1-PQ | Wind | 98 |  | XEL | Brookings 345kV
J460 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-16-1-PQ | Wind | 100 |  | XEL | on Brookings - H081 345kV line approx. 10 miles west of proposed
J460 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-16-1-PQ | Wind | 100 |  | XEL | on Brookings - H081 345kV line approx. 10 miles west of proposed
J488 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-16-1-PQ | Wind | 151.8 |  | OTP | 345kV at new Tap on proposed MVP Big Stone to Ellendale line
J493 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-16-1-PQ | Wind | 150 |  | OTP | Big Stone - Brookings 345kV
J510 | GENTPJU1 | North | 15 - Eastern South Dakota | DIS-16-1-PQ | Gas | 284.5 |  | OTP | Scandinavia Township 113N, Range 48W
J526 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-16-1-PQ | Wind | 150 |  | OTP | Brooking County to Big Stone South 345kV line
J526 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-16-1-PQ | Wind | 150 |  | OTP | Brooking County to Big Stone South 345kV line
J529 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-16-1-PQ | Wind | 125 |  | MEC | Obrien - Kossuth 345kV line
J529 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-16-1-PQ | Wind | 125 |  | MEC | Obrien - Kossuth 345kV line
GEN-2008-098 | GXX048 | Central | 08 - North Oklahoma/South Central Kansas | DIS-10-1 | Wind | 100.3 |  | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-098 | GXX048 | Central | 08 - North Oklahoma/South Central Kansas | DIS-10-1 | Wind | 100.3 |  | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-069 | A1530U1 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-2 | Wind | 299.25 |  | WERE | Union Ridge 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-055 | AEINX | South | 07 - Southwestern Oklahoma | DIS-15-2 | Solar | 40 |  | WFEC | Erick 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-092 | GEWTG2 | South | 14 - South Central Oklahoma | DIS-15-2 | Wind | 140 |  | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-092 | GEWTG2 | South | 14 - South Central Oklahoma | DIS-15-2 | Wind | 110 |  | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-124 | SWTGU1 | Central | 03 - Spearville | DIS-09-1 | Wind | 200.1 |  | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-124 | SWTGU1 | Central | 03 - Spearville | DIS-09-1 | Wind | 200.1 |  | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-129 | GENTPJU1 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-09-1 | CT | 675 |  | KCPL | Pleasant Hill 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-062 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-2 | Wind | 107.06 |  | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-129 | GENTPJU1 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-09-1 | CT | 675 |  | KCPL | Pleasant Hill 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-066 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-2 | Wind | 248.4 |  | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-048 | GEWTG2 | Central | 01 - Woodward | DIS-15-2 | Wind | 199.4 |  | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-129 | GENTPJU1 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-09-1 | CT | 675 |  | KCPL | Pleasant Hill 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-005 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-10-1 | Wind | 598.4 |  | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-005 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-10-1 | Wind | 598.4 |  | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-005 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-10-1 | Wind | 598.4 |  | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-005 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-10-1 | Wind | 598.4 |  | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-073 | GMD0352 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-2 | Wind | 166.32 |  | WERE | Emporia 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-034 | GSCOR1 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-2 | Wind | 200 |  | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-045 | PVGU1 | South | 14 - South Central Oklahoma | DIS-15-2 | Battery | 20 |  | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-005 | VWCOR6 | Central | 08 - North Oklahoma/South Central Kansas | DIS-10-1 | Wind | 598.4 |  | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-064 | SWTGU2 | North | 04 - Northwest Kansas | DIS-15-2 | Wind | 197.8 |  | SUNC | Mingo 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-065 | SWTGU2 | North | 04 - Northwest Kansas | DIS-15-2 | Wind | 202.4 |  | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-052 | VWCOR6 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-2 | Wind | 300 |  | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-088 | VWCOR6 | North | 09 - Nebraska | DIS-15-2 | Wind | 300 |  | NPPD | Moore-Pauline 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-046 | REGCAU1 | North | 16 - Western North Dakota | DIS-15-2 | Wind | 300 |  | WAPA | Tande 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-096 | GEWTG2 | North | 16 - Western North Dakota | DIS-15-2 | Wind | 150 |  | BEPC-SPP | Brady 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
J412 | GEWTG2 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 100 |  | MEC | LeHigh - Raun 345kV line
J412 | GEWTG2 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 100 |  | MEC | LeHigh - Raun 345kV line
GEN-2002-009IS | GEWTG2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 40.5 |  | BEPC-SPP | Ft Thompson 69kV [Hyde 69kV] | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-013IS | GEWTG2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 50 |  | BEPC-SPP | Wessington Springs 230kV
GEN-2007-014IS | GEWTG2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 100 |  | BEPC-SPP | Wessington Springs 230kV
GEN-2009-001IS | GEWTG2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 100 |  | BEPC-SPP | Groton-Watertown 345kV
J455 | REGCAU1 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 29.9 |  | ALTW | Kossuth - Obrien 345kV line
J455 | REGCAU1 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 2.6 |  | ALTW | Kossuth - Obrien 345kV line
J455 | REGCAU1 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 117.5 |  | ALTW | Kossuth - Obrien 345kV line
J455 | REGCAU1 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 2.6 |  | ALTW | Kossuth - Obrien 345kV line
J455 | REGCAU1 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 29.9 |  | ALTW | Kossuth - Obrien 345kV line
J455 | REGCAU1 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 117.5 |  | ALTW | Kossuth - Obrien 345kV line
GEN-2009-001IS | GEWTG2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 100 |  | BEPC-SPP | Groton-Watertown 345kV
GEN-2009-018IS | GENROE | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 99.5 |  | BEPC-SPP | Groton 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-018IS | GENROE | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 0.5 |  | BEPC-SPP | Groton 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-001IS | GEWTG2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 99 |  | BEPC-SPP | Bismarck-Glenham 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-003IS | GEWTG2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 34 |  | BEPC-SPP | Wessington Springs 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-009IS | GEWTG2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 19.5 |  | WAPA | Redfield NW 115kV
GEN-2014-001IS | GEWTG2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 103.24 |  | WAPA | Sulphur 115kV | IA FULLY EXECUTED/ON SCHEDULE
J436 | VWCOR6 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 150 |  | OTP | Big Stone South - Ellendale 345kV line
J437 | VWCOR6 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 150 |  | OTP | Big Stone South - Ellendale 345kV line
J442 | GEWTG2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 200 |  | OTP | Big Stone via a radial 230kV line
GEN-2005-008IS | GEWTG2 | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 49.5 |  | BEPC-SPP | Hilken 230kV [Ecklund 230kV] | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-008IS | GEWTG2 | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 0.5 |  | BEPC-SPP | Hilken 230kV [Ecklund 230kV] | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-015IS | GEWTG2 | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 0.5 |  | BEPC-SPP | Hilken 230kV [Ecklund 230kV] | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-015IS | GEWTG2 | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 49.5 |  | BEPC-SPP | Hilken 230kV [Ecklund 230kV] | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-015IS | GEWTG2 | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 100 |  | BEPC-SPP | Hilken 230kV [Ecklund 230kV]
GEN-2009-026IS | VWCOR6 | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 106.5 |  | BEPC-SPP | Dickenson-Heskett 230kV
GEN-2009-026IS | VWCOR6 | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 3.5 |  | BEPC-SPP | Dickenson-Heskett 230kV
GEN-2014-006IS | GENSAE | North | 16 - Western North Dakota | DIS-15-2-PQ | Gas | 9.44 |  | BEPC-SPP | Williston 115kV
GEN-2014-006IS | GENSAE | North | 16 - Western North Dakota | DIS-15-2-PQ | Gas | 9.44 |  | BEPC-SPP | Williston 115kV
GEN-2014-006IS | GENSAE | North | 16 - Western North Dakota | DIS-15-2-PQ | Gas | 9.44 |  | BEPC-SPP | Williston 115kV
GEN-2014-006IS | GENSAE | North | 16 - Western North Dakota | DIS-15-2-PQ | Gas | 9.44 |  | BEPC-SPP | Williston 115kV
GEN-2014-006IS | GENSAE | North | 16 - Western North Dakota | DIS-15-2-PQ | Gas | 9.44 |  | BEPC-SPP | Williston 115kV
GEN-2014-006IS | GENSAE | North | 16 - Western North Dakota | DIS-15-2-PQ | Gas | 5.86 |  | BEPC-SPP | Williston 115kV
GEN-2014-006IS | GENSAE | North | 16 - Western North Dakota | DIS-15-2-PQ | Gas | 9.44 |  | BEPC-SPP | Williston 115kV
GEN-2014-006IS | GENSAE | North | 16 - Western North Dakota | DIS-15-2-PQ | Gas | 9.44 |  | BEPC-SPP | Williston 115kV
GEN-2014-006IS | GENSAE | North | 16 - Western North Dakota | DIS-15-2-PQ | Gas | 9.44 |  | BEPC-SPP | Williston 115kV
GEN-2014-006IS | GENSAE | North | 16 - Western North Dakota | DIS-15-2-PQ | Gas | 9.44 |  | BEPC-SPP | Williston 115kV
GEN-2014-006IS | GENSAE | North | 16 - Western North Dakota | DIS-15-2-PQ | Gas | 9.44 |  | BEPC-SPP | Williston 115kV
GEN-2014-006IS | GENSAE | North | 16 - Western North Dakota | DIS-15-2-PQ | Gas | 9.44 |  | BEPC-SPP | Williston 115kV
GEN-2014-006IS | GENSAE | North | 16 - Western North Dakota | DIS-15-2-PQ | Gas | 5.86 |  | BEPC-SPP | Williston 115kV
GEN-2014-006IS | GENSAE | North | 16 - Western North Dakota | DIS-15-2-PQ | Gas | 9.44 |  | BEPC-SPP | Williston 115kV
GEN-2014-010IS | VWCOR6 | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 150 |  | BEPC-SPP | Neset 115kV
GEN-2014-014IS | GEWTG2 | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 150 |  | BEPC-SPP | Belfield-Rhame 230kV
MPC01300 | GENROU | North | 16 - Western North Dakota | DIS-15-2-PQ | Coal | 493 |  | OTP | Square Butte 230kV
MPC02100 | GEWTG2 | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 8.95 |  | OTP | Center - Mandan 230kV
MPC02100 | GEWTG2 | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 90.3 |  | OTP | Center - Mandan 230kV
MPC02100 | GEWTG2 | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 0.75 |  | OTP | Center - Mandan 230kV
GEN-2006-002IS | GEWTG2 | North | 17 - Western South Dakota | DIS-15-2-PQ | Wind | 51 |  | WAPA | Wessington Springs 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002IS | GEWTG2 | North | 17 - Western South Dakota | DIS-15-2-PQ | Wind | 2 |  | WAPA | Wessington Springs 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-020AIS | GEWTG2 | North | 17 - Western South Dakota | DIS-15-2-PQ | Wind | 79.6 |  | WAPA | Tripp Junction 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-020AIS | GEWTG2 | North | 17 - Western South Dakota | DIS-15-2-PQ | Wind | 0.4 |  | WAPA | Tripp Junction 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-011 | SWTGU2 | Central | 01 - Woodward | DIS-10-1 | Wind | 227.5 |  | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-011 | SWTGU2 | Central | 01 - Woodward | DIS-10-1 | Wind | 227.5 |  | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036 | None | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-10-2 | Hydro | 5.9 |  | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2015-001 | GENSAL | Central | 03 - Spearville | DIS-15-1 | Thermal | 6.132 |  | SUNC | Ninnescah 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-021 | GEPVG_LV5 | Central | 03 - Spearville | DIS-15-1 | Solar | 20 |  | SUNC | Johnson Corner 115kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2015-002 | GEWTG2 | South | 06 - South Texas Panhandle/New Mexico | DIS-15-1 | Wind | 2 |  | SPS | SP-Yuma 69kV
GEN-2015-014 | GEWTG2 | South | 06 - South Texas Panhandle/New Mexico | DIS-15-1 | Wind | 10.29 |  | SPS | Tap Cochran - Lehman 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-014 | GEWTG2 | South | 06 - South Texas Panhandle/New Mexico | DIS-15-1 | Wind | 4 |  | SPS | Tap Cochran - Lehman 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-014 | GEWTG2 | South | 06 - South Texas Panhandle/New Mexico | DIS-15-1 | Wind | 135.7 |  | SPS | Tap Cochran - Lehman 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-024 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-1 | Wind | 217.8 |  | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036 | None | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-10-2 | Hydro | 5.9 |  | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036 | None | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-10-2 | Hydro | 5.9 |  | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036 | None | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-10-2 | Hydro | 5.9 |  | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036 | None | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-10-2 | Hydro | 5.9 |  | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036 | None | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-10-2 | Hydro | 5.9 |  | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036 | None | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-10-2 | Hydro | 5.9 |  | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-007 | GEWTG2 | North | 09 - Nebraska | DIS-15-1 | Wind | 160 |  | NPPD | Turtle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-023 | GEWTG2 | North | 09 - Nebraska | DIS-15-1 | Wind | 150.36 |  | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-023 | GEWTG2 | North | 09 - Nebraska | DIS-15-1 | Wind | 150.36 |  | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-036 | None | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-10-2 | Hydro | 5.9 |  | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036 | None | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-10-2 | Hydro | 5.9 |  | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-001 | GSCOR1 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-1 | Wind | 202.8 |  | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | SMAXINV | South | 07 - Southwestern Oklahoma | DIS-15-1 | Solar | 120 |  | WFEC | Snyder 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2010-036 | None | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-10-2 | Hydro | 5.9 |  | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036 | None | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-10-2 | Hydro | 5.9 |  | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
J411 | GEWTG2 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 150 |  | MEC | LeHigh - Raun 345kV Line
J411 | GEWTG2 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 25 |  | MEC | LeHigh - Raun 345kV Line
J411 | GEWTG2 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 125 |  | MEC | LeHigh - Raun 345kV Line
G736 | GEWTG2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 200 |  | OTP | Big Stone South 230kV
GEN-2007-017IS | VS17074901 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 100 |  | OPPD | Ft Thompson-Grand Island 345kV
GEN-2007-017IS | VS17074901 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 66 |  | OPPD | Ft Thompson-Grand Island 345kV
GEN-2007-018IS | VS17074901 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 34 |  | OPPD | Ft Thompson-Grand Island 345kV
GEN-2007-018IS | VS17074901 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 100 |  | OPPD | Ft Thompson-Grand Island 345kV
GEN-2007-018IS | VS17074901 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 100 |  | OPPD | Ft Thompson-Grand Island 345kV
J299 | GENROU | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Combined Cycle | 36.5 |  | XEL | Wilmarth
J299 | GENROU | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Combined Cycle | 36.5 |  | XEL | Wilmarth
J385 | PVGU1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Solar | 100 |  | XEL | Chisago 115kV
J400 | PVGU1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Solar | 62 |  | XEL | Lyon County 115kV
J400 | PVGU1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Solar | 0.5 |  | XEL | Lyon County 115kV
J407 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 100 |  | XEL | Glenworth 161kV
J407 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 100 |  | XEL | Glenworth 161kV
J426 | VWCOR6 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 100 |  | XEL | Chanarambie 35.4kV
J405 | GENSAE | North | 16 - Western North Dakota | DIS-15-2-PQ | Gas | 10.4 |  | MDU | MDUs existing Lewis & Clark Jct
J405 | GENSAE | North | 16 - Western North Dakota | DIS-15-2-PQ | Gas | 9.6 |  | MDU | MDUs existing Lewis & Clark Jct
J405 | GENSAE | North | 16 - Western North Dakota | DIS-15-2-PQ | Gas | 9.6 |  | MDU | MDUs existing Lewis & Clark Jct
J405 | GENSAE | North | 16 - Western North Dakota | DIS-15-2-PQ | Gas | 10.4 |  | MDU | MDUs existing Lewis & Clark Jct
GEN-2010-040 | M24G1 | Central | 01 - Woodward | DIS-10-2 | Wind | 298.45 |  | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-040 | WT3G2 | Central | 01 - Woodward | DIS-10-2 | Wind | 298.45 |  | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-008 | VWCOR6 | Central | 03 - Spearville | DIS-11-1 | Wind | 600 |  | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-008 | VWCOR6 | Central | 03 - Spearville | DIS-11-1 | Wind | 600 |  | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-008 | VWCOR6 | Central | 03 - Spearville | DIS-11-1 | Wind | 600 |  | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | VWCOR6 | Central | 01 - Woodward | DIS-11-1 | Wind | 174 |  | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2014-014 | GENSAL | Central | 08 - North Oklahoma/South Central Kansas | DIS-14-2 | Thermal | 54.3 |  | GRDA | Ferguson 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-033 | GEPVG_LV5 | South | 06 - South Texas Panhandle/New Mexico | DIS-14-2 | Solar | 66.8 |  | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-035 | GEPVG_LV5 | South | 06 - South Texas Panhandle/New Mexico | DIS-14-2 | Solar | 30 |  | SPS | Chaves County 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-040 | GEWTG2 | South | 06 - South Texas Panhandle/New Mexico | DIS-14-2 | Wind | 167.9 |  | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-040 | GEWTG2 | South | 06 - South Texas Panhandle/New Mexico | DIS-14-2 | Wind | 151.8 |  | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-057 | GEWTG2 | South | 14 - South Central Oklahoma | DIS-14-2 | Wind | 249.9 |  | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-064 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-14-2 | Wind | 248.4 |  | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | VWCOR6 | Central | 01 - Woodward | DIS-11-1 | Wind | 174 |  | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | GEWTG2 | Central | 01 - Woodward | DIS-11-1 | Wind | 165.6 |  | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | GEWTG2 | Central | 01 - Woodward | DIS-11-1 | Wind | 165.6 |  | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-031 | GEWTG2 | North | 09 - Nebraska | DIS-14-2 | Wind | 35.8 |  | GRIS | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | GEWTG2 | North | 09 - Nebraska | DIS-14-2 | Wind | 5.11 |  | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | GEWTG2 | North | 09 - Nebraska | DIS-14-2 | Wind | 5.11 |  | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-027 | GSCOR1 | South | 06 - South Texas Panhandle/New Mexico | DIS-14-2 | Wind | 148.35 |  | SPS | Tolk - Yoakum 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-034 | REGCAU1 | South | 06 - South Texas Panhandle/New Mexico | DIS-14-2 | Solar | 70 |  | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-039 | REGCAU1 | North | 09 - Nebraska | DIS-14-2 | Wind | 73.4 |  | NPPD | Friend 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-025 | SWTGU2 | North | 04 - Northwest Kansas | DIS-14-2 | Wind | 2.42 |  | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-054 | VWCOR6 | Central | 01 - Woodward | DIS-11-2 | Wind | 300 |  | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-054 | VWCOR6 | Central | 01 - Woodward | DIS-11-2 | Wind | 300 |  | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-033 | XCPVIN | South | 06 - South Texas Panhandle/New Mexico | DIS-14-2 | Solar | 3.2 |  | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
J285 | WT4G1 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 125 |  | MEC | Proposed O'Brien County 345kV
J285 | WT4G1 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 125 |  | MEC | Proposed O'Brien County 345kV
J343 | WT4G1 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 150 |  | MEC | 161kV on Creston-Clarinda line
J316 | GEWTG2 | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 150 |  | MDU | MDU 230kV Tatanka-Ellendale line
GEN-2012-007 | GENTPJU1 | Central | 03 - Spearville | DIS-12-1 | Gas | 120 |  | SUNC | Rubart 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-007 | GENTPJU1 | Central | 03 - Spearville | DIS-12-1 | Gas | 120 |  | SUNC | Rubart 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | GEWTG2 | Central | 01 - Woodward | DIS-14-1 | Wind | 106.47 |  | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-002 | GEWTG2 | Central | 01 - Woodward | DIS-14-1 | Wind | 209.43 |  | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-004 | GEWTG2 | North | 09 - Nebraska | DIS-14-1 | Wind | 3.96 |  | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-013 | GEWTG2 | North | 09 - Nebraska | DIS-14-1 | Wind | 73.39 |  | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-013 | GEWTG2 | North | 09 - Nebraska | DIS-14-1 | Wind | 0.11 |  | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-032 | REGCAU1 | Central | 08 - North Oklahoma/South Central Kansas | DIS-12-2 | Wind | 299 |  | OKGE | Rose Hill-(Ranch Road) Sooner (Open Sky) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-032 | SWTGU2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-12-2 | Wind | 299 |  | OKGE | Rose Hill-(Ranch Road) Sooner (Open Sky) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-004 | GENSAL | North | 04 - Northwest Kansas | DIS-13-2 | Gas | 9.2 |  | SUNC | Garden City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-004 | GENSAL | North | 04 - Northwest Kansas | DIS-13-2 | Gas | 3 |  | SUNC | Garden City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-004 | GENSAL | North | 04 - Northwest Kansas | DIS-13-2 | Gas | 9.2 |  | SUNC | Garden City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-004 | GENSAL | North | 04 - Northwest Kansas | DIS-13-2 | Gas | 3 |  | SUNC | Garden City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-004 | GENSAL | North | 04 - Northwest Kansas | DIS-13-2 | Gas | 9.2 |  | SUNC | Garden City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-004 | GENSAL | North | 04 - Northwest Kansas | DIS-13-2 | Gas | 3 |  | SUNC | Garden City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-031 | GENSAL | North | 04 - Northwest Kansas | DIS-13-2 | Gas | 8.12 |  | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-031 | GENSAL | North | 04 - Northwest Kansas | DIS-13-2 | Gas | 8.27 |  | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-031 | GENSAL | North | 04 - Northwest Kansas | DIS-13-2 | Gas | 8.29 |  | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-031 | GENSAL | North | 04 - Northwest Kansas | DIS-13-2 | Gas | 8.31 |  | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-031 | GENSAL | North | 04 - Northwest Kansas | DIS-13-2 | Gas | 8.31 |  | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-031 | GENSAL | North | 04 - Northwest Kansas | DIS-13-2 | Gas | 8.35 |  | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-031 | GENSAL | North | 04 - Northwest Kansas | DIS-13-2 | Gas | 8.31 |  | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-031 | GENSAL | North | 04 - Northwest Kansas | DIS-13-2 | Gas | 1.15 |  | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-031 | GENSAL | North | 04 - Northwest Kansas | DIS-13-2 | Gas | 8.18 |  | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-031 | GENSAL | North | 04 - Northwest Kansas | DIS-13-2 | Gas | 8.31 |  | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-033 | GENSAL | North | 04 - Northwest Kansas | DIS-13-2 | Gas | 9.34 |  | MIDW | Goodman Energy Center 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-033 | GENSAL | North | 04 - Northwest Kansas | DIS-13-2 | Gas | 9.34 |  | MIDW | Goodman Energy Center 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-033 | GENSAL | North | 04 - Northwest Kansas | DIS-13-2 | Gas | 9.34 |  | MIDW | Goodman Energy Center 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-032 | GEWTG2 | North | 09 - Nebraska | DIS-13-2 | Wind | 202.5 |  | NPPD | Antelope 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-033 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-12-2 | Wind | 107.06 |  | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-033 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-12-2 | Wind | 107.06 |  | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-022 | SMASC139 | South | 06 - South Texas Panhandle/New Mexico | DIS-13-2 | Solar | 28.6 |  | SPS | Norton 115kV Switching Station | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-019 | SWTGU1 | North | 09 - Nebraska | DIS-13-2 | Wind | 73.6 |  | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2013-005 | WT1G1 | South | 06 - South Texas Panhandle/New Mexico | DIS-13-2 | Wind | 19.8 |  | SPS | Clovis Intg. 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
J279 | GENROU | North | 09 - Nebraska | DIS-15-2-PQ | Coal | 30 |  | MEC | Raun 345kV
J274 | WT4G1 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 100 |  | MEC | Winterset. - Creston 161kV
J289 | WT4G1 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 20 |  | MEC | 161kV substation on Winterset Junction to Creston 161kV Line
J278 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 100 |  | XEL | 161kV bus at the Pleasant Valley Station
J278 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 100 |  | XEL | 161kV bus at the Pleasant Valley Station
J290 | VWCOR6 | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 150 |  | XEL | 230kV Rugby to Glenboro
GEN-2013-016 | GENROE | South | 06 - South Texas Panhandle/New Mexico | DIS-13-1 | CT | 195.4 |  | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-012 | GENROU | Central | 08 - North Oklahoma/South Central Kansas | DIS-13-1 | Gas | 1254 |  | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-012 | GENROU | Central | 08 - North Oklahoma/South Central Kansas | DIS-13-1 | Gas | 1254 |  | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-012 | GENROU | Central | 08 - North Oklahoma/South Central Kansas | DIS-13-1 | Gas | 1254 |  | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-012 | GENROU | Central | 08 - North Oklahoma/South Central Kansas | DIS-13-1 | Gas | 1254 |  | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-012 | GENROU | Central | 08 - North Oklahoma/South Central Kansas | DIS-13-1 | Gas | 1254 |  | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-012 | GENROU | Central | 08 - North Oklahoma/South Central Kansas | DIS-13-1 | Gas | 1254 |  | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-012 | GENROU | Central | 08 - North Oklahoma/South Central Kansas | DIS-13-1 | Gas | 1254 |  | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-012 | GENROU | Central | 08 - North Oklahoma/South Central Kansas | DIS-13-1 | Gas | 1254 |  | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-010 | GENROU | Central | 12 - Northwest Arkansas | DIS-13-1 | Coal | 681 |  | AEPW | Turk 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-011 | GENROU | Central | 12 - Northwest Arkansas | DIS-13-1 | Coal | 681 |  | AEPW | Turk 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-008 | GEWTG2 | North | 09 - Nebraska | DIS-13-1 | Wind | 1.2 |  | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-002 | SWTGU1 | South | 06 - South Texas Panhandle/New Mexico | DIS-13-1 | Wind | 18.4 |  | SPS | FE Tucumcari 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-003 | SWTGU1 | South | 06 - South Texas Panhandle/New Mexico | DIS-13-1 | Wind | 18.4 |  | SPS | Clovis Intg. 115kV
GEN-2013-002 | SWTGU1 | North | 09 - Nebraska | DIS-13-1 | Wind | 50.6 |  | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2013-001 | SWTGU2 | South | 02 - Hitchland | DIS-13-1 | Wind | 11.5 |  | SPS | PanTex South 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-007 | VWCOR6 | South | 14 - South Central Oklahoma | DIS-13-1 | Wind | 100 |  | OKGE | Tap Prices Falls - Carter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
J262 | VWCOR6 | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 100 |  | OTP | OTP Jamestown 345/115kV
J263 | VWCOR6 | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 100 |  | OTP | OTP Jamestown 345/115kV
GEN-2012-037 | GENROE | South | 06 - South Texas Panhandle/New Mexico | DIS-12-2 | CT | 196 |  | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-041 | GENROE | Central | 08 - North Oklahoma/South Central Kansas | DIS-12-2 | CT | 103 |  | OMPA | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-034 | GENROU | South | 06 - South Texas Panhandle/New Mexico | DIS-12-2 | CT | 157 |  | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-035 | GENROU | South | 06 - South Texas Panhandle/New Mexico | DIS-12-2 | CT | 157 |  | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-036 | GENROU | South | 06 - South Texas Panhandle/New Mexico | DIS-12-2 | CT | 172 |  | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-021 | GENSAE | North | 09 - Nebraska | DIS-12-2 | Gas | 4.8 |  | LES | Terry Bundy Generating Station 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-028 | GENROU | Central | 08 - North Oklahoma/South Central Kansas | DIS-13-2 | Gas | 516.4 |  | GRDA | Tap N Tulsa - GRDA 1 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-028 | GENROU | Central | 08 - North Oklahoma/South Central Kansas | DIS-13-2 | Gas | 516.4 |  | GRDA | Tap N Tulsa - GRDA 1 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-024 | GSCORE | Central | 03 - Spearville | DIS-12-2 | Wind | 178.2 |  | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-029 | REGCAU1 | Central | 08 - North Oklahoma/South Central Kansas | DIS-13-2 | Wind | 299 |  | OKGE | Renfrow 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-029 | REGCAU1 | Central | 08 - North Oklahoma/South Central Kansas | DIS-13-2 | Wind | 299 |  | OKGE | Renfrow 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-020 | VC18084500 | South | 06 - South Texas Panhandle/New Mexico | DIS-12-2 | Wind | 48.72 |  | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-020 | VC18084500 | South | 06 - South Texas Panhandle/New Mexico | DIS-12-2 | Wind | 430.08 |  | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-028 | VWCOR6 | South | 07 - Southwestern Oklahoma | DIS-12-2 | Wind | 74 |  | WFEC | Gotebo 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-002 | WT1G1 | South | 06 - South Texas Panhandle/New Mexico | DIS-12-2 | Wind | 19.8 |  | SPS | FE-Clovis Interchange 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
J191 | WT4G1 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 101.2 |  | MEC | Rolling Hills 345kV
H081 | VWCOR6 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 201 |  | XEL | Brookings County - Lyon County 345kV
J183 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 100.8 |  | XEL | Split Rock
J183 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 0.1 |  | XEL | Split Rock
J183 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 99.1 |  | XEL | Split Rock
GEN-2014-001 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-14-1 | Wind | 199.5 |  | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-001 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-14-1 | Wind | 199.5 |  | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2012-006 | GNESAL | Central | 03 - Spearville | DIS-12-1 | Steam | 21.21 |  | SUNC | ABBK 2 69kV
GEN-2014-020 | GD0810 | Central | 01 - Woodward | DIS-14-2 | Wind | 99.1 |  | AEPW | Tuttle 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-020 | GD0810 | Central | 01 - Woodward | DIS-14-2 | Wind | 99.1 |  | AEPW | Tuttle 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-001 | WT4G2 | South | 06 - South Texas Panhandle/New Mexico | DIS-12-1 | Wind | 61.2 |  | SPS | Tap Grassland - Borden County 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
G870 | WT1G1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 100.5 |  | ALTW | Hayward - Winnebago 161kV
G870 | WT1G1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 100.5 |  | ALTW | Hayward - Winnebago 161kV
H096 | WT3G2 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 50 |  | ALTW | Grand Junction - Perry 161kV
G826 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 100 |  | XEL | Xcel Lakefield Generation SW - Lakefield Junction 345kV
G826 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 100 |  | XEL | Xcel Lakefield Generation SW - Lakefield Junction 345kV
G735 | WT4G1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 200 |  | ALTW | Lime Creek
G830 | VWCOR6 | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 99 |  | GRE | GRE McHenry
GEN-2011-045 | GENROU | South | 06 - South Texas Panhandle/New Mexico | DIS-11-2 | NG CT | 180 |  | SPS | Jones 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-046 | GENROU | South | 06 - South Texas Panhandle/New Mexico | DIS-11-2 | Diesel CT | 23 |  | SPS | Tucumcari 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-048 | GENROU | South | 06 - South Texas Panhandle/New Mexico | DIS-11-2 | CT | 172 |  | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056 | GENSAL | North | 09 - Nebraska | DIS-11-2 | Hydro | 3.6 |  | NPPD | Jeffrey 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056A | GENSAL | North | 09 - Nebraska | DIS-11-2 | Hydro | 3.6 |  | NPPD | John 1 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056APQ | GENSAL | North | 09 - Nebraska | DIS-11-2 | Hydro | 18 |  | NPPD | John 1 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056B | GENSAL | North | 09 - Nebraska | DIS-11-2 | Hydro | 4.5 |  | NPPD | John 2 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056BPQ | GENSAL | North | 09 - Nebraska | DIS-11-2 | Hydro | 18 |  | NPPD | John 2 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056PQ | GENSAL | North | 09 - Nebraska | DIS-11-2 | Hydro | 18 |  | NPPD | Jeffrey 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-040 | VWCOR6 | South | 14 - South Central Oklahoma | DIS-11-2 | Wind | 76 |  | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-040 | VWCOR6 | South | 14 - South Central Oklahoma | DIS-11-2 | Wind | 74 |  | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-050 | VWCOR6 | South | 14 - South Central Oklahoma | DIS-11-2 | Wind | 108 |  | AEPW | Tap Rush Springs - Marlow 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-057 | VWCOR6 | Central | 08 - North Oklahoma/South Central Kansas | DIS-11-2 | Wind | 150 |  | WERE | Creswell 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-021 | VWCOR6 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-14-2 | Wind | 300 |  | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-021 | VWCOR6 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-14-2 | Wind | 300 |  | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2011-004 | WT3G2 | South | 06 - South Texas Panhandle/New Mexico | DIS-11-2 | Wind | 9 |  | SPS | Pleasant Hill 69kV | Commercial Operation
ASGI-2011-004 | WT3G2 | South | 06 - South Texas Panhandle/New Mexico | DIS-11-2 | Wind | 10.8 |  | SPS | Pleasant Hill 69kV | Commercial Operation
GEN-2010-055 | GENROU | Central | 08 - North Oklahoma/South Central Kansas | DIS-11-1 | Gas | 4.8 |  | AEPW | Wekiwa 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2011-002 | GENSAL | South | 02 - Hitchland | DIS-11-1 | Wind | 10 |  | SPS | Herring 115kV | Commercial Operation
ASGI-2011-002 | GENSAL | South | 02 - Hitchland | DIS-11-1 | Wind | 10 |  | SPS | Herring 115kV | Commercial Operation
GEN-2004-008 | GENTPJU1 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-11-1 | Coal | 904.5 |  | KCPL | Iatan 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-011 | GENTPJU1 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-11-1 | Coal | 0 |  | KCPL | Iatan 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-025 | GEWTG2 | South | 06 - South Texas Panhandle/New Mexico | DIS-11-1 | Wind | 6.86 |  | SPS | Tap Floyd County - Crosby County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-025 | GEWTG2 | South | 06 - South Texas Panhandle/New Mexico | DIS-11-1 | Wind | 2 |  | SPS | Tap Floyd County - Crosby County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-025 | GEWTG2 | South | 06 - South Texas Panhandle/New Mexico | DIS-11-1 | Wind | 2.1 |  | SPS | Tap Floyd County - Crosby County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-025 | GEWTG2 | South | 06 - South Texas Panhandle/New Mexico | DIS-11-1 | Wind | 69 |  | SPS | Tap Floyd County - Crosby County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-010 | GEWTG2 | Central | 01 - Woodward | DIS-11-1 | Wind | 106.47 |  | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-028 | GENROE | Central | 08 - North Oklahoma/South Central Kansas | DIS-14-2 | CC | 0 |  | EMDE | Riverton 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-028 | GENROE | Central | 08 - North Oklahoma/South Central Kansas | DIS-14-2 | CC | 0 |  | EMDE | Riverton 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-057 | GEWTG2 | North | 04 - Northwest Kansas | DIS-11-1 | Wind | 201 |  | MIDW | Rice County 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-018 | GEWTG2 | North | 09 - Nebraska | DIS-11-1 | Wind | 73.6 |  | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-027 | GEWTG2 | North | 09 - Nebraska | DIS-11-1 | Wind | 120 |  | NPPD | Hoskins-Twin Church 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-014 | GSCORE | South | 02 - Hitchland | DIS-11-1 | Wind | 99 |  | OKGE | Beaver County-Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-014 | GSCORE | South | 02 - Hitchland | DIS-11-1 | Wind | 99 |  | OKGE | Beaver County-Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-022 | SWTGU2 | South | 02 - Hitchland | DIS-11-1 | Wind | 149.5 |  | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-022 | SWTGU2 | South | 02 - Hitchland | DIS-11-1 | Wind | 149.5 |  | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-056 | GEWTG2 | Central | 01 - Woodward | DIS-14-2 | Wind | 248.94 |  | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-056 | GEWTG2 | Central | 01 - Woodward | DIS-14-2 | Wind | 248.94 |  | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-056 | GEWTG2 | Central | 01 - Woodward | DIS-14-2 | Wind | 248.94 |  | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | GEWTG2 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-15-1 | Wind | 200.11 |  | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | GEWTG2 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-15-1 | Wind | 200.11 |  | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2011-003 | WT3G2 | South | 06 - South Texas Panhandle/New Mexico | DIS-11-1 | Wind | 10 |  | SPS | Hendricks 69kV | Commercial Operation
GEN-2010-001 | GEWTG2 | South | 02 - Hitchland | DIS-10-2 | Wind | 149.85 |  | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-001 | GEWTG2 | South | 02 - Hitchland | DIS-10-2 | Wind | 149.85 |  | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-020 | GEWTG2 | South | 06 - South Texas Panhandle/New Mexico | DIS-10-2 | Wind | 29.9 |  | SPS | Tap LE-Tatum - LE-Crossroads 69kV | Commercial Operation
GEN-2010-051 | GEWTG2 | North | 09 - Nebraska | DIS-10-2 | Wind | 200 |  | NPPD | Hoskins-Twin Church 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | GEWTG2 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-15-1 | Wind | 200.11 |  | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-015 | SWTGU2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-1 | Wind | 154.575 |  | OKGE | Tap Medford Tap - Coyote 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-015 | SWTGU2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-1 | Wind | 154.575 |  | OKGE | Tap Medford Tap - Coyote 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-016 | GMD0352 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-1 | Wind | 199.275 |  | KCPL | Tap Marmaton - Centerville 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-016 | GMD0352 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-1 | Wind | 199.275 |  | KCPL | Tap Marmaton - Centerville 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-1 | Wind | 215.95 |  | WERE | Tap Thistle - Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-1 | Wind | 215.95 |  | WERE | Tap Thistle - Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-1 | Wind | 215.95 |  | WERE | Tap Thistle - Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-047 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-2 | Wind | 297.8 |  | OKGE | Sooner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-047 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-2 | Wind | 297.8 |  | OKGE | Sooner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-047 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-2 | Wind | 297.8 |  | OKGE | Sooner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-057 | GEWTG2 | Central | 01 - Woodward | DIS-15-2 | Wind | 100.65 |  | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-021 | VWCOR6 | South | 06 - South Texas Panhandle/New Mexico | DIS-10-2 | Wind | 10 |  | SPS | Tap LE-Saunders Tap - LE-Anderson 69kV | Commercial Operation
ASGI-2010-021 | WT1G1 | South | 06 - South Texas Panhandle/New Mexico | DIS-10-2 | Wind | 4.95 |  | SPS | Tap LE-Saunders Tap - LE-Anderson 69kV | Commercial Operation
ASGI-2011-001 | WT3G2 | South | 06 - South Texas Panhandle/New Mexico | DIS-10-2 | Wind | 27.3 |  | SPS | Lovington 115kV | Commercial Operation
GEN-2015-057 | GEWTG2 | Central | 01 - Woodward | DIS-15-2 | Wind | 100.65 |  | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-006 | GENROU | South | 06 - South Texas Panhandle/New Mexico | DIS-10-1 | Gas | 180 |  | SPS | Jones 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-010 | GENSAL | South | 06 - South Texas Panhandle/New Mexico | DIS-10-1 | Gas | 42.196 |  | SPS | Lovington 115kV | Commercial Operation
GEN-2008-047 | GEWTG2 | South | 02 - Hitchland | DIS-10-1 | Wind | 249.9 |  | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-057 | GEWTG2 | Central | 01 - Woodward | DIS-15-2 | Wind | 100.65 |  | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-063 | A1530U1 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-2 | Wind | 299.25 |  | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-063 | A1530U1 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-2 | Wind | 299.25 |  | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-090 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-2 | Wind | 218.5 |  | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-008 | GEWTG2 | North | 04 - Northwest Kansas | DIS-10-1 | Wind | 198.69 |  | MIDW | South Hays 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-123N | GEWTG2 | North | 09 - Nebraska | DIS-10-1 | Wind | 89.66 |  | NPPD | Tap Pauline - Hildreth (Rosemont) 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-090 | SWTGU2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-15-2 | Wind | 218.5 |  | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-093 | GEWTG2 | Central | 01 - Woodward | DIS-15-2 | Wind | 250 |  | OKGE | Gracemont 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2010-003 | GXX048 | Central | 08 - North Oklahoma/South Central Kansas | DIS-10-1 | Wind | 98.7 |  | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-014 | SWTGU1 | South | 02 - Hitchland | DIS-10-1 | Wind | 177.1 |  | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-014 | SWTGU1 | South | 02 - Hitchland | DIS-10-1 | Wind | 181.7 |  | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-093 | GEWTG2 | Central | 01 - Woodward | DIS-15-2 | Wind | 250 |  | OKGE | Gracemont 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-009 | GENSAL | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-1 | Steam Turbine | 29 |  | OKGE | Osage 69kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-009 | GENSAL | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-1 | Steam Turbine | 29 |  | OKGE | Osage 69kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-020 | GEWTG2 | Central | 01 - Woodward | DIS-16-1 | WIND | 148.4 |  | WFEC | Moreland 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-009 | SWTGU2 | Central | 03 - Spearville | DIS-10-1 | Wind | 165.6 |  | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-020 | SWTGU2 | North | 04 - Northwest Kansas | DIS-10-1 | Wind | 48.3 |  | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-037 | VWCOR4 | South | 07 - Southwestern Oklahoma | DIS-10-1 | Wind | 99.83 |  | WFEC | Tap Washita - Blue Canyon Wind 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-022 | VWCOR6 | South | 06 - South Texas Panhandle/New Mexico | DIS-10-1 | Wind | 50 |  | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-022 | VWCOR6 | South | 06 - South Texas Panhandle/New Mexico | DIS-10-1 | Wind | 124 |  | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-022 | VWCOR6 | South | 06 - South Texas Panhandle/New Mexico | DIS-10-1 | Wind | 126 |  | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-020 | GEWTG2 | Central | 01 - Woodward | DIS-16-1 | WIND | 148.4 |  | WFEC | Moreland 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2009-040 | VWCOR6 | North | 09 - Nebraska | DIS-10-1 | Wind | 72 |  | WERE | Tap Smittyville - Knob Hill 115KV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-045 | REGCAU1 | Central | 01 - Woodward | DIS-16-1 | Wind | 478.7 |  | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-045 | REGCAU1 | Central | 01 - Woodward | DIS-16-1 | Wind | 478.7 |  | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-045 | REGCAU1 | Central | 01 - Woodward | DIS-16-1 | Wind | 478.7 |  | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-023 | GEWTG2 | South | 07 - Southwestern Oklahoma | DIS-09-1 | Wind | 73.6 |  | AEPW | Hobart Junction 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-023 | GEWTG2 | South | 07 - Southwestern Oklahoma | DIS-09-1 | Wind | 75.2 |  | AEPW | Hobart Junction 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-092 | GEWTG2 | North | 04 - Northwest Kansas | DIS-09-1 | Wind | 100.24 |  | MIDW | Post Rock 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-092 | GEWTG2 | North | 04 - Northwest Kansas | DIS-09-1 | Wind | 100.24 |  | MIDW | Post Rock 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-037N1 | GEWTG2 | North | 09 - Nebraska | DIS-09-1 | Wind | 75 |  | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044N | GEWTG2 | North | 09 - Nebraska | DIS-09-1 | Wind | 40.5 |  | NPPD | North Petersburg 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | GEWTG2 | North | 09 - Nebraska | DIS-09-1 | Wind | 0.2 |  | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | GEWTG2 | North | 09 - Nebraska | DIS-09-1 | Wind | 0.2 |  | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | GEWTG2 | North | 09 - Nebraska | DIS-09-1 | Wind | 100.3 |  | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | GEWTG2 | North | 09 - Nebraska | DIS-09-1 | Wind | 100.3 |  | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-047 | GENROU | Central | 01 - Woodward | DIS-16-1 | CT | 462.175 |  | OKGE | Mustang 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-047 | GENROU | Central | 01 - Woodward | DIS-16-1 | CT | 462.175 |  | OKGE | Mustang 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-051 | SWTGU2 | South | 02 - Hitchland | DIS-09-1 | Wind | 161 |  | SPS | Potter County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-051 | SWTGU2 | South | 02 - Hitchland | DIS-09-1 | Wind | 161 |  | SPS | Potter County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-025 | SWTGU2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-09-1 | Wind | 59.8 |  | OKGE | TAP Deer Creek - Sinclair 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-079 | SWTGU2 | Central | 03 - Spearville | DIS-09-1 | Wind | 98.9 |  | SUNC | Crooked Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-040 | WT4G2 | Central | 03 - Spearville | DIS-09-1 | Wind | 131.1 |  | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-052 | GENROU | South | 07 - Southwestern Oklahoma | ICS1 | Gas | 48.5 |  | WFEC | Anadarko 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-052 | GENROU | South | 07 - Southwestern Oklahoma | ICS1 | Gas | 49.1 |  | WFEC | Anadarko 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-052 | GENROU | South | 07 - Southwestern Oklahoma | ICS1 | Gas | 49.84 |  | WFEC | Anadarko 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-047 | GENROU | Central | 01 - Woodward | DIS-16-1 | CT | 462.175 |  | OKGE | Mustang 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-047 | GENROU | Central | 01 - Woodward | DIS-16-1 | CT | 462.175 |  | OKGE | Mustang 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-047 | GENROU | Central | 01 - Woodward | DIS-16-1 | CT | 462.175 |  | OKGE | Mustang 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-047 | GENROU | Central | 01 - Woodward | DIS-16-1 | CT | 462.175 |  | OKGE | Mustang 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-047 | GENROU | Central | 01 - Woodward | DIS-16-1 | CT | 462.175 |  | OKGE | Mustang 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-057 | REGCAU1 | Central | 01 - Woodward | DIS-16-1 | Wind | 519.46 |  | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-057 | REGCAU1 | Central | 01 - Woodward | DIS-16-1 | Wind | 519.46 |  | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-057 | REGCAU1 | Central | 01 - Woodward | DIS-16-1 | Wind | 519.46 |  | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2007-043 | GEWTG2 | Central | 01 - Woodward | ICS1 | Wind | 202.5 |  | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-068 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-1 | Wind | 250 |  | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-068 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-1 | Wind | 250 |  | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2007-021 | GEWTG2 | Central | 01 - Woodward | ICS1 | Wind | 209.43 |  | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-071 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-1 | Wind | 198.2 |  | OKGE | Middleton Tap 138kV | IA PENDING
GEN-2016-071 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-1 | Wind | 198.2 |  | OKGE | Middleton Tap 138kV | IA PENDING
GEN-2008-018 | GEWTG2 | Central | 03 - Spearville | ICS1 | Wind | 249.75 |  | SPS | Finney 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-119 | VWCO81 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-2 | Wind | 600 |  | OKGE | Spring Creek-Sooner 345kV | FACILITY STUDY STAGE
GEN-2016-119 | VWCO81 | Central | 08 - North Oklahoma/South Central Kansas | DIS-16-2 | Wind | 600 |  | OKGE | Spring Creek-Sooner 345kV | FACILITY STUDY STAGE
GEN-2007-050 | SWTGU2 | Central | 01 - Woodward | ICS1 | Wind | 170.2 |  | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-003 | SWTGU2 | Central | 01 - Woodward | ICS1 | Wind | 101.2 |  | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-046 | VWCOR6 | South | 02 - Hitchland | ICS1 | Wind | 102 |  | SPS | Hitchland 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-046 | VWCOR6 | South | 02 - Hitchland | ICS1 | Wind | 20 |  | SPS | Hitchland 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-046 | VWCOR6 | South | 02 - Hitchland | ICS1 | Wind | 78 |  | SPS | Hitchland 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-018 | REGCAU1, SMASC126 | Central | 03 - Spearville | DIS-17-1 | Solar | 189 | 189 | SUNC | Thistle 345kV sub | DISIS STAGE | -3.7
GEN-2002-005 | A1530U1 | South | 07 - Southwestern Oklahoma | PQ | Wind | 123 |  | WFEC | Red Hills Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
SPSCarson | CIMTR3 | South | 02 - Hitchland | PQ | Wind | 10 |  | SPS | Martin 115kV | Commercial Operation
SPSDumas19thSt | CIMTR3 | South | 02 - Hitchland | PQ | Wind | 10 |  | SPS | Dumas 19th Street 115kV
SPSDumas19thSt | CIMTR3 | South | 02 - Hitchland | PQ | Wind | 10 |  | SPS | Dumas 19th Street 115kV
SPSEtter | CIMTR3 | South | 02 - Hitchland | PQ | Wind | 10 |  | SPS | Etter 115kV
SPSEtter | CIMTR3 | South | 02 - Hitchland | PQ | Wind | 10 |  | SPS | Etter 115kV
SPSSherman | CIMTR3 | South | 02 - Hitchland | PQ | Wind | 10 |  | SPS | Sherman 115kV
SPSSherman | CIMTR3 | South | 02 - Hitchland | PQ | Wind | 10 |  | SPS | Sherman 115kV
NPPDBrokenBow | GENCLS | North | 09 - Nebraska | PQ | Heat | 7.3 |  | NPPD | Broken Bow 115kV
NPPDBurwell | GENCLS | North | 09 - Nebraska | PQ | Heat | 3.3 |  | NPPD | Ord 115kV
NPPDOrd | GENCLS | North | 09 - Nebraska | PQ | Heat | 10.8 |  | NPPD | Ord 115kV
NPPDStuart | GENCLS | North | 09 - Nebraska | PQ | Heat | 1.8 |  | NPPD | Ainsworth 115kV
GEN-2006-026 | GENROE | South | 06 - South Texas Panhandle/New Mexico | PQ | Gas | 156.476 |  | SPS | Hobbs 230kV & Hobbs 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-026 | GENROE | South | 06 - South Texas Panhandle/New Mexico | PQ | Gas | 156.9 |  | SPS | Hobbs 230kV & Hobbs 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-026 | GENROE | South | 06 - South Texas Panhandle/New Mexico | PQ | Gas | 235.582 |  | SPS | Hobbs 230kV & Hobbs 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-015 | GENROU | South | 06 - South Texas Panhandle/New Mexico | PQ | CT | 150 |  | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-015 | GENROU | South | 06 - South Texas Panhandle/New Mexico | PQ | Gas | 150 |  | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-030 | GENROU | Central | 12 - Northwest Arkansas | PQ | CT | 60 |  | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-040 | GENROU | Central | 12 - Northwest Arkansas | PQ | CT | 60 |  | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
J279NEAL | GENROU | North | 09 - Nebraska | DIS-15-2-PQ | Coal | 680 |  | MEC
GEN-2004-023N | GENROU | North | 09 - Nebraska | PQ | Coal | 75 |  | NPPD | Columbus Co 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
WAPASEAMSSpiritMoundHeat | GENROU | North | 09 - Nebraska | PQ | Heat | 60 |  | BEPC-SPP | Spirit Mound (WAPA) 115kV
WAPASEAMSSpiritMoundHeat | GENROU | North | 09 - Nebraska | PQ | Heat | 60 |  | BEPC-SPP | Spirit Mound (WAPA) 115kV
G261 | GENROU | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Combined Cycle | 183.48 |  | XEL
G261 | GENROU | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Combined Cycle | 116.62 |  | XEL
G261 | GENROU | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Combined Cycle | 188.5 |  | XEL
G261 | GENROU | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Combined Cycle | 188.5 |  | XEL
G370 | GENROU | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Gas | 148 |  | XEL | Anson 4
G370 | GENROU | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Gas | 57 |  | XEL | Anson 4
G389 | GENROU | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Gas | 200 |  | GRE | Elk River 230kV
G741 | GENROU | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Waste Heat Recovery | 1.85 |  | ALTW | Near Alliant 69kV line
G741 | GENROU | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Waste Heat Recovery | 6.15 |  | ALTW | Near Alliant 69kV line
G930 | GENROU | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Coal | 20 |  | XEL | Sherco
G930 | GENROU | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Coal | 20 |  | XEL | Sherco
G930 | GENROU | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Coal | 20 |  | XEL | Sherco
G930SHERCO | GENROU | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Coal | 730 |  | XEL
G930SHERCO | GENROU | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Coal | 40.5 |  | XEL
G930SHERCO | GENROU | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Coal | 730 |  | XEL
G930SHERCO | GENROU | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Coal | 40.5 |  | XEL
G930SHERCO | GENROU | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Coal | 910 |  | XEL
G930SHERCO | GENROU | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Coal | 40.5 |  | XEL
GEN-2006-020S | GENSAL | South | 02 - Hitchland | PQ | Wind | 20 |  | SPS | DWS Frisco 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | GENSAL | South | 02 - Hitchland | PQ | Wind | 80 |  | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | GENSAL | South | 02 - Hitchland | PQ | Wind | 134 |  | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | GENSAL | South | 02 - Hitchland | PQ | Wind | 80 |  | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | GENSAL | South | 02 - Hitchland | PQ | Wind | 76 |  | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-018 | GENSAL | South | 06 - South Texas Panhandle/New Mexico | PQ | CT | 55.122 |  | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-018 | GENSAL | South | 06 - South Texas Panhandle/New Mexico | PQ | CT | 55.122 |  | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-018 | GENSAL | South | 06 - South Texas Panhandle/New Mexico | PQ | CT | 55.122 |  | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
NPPDColumbusHydro | GENSAL | North | 09 - Nebraska | PQ | Hydro | 15 |  | NPPD | Columbus 115kV
NPPDColumbusHydro | GENSAL | North | 09 - Nebraska | PQ | Hydro | 15 |  | NPPD | Columbus 115kV
NPPDColumbusHydro | GENSAL | North | 09 - Nebraska | PQ | Hydro | 15 |  | NPPD | Columbus 115kV
WAPASEAMSFtRandallHydro | GENSAL | North | 09 - Nebraska | PQ | Hydro | 43.9 |  | WAPA | Ft Randle (WAPA) 230kV & 115kV
WAPASEAMSFtRandallHydro | GENSAL | North | 09 - Nebraska | PQ | Hydro | 43.9 |  | WAPA | Ft Randle (WAPA) 230kV & 115kV
WAPASEAMSFtRandallHydro | GENSAL | North | 09 - Nebraska | PQ | Hydro | 43.9 |  | WAPA | Ft Randle (WAPA) 230kV & 115kV
WAPASEAMSFtRandallHydro | GENSAL | North | 09 - Nebraska | PQ | Hydro | 43.9 |  | WAPA | Ft Randle (WAPA) 230kV & 115kV
WAPASEAMSFtRandallHydro | GENSAL | North | 09 - Nebraska | PQ | Hydro | 43.9 |  | WAPA | Ft Randle (WAPA) 230kV & 115kV
WAPASEAMSFtRandallHydro | GENSAL | North | 09 - Nebraska | PQ | Hydro | 43.9 |  | WAPA | Ft Randle (WAPA) 230kV & 115kV
WAPASEAMSFtRandallHydro | GENSAL | North | 09 - Nebraska | PQ | Hydro | 43.9 |  | WAPA | Ft Randle (WAPA) 230kV & 115kV
WAPASEAMSFtRandallHydro | GENSAL | North | 09 - Nebraska | PQ | Hydro | 43.9 |  | WAPA | Ft Randle (WAPA) 230kV & 115kV
WAPASEAMSGavinsPointHydro | GENSAL | North | 09 - Nebraska | PQ | Hydro | 34 |  | WAPA | Gavins Point (WAPA) 115kV
WAPASEAMSGavinsPointHydro | GENSAL | North | 09 - Nebraska | PQ | Hydro | 34 |  | WAPA | Gavins Point (WAPA) 115kV
WAPASEAMSGavinsPointHydro | GENSAL | North | 09 - Nebraska | PQ | Hydro | 34 |  | WAPA | Gavins Point (WAPA) 115kV
GEN-2017-060 | VC18084901, VC19024901 | Central | 12 - Northwest Arkansas | DIS-17-1 | Wind | 149.4 | 149.4 | EDE | LaRussell Energy Center 161kV | DISIS STAGE | -8.2
GEN-2005-008 | GEWTG2 | Central | 01 - Woodward | PQ | Wind | 120 |  | OKGE | Woodward 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-037 | GEWTG2 | Central | 01 - Woodward | PQ | Wind | 102 |  | OKGE | FPL Moreland Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-025A | GEWTG2 | Central | 03 - Spearville | PQ | Wind | 148.5 |  | SUNC | Spearville 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-014 | GEWTG2 | Central | 03 - Spearville | PQ | Wind | 155.2 |  | SUNC | Spearville 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-039A | GEWTG2 | Central | 03 - Spearville | PQ | Wind | 105 |  | SUNC | Shooting Star Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-008 | GEWTG2 | South | 02 - Hitchland | PQ | Wind | 79.5 |  | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-008 | GEWTG2 | South | 02 - Hitchland | PQ | Wind | 82.5 |  | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-008 | GEWTG2 | South | 02 - Hitchland | PQ | Wind | 78 |  | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-020 | GEWTG2 | South | 02 - Hitchland | PQ | Wind | 30 |  | SPS | Martin 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-020 | GEWTG2 | South | 02 - Hitchland | PQ | Wind | 49.6 |  | SPS | Martin 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-020 | GEWTG2 | South | 02 - Hitchland | PQ | Wind | 79.5 |  | SPS | Martin 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
Sunray | GEWTG2 | South | 06 - South Texas Panhandle/New Mexico | PQ | Wind | 49.5 |  | SPS | Valero 115kV
GEN-2003-005 | GEWTG2 | South | 07 - Southwestern Oklahoma | PQ | Wind | 105.6 |  | WFEC | Anadarko - Paradise (Blue Canyon) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-022 | GEWTG2 | South | 07 - Southwestern Oklahoma | PQ | Wind | 156.8 |  | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002 | GEWTG2 | South | 07 - Southwestern Oklahoma | PQ | Wind | 77.76 |  | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002 | GEWTG2 | South | 07 - Southwestern Oklahoma | PQ | Wind | 29.16 |  | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-006 | GEWTG2 | Central | 08 - North Oklahoma/South Central Kansas | PQ | Wind | 150 |  | AECI | Remington 138kV | GIA Executed
J416 | GEWTG2 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 11.5 |  | ALTW
J416 | GEWTG2 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 11 |  | ALTW
J416 | GEWTG2 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 90 |  | ALTW
J416 | GEWTG2 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 87.5 |  | ALTW
GEN-2006-038N005 | GEWTG2 | North | 09 - Nebraska | PQ | Wind | 80 |  | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-038N019 | GEWTG2 | North | 09 - Nebraska | PQ | Wind | 80 |  | NPPD | Petersburg North 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-119O | GEWTG2 | North | 09 - Nebraska | PQ | Wind | 60 |  | OPPD | S1399 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-035 | GXX048 | South | 07 - Southwestern Oklahoma | PQ | Wind | 132 |  | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-046 | M24G1 | Central | 01 - Woodward | PQ | Wind | 132 |  | OKGE | Dewey 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
SPSMooreE | None | South | 02 - Hitchland | PQ | Wind | 7.5 |  | SPS | Moore East 115kV
SPSMooreE | None | South | 02 - Hitchland | PQ | Wind | 10 |  | SPS | Moore East 115kV
SPSHopi | None | South | 06 - South Texas Panhandle/New Mexico | PQ | Solar | 10 |  | SPS | Hopi 115kV
SPSJal | None | South | 06 - South Texas Panhandle/New Mexico | PQ | Solar | 10 |  | SPS | S Jal 115kV
SPSLeaRoad | None | South | 06 - South Texas Panhandle/New Mexico | PQ | Solar | 10 |  | SPS | Lea Road 115kV
SPSMonument | None | South | 06 - South Texas Panhandle/New Mexico | PQ | Solar | 10 |  | SPS | Monument 115kV
SPSOcotillo | None | South | 06 - South Texas Panhandle/New Mexico | PQ | Solar | 10 |  | SPS | S_Jal 115kV
NPPDBuffaloCountySolar | None | North | 09 - Nebraska | PQ | Solar | 10 |  | NPPD | Kearney Northeast
NPPDBurtCountyWind | None | North | 09 - Nebraska | PQ | Wind | 10 |  | NPPD | Tekamah & Oakland 115kV
NPPDBurtCountyWind | None | North | 09 - Nebraska | PQ | Wind | 10 |  | NPPD | Tekamah & Oakland 115kV
GrayCountyWindMontezuma | REGCAU1 | Central | 03 - Spearville | PQ | Wind | 112.2 |  | SUNC | Gray County Tap 115kV
G287 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 49 |  | XEL | Nobles County
G287 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 51 |  | XEL | Nobles County
G287 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 49 |  | XEL | Nobles County
G287 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 51 |  | XEL | Nobles County
G362 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 100 |  | GRE | Pleasant Valley
G362 | REGCAU1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 100 |  | GRE | Pleasant Valley
GEN-2002-022 | SWTEU1 | South | 02 - Hitchland | PQ | Wind | 78.2 |  | SPS | Bushland 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-082 | VC18084901 | Central | 12 - Northwest Arkansas | DIS-17-1 | Wind | 149.4 | 149.4 | EDE | Asbury Plant 161kV | DISIS STAGE | -6
GEN-2002-022 | SWTGU2 | South | 02 - Hitchland | PQ | Wind | 161 |  | SPS | Bushland 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-043 | SWTGU2 | South | 07 - Southwestern Oklahoma | PQ | Wind | 98.9 |  | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-086 | VWCOR8 | Central | 08 - North Oklahoma/South Central Kansas | DIS-17-1 | Wind | 150 | 150 | WERE | Viola 345kV | DISIS STAGE | -13.8
GEN-2001-039M | VWCOR4 | North | 04 - Northwest Kansas | PQ | Wind | 99 |  | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-039M | VWCOR4 | North | 04 - Northwest Kansas | PQ | Wind | 1 |  | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | VWCOR4 | North | 04 - Northwest Kansas | PQ | Wind | 101 |  | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | VWCOR4 | North | 04 - Northwest Kansas | PQ | Wind | 1 |  | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | VWCOR4 | North | 04 - Northwest Kansas | PQ | Wind | 99 |  | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020N | VWCOR4 | North | 09 - Nebraska | PQ | Wind | 42 |  | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-011N08 | VWCOR4 | North | 09 - Nebraska | PQ | Wind | 81 |  | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
LlanoEstacadoWhiteDeer | WT1G1 | South | 02 - Hitchland | PQ | Wind | 80 |  | SPS | Llano Wind 115kV
GEN-2001-036 | WT1G1 | South | 06 - South Texas Panhandle/New Mexico | PQ | Wind | 80 |  | SPS | Norton 115kV Switching Station | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-033 | WT1G1 | South | 06 - South Texas Panhandle/New Mexico | PQ | Wind | 120 |  | SPS | San Juan Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-033 | WT1G1 | South | 06 - South Texas Panhandle/New Mexico | PQ | Wind | 60 |  | SPS | San Juan Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-026 | WT1G1 | South | 07 - Southwestern Oklahoma | PQ | Wind | 74.25 |  | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-021N | WT1G1 | North | 09 - Nebraska | PQ | Wind | 15 |  | NPPD | Ainsworth Wind Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-021N | WT1G1 | North | 09 - Nebraska | PQ | Wind | 60 |  | NPPD | Ainsworth Wind Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
G621 | WT1G1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 20 |  | XEL | Golf - Wookstock 34.5kV
GEN-2001-014 | WT2G1 | Central | 01 - Woodward | PQ | Wind | 94.5 |  | WFEC | Ft Supply 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-024S | WT2G1 | Central | 01 - Woodward | PQ | Wind | 18.9 |  | WFEC | Buffalo Bear Tap 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-009 | WT2G1 | South | 02 - Hitchland | PQ | Wind | 79.8 |  | SPS | Hansford 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-004 | WT2G1 | South | 07 - Southwestern Oklahoma | PQ | Wind | 151.2 |  | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-019 | WT2G1 | North | 04 - Northwest Kansas | PQ | Wind | 100.8 |  | MIDW | Smoky Hills Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-019 | WT2G1 | North | 04 - Northwest Kansas | PQ | Wind | 148.5 |  | MIDW | Smoky Hills Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
R26 | WT3E1 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-15-2-PQ | Wind | 146 |  | MEC | MEC Cooper - Booneville 345kV
G612 | WT3G2 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 150 |  | ALTW | ITC Midwest Fernald 115kV
R15 | WT3G2 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 80 |  | MEC | Pomeroy 161kV
R22 | WT3G2 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 102.5 |  | MEC
R22 | WT3G2 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 97.5 |  | MEC
R23 | WT3G2 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 100 |  | MEC | Monona - Carroll 161kV
R35 | WT3G2 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 27.5 |  | MEC | Pomeroy Wind Farm site
R35 | WT3G2 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 52.5 |  | MEC | Pomeroy Wind Farm site
R49 | WT3G2 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 12 |  | MEC | Pomeroy Generating station
G255 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 50 |  | XEL | Yankee
G255 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 50 |  | XEL | Yankee
G349 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 100 |  | XEL | Brookings County
G349 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 100 |  | XEL | Brookings County
G514 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 148.8 |  | XEL | Lakefield Station via Trimont G263 Interconnect
G514 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 1.2 |  | XEL | Lakefield Station via Trimont G263 Interconnect
G540 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 80 |  | ALTW | Adams - Lime Creek 161kV
G548 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 80 |  | ALTW | Barton 161kV
G595 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 150 |  | ALTW | Lime Creek 161kV
G602 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 16.4 |  | XEL | Nobles County 115kV
G602 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 1.25 |  | XEL | Nobles County 115kV
G602 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 14.35 |  | XEL | Nobles County 115kV
G604 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 44 |  | ALTW | Owatonna - County Line 69kV
G685 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 20 |  | XEL | Lake Lillian - Atwater 69kV
G971 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 20 |  | XEL | 69kV line in SE 1/4 of Sec 17 in Cosmos Twp
GEN-2017-090 | REGCAU1 | Central | 13 - Northeast Kansas/Northwest Missouri | DIS-17-1 | Solar | 150 | 150 | KCPL | Adrian 161kV sub | DISIS STAGE | -9.7
R34 | WT4G1 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 170.2 |  | MEC | Council Bluffs - Madison County 345kV
R34 | WT4G1 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 79.8 |  | MEC | Council Bluffs - Madison County 345kV
R42 | WT4G1 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 136 |  | MEC
R42 | WT4G1 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 114 |  | MEC
R65 | WT4G1 | North | 09 - Nebraska | DIS-15-2-PQ | Wind | 92 |  | MEC | R34 Expansion
G586 | WT4G1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 15 |  | XEL | Xcel New Yankee Sub 34.5kV
G586 | WT4G1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 15 |  | XEL | Xcel New Yankee Sub 34.5kV
ASGI-2016-005NWE205 | GEWTG2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 0.2 |  | WAPA | Tap White Lake - Stickeny 69kV
ASGI-2016-005NWE205 | GEWTG2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 19.8 |  | WAPA | Tap White Lake - Stickeny 69kV
ASGI-2016-007NWE208 | GEWTG2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 0.2 |  | WAPA | Kimball 69kV
ASGI-2016-007NWE208 | GEWTG2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 19.8 |  | WAPA | Kimball 69kV
J091 | WT3G2 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 66 |  | ALTW
R39 | WT4G1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 166.66 |  | MEC | Raun - Lakefield Junction
R39 | WT4G1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 166.66 |  | MEC | Raun - Lakefield Junction
R39 | WT4G1 | North | 15 - Eastern South Dakota | DIS-15-2-PQ | Wind | 166.66 |  | MEC | Raun - Lakefield Junction
G380 | None | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 0.8 |  | OTP | Rugby 115kV
G380 | None | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 67.2 |  | OTP | Rugby 115kV
G380 | None | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 29.4 |  | OTP | Rugby 115kV
G380 | None | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 12.6 |  | OTP | Rugby 115kV
G380 | None | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 40 |  | OTP | Rugby 115kV
G752 | WT3G2 | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 42.5 |  | MDU | Bison - Hettinger 230kV
G752 | WT3G2 | North | 16 - Western North Dakota | DIS-15-2-PQ | Wind | 107.5 |  | MDU | Bison - Hettinger 230kV
Young1 | GENROU | North | 16 - Western North Dakota | DIS-15-2-PQ | Coal | 274 |  | OTP

## Stability Analysis
Region | Group | Season | Model Dispatch | Event ID | Event Description | Event Category | Rotor Angle Stability | Transient Voltage Response > 0.7 p.u. | Transient Voltage Response < 1.2 p.u. | Post Fault Steady State Voltage > 0.9 p.u. | Post Fault Steady State Voltage < 1.1 p.u. | Damping Factor > 0.8 % | Low Voltage Rides Through | Violation Summary | Primary Mitigation | Alternate Mitigation | Alternate Mitigation2 (Informational)
North | 04 - Northwest Kansas | 19W | Transfer | 004-3PH-1 | 3-phase fault on G17-004-TAP to Summit 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-3PH-2 | 3-phase fault on G17-004-TAP to Elm Creek 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-3PH-3 | 3-phase fault on Summit to Geary 345 kVCircuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-3PH-4 | 3-phase fault on Summit - G16-112-TAP 345 kVCircuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-3PH-5 | 3-phase fault on Summit 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-3PH-6 | 3-phase fault on Summit to SMOKYHL 230 kVCircuit 1, near Summit. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-3PH-7 | 3-phase fault on Summit to EMCPHER 230 kVCircuit 1, near Summit. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-3PH-8 | 3-phase fault on Summit to UNIONRG 230 kVCircuit 1, near Summit. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-3PH-9 | 3-phase fault on Summit 230/115/13.8 kVTransformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-3PH-10 | 3-phase fault on Elm Creek 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-3PH-11 | 3-phase fault on Elm Creek to CONCRD 230 kVCircuit 1, near Elm Creek. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-3PH-12 | 3-phase fault on Elm Creek to NMANHT 230 kVCircuit 1, near Elm Creek. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-3PH-13 | 3-phase fault on Elm Creek to MRWYP 230 kVCircuit 1, near Elm Creek. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-3PH-14 | 3-phase fault on Reno to WICHITA 345 kVCircuit 1, near Reno. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-3PH-15 | 3-phase fault on Reno 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-3PH-16 | 3-phase fault on Geary to JEC N 345kVCircuit 1, near Geary. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-3PH-17 | 3-phase fault on Geary 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-3PH-18 | 3-phase fault on CONCRD 230/115/13.8 kVTransformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-3PH-19 | 3-phase fault on NMANHT 230/115/13.8 kVTransformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-3PH-20 | 3-phase fault on NMANHT to EMANHAT 230 kVCircuit 1, near NMANHT. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-3PH-21 | 3-phase fault on RENO to MOUNDRG 115 kVCircuit 1, near RENO. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-3PH-22 | 3-phase fault on WICHITA to BENTON 345kVCircuit 1, near WICHITA. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-3PH-23 | 3-phase fault on WICHITA to BUFFALO 345kVCircuit 2, near WICHITA. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-3PH-24 | 3-phase fault on WICHITA 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-3PH-26 | 3-phase fault on JEC N to MORRIS 345kVCircuit 1, near JEC N. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No
North | 04 - Northwest Kansas | 19W | Transfer | 004-3PH-27 | 3-phase fault on JEC N 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No
North | 04 - Northwest Kansas | 19W | Transfer | 004-3PH-28 | 3-phase fault on UNIONRG to MORRIS 230 kVCircuit 1, near UNIONRG. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No
North | 04 - Northwest Kansas | 19W | Transfer | 004-SB-1 | SLG fault on G17-004-TAP 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of G17-004-TAP 345 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | No
North | 04 - Northwest Kansas | 19W | Transfer | 004-SB-2 | SLG fault on Summit 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Summit 345 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | No
North | 04 - Northwest Kansas | 19W | Transfer | 004-SB-3 | SLG fault on Elk Creek 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Elk Creek 345 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-SB-4 | SLG fault on Summit 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of Summit 230 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-SB-5 | SLG fault on Elk Creek 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of Elk Creek 230 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-SB-6 | SLG fault on Geary 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Geary 345 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-SB-7 | SLG fault on RENO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of RENO 345 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-PO-1-1 | Prior Outage of G17-004-TAP to Summit 345kV Circuit 1, 3-phase fault on Elm Creek 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-PO-1-2 | Prior Outage of G17-004-TAP to Summit 345kV Circuit 1, 3-phase fault on G17-004-TAP to Elm Creek 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-PO-2-1 | Prior Outage of G17-004-TAP to Elm Creek 345kV Circuit 1, 3-phase fault on G17-004-TAP to Summit 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-PO-2-2 | Prior Outage of G17-004-TAP to Elm Creek 345kV Circuit 1, 3-phase fault on Summit to Geary 345 kVCircuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-PO-2-3 | Prior Outage of G17-004-TAP to Elm Creek 345kV Circuit 1, 3-phase fault on Summit - G16-112-TAP - G16-111-TAP - Reno 345 kVCircuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-PO-2-4 | Prior Outage of G17-004-TAP to Elm Creek 345kV Circuit 1, 3-phase fault on Summit 345/230/13.8 kVTransformer 1 | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-PO-3-1 | Prior Outage of SUMMIT to GEARY 345kV Circuit 1, 3-phase fault on G17-004-TAP to Summit 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-PO-3-2 | Prior Outage of SUMMIT to GEARY 345kV Circuit 1, 3-phase fault on G17-004-TAP to ELMCREEK 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-PO-3-3 | Prior Outage of SUMMIT to GEARY 345kVCircuit 1, 3-phase fault on Summit - G16-112-TAP 345 kVCircuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-PO-3-4 | Prior Outage of SUMMIT to GEARY 345kVCircuit 1, 3-phase fault on Summit 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-PO-4-1 | Prior Outage of Summit - G16-112-TAP - G16-111-TAP - Reno 345 kVCircuit 1, 3-phase fault on G17-004-TAP to Summit 345 kV Circuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-PO-4-2 | Prior Outage of Summit - G16-112-TAP - G16-111-TAP - Reno 345 kVCircuit 1, 3-phase fault on G17-004-TAP to ELMCREEK 345 kV Circuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-PO-4-3 | Prior Outage of Summit - G16-112-TAP - G16-111-TAP - Reno 345 kVCircuit 1, 3-phase fault on Summit to Geary 345 kV Circuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-PO-4-4 | Prior Outage of Summit - G16-112-TAP - G16-111-TAP - Reno 345 kV Circuit 1, 3-phase fault on Summit 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-3PH-1 | 3-phase fault on Mingo to REDWILO 345 kV Circuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-3PH-2 | 3-phase fault on Mingo to SETAB 345 kV Circuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-3PH-3 | 3-phase fault on Mingo 345/115/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-3PH-4 | 3-phase fault on Mingo to COLBY 115 kVCircuit 1, near Mingo. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-3PH-5 | 3-phase fault on Mingo to PH RUN 115 kVCircuit 1, near Mingo. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-3PH-6 | 3-phase fault on Mingo to BREWSTR 115 kVCircuit 1, near Mingo. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-3PH-7 | 3-phase fault on REDWILO to POSTROCK 345 kVCircuit 1, near REDWILO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-3PH-8 | 3-phase fault on REDWILO to GENTLMN 345 kVCircuit 1, near REDWILO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-3PH-9 | 3-phase fault on REDWILO to KEYSTON 345 kVCircuit 1, near REDWILO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-3PH-10 | 3-phase fault on REDWILO 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-3PH-11 | 3-phase fault on SETAB to HOLCOMB 345 kVCircuit 1, near SETAB. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-3PH-12 | 3-phase fault on SETAB 345/115/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-3PH-13 | 3-phase fault on COLBY to ATWOOD 115 kVCircuit 1, near COLBY. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-3PH-14 | 3-phase fault on COLBY to SEGNTP 115 kVCircuit 1, near COLBY. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-3PH-15 | 3-phase fault on BREWSTR to GOODLND 115 kVCircuit 1, near BREWSTR. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-3PH-16 | 3-phase fault on PH RUN to SEGUIN 115 kVCircuit 1, near PH RUN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-3PH-17 | 3-phase fault on PH RUN to GRINNEL 115 kVCircuit 1, near PH RUN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-3PH-18 | 3-phase fault on REDWILO to BEVERLY 115 kVCircuit 1, near REDWILO. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-3PH-19 | 3-phase fault on REDWILO to STOCKVL 115 kVCircuit 1, near REDWILO. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-3PH-20 | 3-phase fault on REDWILO to MCCOOK 115 kVCircuit 2, near REDWILO. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-3PH-21 | 3-phase fault on KEYSTON 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-3PH-22 | 3-phase fault on KEYSTON to SIDNEY 345 kVCircuit 1, near KEYSTON. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-3PH-23 | 3-phase fault on KEYSTON to GENTLMN 345 kVCircuit 2, near KEYSTON. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-3PH-24 | 3-phase fault on GENTLMN to THEDFRD 345 kVCircuit 1, near GENTLMN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-3PH-25 | 3-phase fault on GENTLMN to SWEET 345 kVCircuit 1, near GENTLMN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-3PH-26 | 3-phase fault on GENTLMN 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-3PH-27 | 3-phase fault on POSTROCK to SPERVIL 345 kVCircuit 1, near POSTROCK. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-3PH-28 | 3-phase fault on POSTROCK to AXTELL 345 kVCircuit 1, near POSTROCK. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-3PH-29 | 3-phase fault on POSTROCK 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-3PH-30 | 3-phase fault on SETAB to SCOTCTY 115 kVCircuit 1, near SETAB. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-3PH-31 | 3-phase fault on SETAB to CNTRLPL 115 kVCircuit 1, near SETAB. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-3PH-32 | 3-phase fault on HOLCOMB to BUCKNER 345 kVCircuit 1, near HOLCOMB. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-3PH-33 | 3-phase fault on HOLCOMB to FINNEY 345 kVCircuit 1, near HOLCOMB. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-3PH-34 | 3-phase fault on HOLCOMB 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-SB-1 | SLG fault on MINGO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Mingo 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-SB-2 | SLG fault on MINGO 115 kV, stuck breaker results delayed clearing after 16 cycles with loss of Mingo 115 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-SB-3 | SLG fault on REDWILO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of REDWILO 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-SB-4 | SLG fault on SETAB 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of SETAB 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-PO-1-2 | Prior Outage of MINGO to REDWILO 345kVCircuit 1, 3-phase fault on Mingo 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-PO-2-2 | Prior Outage of MINGO to SETAB 345kVCircuit 1, 3-phase fault on Mingo 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-PO-3-1 | Prior Outage of Mingo 345/115/13.8 kVTransformer 1, 3-phase fault on Mingo to REDWILO 345 kVCircuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 013-PO-3-2 | Prior Outage of Mingo 345/115/13.8 kVTransformer 1, 3-phase fault on Mingo to SETAB 345 kVCircuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | TIE-3PH-1 | 3-phase fault on BLACKBERRY to NEOSHO 345 kVCircuit 1, near BLACKBERRY. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | TIE-3PH-2 | 3-phase fault on DELWARE to NEOSHO 345 kVCircuit 1, near DELWARE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | TIE-3PH-3 | 3-phase fault on DGRASSE to THISTLE 345 kVCircuit 1, near DGRASSE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | TIE-3PH-4 | 3-phase fault on CARPENTER to HARBNGR 345 kVCircuit 1, near CARPENTER. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | TIE-3PH-5 | 3-phase fault on FINNEY to HOLCOMB 345 kVCircuit 1, near FINNEY. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | TIE-3PH-6 | 3-phase fault on STRANGER to IATAN 345 kVCircuit 1, near STRANGR. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | TIE-3PH-7 | 3-phase fault on SWISVAL to W.GRDNR 345 kVCircuit 1, near SWISVAL. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | TIE-3PH-8 | 3-phase fault on 87TH to CRAIG 345 kVCircuit 1, near 87TH. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | TIE-3PH-9 | 3-phase fault on BUFFALO to THISTLE 345 kVCircuit 1, near BUFFALO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | TIE-3PH-10 | 3-phase fault on NEOSHO to LACYGNE 345 kVCircuit 1, near NEOSHO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | TIE-3PH-11 | 3-phase fault on ROSEHIL to G15-052T 345 kVCircuit 1, near ROSEHIL. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | TIE-SB-1 | SLG fault on HOLCOMB 345 kV, , stuck breaker results delayed clearing after 16 cycles with loss of HOLCOMB 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | TIE-SB-2 | SLG fault on NEOSHO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of NEOSHO 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | TIE-SB-3 | SLG fault on LACYGNE 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of LACYGNE to WAVERLY 345 kVCircuit 1 and LACYGNE to NEOSHO 345 kVCircuit 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | TIE-SB-4 | SLG fault on 87TH 345 Kv, stuck breaker results delayed clearing after 16 cycles with loss of 87TH 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | TIE-SB-5 | SLG fault on W.GRDNR 345 Kv, stuck breaker results delayed clearing after 16 cycles with loss of W.GRDNR 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | TIE-SB-6 | SLG fault on THISTLE 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of THISTLE to BUFFALO 345 kVCircuit 1, THISTLE to CLARKCOUNTY 345 kVCircuit 1 and THISTLE 345/115/13.8 kVtransformer 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | TIE-PO-1-2 | Prior Outage of BLACKBERRY to NEOSHO 345kV Circuit 1, 3-phase fault on 87TH to CRAIG 345 kV Circuit 1, near 87TH. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | TIE-PO-1-3 | Prior Outage of BLACKBERRY to NEOSHO 345kV Circuit 1, 3-phase fault on SWISVAL to W.GRDNR 345 kV Circuit 1, near SWISVAL. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | TIE-PO-2-1 | Prior Outage of WAVERLY to LACYGNE 345kV Circuit 1, 3-phase fault on 87TH to CRAIG 345 kV Circuit 1, near 87TH. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | TIE-PO-2-2 | Prior Outage of WAVERLY to LACYGNE 345kV Circuit 1, 3-phase fault on SWISVAL to W.GRDNR 345 kV Circuit 1, near SWISVAL. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | TIE-PO-2-3 | Prior Outage of WAVERLY to LACYGNE 345kV Circuit 1, 3-phase fault on BLACKBERRY to NEOSHO 345 kV Circuit 1, near BLACKBERRY. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | TIE-PO-3-2 | Prior Outage of 87TH to CRAIG 345kV Circuit 1, 3-phase fault on SWISVAL to W.GRDNR 345 kV Circuit 1, near SWISVAL. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | TIE-PO-3-3 | Prior Outage of 87TH to CRAIG 345kV Circuit 1, 3-phase fault on BLACKBERRY to NEOSHO 345 kV Circuit 1, near BLACKBERRY. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | TIE-PO-4-2 | Prior Outage of SWISVAL to W.GRDNR 345kV Circuit 1, 3-phase fault on 87TH to CRAIG 345 kV Circuit 1, near 87TH. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | TIE-PO-4-3 | Prior Outage of SWISVAL to W.GRDNR 345kV Circuit 1, 3-phase fault on BLACKBERRY to NEOSHO 345 kV Circuit 1, near BLACKBERRY. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-3PH-1 | 3-phase fault on G17-004-TAP to Summit 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-3PH-2 | 3-phase fault on G17-004-TAP to Elm Creek 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-3PH-3 | 3-phase fault on Summit to Geary 345 kVCircuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-3PH-4 | 3-phase fault on Summit - G16-112-TAP 345 kVCircuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-3PH-5 | 3-phase fault on Summit 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-3PH-6 | 3-phase fault on Summit to SMOKYHL 230 kVCircuit 1, near Summit. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-3PH-7 | 3-phase fault on Summit to EMCPHER 230 kVCircuit 1, near Summit. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-3PH-8 | 3-phase fault on Summit to UNIONRG 230 kVCircuit 1, near Summit. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-3PH-9 | 3-phase fault on Summit 230/115/13.8 kVTransformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-3PH-10 | 3-phase fault on Elm Creek 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-3PH-11 | 3-phase fault on Elm Creek to CONCRD 230 kVCircuit 1, near Elm Creek. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-3PH-12 | 3-phase fault on Elm Creek to NMANHT 230 kVCircuit 1, near Elm Creek. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-3PH-13 | 3-phase fault on Elm Creek to MRWYP 230 kVCircuit 1, near Elm Creek. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-3PH-14 | 3-phase fault on Reno to WICHITA 345 kVCircuit 1, near Reno. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-3PH-15 | 3-phase fault on Reno 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-3PH-16 | 3-phase fault on Geary to JEC N 345kVCircuit 1, near Geary. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-3PH-17 | 3-phase fault on Geary 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-3PH-18 | 3-phase fault on CONCRD 230/115/13.8 kVTransformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-3PH-19 | 3-phase fault on NMANHT 230/115/13.8 kVTransformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-3PH-20 | 3-phase fault on NMANHT to EMANHAT 230 kVCircuit 1, near NMANHT. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-3PH-21 | 3-phase fault on RENO to MOUNDRG 115 kVCircuit 1, near RENO. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-3PH-22 | 3-phase fault on WICHITA to BENTON 345kVCircuit 1, near WICHITA. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-3PH-23 | 3-phase fault on WICHITA to BUFFALO 345kVCircuit 2, near WICHITA. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-3PH-24 | 3-phase fault on WICHITA 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-3PH-26 | 3-phase fault on JEC N to MORRIS 345kVCircuit 1, near JEC N. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-3PH-27 | 3-phase fault on JEC N 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-3PH-28 | 3-phase fault on UNIONRG to MORRIS 230 kVCircuit 1, near UNIONRG. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-SB-1 | SLG fault on G17-004-TAP 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of G17-004-TAP 345 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-SB-2 | SLG fault on Summit 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Summit 345 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-SB-3 | SLG fault on Elk Creek 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Elk Creek 345 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-SB-4 | SLG fault on Summit 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of Summit 230 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-SB-5 | SLG fault on Elk Creek 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of Elk Creek 230 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-SB-6 | SLG fault on Geary 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Geary 345 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-SB-7 | SLG fault on RENO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of RENO 345 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-PO-1-1 | Prior Outage of G17-004-TAP to Summit 345kV Circuit 1, 3-phase fault on Elm Creek 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-PO-1-2 | Prior Outage of G17-004-TAP to Summit 345kV Circuit 1, 3-phase fault on G17-004-TAP to Elm Creek 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-PO-2-1 | Prior Outage of G17-004-TAP to Elm Creek 345kV Circuit 1, 3-phase fault on G17-004-TAP to Summit 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-PO-2-2 | Prior Outage of G17-004-TAP to Elm Creek 345kV Circuit 1, 3-phase fault on Summit to Geary 345 kVCircuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-PO-2-3 | Prior Outage of G17-004-TAP to Elm Creek 345kV Circuit 1, 3-phase fault on Summit - G16-112-TAP - G16-111-TAP - Reno 345 kVCircuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-PO-2-4 | Prior Outage of G17-004-TAP to Elm Creek 345kV Circuit 1, 3-phase fault on Summit 345/230/13.8 kVTransformer 1 | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-PO-3-1 | Prior Outage of SUMMIT to GEARY 345kV Circuit 1, 3-phase fault on G17-004-TAP to Summit 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-PO-3-2 | Prior Outage of SUMMIT to GEARY 345kV Circuit 1, 3-phase fault on G17-004-TAP to ELMCREEK 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-PO-3-3 | Prior Outage of SUMMIT to GEARY 345kVCircuit 1, 3-phase fault on Summit - G16-112-TAP 345 kVCircuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-PO-3-4 | Prior Outage of SUMMIT to GEARY 345kVCircuit 1, 3-phase fault on Summit 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-PO-4-1 | Prior Outage of Summit - G16-112-TAP - G16-111-TAP - Reno 345 kVCircuit 1, 3-phase fault on G17-004-TAP to Summit 345 kV Circuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-PO-4-2 | Prior Outage of Summit - G16-112-TAP - G16-111-TAP - Reno 345 kVCircuit 1, 3-phase fault on G17-004-TAP to ELMCREEK 345 kV Circuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-PO-4-3 | Prior Outage of Summit - G16-112-TAP - G16-111-TAP - Reno 345 kVCircuit 1, 3-phase fault on Summit to Geary 345 kV Circuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 004-PO-4-4 | Prior Outage of Summit - G16-112-TAP - G16-111-TAP - Reno 345 kV Circuit 1, 3-phase fault on Summit 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-3PH-1 | 3-phase fault on Mingo to REDWILO 345 kV Circuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-3PH-2 | 3-phase fault on Mingo to SETAB 345 kV Circuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-3PH-3 | 3-phase fault on Mingo 345/115/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-3PH-4 | 3-phase fault on Mingo to COLBY 115 kVCircuit 1, near Mingo. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-3PH-5 | 3-phase fault on Mingo to PH RUN 115 kVCircuit 1, near Mingo. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-3PH-6 | 3-phase fault on Mingo to BREWSTR 115 kVCircuit 1, near Mingo. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-3PH-7 | 3-phase fault on REDWILO to POSTROCK 345 kVCircuit 1, near REDWILO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-3PH-8 | 3-phase fault on REDWILO to GENTLMN 345 kVCircuit 1, near REDWILO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-3PH-9 | 3-phase fault on REDWILO to KEYSTON 345 kVCircuit 1, near REDWILO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-3PH-10 | 3-phase fault on REDWILO 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-3PH-11 | 3-phase fault on SETAB to HOLCOMB 345 kVCircuit 1, near SETAB. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-3PH-12 | 3-phase fault on SETAB 345/115/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-3PH-13 | 3-phase fault on COLBY to ATWOOD 115 kVCircuit 1, near COLBY. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-3PH-14 | 3-phase fault on COLBY to SEGNTP 115 kVCircuit 1, near COLBY. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-3PH-15 | 3-phase fault on BREWSTR to GOODLND 115 kVCircuit 1, near BREWSTR. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-3PH-16 | 3-phase fault on PH RUN to SEGUIN 115 kVCircuit 1, near PH RUN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-3PH-17 | 3-phase fault on PH RUN to GRINNEL 115 kVCircuit 1, near PH RUN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-3PH-18 | 3-phase fault on REDWILO to BEVERLY 115 kVCircuit 1, near REDWILO. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-3PH-19 | 3-phase fault on REDWILO to STOCKVL 115 kVCircuit 1, near REDWILO. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-3PH-20 | 3-phase fault on REDWILO to MCCOOK 115 kVCircuit 2, near REDWILO. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-3PH-21 | 3-phase fault on KEYSTON 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-3PH-22 | 3-phase fault on KEYSTON to SIDNEY 345 kVCircuit 1, near KEYSTON. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-3PH-23 | 3-phase fault on KEYSTON to GENTLMN 345 kVCircuit 2, near KEYSTON. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-3PH-24 | 3-phase fault on GENTLMN to THEDFRD 345 kVCircuit 1, near GENTLMN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-3PH-25 | 3-phase fault on GENTLMN to SWEET 345 kVCircuit 1, near GENTLMN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-3PH-26 | 3-phase fault on GENTLMN 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-3PH-27 | 3-phase fault on POSTROCK to SPERVIL 345 kVCircuit 1, near POSTROCK. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-3PH-28 | 3-phase fault on POSTROCK to AXTELL 345 kVCircuit 1, near POSTROCK. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-3PH-29 | 3-phase fault on POSTROCK 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-3PH-30 | 3-phase fault on SETAB to SCOTCTY 115 kVCircuit 1, near SETAB. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-3PH-31 | 3-phase fault on SETAB to CNTRLPL 115 kVCircuit 1, near SETAB. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-3PH-32 | 3-phase fault on HOLCOMB to BUCKNER 345 kVCircuit 1, near HOLCOMB. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-3PH-33 | 3-phase fault on HOLCOMB to FINNEY 345 kVCircuit 1, near HOLCOMB. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-3PH-34 | 3-phase fault on HOLCOMB 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-SB-1 | SLG fault on MINGO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Mingo 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-SB-2 | SLG fault on MINGO 115 kV, stuck breaker results delayed clearing after 16 cycles with loss of Mingo 115 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-SB-3 | SLG fault on REDWILO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of REDWILO 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-SB-4 | SLG fault on SETAB 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of SETAB 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-PO-1-2 | Prior Outage of MINGO to REDWILO 345kVCircuit 1, 3-phase fault on Mingo 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-PO-2-2 | Prior Outage of MINGO to SETAB 345kVCircuit 1, 3-phase fault on Mingo 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-PO-3-1 | Prior Outage of Mingo 345/115/13.8 kVTransformer 1, 3-phase fault on Mingo to REDWILO 345 kVCircuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | 013-PO-3-2 | Prior Outage of Mingo 345/115/13.8 kVTransformer 1, 3-phase fault on Mingo to SETAB 345 kVCircuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | TIE-3PH-1 | 3-phase fault on BLACKBERRY to NEOSHO 345 kVCircuit 1, near BLACKBERRY. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | TIE-3PH-2 | 3-phase fault on DELWARE to NEOSHO 345 kVCircuit 1, near DELWARE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | TIE-3PH-3 | 3-phase fault on DGRASSE to THISTLE 345 kVCircuit 1, near DGRASSE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | TIE-3PH-4 | 3-phase fault on CARPENTER to HARBNGR 345 kVCircuit 1, near CARPENTER. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | TIE-3PH-5 | 3-phase fault on FINNEY to HOLCOMB 345 kVCircuit 1, near FINNEY. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | TIE-3PH-6 | 3-phase fault on STRANGER to IATAN 345 kVCircuit 1, near STRANGR. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | TIE-3PH-7 | 3-phase fault on SWISVAL to W.GRDNR 345 kVCircuit 1, near SWISVAL. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | TIE-3PH-8 | 3-phase fault on 87TH to CRAIG 345 kVCircuit 1, near 87TH. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | TIE-3PH-9 | 3-phase fault on BUFFALO to THISTLE 345 kVCircuit 1, near BUFFALO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | TIE-3PH-10 | 3-phase fault on NEOSHO to LACYGNE 345 kVCircuit 1, near NEOSHO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | TIE-3PH-11 | 3-phase fault on ROSEHIL to G15-052T 345 kVCircuit 1, near ROSEHIL. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | TIE-3PH-12 | 3-phase fault on WAVERLY to LACYGNE 345 kVCircuit 1, near LACYGNE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | TIE-SB-1 | SLG fault on HOLCOMB 345 kV, , stuck breaker results delayed clearing after 16 cycles with loss of HOLCOMB 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | TIE-SB-2 | SLG fault on NEOSHO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of NEOSHO 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | TIE-SB-3 | SLG fault on LACYGNE 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of LACYGNE to WAVERLY 345 kVCircuit 1 and LACYGNE to NEOSHO 345 kVCircuit 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | TIE-SB-4 | SLG fault on 87TH 345 Kv, stuck breaker results delayed clearing after 16 cycles with loss of 87TH 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | TIE-SB-5 | SLG fault on W.GRDNR 345 Kv, stuck breaker results delayed clearing after 16 cycles with loss of W.GRDNR 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | TIE-SB-6 | SLG fault on THISTLE 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of THISTLE to BUFFALO 345 kVCircuit 1, THISTLE to CLARKCOUNTY 345 kVCircuit 1 and THISTLE 345/115/13.8 kVtransformer 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | TIE-PO-1-1 | Prior Outage of BLACKBERRY to NEOSHO 345kV Circuit 1, 3-phase fault on WAVERLY to LACYGNE 345 kV Circuit 1, near LACYGNE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | TIE-PO-1-2 | Prior Outage of BLACKBERRY to NEOSHO 345kV Circuit 1, 3-phase fault on 87TH to CRAIG 345 kV Circuit 1, near 87TH. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | TIE-PO-1-3 | Prior Outage of BLACKBERRY to NEOSHO 345kV Circuit 1, 3-phase fault on SWISVAL to W.GRDNR 345 kV Circuit 1, near SWISVAL. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | TIE-PO-2-1 | Prior Outage of WAVERLY to LACYGNE 345kV Circuit 1, 3-phase fault on 87TH to CRAIG 345 kV Circuit 1, near 87TH. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | TIE-PO-2-2 | Prior Outage of WAVERLY to LACYGNE 345kV Circuit 1, 3-phase fault on SWISVAL to W.GRDNR 345 kV Circuit 1, near SWISVAL. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | TIE-PO-2-3 | Prior Outage of WAVERLY to LACYGNE 345kV Circuit 1, 3-phase fault on BLACKBERRY to NEOSHO 345 kV Circuit 1, near BLACKBERRY. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | TIE-PO-3-1 | Prior Outage of 87TH to CRAIG 345kV Circuit 1, 3-phase fault on WAVERLY to LACYGNE 345 kV Circuit 1, near LACYGNE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | TIE-PO-3-2 | Prior Outage of 87TH to CRAIG 345kV Circuit 1, 3-phase fault on SWISVAL to W.GRDNR 345 kV Circuit 1, near SWISVAL. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | TIE-PO-3-3 | Prior Outage of 87TH to CRAIG 345kV Circuit 1, 3-phase fault on BLACKBERRY to NEOSHO 345 kV Circuit 1, near BLACKBERRY. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | TIE-PO-4-1 | Prior Outage of SWISVAL to W.GRDNR 345kV Circuit 1, 3-phase fault on WAVERLY to LACYGNE 345 kV Circuit 1, near LACYGNE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | TIE-PO-4-2 | Prior Outage of SWISVAL to W.GRDNR 345kV Circuit 1, 3-phase fault on 87TH to CRAIG 345 kV Circuit 1, near 87TH. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21L | Transfer | TIE-PO-4-3 | Prior Outage of SWISVAL to W.GRDNR 345kV Circuit 1, 3-phase fault on BLACKBERRY to NEOSHO 345 kV Circuit 1, near BLACKBERRY. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-3PH-1 | 3-phase fault on G17-004-TAP to Summit 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-3PH-2 | 3-phase fault on G17-004-TAP to Elm Creek 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-3PH-3 | 3-phase fault on Summit to Geary 345 kVCircuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-3PH-4 | 3-phase fault on Summit - G16-112-TAP 345 kVCircuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-3PH-5 | 3-phase fault on Summit 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-3PH-6 | 3-phase fault on Summit to SMOKYHL 230 kVCircuit 1, near Summit. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-3PH-7 | 3-phase fault on Summit to EMCPHER 230 kVCircuit 1, near Summit. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-3PH-8 | 3-phase fault on Summit to UNIONRG 230 kVCircuit 1, near Summit. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-3PH-9 | 3-phase fault on Summit 230/115/13.8 kVTransformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-3PH-10 | 3-phase fault on Elm Creek 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-3PH-11 | 3-phase fault on Elm Creek to CONCRD 230 kVCircuit 1, near Elm Creek. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-3PH-12 | 3-phase fault on Elm Creek to NMANHT 230 kVCircuit 1, near Elm Creek. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-3PH-13 | 3-phase fault on Elm Creek to MRWYP 230 kVCircuit 1, near Elm Creek. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-3PH-14 | 3-phase fault on Reno to WICHITA 345 kVCircuit 1, near Reno. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-3PH-15 | 3-phase fault on Reno 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-3PH-16 | 3-phase fault on Geary to JEC N 345kVCircuit 1, near Geary. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-3PH-17 | 3-phase fault on Geary 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-3PH-18 | 3-phase fault on CONCRD 230/115/13.8 kVTransformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-3PH-19 | 3-phase fault on NMANHT 230/115/13.8 kVTransformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-3PH-20 | 3-phase fault on NMANHT to EMANHAT 230 kVCircuit 1, near NMANHT. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-3PH-21 | 3-phase fault on RENO to MOUNDRG 115 kVCircuit 1, near RENO. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-3PH-22 | 3-phase fault on WICHITA to BENTON 345kVCircuit 1, near WICHITA. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-3PH-23 | 3-phase fault on WICHITA to BUFFALO 345kVCircuit 2, near WICHITA. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-3PH-24 | 3-phase fault on WICHITA 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-3PH-27 | 3-phase fault on JEC N 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No
North | 04 - Northwest Kansas | 21S | Transfer | 004-3PH-28 | 3-phase fault on UNIONRG to MORRIS 230 kVCircuit 1, near UNIONRG. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No
North | 04 - Northwest Kansas | 21S | Transfer | 004-SB-1 | SLG fault on G17-004-TAP 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of G17-004-TAP 345 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | No
North | 04 - Northwest Kansas | 21S | Transfer | 004-SB-2 | SLG fault on Summit 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Summit 345 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | No
North | 04 - Northwest Kansas | 21S | Transfer | 004-SB-3 | SLG fault on Elk Creek 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Elk Creek 345 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-SB-4 | SLG fault on Summit 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of Summit 230 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-SB-5 | SLG fault on Elk Creek 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of Elk Creek 230 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-SB-6 | SLG fault on Geary 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Geary 345 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-SB-7 | SLG fault on RENO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of RENO 345 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-PO-1-1 | Prior Outage of G17-004-TAP to Summit 345kV Circuit 1, 3-phase fault on Elm Creek 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-PO-1-2 | Prior Outage of G17-004-TAP to Summit 345kV Circuit 1, 3-phase fault on G17-004-TAP to Elm Creek 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-PO-2-1 | Prior Outage of G17-004-TAP to Elm Creek 345kV Circuit 1, 3-phase fault on G17-004-TAP to Summit 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-PO-2-2 | Prior Outage of G17-004-TAP to Elm Creek 345kV Circuit 1, 3-phase fault on Summit to Geary 345 kVCircuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-PO-2-3 | Prior Outage of G17-004-TAP to Elm Creek 345kV Circuit 1, 3-phase fault on Summit - G16-112-TAP - G16-111-TAP - Reno 345 kVCircuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-PO-2-4 | Prior Outage of G17-004-TAP to Elm Creek 345kV Circuit 1, 3-phase fault on Summit 345/230/13.8 kVTransformer 1 | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-PO-3-1 | Prior Outage of SUMMIT to GEARY 345kV Circuit 1, 3-phase fault on G17-004-TAP to Summit 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-PO-3-2 | Prior Outage of SUMMIT to GEARY 345kV Circuit 1, 3-phase fault on G17-004-TAP to ELMCREEK 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-PO-3-3 | Prior Outage of SUMMIT to GEARY 345kVCircuit 1, 3-phase fault on Summit - G16-112-TAP 345 kVCircuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-PO-3-4 | Prior Outage of SUMMIT to GEARY 345kVCircuit 1, 3-phase fault on Summit 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-PO-4-1 | Prior Outage of Summit - G16-112-TAP - G16-111-TAP - Reno 345 kVCircuit 1, 3-phase fault on G17-004-TAP to Summit 345 kV Circuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-PO-4-2 | Prior Outage of Summit - G16-112-TAP - G16-111-TAP - Reno 345 kVCircuit 1, 3-phase fault on G17-004-TAP to ELMCREEK 345 kV Circuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-PO-4-3 | Prior Outage of Summit - G16-112-TAP - G16-111-TAP - Reno 345 kVCircuit 1, 3-phase fault on Summit to Geary 345 kV Circuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 004-PO-4-4 | Prior Outage of Summit - G16-112-TAP - G16-111-TAP - Reno 345 kV Circuit 1, 3-phase fault on Summit 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-3PH-1 | 3-phase fault on Mingo to REDWILO 345 kV Circuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-3PH-2 | 3-phase fault on Mingo to SETAB 345 kV Circuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-3PH-3 | 3-phase fault on Mingo 345/115/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-3PH-4 | 3-phase fault on Mingo to COLBY 115 kVCircuit 1, near Mingo. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-3PH-5 | 3-phase fault on Mingo to PH RUN 115 kVCircuit 1, near Mingo. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-3PH-6 | 3-phase fault on Mingo to BREWSTR 115 kVCircuit 1, near Mingo. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-3PH-7 | 3-phase fault on REDWILO to POSTROCK 345 kVCircuit 1, near REDWILO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-3PH-8 | 3-phase fault on REDWILO to GENTLMN 345 kVCircuit 1, near REDWILO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-3PH-9 | 3-phase fault on REDWILO to KEYSTON 345 kVCircuit 1, near REDWILO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-3PH-10 | 3-phase fault on REDWILO 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-3PH-11 | 3-phase fault on SETAB to HOLCOMB 345 kVCircuit 1, near SETAB. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-3PH-12 | 3-phase fault on SETAB 345/115/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-3PH-13 | 3-phase fault on COLBY to ATWOOD 115 kVCircuit 1, near COLBY. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-3PH-14 | 3-phase fault on COLBY to SEGNTP 115 kVCircuit 1, near COLBY. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-3PH-15 | 3-phase fault on BREWSTR to GOODLND 115 kVCircuit 1, near BREWSTR. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-3PH-16 | 3-phase fault on PH RUN to SEGUIN 115 kVCircuit 1, near PH RUN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-3PH-17 | 3-phase fault on PH RUN to GRINNEL 115 kVCircuit 1, near PH RUN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-3PH-18 | 3-phase fault on REDWILO to BEVERLY 115 kVCircuit 1, near REDWILO. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-3PH-19 | 3-phase fault on REDWILO to STOCKVL 115 kVCircuit 1, near REDWILO. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-3PH-20 | 3-phase fault on REDWILO to MCCOOK 115 kVCircuit 2, near REDWILO. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-3PH-21 | 3-phase fault on KEYSTON 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-3PH-22 | 3-phase fault on KEYSTON to SIDNEY 345 kVCircuit 1, near KEYSTON. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-3PH-23 | 3-phase fault on KEYSTON to GENTLMN 345 kVCircuit 2, near KEYSTON. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-3PH-24 | 3-phase fault on GENTLMN to THEDFRD 345 kVCircuit 1, near GENTLMN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-3PH-25 | 3-phase fault on GENTLMN to SWEET 345 kVCircuit 1, near GENTLMN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-3PH-26 | 3-phase fault on GENTLMN 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-3PH-27 | 3-phase fault on POSTROCK to SPERVIL 345 kVCircuit 1, near POSTROCK. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-3PH-28 | 3-phase fault on POSTROCK to AXTELL 345 kVCircuit 1, near POSTROCK. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-3PH-29 | 3-phase fault on POSTROCK 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-3PH-30 | 3-phase fault on SETAB to SCOTCTY 115 kVCircuit 1, near SETAB. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-3PH-31 | 3-phase fault on SETAB to CNTRLPL 115 kVCircuit 1, near SETAB. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-3PH-32 | 3-phase fault on HOLCOMB to BUCKNER 345 kVCircuit 1, near HOLCOMB. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-3PH-33 | 3-phase fault on HOLCOMB to FINNEY 345 kVCircuit 1, near HOLCOMB. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-3PH-34 | 3-phase fault on HOLCOMB 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-SB-1 | SLG fault on MINGO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Mingo 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-SB-2 | SLG fault on MINGO 115 kV, stuck breaker results delayed clearing after 16 cycles with loss of Mingo 115 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-SB-3 | SLG fault on REDWILO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of REDWILO 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-SB-4 | SLG fault on SETAB 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of SETAB 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-PO-1-2 | Prior Outage of MINGO to REDWILO 345kVCircuit 1, 3-phase fault on Mingo 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-PO-2-2 | Prior Outage of MINGO to SETAB 345kVCircuit 1, 3-phase fault on Mingo 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-PO-3-1 | Prior Outage of Mingo 345/115/13.8 kVTransformer 1, 3-phase fault on Mingo to REDWILO 345 kVCircuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | 013-PO-3-2 | Prior Outage of Mingo 345/115/13.8 kVTransformer 1, 3-phase fault on Mingo to SETAB 345 kVCircuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | TIE-3PH-1 | 3-phase fault on BLACKBERRY to NEOSHO 345 kVCircuit 1, near BLACKBERRY. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | TIE-3PH-2 | 3-phase fault on DELWARE to NEOSHO 345 kVCircuit 1, near DELWARE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | TIE-3PH-3 | 3-phase fault on DGRASSE to THISTLE 345 kVCircuit 1, near DGRASSE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | TIE-3PH-4 | 3-phase fault on CARPENTER to HARBNGR 345 kVCircuit 1, near CARPENTER. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | TIE-3PH-5 | 3-phase fault on FINNEY to HOLCOMB 345 kVCircuit 1, near FINNEY. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | TIE-3PH-6 | 3-phase fault on STRANGER to IATAN 345 kVCircuit 1, near STRANGR. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | TIE-3PH-7 | 3-phase fault on SWISVAL to W.GRDNR 345 kVCircuit 1, near SWISVAL. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | TIE-3PH-8 | 3-phase fault on 87TH to CRAIG 345 kVCircuit 1, near 87TH. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | TIE-3PH-9 | 3-phase fault on BUFFALO to THISTLE 345 kVCircuit 1, near BUFFALO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | TIE-3PH-10 | 3-phase fault on NEOSHO to LACYGNE 345 kVCircuit 1, near NEOSHO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | TIE-3PH-11 | 3-phase fault on ROSEHIL to G15-052T 345 kVCircuit 1, near ROSEHIL. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | TIE-SB-1 | SLG fault on HOLCOMB 345 kV, , stuck breaker results delayed clearing after 16 cycles with loss of HOLCOMB 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | TIE-SB-2 | SLG fault on NEOSHO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of NEOSHO 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | TIE-SB-3 | SLG fault on LACYGNE 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of LACYGNE to WAVERLY 345 kVCircuit 1 and LACYGNE to NEOSHO 345 kVCircuit 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | TIE-SB-4 | SLG fault on 87TH 345 Kv, stuck breaker results delayed clearing after 16 cycles with loss of 87TH 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | TIE-SB-5 | SLG fault on W.GRDNR 345 Kv, stuck breaker results delayed clearing after 16 cycles with loss of W.GRDNR 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | TIE-SB-6 | SLG fault on THISTLE 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of THISTLE to BUFFALO 345 kVCircuit 1, THISTLE to CLARKCOUNTY 345 kVCircuit 1 and THISTLE 345/115/13.8 kVtransformer 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | TIE-PO-1-2 | Prior Outage of BLACKBERRY to NEOSHO 345kV Circuit 1, 3-phase fault on 87TH to CRAIG 345 kV Circuit 1, near 87TH. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | TIE-PO-1-3 | Prior Outage of BLACKBERRY to NEOSHO 345kV Circuit 1, 3-phase fault on SWISVAL to W.GRDNR 345 kV Circuit 1, near SWISVAL. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | TIE-PO-2-1 | Prior Outage of WAVERLY to LACYGNE 345kV Circuit 1, 3-phase fault on 87TH to CRAIG 345 kV Circuit 1, near 87TH. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | TIE-PO-2-2 | Prior Outage of WAVERLY to LACYGNE 345kV Circuit 1, 3-phase fault on SWISVAL to W.GRDNR 345 kV Circuit 1, near SWISVAL. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | TIE-PO-2-3 | Prior Outage of WAVERLY to LACYGNE 345kV Circuit 1, 3-phase fault on BLACKBERRY to NEOSHO 345 kV Circuit 1, near BLACKBERRY. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | TIE-PO-3-2 | Prior Outage of 87TH to CRAIG 345kV Circuit 1, 3-phase fault on SWISVAL to W.GRDNR 345 kV Circuit 1, near SWISVAL. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | TIE-PO-3-3 | Prior Outage of 87TH to CRAIG 345kV Circuit 1, 3-phase fault on BLACKBERRY to NEOSHO 345 kV Circuit 1, near BLACKBERRY. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | TIE-PO-4-2 | Prior Outage of SWISVAL to W.GRDNR 345kV Circuit 1, 3-phase fault on 87TH to CRAIG 345 kV Circuit 1, near 87TH. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 21S | Transfer | TIE-PO-4-3 | Prior Outage of SWISVAL to W.GRDNR 345kV Circuit 1, 3-phase fault on BLACKBERRY to NEOSHO 345 kV Circuit 1, near BLACKBERRY. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-3PH-1 | 3-phase fault on G17-004-TAP to Summit 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-3PH-2 | 3-phase fault on G17-004-TAP to Elm Creek 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-3PH-3 | 3-phase fault on Summit to Geary 345 kVCircuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-3PH-4 | 3-phase fault on Summit - G16-112-TAP 345 kVCircuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-3PH-5 | 3-phase fault on Summit 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-3PH-6 | 3-phase fault on Summit to SMOKYHL 230 kVCircuit 1, near Summit. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-3PH-7 | 3-phase fault on Summit to EMCPHER 230 kVCircuit 1, near Summit. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-3PH-8 | 3-phase fault on Summit to UNIONRG 230 kVCircuit 1, near Summit. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-3PH-9 | 3-phase fault on Summit 230/115/13.8 kVTransformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-3PH-10 | 3-phase fault on Elm Creek 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-3PH-11 | 3-phase fault on Elm Creek to CONCRD 230 kVCircuit 1, near Elm Creek. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-3PH-12 | 3-phase fault on Elm Creek to NMANHT 230 kVCircuit 1, near Elm Creek. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-3PH-13 | 3-phase fault on Elm Creek to MRWYP 230 kVCircuit 1, near Elm Creek. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-3PH-14 | 3-phase fault on Reno to WICHITA 345 kVCircuit 1, near Reno. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-3PH-15 | 3-phase fault on Reno 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-3PH-16 | 3-phase fault on Geary to JEC N 345kVCircuit 1, near Geary. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-3PH-17 | 3-phase fault on Geary 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-3PH-18 | 3-phase fault on CONCRD 230/115/13.8 kVTransformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-3PH-19 | 3-phase fault on NMANHT 230/115/13.8 kVTransformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-3PH-20 | 3-phase fault on NMANHT to EMANHAT 230 kVCircuit 1, near NMANHT. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-3PH-21 | 3-phase fault on RENO to MOUNDRG 115 kVCircuit 1, near RENO. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-3PH-22 | 3-phase fault on WICHITA to BENTON 345kVCircuit 1, near WICHITA. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-3PH-23 | 3-phase fault on WICHITA to BUFFALO 345kVCircuit 2, near WICHITA. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-3PH-24 | 3-phase fault on WICHITA 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-3PH-27 | 3-phase fault on JEC N 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-3PH-28 | 3-phase fault on UNIONRG to MORRIS 230 kVCircuit 1, near UNIONRG. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-SB-1 | SLG fault on G17-004-TAP 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of G17-004-TAP 345 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-SB-2 | SLG fault on Summit 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Summit 345 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-SB-3 | SLG fault on Elk Creek 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Elk Creek 345 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-SB-4 | SLG fault on Summit 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of Summit 230 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-SB-5 | SLG fault on Elk Creek 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of Elk Creek 230 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-SB-6 | SLG fault on Geary 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Geary 345 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-SB-7 | SLG fault on RENO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of RENO 345 kVbus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-PO-1-1 | Prior Outage of G17-004-TAP to Summit 345kV Circuit 1, 3-phase fault on Elm Creek 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-PO-1-2 | Prior Outage of G17-004-TAP to Summit 345kV Circuit 1, 3-phase fault on G17-004-TAP to Elm Creek 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-PO-2-1 | Prior Outage of G17-004-TAP to Elm Creek 345kV Circuit 1, 3-phase fault on G17-004-TAP to Summit 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-PO-2-2 | Prior Outage of G17-004-TAP to Elm Creek 345kV Circuit 1, 3-phase fault on Summit to Geary 345 kVCircuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-PO-2-3 | Prior Outage of G17-004-TAP to Elm Creek 345kV Circuit 1, 3-phase fault on Summit - G16-112-TAP - G16-111-TAP - Reno 345 kVCircuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-PO-2-4 | Prior Outage of G17-004-TAP to Elm Creek 345kV Circuit 1, 3-phase fault on Summit 345/230/13.8 kVTransformer 1 | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-PO-3-1 | Prior Outage of SUMMIT to GEARY 345kV Circuit 1, 3-phase fault on G17-004-TAP to Summit 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-PO-3-2 | Prior Outage of SUMMIT to GEARY 345kV Circuit 1, 3-phase fault on G17-004-TAP to ELMCREEK 345 kVCircuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-PO-3-3 | Prior Outage of SUMMIT to GEARY 345kVCircuit 1, 3-phase fault on Summit - G16-112-TAP 345 kVCircuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-PO-3-4 | Prior Outage of SUMMIT to GEARY 345kVCircuit 1, 3-phase fault on Summit 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-PO-4-1 | Prior Outage of Summit - G16-112-TAP - G16-111-TAP - Reno 345 kVCircuit 1, 3-phase fault on G17-004-TAP to Summit 345 kV Circuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-PO-4-2 | Prior Outage of Summit - G16-112-TAP - G16-111-TAP - Reno 345 kVCircuit 1, 3-phase fault on G17-004-TAP to ELMCREEK 345 kV Circuit 1, near G17-004-TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-PO-4-3 | Prior Outage of Summit - G16-112-TAP - G16-111-TAP - Reno 345 kVCircuit 1, 3-phase fault on Summit to Geary 345 kV Circuit 1, near Summit. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 004-PO-4-4 | Prior Outage of Summit - G16-112-TAP - G16-111-TAP - Reno 345 kV Circuit 1, 3-phase fault on Summit 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-3PH-1 | 3-phase fault on Mingo to REDWILO 345 kV Circuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-3PH-2 | 3-phase fault on Mingo to SETAB 345 kV Circuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-3PH-3 | 3-phase fault on Mingo 345/115/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-3PH-4 | 3-phase fault on Mingo to COLBY 115 kVCircuit 1, near Mingo. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-3PH-5 | 3-phase fault on Mingo to PH RUN 115 kVCircuit 1, near Mingo. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-3PH-6 | 3-phase fault on Mingo to BREWSTR 115 kVCircuit 1, near Mingo. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-3PH-7 | 3-phase fault on REDWILO to POSTROCK 345 kVCircuit 1, near REDWILO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-3PH-8 | 3-phase fault on REDWILO to GENTLMN 345 kVCircuit 1, near REDWILO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-3PH-9 | 3-phase fault on REDWILO to KEYSTON 345 kVCircuit 1, near REDWILO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-3PH-10 | 3-phase fault on REDWILO 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-3PH-11 | 3-phase fault on SETAB to HOLCOMB 345 kVCircuit 1, near SETAB. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-3PH-12 | 3-phase fault on SETAB 345/115/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-3PH-13 | 3-phase fault on COLBY to ATWOOD 115 kVCircuit 1, near COLBY. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-3PH-14 | 3-phase fault on COLBY to SEGNTP 115 kVCircuit 1, near COLBY. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-3PH-15 | 3-phase fault on BREWSTR to GOODLND 115 kVCircuit 1, near BREWSTR. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-3PH-16 | 3-phase fault on PH RUN to SEGUIN 115 kVCircuit 1, near PH RUN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-3PH-17 | 3-phase fault on PH RUN to GRINNEL 115 kVCircuit 1, near PH RUN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-3PH-18 | 3-phase fault on REDWILO to BEVERLY 115 kVCircuit 1, near REDWILO. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-3PH-19 | 3-phase fault on REDWILO to STOCKVL 115 kVCircuit 1, near REDWILO. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-3PH-20 | 3-phase fault on REDWILO to MCCOOK 115 kVCircuit 2, near REDWILO. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-3PH-21 | 3-phase fault on KEYSTON 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-3PH-22 | 3-phase fault on KEYSTON to SIDNEY 345 kVCircuit 1, near KEYSTON. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-3PH-23 | 3-phase fault on KEYSTON to GENTLMN 345 kVCircuit 2, near KEYSTON. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-3PH-24 | 3-phase fault on GENTLMN to THEDFRD 345 kVCircuit 1, near GENTLMN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-3PH-25 | 3-phase fault on GENTLMN to SWEET 345 kVCircuit 1, near GENTLMN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-3PH-26 | 3-phase fault on GENTLMN 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-3PH-27 | 3-phase fault on POSTROCK to SPERVIL 345 kVCircuit 1, near POSTROCK. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-3PH-28 | 3-phase fault on POSTROCK to AXTELL 345 kVCircuit 1, near POSTROCK. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-3PH-29 | 3-phase fault on POSTROCK 345/230/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-3PH-30 | 3-phase fault on SETAB to SCOTCTY 115 kVCircuit 1, near SETAB. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-3PH-31 | 3-phase fault on SETAB to CNTRLPL 115 kVCircuit 1, near SETAB. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-3PH-32 | 3-phase fault on HOLCOMB to BUCKNER 345 kVCircuit 1, near HOLCOMB. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-3PH-33 | 3-phase fault on HOLCOMB to FINNEY 345 kVCircuit 1, near HOLCOMB. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-3PH-34 | 3-phase fault on HOLCOMB 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-SB-1 | SLG fault on MINGO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Mingo 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-SB-2 | SLG fault on MINGO 115 kV, stuck breaker results delayed clearing after 16 cycles with loss of Mingo 115 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-SB-3 | SLG fault on REDWILO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of REDWILO 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-SB-4 | SLG fault on SETAB 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of SETAB 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-PO-1-2 | Prior Outage of MINGO to REDWILO 345kVCircuit 1, 3-phase fault on Mingo 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-PO-2-2 | Prior Outage of MINGO to SETAB 345kVCircuit 1, 3-phase fault on Mingo 345/115/13.8 kVTransformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-PO-3-1 | Prior Outage of Mingo 345/115/13.8 kVTransformer 1, 3-phase fault on Mingo to REDWILO 345 kVCircuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | 013-PO-3-2 | Prior Outage of Mingo 345/115/13.8 kVTransformer 1, 3-phase fault on Mingo to SETAB 345 kVCircuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | TIE-3PH-1 | 3-phase fault on BLACKBERRY to NEOSHO 345 kVCircuit 1, near BLACKBERRY. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | TIE-3PH-2 | 3-phase fault on DELWARE to NEOSHO 345 kVCircuit 1, near DELWARE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | TIE-3PH-3 | 3-phase fault on DGRASSE to THISTLE 345 kVCircuit 1, near DGRASSE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | TIE-3PH-4 | 3-phase fault on CARPENTER to HARBNGR 345 kVCircuit 1, near CARPENTER. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | TIE-3PH-5 | 3-phase fault on FINNEY to HOLCOMB 345 kVCircuit 1, near FINNEY. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | TIE-3PH-6 | 3-phase fault on STRANGER to IATAN 345 kVCircuit 1, near STRANGR. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | TIE-3PH-7 | 3-phase fault on SWISVAL to W.GRDNR 345 kVCircuit 1, near SWISVAL. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | TIE-3PH-8 | 3-phase fault on 87TH to CRAIG 345 kVCircuit 1, near 87TH. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | TIE-3PH-9 | 3-phase fault on BUFFALO to THISTLE 345 kVCircuit 1, near BUFFALO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | TIE-3PH-10 | 3-phase fault on NEOSHO to LACYGNE 345 kVCircuit 1, near NEOSHO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | TIE-3PH-11 | 3-phase fault on ROSEHIL to G15-052T 345 kVCircuit 1, near ROSEHIL. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | TIE-SB-1 | SLG fault on HOLCOMB 345 kV, , stuck breaker results delayed clearing after 16 cycles with loss of HOLCOMB 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | TIE-SB-2 | SLG fault on NEOSHO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of NEOSHO 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | TIE-SB-3 | SLG fault on LACYGNE 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of LACYGNE to WAVERLY 345 kVCircuit 1 and LACYGNE to NEOSHO 345 kVCircuit 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | TIE-SB-4 | SLG fault on 87TH 345 Kv, stuck breaker results delayed clearing after 16 cycles with loss of 87TH 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | TIE-SB-5 | SLG fault on W.GRDNR 345 Kv, stuck breaker results delayed clearing after 16 cycles with loss of W.GRDNR 345 kVbus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | TIE-SB-6 | SLG fault on THISTLE 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of THISTLE to BUFFALO 345 kVCircuit 1, THISTLE to CLARKCOUNTY 345 kVCircuit 1 and THISTLE 345/115/13.8 kVtransformer 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | TIE-PO-1-2 | Prior Outage of BLACKBERRY to NEOSHO 345kV Circuit 1, 3-phase fault on 87TH to CRAIG 345 kV Circuit 1, near 87TH. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | TIE-PO-1-3 | Prior Outage of BLACKBERRY to NEOSHO 345kV Circuit 1, 3-phase fault on SWISVAL to W.GRDNR 345 kV Circuit 1, near SWISVAL. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | TIE-PO-2-1 | Prior Outage of WAVERLY to LACYGNE 345kV Circuit 1, 3-phase fault on 87TH to CRAIG 345 kV Circuit 1, near 87TH. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | TIE-PO-2-2 | Prior Outage of WAVERLY to LACYGNE 345kV Circuit 1, 3-phase fault on SWISVAL to W.GRDNR 345 kV Circuit 1, near SWISVAL. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | TIE-PO-2-3 | Prior Outage of WAVERLY to LACYGNE 345kV Circuit 1, 3-phase fault on BLACKBERRY to NEOSHO 345 kV Circuit 1, near BLACKBERRY. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | TIE-PO-3-2 | Prior Outage of 87TH to CRAIG 345kV Circuit 1, 3-phase fault on SWISVAL to W.GRDNR 345 kV Circuit 1, near SWISVAL. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | TIE-PO-3-3 | Prior Outage of 87TH to CRAIG 345kV Circuit 1, 3-phase fault on BLACKBERRY to NEOSHO 345 kV Circuit 1, near BLACKBERRY. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | TIE-PO-4-2 | Prior Outage of SWISVAL to W.GRDNR 345kV Circuit 1, 3-phase fault on 87TH to CRAIG 345 kV Circuit 1, near 87TH. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 28S | Transfer | TIE-PO-4-3 | Prior Outage of SWISVAL to W.GRDNR 345kV Circuit 1, 3-phase fault on BLACKBERRY to NEOSHO 345 kV Circuit 1, near BLACKBERRY. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-01 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-02 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-03 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-04 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-05 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-06 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-07 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-08 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-09 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-10 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-11 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-12 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-13 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-14 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-15 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-16 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-17 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-18 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-19 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-20 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-21 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-22 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-23 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-SLG-24 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-SLG-25 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-SLG-26 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-SLG-27 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-SLG-28 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-SLG-29 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-SLG-30 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-SLG-31 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-SLG-32 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-SLG-33 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-SLG-34 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-SLG-35 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-37 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-38 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-39 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-41 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-42 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-43 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-44 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-45 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-46 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-47 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-48 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-49 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-50 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-51 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-52 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-53 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-54 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-55 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-01 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-02 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-03 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-04 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-05 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-06 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-07 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-08 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-09 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-10 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-11 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-12 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-13 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-14 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-15 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-16 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-17 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-18 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-19 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-20 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-21 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-22 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-23 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-SLG-24 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-SLG-25 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-SLG-26 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-SLG-27 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-SLG-28 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-SLG-29 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-SLG-30 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-SLG-31 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-SLG-32 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-SLG-33 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-SLG-34 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-SLG-35 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-37 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-38 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-39 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-41 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-42 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-43 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-44 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-45 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-46 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-47 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-48 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-49 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-50 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-51 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-52 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-53 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-54 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-55 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-01 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-02 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-03 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-04 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-05 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-06 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-07 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-08 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-09 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-10 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-11 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-12 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-13 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-14 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-15 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-16 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-17 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-18 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-19 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-20 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-21 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-22 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-23 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-SLG-24 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-SLG-25 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-SLG-26 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-SLG-27 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-SLG-28 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-SLG-29 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-SLG-30 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-SLG-31 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-SLG-32 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-SLG-33 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-SLG-34 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-SLG-35 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-37 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-38 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-39 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-41 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-42 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-43 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-44 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-45 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-46 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-47 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-48 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-49 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-50 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-51 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-52 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-53 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-54 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-55 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-01 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-02 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-03 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-04 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-05 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-06 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-07 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-08 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-09 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-10 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-11 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-12 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-13 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-14 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-15 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-16 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-17 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-18 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-19 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-20 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-21 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-22 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-23 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-SLG-24 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-SLG-25 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-SLG-26 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-SLG-27 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-SLG-28 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-SLG-29 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-SLG-30 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-SLG-31 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-SLG-32 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-SLG-33 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-SLG-34 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-SLG-35 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-37 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-38 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-39 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-41 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-42 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-43 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-44 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-45 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-46 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-47 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-48 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-49 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-50 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-51 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-52 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-53 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-54 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-55 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-008-3ph-01 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-008-3ph-02 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-008-3ph-03 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-008-3ph-04 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-008-3ph-05 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-008-3ph-06 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-008-3ph-07 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-008-3ph-08 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-008-3ph-09 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-008-3ph-10 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-008-3ph-11 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-008-3ph-12 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-008-3ph-13 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-008-3ph-14 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-008-3ph-15 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-008-SLG-16 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-008-SLG-17 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-008-SLG-18 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-008-SLG-19 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-008-SLG-20 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-008-SLG-21 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-008-SLG-22 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-008-SLG-23 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-008-3ph-24 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-008-3ph-25 | Prior Outage of Pauline to G15-088-TAP 345kV crt 1. 3-phase fault on Pauline 345/115/13.8kV Transformer T1, near Pauline 345kV. Clear fault after 6 cycles | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-008-3ph-26 | Prior Outage of Pauline to AXTELL 345kV crt 1. 3-ph fault on Pauline to G15-088-TAP 345kV crt 1, near Pauline. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-008-3ph-27 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-008-3ph-28 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-008-3ph-29 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-008-3ph-30 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-008-3ph-31 | Prior Outage of G15-088-TAP to Moore 345kV crt 1. 3-ph fault on Pauline to AXTELL 345kV crt 1, near Pauline. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | LVRT VIOL - (G17-008 over voltage trip). After fault cleared, the Pauline area turned very weak, the power interaction between G15-088 and G17-008 caused generator trip. | Curtail G17-008 and G15-088 by 50% of their maximum capacity post outage of G15-088 Tap – Moore. in anticipation of contingencies in the system.
North | 09 - Nebraska | 19W | Transfer | G17-008-3ph-32 | Prior Outage of G15-088-TAP to Moore 345kV crt 1. 3-ph fault on Pauline 345/115/13.8kV TF T1, near Pauline 345kV. Clear fault after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | LVRT VIOL - (G17-008 over voltage trip). After fault cleared, the Pauline area turned very weak, the power interaction between G15-088 and G17-008 caused generator trip. | Curtail G17-008 and G15-088 by 50% of their maximum capacity post outage of G15-088 Tap – Moore. in anticipation of contingencies in the system.
North | 09 - Nebraska | 21S | Transfer | G17-008-3ph-01 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-008-3ph-02 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-008-3ph-03 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-008-3ph-04 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-008-3ph-05 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-008-3ph-06 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-008-3ph-07 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-008-3ph-08 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-008-3ph-09 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-008-3ph-10 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-008-3ph-11 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-008-3ph-12 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-008-3ph-13 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-008-3ph-14 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-008-3ph-15 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-008-SLG-16 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-008-SLG-17 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-008-SLG-18 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-008-SLG-19 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-008-SLG-20 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-008-SLG-21 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-008-SLG-22 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-008-SLG-23 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-008-3ph-24 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-008-3ph-25 | Prior Outage of Pauline to G15-088-TAP 345kV crt 1. 3-phase fault on Pauline 345/115/13.8kV Transformer T1, near Pauline 345kV. Clear fault after 6 cycles | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-008-3ph-26 | Prior Outage of Pauline to AXTELL 345kV crt 1. 3-ph fault on Pauline to G15-088-TAP 345kV crt 1, near Pauline. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-008-3ph-27 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-008-3ph-28 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-008-3ph-29 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-008-3ph-30 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-008-3ph-31 | Prior Outage of G15-088-TAP to Moore 345kV crt 1. 3-ph fault on Pauline to AXTELL 345kV crt 1, near Pauline. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | LVRT VIOL - (G17-008, G15-088 over voltage trip). After fault cleared, the Pauline station turned very weak, the power interaction between G15-088 and G17-008 caused generator trip. | Curtail G17-008 and G15-088 by 50% of their maximum capacity post outage of G15-088 Tap – Moore. in anticipation of contingencies in the system.
North | 09 - Nebraska | 21L | Transfer | G17-008-3ph-01 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-008-3ph-02 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-008-3ph-03 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-008-3ph-04 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-008-3ph-05 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-008-3ph-06 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-008-3ph-07 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-008-3ph-08 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-008-3ph-09 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-008-3ph-10 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-008-3ph-11 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-008-3ph-12 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-008-3ph-13 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-008-3ph-14 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-008-3ph-15 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-008-SLG-16 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-008-SLG-17 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-008-SLG-18 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-008-SLG-19 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-008-SLG-20 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-008-SLG-21 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-008-SLG-22 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-008-SLG-23 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-008-3ph-24 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-008-3ph-25 | Prior Outage of Pauline to G15-088-TAP 345kV crt 1. 3-phase fault on Pauline 345/115/13.8kV Transformer T1, near Pauline 345kV. Clear fault after 6 cycles | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-008-3ph-26 | Prior Outage of Pauline to AXTELL 345kV crt 1. 3-ph fault on Pauline to G15-088-TAP 345kV crt 1, near Pauline. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-008-3ph-27 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-008-3ph-28 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-008-3ph-29 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-008-3ph-30 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-008-3ph-31 | Prior Outage of G15-088-TAP to Moore 345kV crt 1. 3-ph fault on Pauline to AXTELL 345kV crt 1, near Pauline. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | LVRT VIOL - (G17-008, G15-088 over voltage trip). After fault cleared, the Pauline area turned very weak, the power interaction between G15-088 and G17-008 caused generator trip. | Curtail G17-008 and G15-088 by 50% of their maximum capacity post outage of G15-088 Tap – Moore. in anticipation of contingencies in the system.
North | 09 - Nebraska | 21L | Transfer | G17-008-3ph-32 | Prior Outage of G15-088-TAP to Moore 345kV crt 1. 3-ph fault on Pauline 345/115/13.8kV TF T1, near Pauline 345kV. Clear fault after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | LVRT VIOL - (G17-008 over voltage trip). After fault cleared, the Pauline area turned very weak, the power interaction between G15-088 and G17-008 caused generator trip. | Curtail G17-008 and G15-088 by 50% of their maximum capacity post outage of G15-088 Tap – Moore. in anticipation of contingencies in the system.
North | 09 - Nebraska | 28S | Transfer | G17-008-3ph-01 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-008-3ph-02 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-008-3ph-03 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-008-3ph-04 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-008-3ph-05 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-008-3ph-06 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-008-3ph-07 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-008-3ph-08 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-008-3ph-09 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-008-3ph-10 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-008-3ph-11 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-008-3ph-12 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-008-3ph-13 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-008-3ph-14 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-008-3ph-15 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-008-SLG-16 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-008-SLG-17 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-008-SLG-18 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-008-SLG-19 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-008-SLG-20 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-008-SLG-21 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-008-SLG-22 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-008-SLG-23 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-008-3ph-24 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-008-3ph-25 | Prior Outage of Pauline to G15-088-TAP 345kV crt 1. 3-phase fault on Pauline 345/115/13.8kV Transformer T1, near Pauline 345kV. Clear fault after 6 cycles | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-008-3ph-26 | Prior Outage of Pauline to AXTELL 345kV crt 1. 3-ph fault on Pauline to G15-088-TAP 345kV crt 1, near Pauline. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-008-3ph-27 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-008-3ph-28 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-008-3ph-29 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-008-3ph-30 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-008-3ph-31 | Prior Outage of G15-088-TAP to Moore 345kV crt 1. 3-ph fault on Pauline to AXTELL 345kV crt 1, near Pauline. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | LVRT VIOL - (G17-008, G15-088 over voltage trip). After fault cleared, the Pauline area turned very weak, the power interaction between G15-088 and G17-008 caused generator trip. | Curtail G17-008 and G15-088 by 50% of their maximum capacity post outage of G15-088 Tap – Moore. in anticipation of contingencies in the system.
North | 09 - Nebraska | 19W | Transfer | G17-031-3ph-01 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-031-3ph-02 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-031-3ph-03 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-031-3ph-04 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-031-3ph-05 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-031-3ph-06 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-031-3ph-07 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-031-3ph-08 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-031-3ph-09 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-031-3ph-10 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-031-3ph-11 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-031-3ph-12 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-031-3ph-13 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-031-3ph-14 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-031-3ph-15 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-031-3ph-16 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-031-3ph-17 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-031-3ph-18 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-031-3ph-19 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-031-SLG-20 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-031-SLG-21 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-031-SLG-22 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-031-SLG-23 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-031-SLG-24 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-031-SLG-25 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-031-SLG-26 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-031-SLG-27 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-031-SLG-28 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-031-SLG-29 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-031-SLG-30 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-031-SLG-31 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-031-SLG-32 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-031-3ph-33 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-031-3ph-34 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-031-3ph-35 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-031-3ph-36 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-031-3ph-01 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-031-3ph-02 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-031-3ph-03 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-031-3ph-04 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-031-3ph-05 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-031-3ph-06 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-031-3ph-07 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-031-3ph-08 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-031-3ph-09 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-031-3ph-10 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-031-3ph-11 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-031-3ph-12 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-031-3ph-13 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-031-3ph-14 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-031-3ph-15 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-031-3ph-16 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-031-3ph-17 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-031-3ph-18 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-031-3ph-19 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-031-SLG-20 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-031-SLG-21 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-031-SLG-22 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-031-SLG-23 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-031-SLG-24 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-031-SLG-25 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-031-SLG-26 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-031-SLG-27 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-031-SLG-28 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-031-SLG-29 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-031-SLG-30 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-031-SLG-31 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-031-SLG-32 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-031-3ph-33 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-031-3ph-34 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-031-3ph-35 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-031-3ph-36 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-031-3ph-01 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-031-3ph-02 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-031-3ph-03 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-031-3ph-04 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-031-3ph-05 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-031-3ph-06 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-031-3ph-07 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-031-3ph-08 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-031-3ph-09 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-031-3ph-10 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-031-3ph-11 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-031-3ph-12 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-031-3ph-13 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-031-3ph-14 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-031-3ph-15 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-031-3ph-16 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-031-3ph-17 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-031-3ph-18 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-031-3ph-19 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-031-SLG-20 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-031-SLG-21 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-031-SLG-22 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-031-SLG-23 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-031-SLG-24 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-031-SLG-25 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-031-SLG-26 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-031-SLG-27 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-031-SLG-28 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-031-SLG-29 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-031-SLG-30 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-031-SLG-31 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-031-SLG-32 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-031-3ph-33 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-031-3ph-34 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-031-3ph-35 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-031-3ph-36 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-031-3ph-01 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-031-3ph-02 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-031-3ph-03 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-031-3ph-04 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-031-3ph-05 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-031-3ph-06 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-031-3ph-07 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-031-3ph-08 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-031-3ph-09 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-031-3ph-10 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-031-3ph-11 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-031-3ph-12 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-031-3ph-13 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-031-3ph-14 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-031-3ph-15 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-031-3ph-16 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-031-3ph-17 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-031-3ph-18 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-031-3ph-19 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-031-SLG-20 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-031-SLG-21 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-031-SLG-22 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-031-SLG-23 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-031-SLG-24 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-031-SLG-25 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-031-SLG-26 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-031-SLG-27 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-031-SLG-28 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-031-SLG-29 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-031-SLG-30 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-031-SLG-31 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-031-SLG-32 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-031-3ph-33 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-031-3ph-34 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-031-3ph-35 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-031-3ph-36 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-01 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-02 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-03 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-04 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-05 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-06 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-07 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-08 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-09 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-10 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-11 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-12 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-13 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-14 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-15 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-16 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-17 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-18 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-19 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-20 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-21 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-22 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-23 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-24 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-25 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-26 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-27 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-28 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-29 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-30 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-31 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-32 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-33 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-SLG-34 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-SLG-35 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-SLG-36 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-SLG-37 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-SLG-38 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-SLG-39 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-SLG-40 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-SLG-41 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-SLG-42 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-SLG-43 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-SLG-44 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-SLG-45 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-SLG-46 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-SLG-47 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-SLG-48 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-SLG-49 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-SLG-50 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-SLG-51 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-SLG-52 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-53 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-54 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-55 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-56 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-57 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-58 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-59 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-60 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-61 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-62 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-63 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-64 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-055-3ph-65 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-01 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-02 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-03 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-04 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-05 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-06 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-07 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-08 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-09 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-10 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-11 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-12 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-13 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-14 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-15 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-16 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-17 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-18 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-19 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-20 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-21 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-22 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-23 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-24 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-25 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-26 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-27 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-28 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-29 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-30 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-31 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-32 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-33 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-SLG-34 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-SLG-35 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-SLG-36 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-SLG-37 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-SLG-38 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-SLG-39 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-SLG-40 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-SLG-41 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-SLG-42 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-SLG-43 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-SLG-44 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-SLG-45 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-SLG-46 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-SLG-47 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-SLG-48 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-SLG-49 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-SLG-50 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-SLG-51 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-SLG-52 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-53 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-54 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-55 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-56 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-57 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-58 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-59 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-60 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-61 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-62 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-63 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-64 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-055-3ph-65 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-01 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-02 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-03 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-04 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-05 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-06 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-07 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-08 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-09 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-10 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-11 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-12 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-13 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-14 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-15 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-16 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-17 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-18 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-19 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-20 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-21 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-22 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-23 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-24 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-25 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-26 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-27 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-28 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-29 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-30 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-31 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-32 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-33 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-SLG-34 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-SLG-35 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-SLG-36 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-SLG-37 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-SLG-38 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-SLG-39 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-SLG-40 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-SLG-41 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-SLG-42 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-SLG-43 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-SLG-44 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-SLG-45 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-SLG-46 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-SLG-47 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-SLG-48 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-SLG-49 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-SLG-50 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-SLG-51 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-SLG-52 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-53 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-54 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-55 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-56 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-57 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-58 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-59 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-60 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-61 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-62 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-63 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-64 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-055-3ph-65 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-01 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-02 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-03 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-04 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-05 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-06 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-07 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-08 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-09 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-10 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-11 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-12 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-13 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-14 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-15 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-16 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-17 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-18 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-19 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-20 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-21 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-22 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-23 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-24 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-25 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-26 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-27 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-28 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-29 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-30 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-31 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-32 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-33 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-SLG-34 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-SLG-35 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-SLG-36 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-SLG-37 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-SLG-38 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-SLG-39 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-SLG-40 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-SLG-41 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-SLG-42 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-SLG-43 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-SLG-44 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-SLG-45 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-SLG-46 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-SLG-47 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-SLG-48 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-SLG-49 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-SLG-50 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-SLG-51 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-SLG-52 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-53 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-54 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-55 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-56 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-57 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-58 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-59 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-60 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-61 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-62 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-63 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-64 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-055-3ph-65 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-085-3ph-01 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-085-3ph-02 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-085-3ph-03 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-085-3ph-04 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-085-3ph-05 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-085-3ph-06 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-085-3ph-07 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-085-3ph-08 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-085-3ph-09 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-085-3ph-10 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-085-3ph-11 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-085-3ph-12 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-085-3ph-13 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-085-3ph-14 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-085-SLG-15 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-085-SLG-16 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-085-SLG-17 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-085-SLG-18 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-085-SLG-19 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-085-SLG-20 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-085-SLG-21 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-085-SLG-22 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-085-3ph-23 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-085-3ph-24 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-085-3ph-25 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | G17-085-3ph-26 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-085-3ph-01 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-085-3ph-02 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-085-3ph-03 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-085-3ph-04 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-085-3ph-05 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-085-3ph-06 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-085-3ph-07 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-085-3ph-08 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-085-3ph-09 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-085-3ph-10 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-085-3ph-11 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-085-3ph-12 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-085-3ph-13 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-085-3ph-14 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-085-SLG-15 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-085-SLG-16 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-085-SLG-17 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-085-SLG-18 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-085-SLG-19 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-085-SLG-20 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-085-SLG-21 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-085-SLG-22 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-085-3ph-23 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | G17-085-3ph-24 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-085-3ph-01 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-085-3ph-02 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-085-3ph-03 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-085-3ph-04 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-085-3ph-05 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-085-3ph-06 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-085-3ph-07 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-085-3ph-08 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-085-3ph-09 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-085-3ph-10 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-085-3ph-11 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-085-3ph-12 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-085-3ph-13 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-085-3ph-14 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-085-SLG-15 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-085-SLG-16 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-085-SLG-17 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-085-SLG-18 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-085-SLG-19 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-085-SLG-20 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-085-SLG-21 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-085-SLG-22 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-085-3ph-23 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-085-3ph-24 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-085-3ph-25 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | G17-085-3ph-26 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-085-3ph-01 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-085-3ph-02 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-085-3ph-03 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-085-3ph-04 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-085-3ph-05 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-085-3ph-06 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-085-3ph-07 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-085-3ph-08 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-085-3ph-09 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-085-3ph-10 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-085-3ph-11 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-085-3ph-12 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-085-3ph-13 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-085-3ph-14 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-085-SLG-15 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-085-SLG-16 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-085-SLG-17 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-085-SLG-18 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-085-SLG-19 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-085-SLG-20 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-085-SLG-21 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-085-SLG-22 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-085-3ph-23 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-085-3ph-24 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-085-3ph-25 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | G17-085-3ph-26 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | Tie-3ph-01 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | Tie-3ph-02 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | Tie-3ph-03 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | Tie-3ph-04 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | Tie-3ph-05 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | Tie-3ph-06 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | Tie-3ph-07 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | Tie-3ph-08 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | Tie-3ph-09 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | Tie-3ph-10 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | Tie-3ph-11 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | Tie-3ph-12 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | Tie-3ph-13 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | Tie-3ph-14 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | Tie-3ph-15 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | Tie-3ph-16 | 3-ph fault on GRPRAR2-LNX3 to FTTHOM2-LNX3 345kV crt 1, near GRPRAR2-LNX3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | Tie-3ph-17 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | Tie-SLG-18 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | Tie-SLG-19 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | Tie-SLG-20 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | Tie-SLG-21 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | Tie-SLG-22 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | Tie-SLG-23 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | Tie-SLG-24 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | Tie-SLG-25 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | Tie-SLG-26 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | Tie-SLG-27 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | Tie-SLG-28 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | Tie-SLG-29 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | Tie-SLG-30 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | Tie-3ph-31 | Prior Outage of COOPER to ST JOE 345kV crt 1. 3-ph fault on COOPER to 7FAIRPT 345kV crt 1. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | Tie-3ph-32 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | Tie-3ph-33 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | Tie-3ph-34 | Prior Outage of COOPER to 7FAIRPT 345kV crt 1. 3-ph fault on COOPER to ST JOE 345kV crt 1. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | Tie-3ph-35 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | Tie-3ph-36 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | Tie-3ph-37 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | Tie-3ph-38 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Transfer | Tie-3ph-39 | Outage of MEADOWGROVE to FTRANDL4 230kV crt 1. 3-ph fault on GRPRAR2-LNX3 to FTTHOM2-LNX3 345kV crt 1, near GRPRAR2-LNX3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | Tie-3ph-01 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | Tie-3ph-02 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | Tie-3ph-03 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | Tie-3ph-04 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | Tie-3ph-05 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | Tie-3ph-06 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | Tie-3ph-07 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | Tie-3ph-08 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | Tie-3ph-09 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | Tie-3ph-10 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | Tie-3ph-11 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | Tie-3ph-12 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | Tie-3ph-13 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | Tie-3ph-14 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | Tie-3ph-15 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | Tie-3ph-16 | 3-ph fault on GRPRAR2-LNX3 to FTTHOM2-LNX3 345kV crt 1, near GRPRAR2-LNX3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | Tie-3ph-17 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | Tie-SLG-18 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | Tie-SLG-19 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | Tie-SLG-20 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | Tie-SLG-21 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | Tie-SLG-22 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | Tie-SLG-23 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | Tie-SLG-24 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | Tie-SLG-25 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | Tie-SLG-26 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | Tie-SLG-27 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | Tie-SLG-28 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | Tie-SLG-29 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | Tie-SLG-30 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | Tie-3ph-31 | Prior Outage of COOPER to ST JOE 345kV crt 1. 3-ph fault on COOPER to 7FAIRPT 345kV crt 1. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | Tie-3ph-32 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | Tie-3ph-33 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | Tie-3ph-34 | Prior Outage of COOPER to 7FAIRPT 345kV crt 1. 3-ph fault on COOPER to ST JOE 345kV crt 1. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | Tie-3ph-35 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | Tie-3ph-36 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | Tie-3ph-37 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | Tie-3ph-38 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Transfer | Tie-3ph-39 | Outage of MEADOWGROVE to FTRANDL4 230kV crt 1. 3-ph fault on GRPRAR2-LNX3 to FTTHOM2-LNX3 345kV crt 1, near GRPRAR2-LNX3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | Tie-3ph-01 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | Tie-3ph-02 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | Tie-3ph-03 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | Tie-3ph-04 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | Tie-3ph-05 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | Tie-3ph-06 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | Tie-3ph-07 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | Tie-3ph-08 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | Tie-3ph-09 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | Tie-3ph-10 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | Tie-3ph-11 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | Tie-3ph-12 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | Tie-3ph-13 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | Tie-3ph-14 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | Tie-3ph-15 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | Tie-3ph-16 | 3-ph fault on GRPRAR2-LNX3 to FTTHOM2-LNX3 345kV crt 1, near GRPRAR2-LNX3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | Tie-3ph-17 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | Tie-SLG-18 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | Tie-SLG-19 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | Tie-SLG-20 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | Tie-SLG-21 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | Tie-SLG-22 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | Tie-SLG-23 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | Tie-SLG-24 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | Tie-SLG-25 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | Tie-SLG-26 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | Tie-SLG-27 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | Tie-SLG-28 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | Tie-SLG-29 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | Tie-SLG-30 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | Tie-3ph-31 | Prior Outage of COOPER to ST JOE 345kV crt 1. 3-ph fault on COOPER to 7FAIRPT 345kV crt 1. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | Yes | Yes | No | Yes | Yes | Yes | Outflow power transferred to tie line Red Willow - Mingo, caused overload and low voltage issue. Generator Gentleman lost its stability. | Remove high speed reclose
North | 09 - Nebraska | 21L | Transfer | Tie-3ph-32 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | Tie-3ph-33 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | Tie-3ph-34 | Prior Outage of COOPER to 7FAIRPT 345kV crt 1. 3-ph fault on COOPER to ST JOE 345kV crt 1. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | Yes | Yes | No | Yes | Yes | Yes | Outflow power tranfered to tie line Red Willow - Mingo, caused overload and low voltage issue. Generator Gentleman lost its stability. | Remove high speed reclose
North | 09 - Nebraska | 21L | Transfer | Tie-3ph-35 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | Tie-3ph-36 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | Tie-3ph-37 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | Tie-3ph-38 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L | Transfer | Tie-3ph-39 | Outage of MEADOWGROVE to FTRANDL4 230kV crt 1. 3-ph fault on GRPRAR2-LNX3 to FTTHOM2-LNX3 345kV crt 1, near GRPRAR2-LNX3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | Tie-3ph-01 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | Tie-3ph-02 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | Tie-3ph-03 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | Tie-3ph-04 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | Tie-3ph-05 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | Tie-3ph-06 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | Tie-3ph-07 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | Tie-3ph-08 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | Tie-3ph-09 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | Tie-3ph-10 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | Tie-3ph-11 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | Tie-3ph-12 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | Tie-3ph-13 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | Tie-3ph-14 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | Tie-3ph-15 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | Tie-3ph-16 | 3-ph fault on GRPRAR2-LNX3 to FTTHOM2-LNX3 345kV crt 1, near GRPRAR2-LNX3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | Tie-3ph-17 |  | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | Tie-SLG-18 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | Tie-SLG-19 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | Tie-SLG-20 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | Tie-SLG-21 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | Tie-SLG-22 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | Tie-SLG-23 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | Tie-SLG-24 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | Tie-SLG-25 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | Tie-SLG-26 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | Tie-SLG-27 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | Tie-SLG-28 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | Tie-SLG-29 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | Tie-SLG-30 |  | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | Tie-3ph-31 | Prior Outage of COOPER to ST JOE 345kV crt 1. 3-ph fault on COOPER to 7FAIRPT 345kV crt 1. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | Tie-3ph-32 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | Tie-3ph-33 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | Tie-3ph-34 | Prior Outage of COOPER to 7FAIRPT 345kV crt 1. 3-ph fault on COOPER to ST JOE 345kV crt 1. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | Tie-3ph-35 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | Tie-3ph-36 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | Tie-3ph-37 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | Tie-3ph-38 |  | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Transfer | Tie-3ph-39 | Outage of MEADOWGROVE to FTRANDL4 230kV crt 1. 3-ph fault on GRPRAR2-LNX3 to FTTHOM2-LNX3 345kV crt 1, near GRPRAR2-LNX3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-1 | 3-phase fault on G16-017_TAP to Leland Olds 345kV Circuit 1, near G16-017_TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-2 | 3-phase fault on Leland Olds to Antelope 345kV Circuit 2, near Leland Olds. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-3 | 3-phase fault on Leland Olds to Groton 345kV Circuit 1, near Leland Olds. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-4 | 3-phase fault on Leland Olds 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-5 | 3-phase fault on Fort Thompson to Grand Prairie 345kV Circuit 1, near Fort Thompson. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-6 | 3-phase fault on Fort Thompson 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-7 | 3-phase fault on Antelope to ROUNDUP 345kV Circuit 2, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-8 | 3-phase fault on Antelope to CHARL_CK 345kV Circuit 1, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-9 | 3-phase fault on Antelope to Broadland 345kV Circuit 1, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-10 | 3-phase fault on Leland Olds to Logan 230kV Circuit 1, near Leland. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-11 | 3-phase fault on Leland Olds to Garrison 230kV Circuit 1, near Leland. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-12 | 3-phase fault on Leland Olds to WASHBRN 230kV Circuit 1, near Leland. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-13 | 3-phase fault on Leland Olds to GRE-STANTON 230kV Circuit 1, near Leland. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-14 | 3-phase fault on BASIN 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-15 | 3-phase fault on Groton to G09_001IST 345kV Circuit 1, near Groton. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-16 | 3-phase fault on Groton 345/115/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-17 | 3-phase fault on Fort Thompson to BIGBND 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-18 | 3-phase fault on Fort Thompson to LETCHER 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-19 | 3-phase fault on Fort Thompson to FTRANDL 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-20 | 3-phase fault on Fort Thompson to LAKPLAT 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-21 | 3-phase fault on Fort Thompson to OAHE 230kV Circuit 3, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-22 | 3-phase fault on Grand Prairie to Holt Co. 345kV Circuit 1, near Grand Prairie. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-23 | 3-phase fault on Grand Prairie to GRPR1 345kV Circuit 1, near Grand Prairie. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-24 | 3-phase fault on ROUNDUP 345/115/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-25 | 3-phase fault on CHARL_CK 345/115/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-26 | 3-phase fault on CHARL_CK 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-27 | 3-phase fault on CHARL_CK to ROUNDUP 345kV Circuit 1, near CHARL_CK. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-28 | 3-phase fault on CHARL_CK to PATENTGT 345kV Circuit 1, near CHARL_CK. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-29 | 3-phase fault on CHARL_CK to BELFELD 345kV Circuit 1, near CHARL_CK. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-30 | 3-phase fault on BROADLND 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-31 | 3-phase fault on GARRISN to JAMESTN 230kV Circuit 1, near GARRISN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-32 | 3-phase fault on GARRISN to HILKEN 230kV Circuit 1, near GARRISN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-33 | 3-phase fault on GARRISN 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-34 | 3-phase fault on GRE-STANTON to SQBUTTE 230kV Circuit 1, near GRE-STANTON. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-35 | 3-phase fault on GRE-STANTON to GRE-COAL TP4 230kV Circuit 1, near GRE-STANTON. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-36 | 3-phase fault on GRE-STANTON to GRE-COAL CR4 230kV Circuit 1, near GRE-STANTON. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-37 | 3-phase fault on LOGAN to BLAISDEL 230kV Circuit 1, near LOGAN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-38 | 3-phase fault on LOGAN 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-39 | 3-phase fault on WASHBRN to BISMARK 230kV Circuit 1, near WASHBRN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-40 | 3-phase fault on G09_001IST to WATERTN 345kV Circuit 1, near G09_001IST. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-41 | 3-phase fault on G09_001IST to CROCKER 345kV Circuit 1, near G09_001IST. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-42 | 3-phase fault on GROTON to ORDWAY 115kV Circuit 1, near GROTON. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-43 | 3-phase fault on GROTON to BRISTOL 115kV Circuit 1, near GROTON. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-44 | 3-phase fault on GROTON to ADBNSBT 115kV Circuit 1, near GROTON. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-PO-1-9 | Prior Outage of G16-017_TAP to Fort Thompson 345kV Circuit 1. 3-phase fault on G16-017_TAP to Leland Olds 345kV Circuit 1, near G16-017_TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-PO-2-1 | Prior Outage of Leland Olds to Groton 345kV Circuit 1. 3-phase fault on Leland Olds to Antelope 345kV Circuit 2, near Leland Olds. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-PO-2-2 | Prior Outage of Leland Olds to Groton 345kV Circuit 1. 3-phase fault on Antelope to ROUNDUP 345kV Circuit 2, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-PO-2-3 | Prior Outage of Leland Olds to Groton 345kV Circuit 1. 3-phase fault on Antelope to CHARL_CK 345kV Circuit 1, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-PO-2-4 | Prior Outage of Leland Olds to Groton 345kV Circuit 1. 3-phase fault on Antelope to Broadland 345kV Circuit 1, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-PO-2-6 | Prior Outage of Leland Olds to Groton 345kV Circuit 1. 3-phase fault on Fort Thompson to Grand Prairie 345kV Circuit 1, near Fort Thompson. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-PO-2-7 | Prior Outage of Leland Olds to Groton 345kV Circuit 1. 3-phase fault on Fort Thompson 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-PO-2-8 | Prior Outage of Leland Olds to Groton 345kV Circuit 1. 3-phase fault on Leland Olds 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-PO-2-9 | Prior Outage of Leland Olds to Groton 345kV Circuit 1. 3-phase fault on Leland Olds to Groton 345kV Circuit 1, near Leland Olds. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-PO-3-1 | Prior Outage of Leland Olds to Antelope 345kV Circuit 1. 3-phase fault on Leland Olds to Groton 345kV Circuit 1, near Leland Olds. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-PO-3-3 | Prior Outage of Leland Olds to Antelope 345kV Circuit 1. 3-phase fault on Fort Thompson to Grand Prairie 345kV Circuit 1, near Fort Thompson. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-PO-3-4 | Prior Outage of Leland Olds to Antelope 345kV Circuit 1. 3-phase fault on Fort Thompson 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-PO-3-5 | Prior Outage of Leland Olds to Antelope 345kV Circuit 1. 3-phase fault on Leland Olds 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-PO-4-1 | Prior Outage of Leland Olds 345/230/13.8 kV Transformer 1. 3-phase fault on Leland Olds to Groton 345kV Circuit 1, near Leland Olds. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-PO-4-3 | Prior Outage of Leland Olds 345/230/13.8 kV Transformer 1. 3-phase fault on Fort Thompson to Grand Prairie 345kV Circuit 1, near Fort Thompson. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-PO-4-4 | Prior Outage of Leland Olds 345/230/13.8 kV Transformer 1. 3-phase fault on Fort Thompson 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-PO-4-5 | Prior Outage of Leland Olds 345/230/13.8 kV Transformer 1. 3-phase fault on Leland Olds to Antelope 345kV Circuit 2, near Leland Olds. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-PO-4-6 | Prior Outage of Leland Olds 345/230/13.8 kV Transformer 1. 3-phase fault on Antelope to ROUNDUP 345kV Circuit 2, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-PO-4-7 | Prior Outage of Leland Olds 345/230/13.8 kV Transformer 1. 3-phase fault on Antelope to CHARL_CK 345kV Circuit 1, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-PO-4-8 | Prior Outage of Leland Olds 345/230/13.8 kV Transformer 1. 3-phase fault on Antelope to Broadland 345kV Circuit 1, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-PO-5-1 | Prior Outage of G16-017_TAP to Leland Olds 345kV Circuit 1. 3-phase fault on G16-017_TAP to Fort Thompson 345kV Circuit 1, near G16-017_TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-PO-5-2 | Prior Outage of G16-017_TAP to Leland Olds 345kV Circuit 1. 3-phase fault on Fort Thompson to Grand Prairie 345kV Circuit 1, near Fort Thompson. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-SB-1 | SLG fault on Leland Olds 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Leland Olds to Antelope 345 kV Circuit 1, Leland Olds to Groton 345 kV Circuit 1, Leland Olds to G16-017 TAP Circuit 1 and Leland Olds generator 2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-SB-3 | SLG fault on Antelope 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Antelope 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-SB-4 | SLG fault on Groton 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Groton 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-SB-5 | SLG fault on Leland Olds 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of Leland Olds 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 103-SB-6 | SLG fault on G16-017_TAP 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of G16-017_TAP 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-3PH-1 | 3-phase fault on G17-094-TAP to Fort Thompson 230 kV Circuit 2, near G17-094-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-3PH-2 | 3-phase fault on G17-094-TAP to Huron 230 kV Circuit 2, near G17-094-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-3PH-3 | 3-phase fault on Huron to Broadland 230 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-3PH-4 | 3-phase fault on Huron to Capenter 230 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-3PH-5 | 3-phase fault on Huron to WATERTN 230 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-3PH-6 | 3-phase fault on Huron 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-3PH-7 | 3-phase fault on Fort Thompson 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-3PH-8 | 3-phase fault on Fault Thompson to Leland Olds 345 kV Circuit 1, near Fort Thompson. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 19W | Transfer | 094-3PH-9 | 3-phase fault on CAPENTER 230/69 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-3PH-10 | 3-phase fault on CAPENTER to WATERTN 230 kV Circuit 1, near CAPENTER. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-3PH-11 | 3-phase fault on WATERTN to BLAIR 230 kV Circuit 1, near WATERTN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-3PH-12 | 3-phase fault on WATERTN to APPLEDORN 230 kV Circuit 1, near WATERTN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-3PH-13 | 3-phase fault on WATERTN 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-3PH-14 | 3-phase fault on WATERTN 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-3PH-15 | 3-phase fault on WATERTN to G09_001IST 345 kV Circuit 1, near WATERTN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-3PH-16 | 3-phase fault on WATERTN to WHITE 345 kV Circuit 1, near WATERTN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-3PH-17 | 3-phase fault on Huron to HURONWP 115 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-3PH-18 | 3-phase fault on Huron to Redfield 115 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-3PH-19 | 3-phase fault on Huron to WOONSKT 115 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-3PH-20 | 3-phase fault on HURON 115/69 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-3PH-21 | 3-phase fault on Broadland 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-3PH-22 | 3-phase fault on Broadland to ANTELOPE 345 kV Circuit 1, near Broadland. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-3PH-23 | 3-phase fault on LETCHER to SIOUXFL 230 kV Circuit 1, near LETCHER. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-3PH-24 | 3-phase fault on LETCHER 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-3PH-25 | 3-phase fault on OAHE to PHILIP 230 kV Circuit 1, near OAHE. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-3PH-26 | 3-phase fault on OAHE to SULLYBT 230 kV Circuit 1, near OAHE. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-3PH-27 | 3-phase fault on OAHE 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-3PH-28 | 3-phase fault on FTRANDL to SIOUXCY 230 kV Circuit 1, near FTRANDL. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-3PH-29 | 3-phase fault on FTRANDL to UTICAJC 230 kV Circuit 1, near FTRANDL. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-3PH-30 | 3-phase fault on FTRANDL to MEADOWGROVE 230 kV Circuit 1, near FTRANDL. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-3PH-31 | 3-phase fault on FTRANDL to LAKPLAT 230 kV Circuit 1, near FTRANDL. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-3PH-32 | 3-phase fault on FTRANDL 230/115 kV Transformer 2. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-PO-1-1 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on G17-094-TAP to Fort Thompson 230kV Circuit 2, near G17-04-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-PO-1-2 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on G17-094-TAP to Huron 230 kV Circuit 2, near G17-094-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-PO-1-3 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Fort Thompson to LETCHER 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-PO-1-4 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Fort Thompson to FTRANDL 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-PO-1-5 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Huron to WATERTN 230 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-PO-2-1 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on G17-094-TAP to Fort Thompson 230kV Circuit 2, near G17-04-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-PO-2-2 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on G17-094-TAP to Huron 230 kV Circuit 2, near G17-094-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-PO-2-3 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Fort Thompson to LETCHER 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-PO-2-4 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Fort Thompson to FTRANDL 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-PO-2-5 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Huron to WATERTN 230 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-SB-1 | SLG fault on G17-094-TAP 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of G17-094-TAP 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-SB-2 | SLG fault on Fort Thompson 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of Fort Thompson 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-SB-3 | SLG fault on Huron 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of Huron 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-SB-4 | SLG fault on Fort Thompson 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Fort Thompson 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | No | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 19W | Transfer | 094-SB-5 | SLG fault on Huron 115 kV, stuck breaker results delayed clearing after 16 cycles with loss of Huron 115 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-SB-6 | SLG fault on FTRANDL 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of FTRANDL 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-SB-7 | SLG fault on OAHE 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of OAHE 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | 094-SB-8 | SLG fault on WATERTN 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of WATERTN 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | TIE-3PH-1 | 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | TIE-3PH-2 | 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | TIE-3PH-3 | 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 1, near BRKNGCO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | TIE-3PH-4 | 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | TIE-3PH-5 | 3-phase fault on KEYSTON to SD.LS-KS 345 kV Circuit 1, near KEYSTON. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | TIE-3PH-6 | 3-phase fault on THEDFRD to HOLT. CO 345 kV Circuit 1, near THEDFRD. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | TIE-3PH-7 | 3-phase fault on HOLT. CO to ANTELOPE 345 kV Circuit 1, near HOLT. CO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | TIE-3PH-8 | 3-phase fault on HOLT. CO to GR ISLD 345 kV Circuit 1, near HOLT. CO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | TIE-3PH-9 | 3-phase fault on BOBCAT.C to STEGALL 345 kV Circuit 1, near BOBCAT.C. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | TIE-3PH-10 | 3-phase fault on GRPR1 to GR PRAIRIE 345 kV Circuit 1, near GRPR1. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | TIE-PO-1-1 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | TIE-PO-1-2 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3 . Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | TIE-PO-1-3 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | TIE-PO-1-4 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | TIE-PO-2-1 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | TIE-PO-2-2 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | TIE-PO-2-3 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | TIE-PO-3-1 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | TIE-PO-3-2 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | TIE-PO-3-3 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | TIE-SB-1 | SLG fault on BRKNGCO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of BRKNGCO to White 345 kV Circuit1 and BRKNGCO 345/115/13.8 kV Transformer 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | TIE-SB-2 | SLG fault on SPLT RK3 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of SPLT RK3 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | TIE-SB-3 | SLG fault on RAUN 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of RAUN 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | TIE-SB-4 | SLG fault on KEYSTON 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of KEYSTON 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | TIE-SB-5 | SLG fault on THEDFRD 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of THEDFRD 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | TIE-SB-6 | SLG fault on BOBCAT.C 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of BOBCAT.C 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Transfer | TIE-SB-7 | SLG fault on SIOUXCY 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of SIOUXCY 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-1 | 3-phase fault on G16-017_TAP to Leland Olds 345kV Circuit 1, near G16-017_TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-2 | 3-phase fault on Leland Olds to Antelope 345kV Circuit 2, near Leland Olds. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-3 | 3-phase fault on Leland Olds to Groton 345kV Circuit 1, near Leland Olds. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-4 | 3-phase fault on Leland Olds 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-5 | 3-phase fault on Fort Thompson to Grand Prairie 345kV Circuit 1, near Fort Thompson. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-6 | 3-phase fault on Fort Thompson 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-7 | 3-phase fault on Antelope to ROUNDUP 345kV Circuit 2, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-8 | 3-phase fault on Antelope to CHARL_CK 345kV Circuit 1, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-9 | 3-phase fault on Antelope to Broadland 345kV Circuit 1, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-10 | 3-phase fault on Leland Olds to Logan 230kV Circuit 1, near Leland. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-11 | 3-phase fault on Leland Olds to Garrison 230kV Circuit 1, near Leland. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-12 | 3-phase fault on Leland Olds to WASHBRN 230kV Circuit 1, near Leland. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-13 | 3-phase fault on Leland Olds to GRE-STANTON 230kV Circuit 1, near Leland. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-14 | 3-phase fault on BASIN 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-15 | 3-phase fault on Groton to G09_001IST 345kV Circuit 1, near Groton. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-16 | 3-phase fault on Groton 345/115/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-17 | 3-phase fault on Fort Thompson to BIGBND 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-18 | 3-phase fault on Fort Thompson to LETCHER 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-19 | 3-phase fault on Fort Thompson to FTRANDL 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-20 | 3-phase fault on Fort Thompson to LAKPLAT 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-21 | 3-phase fault on Fort Thompson to OAHE 230kV Circuit 3, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-22 | 3-phase fault on Grand Prairie to Holt Co. 345kV Circuit 1, near Grand Prairie. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-23 | 3-phase fault on Grand Prairie to GRPR1 345kV Circuit 1, near Grand Prairie. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-24 | 3-phase fault on ROUNDUP 345/115/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-25 | 3-phase fault on CHARL_CK 345/115/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-26 | 3-phase fault on CHARL_CK 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-27 | 3-phase fault on CHARL_CK to ROUNDUP 345kV Circuit 1, near CHARL_CK. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-28 | 3-phase fault on CHARL_CK to PATENTGT 345kV Circuit 1, near CHARL_CK. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-29 | 3-phase fault on CHARL_CK to BELFELD 345kV Circuit 1, near CHARL_CK. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-30 | 3-phase fault on BROADLND 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-31 | 3-phase fault on GARRISN to JAMESTN 230kV Circuit 1, near GARRISN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-32 | 3-phase fault on GARRISN to HILKEN 230kV Circuit 1, near GARRISN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-33 | 3-phase fault on GARRISN 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-34 | 3-phase fault on GRE-STANTON to SQBUTTE 230kV Circuit 1, near GRE-STANTON. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-35 | 3-phase fault on GRE-STANTON to GRE-COAL TP4 230kV Circuit 1, near GRE-STANTON. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-36 | 3-phase fault on GRE-STANTON to GRE-COAL CR4 230kV Circuit 1, near GRE-STANTON. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-37 | 3-phase fault on LOGAN to BLAISDEL 230kV Circuit 1, near LOGAN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-38 | 3-phase fault on LOGAN 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-39 | 3-phase fault on WASHBRN to BISMARK 230kV Circuit 1, near WASHBRN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-40 | 3-phase fault on G09_001IST to WATERTN 345kV Circuit 1, near G09_001IST. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-41 | 3-phase fault on G09_001IST to CROCKER 345kV Circuit 1, near G09_001IST. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-42 | 3-phase fault on GROTON to ORDWAY 115kV Circuit 1, near GROTON. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-43 | 3-phase fault on GROTON to BRISTOL 115kV Circuit 1, near GROTON. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-44 | 3-phase fault on GROTON to ADBNSBT 115kV Circuit 1, near GROTON. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-PO-1-9 | Prior Outage of G16-017_TAP to Fort Thompson 345kV Circuit 1. 3-phase fault on G16-017_TAP to Leland Olds 345kV Circuit 1, near G16-017_TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-PO-2-1 | Prior Outage of Leland Olds to Groton 345kV Circuit 1. 3-phase fault on Leland Olds to Antelope 345kV Circuit 2, near Leland Olds. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-PO-2-2 | Prior Outage of Leland Olds to Groton 345kV Circuit 1. 3-phase fault on Antelope to ROUNDUP 345kV Circuit 2, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-PO-2-3 | Prior Outage of Leland Olds to Groton 345kV Circuit 1. 3-phase fault on Antelope to CHARL_CK 345kV Circuit 1, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-PO-2-4 | Prior Outage of Leland Olds to Groton 345kV Circuit 1. 3-phase fault on Antelope to Broadland 345kV Circuit 1, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-PO-2-6 | Prior Outage of Leland Olds to Groton 345kV Circuit 1. 3-phase fault on Fort Thompson to Grand Prairie 345kV Circuit 1, near Fort Thompson. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-PO-2-7 | Prior Outage of Leland Olds to Groton 345kV Circuit 1. 3-phase fault on Fort Thompson 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-PO-2-8 | Prior Outage of Leland Olds to Groton 345kV Circuit 1. 3-phase fault on Leland Olds 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-PO-2-9 | Prior Outage of Leland Olds to Groton 345kV Circuit 1. 3-phase fault on Leland Olds to Groton 345kV Circuit 1, near Leland Olds. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-PO-3-1 | Prior Outage of Leland Olds to Antelope 345kV Circuit 1. 3-phase fault on Leland Olds to Groton 345kV Circuit 1, near Leland Olds. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-PO-3-3 | Prior Outage of Leland Olds to Antelope 345kV Circuit 1. 3-phase fault on Fort Thompson to Grand Prairie 345kV Circuit 1, near Fort Thompson. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-PO-3-4 | Prior Outage of Leland Olds to Antelope 345kV Circuit 1. 3-phase fault on Fort Thompson 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-PO-3-5 | Prior Outage of Leland Olds to Antelope 345kV Circuit 1. 3-phase fault on Leland Olds 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-PO-4-1 | Prior Outage of Leland Olds 345/230/13.8 kV Transformer 1. 3-phase fault on Leland Olds to Groton 345kV Circuit 1, near Leland Olds. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-PO-4-3 | Prior Outage of Leland Olds 345/230/13.8 kV Transformer 1. 3-phase fault on Fort Thompson to Grand Prairie 345kV Circuit 1, near Fort Thompson. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-PO-4-4 | Prior Outage of Leland Olds 345/230/13.8 kV Transformer 1. 3-phase fault on Fort Thompson 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-PO-4-5 | Prior Outage of Leland Olds 345/230/13.8 kV Transformer 1. 3-phase fault on Leland Olds to Antelope 345kV Circuit 2, near Leland Olds. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-PO-4-6 | Prior Outage of Leland Olds 345/230/13.8 kV Transformer 1. 3-phase fault on Antelope to ROUNDUP 345kV Circuit 2, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-PO-4-7 | Prior Outage of Leland Olds 345/230/13.8 kV Transformer 1. 3-phase fault on Antelope to CHARL_CK 345kV Circuit 1, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-PO-4-8 | Prior Outage of Leland Olds 345/230/13.8 kV Transformer 1. 3-phase fault on Antelope to Broadland 345kV Circuit 1, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-PO-5-1 | Prior Outage of G16-017_TAP to Leland Olds 345kV Circuit 1. 3-phase fault on G16-017_TAP to Fort Thompson 345kV Circuit 1, near G16-017_TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-PO-5-2 | Prior Outage of G16-017_TAP to Leland Olds 345kV Circuit 1. 3-phase fault on Fort Thompson to Grand Prairie 345kV Circuit 1, near Fort Thompson. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-SB-3 | SLG fault on Antelope 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Antelope 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-SB-4 | SLG fault on Groton 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Groton 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-SB-5 | SLG fault on Leland Olds 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of Leland Olds 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-SB-6 | SLG fault on G16-017_TAP 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of G16-017_TAP 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-3PH-1 | 3-phase fault on G17-094-TAP to Fort Thompson 230 kV Circuit 2, near G17-094-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-3PH-2 | 3-phase fault on G17-094-TAP to Huron 230 kV Circuit 2, near G17-094-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-3PH-3 | 3-phase fault on Huron to Broadland 230 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-3PH-4 | 3-phase fault on Huron to Capenter 230 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-3PH-5 | 3-phase fault on Huron to WATERTN 230 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-3PH-6 | 3-phase fault on Huron 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-3PH-7 | 3-phase fault on Fort Thompson 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-3PH-8 | 3-phase fault on Fault Thompson to Leland Olds 345 kV Circuit 1, near Fort Thompson. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 21L | Transfer | 094-3PH-9 | 3-phase fault on CAPENTER 230/69 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-3PH-10 | 3-phase fault on CAPENTER to WATERTN 230 kV Circuit 1, near CAPENTER. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-3PH-11 | 3-phase fault on WATERTN to BLAIR 230 kV Circuit 1, near WATERTN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-3PH-12 | 3-phase fault on WATERTN to APPLEDORN 230 kV Circuit 1, near WATERTN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-3PH-13 | 3-phase fault on WATERTN 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-3PH-14 | 3-phase fault on WATERTN 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-3PH-15 | 3-phase fault on WATERTN to G09_001IST 345 kV Circuit 1, near WATERTN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-3PH-16 | 3-phase fault on WATERTN to WHITE 345 kV Circuit 1, near WATERTN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-3PH-17 | 3-phase fault on Huron to HURONWP 115 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-3PH-18 | 3-phase fault on Huron to Redfield 115 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-3PH-19 | 3-phase fault on Huron to WOONSKT 115 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-3PH-20 | 3-phase fault on HURON 115/69 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-3PH-21 | 3-phase fault on Broadland 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-3PH-22 | 3-phase fault on Broadland to ANTELOPE 345 kV Circuit 1, near Broadland. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-3PH-23 | 3-phase fault on LETCHER to SIOUXFL 230 kV Circuit 1, near LETCHER. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-3PH-24 | 3-phase fault on LETCHER 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-3PH-25 | 3-phase fault on OAHE to PHILIP 230 kV Circuit 1, near OAHE. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-3PH-26 | 3-phase fault on OAHE to SULLYBT 230 kV Circuit 1, near OAHE. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-3PH-27 | 3-phase fault on OAHE 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-3PH-28 | 3-phase fault on FTRANDL to SIOUXCY 230 kV Circuit 1, near FTRANDL. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-3PH-29 | 3-phase fault on FTRANDL to UTICAJC 230 kV Circuit 1, near FTRANDL. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-3PH-30 | 3-phase fault on FTRANDL to MEADOWGROVE 230 kV Circuit 1, near FTRANDL. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-3PH-31 | 3-phase fault on FTRANDL to LAKPLAT 230 kV Circuit 1, near FTRANDL. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-3PH-32 | 3-phase fault on FTRANDL 230/115 kV Transformer 2. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-PO-1-1 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on G17-094-TAP to Fort Thompson 230kV Circuit 2, near G17-04-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-PO-1-2 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on G17-094-TAP to Huron 230 kV Circuit 2, near G17-094-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-PO-1-3 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Fort Thompson to LETCHER 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-PO-1-4 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Fort Thompson to FTRANDL 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-PO-1-5 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Huron to WATERTN 230 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-PO-2-1 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on G17-094-TAP to Fort Thompson 230kV Circuit 2, near G17-04-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-PO-2-2 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on G17-094-TAP to Huron 230 kV Circuit 2, near G17-094-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-PO-2-3 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Fort Thompson to LETCHER 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-PO-2-4 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Fort Thompson to FTRANDL 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-PO-2-5 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Huron to WATERTN 230 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-SB-1 | SLG fault on G17-094-TAP 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of G17-094-TAP 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-SB-2 | SLG fault on Fort Thompson 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of Fort Thompson 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-SB-3 | SLG fault on Huron 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of Huron 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-SB-4 | SLG fault on Fort Thompson 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Fort Thompson 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | No | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 21L | Transfer | 094-SB-5 | SLG fault on Huron 115 kV, stuck breaker results delayed clearing after 16 cycles with loss of Huron 115 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-SB-6 | SLG fault on FTRANDL 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of FTRANDL 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-SB-7 | SLG fault on OAHE 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of OAHE 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 094-SB-8 | SLG fault on WATERTN 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of WATERTN 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | TIE-3PH-1 | 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | TIE-3PH-2 | 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | TIE-3PH-3 | 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 1, near BRKNGCO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | TIE-3PH-4 | 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | TIE-3PH-5 | 3-phase fault on KEYSTON to SD.LS-KS 345 kV Circuit 1, near KEYSTON. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | TIE-3PH-6 | 3-phase fault on THEDFRD to HOLT. CO 345 kV Circuit 1, near THEDFRD. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | TIE-3PH-7 | 3-phase fault on HOLT. CO to ANTELOPE 345 kV Circuit 1, near HOLT. CO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | TIE-3PH-8 | 3-phase fault on HOLT. CO to GR ISLD 345 kV Circuit 1, near HOLT. CO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | TIE-3PH-9 | 3-phase fault on BOBCAT.C to STEGALL 345 kV Circuit 1, near BOBCAT.C. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | TIE-3PH-10 | 3-phase fault on GRPR1 to GR PRAIRIE 345 kV Circuit 1, near GRPR1. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | TIE-PO-1-1 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | TIE-PO-1-2 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3 . Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | TIE-PO-1-3 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | TIE-PO-1-4 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | TIE-PO-2-1 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | TIE-PO-2-2 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | TIE-PO-2-3 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | TIE-PO-3-1 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | TIE-PO-3-2 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | TIE-PO-3-3 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | TIE-SB-1 | SLG fault on BRKNGCO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of BRKNGCO to White 345 kV Circuit1 and BRKNGCO 345/115/13.8 kV Transformer 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | TIE-SB-2 | SLG fault on SPLT RK3 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of SPLT RK3 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | TIE-SB-3 | SLG fault on RAUN 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of RAUN 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | TIE-SB-4 | SLG fault on KEYSTON 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of KEYSTON 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | TIE-SB-5 | SLG fault on THEDFRD 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of THEDFRD 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | TIE-SB-6 | SLG fault on BOBCAT.C 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of BOBCAT.C 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | TIE-SB-7 | SLG fault on SIOUXCY 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of SIOUXCY 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-1 | 3-phase fault on G16-017_TAP to Leland Olds 345kV Circuit 1, near G16-017_TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-2 | 3-phase fault on Leland Olds to Antelope 345kV Circuit 2, near Leland Olds. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-3 | 3-phase fault on Leland Olds to Groton 345kV Circuit 1, near Leland Olds. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-4 | 3-phase fault on Leland Olds 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-5 | 3-phase fault on Fort Thompson to Grand Prairie 345kV Circuit 1, near Fort Thompson. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-6 | 3-phase fault on Fort Thompson 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-7 | 3-phase fault on Antelope to ROUNDUP 345kV Circuit 2, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-8 | 3-phase fault on Antelope to CHARL_CK 345kV Circuit 1, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-9 | 3-phase fault on Antelope to Broadland 345kV Circuit 1, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-10 | 3-phase fault on Leland Olds to Logan 230kV Circuit 1, near Leland. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-11 | 3-phase fault on Leland Olds to Garrison 230kV Circuit 1, near Leland. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-12 | 3-phase fault on Leland Olds to WASHBRN 230kV Circuit 1, near Leland. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-13 | 3-phase fault on Leland Olds to GRE-STANTON 230kV Circuit 1, near Leland. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-14 | 3-phase fault on BASIN 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-15 | 3-phase fault on Groton to G09_001IST 345kV Circuit 1, near Groton. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-16 | 3-phase fault on Groton 345/115/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-17 | 3-phase fault on Fort Thompson to BIGBND 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-18 | 3-phase fault on Fort Thompson to LETCHER 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-19 | 3-phase fault on Fort Thompson to FTRANDL 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-20 | 3-phase fault on Fort Thompson to LAKPLAT 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-21 | 3-phase fault on Fort Thompson to OAHE 230kV Circuit 3, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-22 | 3-phase fault on Grand Prairie to Holt Co. 345kV Circuit 1, near Grand Prairie. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-23 | 3-phase fault on Grand Prairie to GRPR1 345kV Circuit 1, near Grand Prairie. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-24 | 3-phase fault on ROUNDUP 345/115/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-25 | 3-phase fault on CHARL_CK 345/115/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-26 | 3-phase fault on CHARL_CK 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-27 | 3-phase fault on CHARL_CK to ROUNDUP 345kV Circuit 1, near CHARL_CK. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-28 | 3-phase fault on CHARL_CK to PATENTGT 345kV Circuit 1, near CHARL_CK. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-29 | 3-phase fault on CHARL_CK to BELFELD 345kV Circuit 1, near CHARL_CK. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-30 | 3-phase fault on BROADLND 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-31 | 3-phase fault on GARRISN to JAMESTN 230kV Circuit 1, near GARRISN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-32 | 3-phase fault on GARRISN to HILKEN 230kV Circuit 1, near GARRISN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-33 | 3-phase fault on GARRISN 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-34 | 3-phase fault on GRE-STANTON to SQBUTTE 230kV Circuit 1, near GRE-STANTON. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-35 | 3-phase fault on GRE-STANTON to GRE-COAL TP4 230kV Circuit 1, near GRE-STANTON. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-36 | 3-phase fault on GRE-STANTON to GRE-COAL CR4 230kV Circuit 1, near GRE-STANTON. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-37 | 3-phase fault on LOGAN to BLAISDEL 230kV Circuit 1, near LOGAN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-38 | 3-phase fault on LOGAN 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-39 | 3-phase fault on WASHBRN to BISMARK 230kV Circuit 1, near WASHBRN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-40 | 3-phase fault on G09_001IST to WATERTN 345kV Circuit 1, near G09_001IST. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-41 | 3-phase fault on G09_001IST to CROCKER 345kV Circuit 1, near G09_001IST. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-42 | 3-phase fault on GROTON to ORDWAY 115kV Circuit 1, near GROTON. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-43 | 3-phase fault on GROTON to BRISTOL 115kV Circuit 1, near GROTON. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-44 | 3-phase fault on GROTON to ADBNSBT 115kV Circuit 1, near GROTON. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-PO-1-6 | Prior Outage of G16-017_TAP to Fort Thompson 345kV Circuit 1. 3-phase fault on Groton to G09_001IST 345kV Circuit 1, near Groton. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-PO-1-7 | Prior Outage of G16-017_TAP to Fort Thompson 345kV Circuit 1. 3-phase fault on Groton 345/115/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-PO-1-9 | Prior Outage of G16-017_TAP to Fort Thompson 345kV Circuit 1. 3-phase fault on G16-017_TAP to Leland Olds 345kV Circuit 1, near G16-017_TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-PO-2-1 | Prior Outage of Leland Olds to Groton 345kV Circuit 1. 3-phase fault on Leland Olds to Antelope 345kV Circuit 2, near Leland Olds. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-PO-2-2 | Prior Outage of Leland Olds to Groton 345kV Circuit 1. 3-phase fault on Antelope to ROUNDUP 345kV Circuit 2, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-PO-2-3 | Prior Outage of Leland Olds to Groton 345kV Circuit 1. 3-phase fault on Antelope to CHARL_CK 345kV Circuit 1, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-PO-2-4 | Prior Outage of Leland Olds to Groton 345kV Circuit 1. 3-phase fault on Antelope to Broadland 345kV Circuit 1, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-PO-2-6 | Prior Outage of Leland Olds to Groton 345kV Circuit 1. 3-phase fault on Fort Thompson to Grand Prairie 345kV Circuit 1, near Fort Thompson. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-PO-2-7 | Prior Outage of Leland Olds to Groton 345kV Circuit 1. 3-phase fault on Fort Thompson 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-PO-2-8 | Prior Outage of Leland Olds to Groton 345kV Circuit 1. 3-phase fault on Leland Olds 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-PO-2-9 | Prior Outage of Leland Olds to Groton 345kV Circuit 1. 3-phase fault on Leland Olds to Groton 345kV Circuit 1, near Leland Olds. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-PO-3-1 | Prior Outage of Leland Olds to Antelope 345kV Circuit 1. 3-phase fault on Leland Olds to Groton 345kV Circuit 1, near Leland Olds. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-PO-3-3 | Prior Outage of Leland Olds to Antelope 345kV Circuit 1. 3-phase fault on Fort Thompson to Grand Prairie 345kV Circuit 1, near Fort Thompson. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-PO-3-4 | Prior Outage of Leland Olds to Antelope 345kV Circuit 1. 3-phase fault on Fort Thompson 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-PO-3-5 | Prior Outage of Leland Olds to Antelope 345kV Circuit 1. 3-phase fault on Leland Olds 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-PO-4-1 | Prior Outage of Leland Olds 345/230/13.8 kV Transformer 1. 3-phase fault on Leland Olds to Groton 345kV Circuit 1, near Leland Olds. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-PO-4-3 | Prior Outage of Leland Olds 345/230/13.8 kV Transformer 1. 3-phase fault on Fort Thompson to Grand Prairie 345kV Circuit 1, near Fort Thompson. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-PO-4-4 | Prior Outage of Leland Olds 345/230/13.8 kV Transformer 1. 3-phase fault on Fort Thompson 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-PO-4-5 | Prior Outage of Leland Olds 345/230/13.8 kV Transformer 1. 3-phase fault on Leland Olds to Antelope 345kV Circuit 2, near Leland Olds. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-PO-4-6 | Prior Outage of Leland Olds 345/230/13.8 kV Transformer 1. 3-phase fault on Antelope to ROUNDUP 345kV Circuit 2, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-PO-4-7 | Prior Outage of Leland Olds 345/230/13.8 kV Transformer 1. 3-phase fault on Antelope to CHARL_CK 345kV Circuit 1, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-PO-4-8 | Prior Outage of Leland Olds 345/230/13.8 kV Transformer 1. 3-phase fault on Antelope to Broadland 345kV Circuit 1, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-PO-5-1 | Prior Outage of G16-017_TAP to Leland Olds 345kV Circuit 1. 3-phase fault on G16-017_TAP to Fort Thompson 345kV Circuit 1, near G16-017_TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-PO-5-2 | Prior Outage of G16-017_TAP to Leland Olds 345kV Circuit 1. 3-phase fault on Fort Thompson to Grand Prairie 345kV Circuit 1, near Fort Thompson. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-PO-5-3 | Prior Outage of G16-017_TAP to Leland Olds 345kV Circuit 1. 3-phase fault on Fort Thompson 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 21S | Transfer | 103-SB-1 | SLG fault on Leland Olds 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Leland Olds to Antelope 345 kV Circuit 1, Leland Olds to Groton 345 kV Circuit 1, Leland Olds to G16-017 TAP Circuit 1 and Leland Olds generator 2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-SB-3 | SLG fault on Antelope 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Antelope 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-SB-4 | SLG fault on Groton 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Groton 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-SB-5 | SLG fault on Leland Olds 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of Leland Olds 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 103-SB-6 | SLG fault on G16-017_TAP 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of G16-017_TAP 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-3PH-1 | 3-phase fault on G17-094-TAP to Fort Thompson 230 kV Circuit 2, near G17-094-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-3PH-2 | 3-phase fault on G17-094-TAP to Huron 230 kV Circuit 2, near G17-094-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-3PH-3 | 3-phase fault on Huron to Broadland 230 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-3PH-4 | 3-phase fault on Huron to Capenter 230 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-3PH-5 | 3-phase fault on Huron to WATERTN 230 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-3PH-6 | 3-phase fault on Huron 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-3PH-7 | 3-phase fault on Fort Thompson 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-3PH-8 | 3-phase fault on Fault Thompson to Leland Olds 345 kV Circuit 1, near Fort Thompson. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-3PH-9 | 3-phase fault on CAPENTER 230/69 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-3PH-10 | 3-phase fault on CAPENTER to WATERTN 230 kV Circuit 1, near CAPENTER. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-3PH-11 | 3-phase fault on WATERTN to BLAIR 230 kV Circuit 1, near WATERTN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-3PH-12 | 3-phase fault on WATERTN to APPLEDORN 230 kV Circuit 1, near WATERTN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-3PH-13 | 3-phase fault on WATERTN 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-3PH-14 | 3-phase fault on WATERTN 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-3PH-15 | 3-phase fault on WATERTN to G09_001IST 345 kV Circuit 1, near WATERTN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-3PH-16 | 3-phase fault on WATERTN to WHITE 345 kV Circuit 1, near WATERTN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-3PH-17 | 3-phase fault on Huron to HURONWP 115 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-3PH-18 | 3-phase fault on Huron to Redfield 115 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-3PH-19 | 3-phase fault on Huron to WOONSKT 115 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-3PH-20 | 3-phase fault on HURON 115/69 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-3PH-21 | 3-phase fault on Broadland 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-3PH-22 | 3-phase fault on Broadland to ANTELOPE 345 kV Circuit 1, near Broadland. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-3PH-23 | 3-phase fault on LETCHER to SIOUXFL 230 kV Circuit 1, near LETCHER. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-3PH-24 | 3-phase fault on LETCHER 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-3PH-25 | 3-phase fault on OAHE to PHILIP 230 kV Circuit 1, near OAHE. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-3PH-26 | 3-phase fault on OAHE to SULLYBT 230 kV Circuit 1, near OAHE. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-3PH-27 | 3-phase fault on OAHE 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-3PH-28 | 3-phase fault on FTRANDL to SIOUXCY 230 kV Circuit 1, near FTRANDL. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-3PH-29 | 3-phase fault on FTRANDL to UTICAJC 230 kV Circuit 1, near FTRANDL. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-3PH-30 | 3-phase fault on FTRANDL to MEADOWGROVE 230 kV Circuit 1, near FTRANDL. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-3PH-31 | 3-phase fault on FTRANDL to LAKPLAT 230 kV Circuit 1, near FTRANDL. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-3PH-32 | 3-phase fault on FTRANDL 230/115 kV Transformer 2. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-PO-1-1 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on G17-094-TAP to Fort Thompson 230kV Circuit 2, near G17-04-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-PO-1-2 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on G17-094-TAP to Huron 230 kV Circuit 2, near G17-094-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-PO-1-3 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Fort Thompson to LETCHER 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-PO-1-4 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Fort Thompson to FTRANDL 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-PO-1-5 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Huron to WATERTN 230 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-PO-2-1 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on G17-094-TAP to Fort Thompson 230kV Circuit 2, near G17-04-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-PO-2-2 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on G17-094-TAP to Huron 230 kV Circuit 2, near G17-094-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-PO-2-3 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Fort Thompson to LETCHER 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-PO-2-4 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Fort Thompson to FTRANDL 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-PO-2-5 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Huron to WATERTN 230 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-SB-1 | SLG fault on G17-094-TAP 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of G17-094-TAP 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-SB-2 | SLG fault on Fort Thompson 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of Fort Thompson 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-SB-3 | SLG fault on Huron 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of Huron 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-SB-4 | SLG fault on Fort Thompson 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Fort Thompson 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | No | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 21S | Transfer | 094-SB-5 | SLG fault on Huron 115 kV, stuck breaker results delayed clearing after 16 cycles with loss of Huron 115 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-SB-6 | SLG fault on FTRANDL 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of FTRANDL 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-SB-7 | SLG fault on OAHE 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of OAHE 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | 094-SB-8 | SLG fault on WATERTN 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of WATERTN 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | TIE-3PH-1 | 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | TIE-3PH-2 | 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | TIE-3PH-3 | 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 1, near BRKNGCO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | TIE-3PH-4 | 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | TIE-3PH-5 | 3-phase fault on KEYSTON to SD.LS-KS 345 kV Circuit 1, near KEYSTON. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | TIE-3PH-6 | 3-phase fault on THEDFRD to HOLT. CO 345 kV Circuit 1, near THEDFRD. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | TIE-3PH-7 | 3-phase fault on HOLT. CO to ANTELOPE 345 kV Circuit 1, near HOLT. CO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | TIE-3PH-8 | 3-phase fault on HOLT. CO to GR ISLD 345 kV Circuit 1, near HOLT. CO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | TIE-3PH-9 | 3-phase fault on BOBCAT.C to STEGALL 345 kV Circuit 1, near BOBCAT.C. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | TIE-3PH-10 | 3-phase fault on GRPR1 to GR PRAIRIE 345 kV Circuit 1, near GRPR1. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | TIE-PO-1-1 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | TIE-PO-1-2 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3 . Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | TIE-PO-1-3 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | TIE-PO-1-4 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | TIE-PO-2-1 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | TIE-PO-2-2 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | TIE-PO-2-3 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | TIE-PO-3-1 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | TIE-PO-3-2 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | TIE-PO-3-3 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | TIE-SB-1 | SLG fault on BRKNGCO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of BRKNGCO to White 345 kV Circuit1 and BRKNGCO 345/115/13.8 kV Transformer 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | TIE-SB-2 | SLG fault on SPLT RK3 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of SPLT RK3 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | TIE-SB-3 | SLG fault on RAUN 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of RAUN 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | TIE-SB-4 | SLG fault on KEYSTON 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of KEYSTON 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | TIE-SB-5 | SLG fault on THEDFRD 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of THEDFRD 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | TIE-SB-6 | SLG fault on BOBCAT.C 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of BOBCAT.C 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Transfer | TIE-SB-7 | SLG fault on SIOUXCY 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of SIOUXCY 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-1 | 3-phase fault on G16-017_TAP to Leland Olds 345kV Circuit 1, near G16-017_TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-2 | 3-phase fault on Leland Olds to Antelope 345kV Circuit 2, near Leland Olds. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-3 | 3-phase fault on Leland Olds to Groton 345kV Circuit 1, near Leland Olds. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-4 | 3-phase fault on Leland Olds 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-5 | 3-phase fault on Fort Thompson to Grand Prairie 345kV Circuit 1, near Fort Thompson. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-6 | 3-phase fault on Fort Thompson 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-7 | 3-phase fault on Antelope to ROUNDUP 345kV Circuit 2, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-8 | 3-phase fault on Antelope to CHARL_CK 345kV Circuit 1, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-9 | 3-phase fault on Antelope to Broadland 345kV Circuit 1, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-10 | 3-phase fault on Leland Olds to Logan 230kV Circuit 1, near Leland. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-11 | 3-phase fault on Leland Olds to Garrison 230kV Circuit 1, near Leland. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-12 | 3-phase fault on Leland Olds to WASHBRN 230kV Circuit 1, near Leland. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-13 | 3-phase fault on Leland Olds to GRE-STANTON 230kV Circuit 1, near Leland. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-14 | 3-phase fault on BASIN 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-15 | 3-phase fault on Groton to G09_001IST 345kV Circuit 1, near Groton. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-16 | 3-phase fault on Groton 345/115/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-17 | 3-phase fault on Fort Thompson to BIGBND 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-18 | 3-phase fault on Fort Thompson to LETCHER 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-19 | 3-phase fault on Fort Thompson to FTRANDL 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-20 | 3-phase fault on Fort Thompson to LAKPLAT 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-21 | 3-phase fault on Fort Thompson to OAHE 230kV Circuit 3, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-22 | 3-phase fault on Grand Prairie to Holt Co. 345kV Circuit 1, near Grand Prairie. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-23 | 3-phase fault on Grand Prairie to GRPR1 345kV Circuit 1, near Grand Prairie. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-24 | 3-phase fault on ROUNDUP 345/115/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-25 | 3-phase fault on CHARL_CK 345/115/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-26 | 3-phase fault on CHARL_CK 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-27 | 3-phase fault on CHARL_CK to ROUNDUP 345kV Circuit 1, near CHARL_CK. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-28 | 3-phase fault on CHARL_CK to PATENTGT 345kV Circuit 1, near CHARL_CK. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-29 | 3-phase fault on CHARL_CK to BELFELD 345kV Circuit 1, near CHARL_CK. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-30 | 3-phase fault on BROADLND 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-31 | 3-phase fault on GARRISN to JAMESTN 230kV Circuit 1, near GARRISN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-32 | 3-phase fault on GARRISN to HILKEN 230kV Circuit 1, near GARRISN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-33 | 3-phase fault on GARRISN 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-34 | 3-phase fault on GRE-STANTON to SQBUTTE 230kV Circuit 1, near GRE-STANTON. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-35 | 3-phase fault on GRE-STANTON to GRE-COAL TP4 230kV Circuit 1, near GRE-STANTON. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-36 | 3-phase fault on GRE-STANTON to GRE-COAL CR4 230kV Circuit 1, near GRE-STANTON. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-37 | 3-phase fault on LOGAN to BLAISDEL 230kV Circuit 1, near LOGAN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-38 | 3-phase fault on LOGAN 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-39 | 3-phase fault on WASHBRN to BISMARK 230kV Circuit 1, near WASHBRN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-40 | 3-phase fault on G09_001IST to WATERTN 345kV Circuit 1, near G09_001IST. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-41 | 3-phase fault on G09_001IST to CROCKER 345kV Circuit 1, near G09_001IST. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-42 | 3-phase fault on GROTON to ORDWAY 115kV Circuit 1, near GROTON. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-43 | 3-phase fault on GROTON to BRISTOL 115kV Circuit 1, near GROTON. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-44 | 3-phase fault on GROTON to ADBNSBT 115kV Circuit 1, near GROTON. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-PO-1-6 | Prior Outage of G16-017_TAP to Fort Thompson 345kV Circuit 1. 3-phase fault on Groton to G09_001IST 345kV Circuit 1, near Groton. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-PO-1-7 | Prior Outage of G16-017_TAP to Fort Thompson 345kV Circuit 1. 3-phase fault on Groton 345/115/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-PO-1-9 | Prior Outage of G16-017_TAP to Fort Thompson 345kV Circuit 1. 3-phase fault on G16-017_TAP to Leland Olds 345kV Circuit 1, near G16-017_TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-PO-2-1 | Prior Outage of Leland Olds to Groton 345kV Circuit 1. 3-phase fault on Leland Olds to Antelope 345kV Circuit 2, near Leland Olds. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-PO-2-2 | Prior Outage of Leland Olds to Groton 345kV Circuit 1. 3-phase fault on Antelope to ROUNDUP 345kV Circuit 2, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-PO-2-3 | Prior Outage of Leland Olds to Groton 345kV Circuit 1. 3-phase fault on Antelope to CHARL_CK 345kV Circuit 1, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-PO-2-4 | Prior Outage of Leland Olds to Groton 345kV Circuit 1. 3-phase fault on Antelope to Broadland 345kV Circuit 1, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-PO-2-6 | Prior Outage of Leland Olds to Groton 345kV Circuit 1. 3-phase fault on Fort Thompson to Grand Prairie 345kV Circuit 1, near Fort Thompson. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-PO-2-7 | Prior Outage of Leland Olds to Groton 345kV Circuit 1. 3-phase fault on Fort Thompson 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-PO-2-8 | Prior Outage of Leland Olds to Groton 345kV Circuit 1. 3-phase fault on Leland Olds 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-PO-2-9 | Prior Outage of Leland Olds to Groton 345kV Circuit 1. 3-phase fault on Leland Olds to Groton 345kV Circuit 1, near Leland Olds. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-PO-3-1 | Prior Outage of Leland Olds to Antelope 345kV Circuit 1. 3-phase fault on Leland Olds to Groton 345kV Circuit 1, near Leland Olds. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-PO-3-3 | Prior Outage of Leland Olds to Antelope 345kV Circuit 1. 3-phase fault on Fort Thompson to Grand Prairie 345kV Circuit 1, near Fort Thompson. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-PO-3-4 | Prior Outage of Leland Olds to Antelope 345kV Circuit 1. 3-phase fault on Fort Thompson 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-PO-3-5 | Prior Outage of Leland Olds to Antelope 345kV Circuit 1. 3-phase fault on Leland Olds 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-PO-4-1 | Prior Outage of Leland Olds 345/230/13.8 kV Transformer 1. 3-phase fault on Leland Olds to Groton 345kV Circuit 1, near Leland Olds. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-PO-4-3 | Prior Outage of Leland Olds 345/230/13.8 kV Transformer 1. 3-phase fault on Fort Thompson to Grand Prairie 345kV Circuit 1, near Fort Thompson. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-PO-4-4 | Prior Outage of Leland Olds 345/230/13.8 kV Transformer 1. 3-phase fault on Fort Thompson 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-PO-4-5 | Prior Outage of Leland Olds 345/230/13.8 kV Transformer 1. 3-phase fault on Leland Olds to Antelope 345kV Circuit 2, near Leland Olds. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-PO-4-6 | Prior Outage of Leland Olds 345/230/13.8 kV Transformer 1. 3-phase fault on Antelope to ROUNDUP 345kV Circuit 2, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-PO-4-7 | Prior Outage of Leland Olds 345/230/13.8 kV Transformer 1. 3-phase fault on Antelope to CHARL_CK 345kV Circuit 1, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-PO-4-8 | Prior Outage of Leland Olds 345/230/13.8 kV Transformer 1. 3-phase fault on Antelope to Broadland 345kV Circuit 1, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-PO-5-1 | Prior Outage of G16-017_TAP to Leland Olds 345kV Circuit 1. 3-phase fault on G16-017_TAP to Fort Thompson 345kV Circuit 1, near G16-017_TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-PO-5-2 | Prior Outage of G16-017_TAP to Leland Olds 345kV Circuit 1. 3-phase fault on Fort Thompson to Grand Prairie 345kV Circuit 1, near Fort Thompson. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-SB-1 | SLG fault on Leland Olds 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Leland Olds to Antelope 345 kV Circuit 1, Leland Olds to Groton 345 kV Circuit 1, Leland Olds to G16-017 TAP Circuit 1 and Leland Olds generator 2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-SB-3 | SLG fault on Antelope 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Antelope 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-SB-4 | SLG fault on Groton 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Groton 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-SB-5 | SLG fault on Leland Olds 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of Leland Olds 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 103-SB-6 | SLG fault on G16-017_TAP 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of G16-017_TAP 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-3PH-1 | 3-phase fault on G17-094-TAP to Fort Thompson 230 kV Circuit 2, near G17-094-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-3PH-2 | 3-phase fault on G17-094-TAP to Huron 230 kV Circuit 2, near G17-094-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-3PH-3 | 3-phase fault on Huron to Broadland 230 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-3PH-4 | 3-phase fault on Huron to Capenter 230 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-3PH-5 | 3-phase fault on Huron to WATERTN 230 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-3PH-6 | 3-phase fault on Huron 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-3PH-7 | 3-phase fault on Fort Thompson 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-3PH-8 | 3-phase fault on Fault Thompson to Leland Olds 345 kV Circuit 1, near Fort Thompson. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 28S | Transfer | 094-3PH-9 | 3-phase fault on CAPENTER 230/69 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-3PH-10 | 3-phase fault on CAPENTER to WATERTN 230 kV Circuit 1, near CAPENTER. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-3PH-11 | 3-phase fault on WATERTN to BLAIR 230 kV Circuit 1, near WATERTN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-3PH-12 | 3-phase fault on WATERTN to APPLEDORN 230 kV Circuit 1, near WATERTN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-3PH-13 | 3-phase fault on WATERTN 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-3PH-14 | 3-phase fault on WATERTN 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-3PH-15 | 3-phase fault on WATERTN to G09_001IST 345 kV Circuit 1, near WATERTN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-3PH-16 | 3-phase fault on WATERTN to WHITE 345 kV Circuit 1, near WATERTN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-3PH-17 | 3-phase fault on Huron to HURONWP 115 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-3PH-18 | 3-phase fault on Huron to Redfield 115 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-3PH-19 | 3-phase fault on Huron to WOONSKT 115 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-3PH-20 | 3-phase fault on HURON 115/69 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-3PH-21 | 3-phase fault on Broadland 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-3PH-22 | 3-phase fault on Broadland to ANTELOPE 345 kV Circuit 1, near Broadland. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-3PH-23 | 3-phase fault on LETCHER to SIOUXFL 230 kV Circuit 1, near LETCHER. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-3PH-24 | 3-phase fault on LETCHER 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-3PH-25 | 3-phase fault on OAHE to PHILIP 230 kV Circuit 1, near OAHE. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-3PH-26 | 3-phase fault on OAHE to SULLYBT 230 kV Circuit 1, near OAHE. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-3PH-27 | 3-phase fault on OAHE 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-3PH-28 | 3-phase fault on FTRANDL to SIOUXCY 230 kV Circuit 1, near FTRANDL. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-3PH-29 | 3-phase fault on FTRANDL to UTICAJC 230 kV Circuit 1, near FTRANDL. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-3PH-30 | 3-phase fault on FTRANDL to MEADOWGROVE 230 kV Circuit 1, near FTRANDL. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-3PH-31 | 3-phase fault on FTRANDL to LAKPLAT 230 kV Circuit 1, near FTRANDL. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-3PH-32 | 3-phase fault on FTRANDL 230/115 kV Transformer 2. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-PO-1-1 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on G17-094-TAP to Fort Thompson 230kV Circuit 2, near G17-04-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-PO-1-2 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on G17-094-TAP to Huron 230 kV Circuit 2, near G17-094-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-PO-1-3 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Fort Thompson to LETCHER 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-PO-1-4 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Fort Thompson to FTRANDL 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-PO-1-5 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Huron to WATERTN 230 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-PO-2-1 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on G17-094-TAP to Fort Thompson 230kV Circuit 2, near G17-04-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-PO-2-2 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on G17-094-TAP to Huron 230 kV Circuit 2, near G17-094-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-PO-2-3 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Fort Thompson to LETCHER 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-PO-2-4 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Fort Thompson to FTRANDL 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-PO-2-5 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Huron to WATERTN 230 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-SB-1 | SLG fault on G17-094-TAP 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of G17-094-TAP 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-SB-2 | SLG fault on Fort Thompson 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of Fort Thompson 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-SB-3 | SLG fault on Huron 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of Huron 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-SB-5 | SLG fault on Huron 115 kV, stuck breaker results delayed clearing after 16 cycles with loss of Huron 115 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-SB-6 | SLG fault on FTRANDL 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of FTRANDL 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-SB-7 | SLG fault on OAHE 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of OAHE 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | 094-SB-8 | SLG fault on WATERTN 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of WATERTN 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | TIE-3PH-1 | 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | TIE-3PH-2 | 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | TIE-3PH-3 | 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 1, near BRKNGCO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | TIE-3PH-4 | 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | TIE-3PH-5 | 3-phase fault on KEYSTON to SD.LS-KS 345 kV Circuit 1, near KEYSTON. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | TIE-3PH-6 | 3-phase fault on THEDFRD to HOLT. CO 345 kV Circuit 1, near THEDFRD. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | TIE-3PH-7 | 3-phase fault on HOLT. CO to ANTELOPE 345 kV Circuit 1, near HOLT. CO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | TIE-3PH-8 | 3-phase fault on HOLT. CO to GR ISLD 345 kV Circuit 1, near HOLT. CO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | TIE-3PH-9 | 3-phase fault on BOBCAT.C to STEGALL 345 kV Circuit 1, near BOBCAT.C. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | TIE-3PH-10 | 3-phase fault on GRPR1 to GR PRAIRIE 345 kV Circuit 1, near GRPR1. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | TIE-PO-1-1 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | TIE-PO-1-2 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3 . Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | TIE-PO-1-3 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | TIE-PO-1-4 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | TIE-PO-2-1 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | TIE-PO-2-2 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | TIE-PO-2-3 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | TIE-PO-3-1 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | TIE-PO-3-2 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | TIE-PO-3-3 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | TIE-SB-1 | SLG fault on BRKNGCO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of BRKNGCO to White 345 kV Circuit1 and BRKNGCO 345/115/13.8 kV Transformer 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | TIE-SB-2 | SLG fault on SPLT RK3 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of SPLT RK3 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | TIE-SB-3 | SLG fault on RAUN 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of RAUN 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | TIE-SB-4 | SLG fault on KEYSTON 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of KEYSTON 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | TIE-SB-5 | SLG fault on THEDFRD 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of THEDFRD 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | TIE-SB-6 | SLG fault on BOBCAT.C 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of BOBCAT.C 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Transfer | TIE-SB-7 | SLG fault on SIOUXCY 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of SIOUXCY 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-1 | 3-phase fault on RHAME to DAGLUM 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-2 | 3-phase fault on RHAME to BOWMAN 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-3 | 3-phase fault on RHAME to BAKER 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-5 | 3-phase fault on DAGLUM to BRADYWND 230 kV Circuit 1, near DAGLUM. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-6 | 3-phase fault on BOWMAN to HERINGR 230 kV Circuit 1, near BOWMAN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-7 | 3-phase fault on BOWMAN 230/115 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-8 | 3-phase fault on BAKER to MI CTYE 230 kV Circuit 1, near BAKER. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-9 | 3-phase fault on BAKER 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-10 | 3-phase fault on BELFELD to DICKINSN 230 kV Circuit 1, near BELFELD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-11 | 3-phase fault on BELFELD to S.HEART 230 kV Circuit 1, near BELFELD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-12 | 3-phase fault on BELFELD to MEDORA 230 kV Circuit 1, near BELFELD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-13 | 3-phase fault on BELFELD 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-14 | 3-phase fault on BELFELD to CHARL_CK 345 kV Circuit 1, near BELFELD. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-15 | 3-phase fault on BOWMAN to NBURR 115 kV Circuit 1, near BOWMAN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-16 | 3-phase fault on HETINGR to BISON 230 kV Circuit 1, near HERINGR. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-17 | 3-phase fault on HETINGR 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-18 | 3-phase fault on BAKER to CABINCR 115 kV Circuit 1, near BAKER. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-19 | 3-phase fault on BAKER 115/69 kV Transformer 2. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-20 | 3-phase fault on MI CTYE to DAWSON 230 kV Circuit 1, near MI CTYE. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-21 | 3-phase fault on MI CTYE 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-PO-1-1 | Prior Outage of RHAME to DAGLUM 230 kV Circuit 1. 3-phase fault on RHAME to BOWMAN 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-PO-1-2 | Prior Outage of RHAME to DAGLUM 230 kV Circuit 1. 3-phase fault on RHAME to BAKER 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-PO-2-1 | Prior Outage of RHAME to BOWMAN 230 kV Circuit 1. 3-phase fault on RHAME to DAGLUM 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-PO-2-2 | Prior Outage of RHAME to BOWMAN 230 kV Circuit 1. 3-phase fault on RHAME to BAKER 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-PO-3-1 | Prior Outage of RHAME to BAKER 230 kV Circuit 1. 3-phase fault on RHAME to DAGLUM 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-PO-3-2 | Prior Outage of RHAME to BAKER 230 kV Circuit 1. 3-phase fault on RHAME to BOWMAN 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-SB-1 | SLG fault on RHAME 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of RHAME 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-SB-2 | SLG fault on DALGUM 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of DALGUM 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-SB-3 | SLG fault on BOWMAN 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of BOWMAN 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-SB-4 | SLG fault on BAKER 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of BAKER 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-SB-6 | SLG fault on BELFELD 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of BELFELD 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-SB-7 | SLG fault on HETINGR 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of HETINGR 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-SB-8 | SLG fault on MI CTYE 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of MI CTYE 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-1 | 3-phase fault on G17-048-TAP to WHEELOCK 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-2 | 3-phase fault on G17-048-TAP to TIOGA 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-3 | 3-phase fault on WHEELOCK 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-4 | 3-phase fault on WHEELOCK to WILISTN 230 kV Circuit 1, near WHEELOCK. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-5 | 3-phase fault on TIOGA to BLAISDEL 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-6 | 3-phase fault on TIOGA to BDV 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-7 | 3-phase fault on TIOGA to NESET 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-8 | 3-phase fault on TIOGA 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-9 | 3-phase fault on WILISTN 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-10 | 3-phase fault on WILISTN to JUDSON 230 kV Circuit 1, near WILISTN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-11 | 3-phase fault on WILISTN to WATFORD 230 kV Circuit 1, near WILISTN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-12 | 3-phase fault on WHEELOCK to ELLISVIL 115 kV Circuit 1, near WHEELOCK. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-13 | 3-phase fault on WHEELOCK to WHEELS_T 115 kV Circuit 1, near WHEELOCK. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-14 | 3-phase fault on BLAISDEL to LOGAN 230 kV Circuit 1, near BLAISDEL. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-15 | 3-phase fault on BLAISDEL 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-16 | 3-phase fault on BD to REGINA 230 kV Circuit 1, near BD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | No | 672321 SHAND generator rotor angle unstable (first swing) and tripped | Remove high speed reclose
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-17 | 3-phase fault on BD to AUBURNTON 230 kV Circuit 1, near BD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | No | 672321 SHAND generator rotor angle unstable (first swing) and tripped | Remove high speed reclose
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-18 | 3-phase fault on BD to SHAND 230 kV Circuit 1, near BD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | No | 672321 SHAND generator rotor angle unstable (first swing) and tripped | Remove high speed reclose
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-19 | 3-phase fault on BD to KISBEY TAP 230 kV Circuit 1, near BD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | No | 672321 SHAND generator rotor angle unstable (first swing) and tripped | Remove high speed reclose
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-20 | 3-phase fault on BD 230/115 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-21 | 3-phase fault on NESET to TANDE 230 kV Circuit 1, near NESET. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-22 | 3-phase fault on NESET 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-23 | 3-phase fault on TIOGA to NESET 115 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-24 | 3-phase fault on TIOGA to STANLEY 115 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-25 | 3-phase fault on TIOGA to RAY JCT 115 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-PO-1-1 | Apply 3-phase fault on G17-048-TAP to TIOGA 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-PO-1-2 | Apply 3-phase fault on TIOGA to NESET 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-PO-1-3 | Apply 3-phase fault on TIOGA to BLAISDEL 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-PO-1-4 | Apply 3-phase fault on TIOGA to BDV 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-PO-2-1 | Apply 3-phase fault on G17-048-TAP to WHEELOCK 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-PO-2-2 | Apply 3-phase fault on WHEELOCK to WILISTN 230 kV Circuit 1, near WHEELOCK. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-PO-2-3 | Apply 3-phase fault on WHEELOCK 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-PO-3-1 | Apply 3-phase fault on G17-048-TAP to TIOGA 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-PO-3-2 | Apply 3-phase fault on G17-048-TAP to WHEELOCK 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-PO-3-3 | Apply 3-phase fault on TIOGA to BLAISDEL 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-PO-3-4 | Apply 3-phase fault on TIOGA to BDV 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-SB-1 | SLG fault on G17-048-TAP 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of G17-048-TAP 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-SB-2 | SLG fault on WHEELOCK 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of WHEELOCK 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-SB-4 | SLG fault on TIOGA 115 kV, stuck breaker results delayed clearing after 16 cycles with loss of TIOGA 115 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-SB-5 | SLG fault on WILISTN 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of WILISTN 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-SB-6 | SLG fault on BLAISDEL 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of BLAISDEL 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-SB-7 | SLG fault on BD 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of BD to Regina 230 kV Circuit 1, BD to AUBURNTON 230 kV Circuit 1, BD to KISBEY 230 kV Circuit 1, BD Generator 5 and BD Generator 6. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-SB-8 | SLG fault on NESET 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of NESET 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-3PH-1 | 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-3PH-2 | 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK33-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-3PH-3 | 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 1, near BRKNGCO3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-3PH-4 | 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-3PH-5 | 3-phase fault on KEYSTON to SD.LS-KS 345 kV Circuit 1, near KEYSTON3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-3PH-6 | 3-phase fault on THEDFRD to HOLT. CO 345 kV Circuit 1, near THEDFRD3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-3PH-7 | 3-phase fault on HOLT. CO to ANTELOPE 345 kV Circuit 1, near HOLT. CO3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-3PH-8 | 3-phase fault on HOLT. CO to GR ISLD 345 kV Circuit 1, near HOLT. CO3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-3PH-9 | 3-phase fault on BOBCAT.C to STEGALL 345 kV Circuit 1, near BOBCAT.C3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-PO-1-1 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-PO-1-2 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK33-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-PO-1-3 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK33-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-PO-1-4 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-PO-2-1 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-PO-2-2 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK33-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-PO-2-3 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-PO-3-1 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-PO-3-2 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK33-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-PO-3-3 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-SB-1 | SLG fault on BRKNGCO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of BRKNGCO 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-SB-2 | SLG fault on SPLT RK3 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of SPLT RK3 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-SB-3 | SLG fault on RAUN 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of RAUN 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-SB-4 | SLG fault on KEYSTON 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of KEYSTON 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-SB-5 | SLG fault on THEDFRD 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of THEDFRD 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-SB-6 | SLG fault on BOBCAT.C 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of BOBCAT.C 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-SB-7 | SLG fault on SIOUXCY 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of SIOUXCY 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-1 | 3-phase fault on RHAME to DAGLUM 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-2 | 3-phase fault on RHAME to BOWMAN 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-3 | 3-phase fault on RHAME to BAKER 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-5 | 3-phase fault on DAGLUM to BRADYWND 230 kV Circuit 1, near DAGLUM. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-6 | 3-phase fault on BOWMAN to HERINGR 230 kV Circuit 1, near BOWMAN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-7 | 3-phase fault on BOWMAN 230/115 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-8 | 3-phase fault on BAKER to MI CTYE 230 kV Circuit 1, near BAKER. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-9 | 3-phase fault on BAKER 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-10 | 3-phase fault on BELFELD to DICKINSN 230 kV Circuit 1, near BELFELD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-11 | 3-phase fault on BELFELD to S.HEART 230 kV Circuit 1, near BELFELD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-12 | 3-phase fault on BELFELD to MEDORA 230 kV Circuit 1, near BELFELD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-13 | 3-phase fault on BELFELD 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-14 | 3-phase fault on BELFELD to CHARL_CK 345 kV Circuit 1, near BELFELD. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-15 | 3-phase fault on BOWMAN to NBURR 115 kV Circuit 1, near BOWMAN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-16 | 3-phase fault on HETINGR to BISON 230 kV Circuit 1, near HERINGR. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-17 | 3-phase fault on HETINGR 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-18 | 3-phase fault on BAKER to CABINCR 115 kV Circuit 1, near BAKER. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-19 | 3-phase fault on BAKER 115/69 kV Transformer 2. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-20 | 3-phase fault on MI CTYE to DAWSON 230 kV Circuit 1, near MI CTYE. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-21 | 3-phase fault on MI CTYE 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-PO-1-1 | Prior Outage of RHAME to DAGLUM 230 kV Circuit 1. 3-phase fault on RHAME to BOWMAN 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-PO-1-2 | Prior Outage of RHAME to DAGLUM 230 kV Circuit 1. 3-phase fault on RHAME to BAKER 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-PO-2-1 | Prior Outage of RHAME to BOWMAN 230 kV Circuit 1. 3-phase fault on RHAME to DAGLUM 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-PO-2-2 | Prior Outage of RHAME to BOWMAN 230 kV Circuit 1. 3-phase fault on RHAME to BAKER 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-PO-3-1 | Prior Outage of RHAME to BAKER 230 kV Circuit 1. 3-phase fault on RHAME to DAGLUM 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-PO-3-2 | Prior Outage of RHAME to BAKER 230 kV Circuit 1. 3-phase fault on RHAME to BOWMAN 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-SB-1 | SLG fault on RHAME 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of RHAME 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-SB-2 | SLG fault on DALGUM 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of DALGUM 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-SB-3 | SLG fault on BOWMAN 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of BOWMAN 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-SB-4 | SLG fault on BAKER 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of BAKER 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-SB-6 | SLG fault on BELFELD 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of BELFELD 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-SB-7 | SLG fault on HETINGR 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of HETINGR 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-SB-8 | SLG fault on MI CTYE 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of MI CTYE 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-1 | 3-phase fault on G17-048-TAP to WHEELOCK 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-2 | 3-phase fault on G17-048-TAP to TIOGA 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-3 | 3-phase fault on WHEELOCK 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-4 | 3-phase fault on WHEELOCK to WILISTN 230 kV Circuit 1, near WHEELOCK. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-5 | 3-phase fault on TIOGA to BLAISDEL 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-6 | 3-phase fault on TIOGA to BDV 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-7 | 3-phase fault on TIOGA to NESET 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-8 | 3-phase fault on TIOGA 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-9 | 3-phase fault on WILISTN 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-10 | 3-phase fault on WILISTN to JUDSON 230 kV Circuit 1, near WILISTN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-11 | 3-phase fault on WILISTN to WATFORD 230 kV Circuit 1, near WILISTN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-12 | 3-phase fault on WHEELOCK to ELLISVIL 115 kV Circuit 1, near WHEELOCK. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-13 | 3-phase fault on WHEELOCK to WHEELS_T 115 kV Circuit 1, near WHEELOCK. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-14 | 3-phase fault on BLAISDEL to LOGAN 230 kV Circuit 1, near BLAISDEL. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-15 | 3-phase fault on BLAISDEL 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-16 | 3-phase fault on BD to REGINA 230 kV Circuit 1, near BD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | No | 672321 SHAND and 672303 BD generators rotor angle unstable (first swing) and tripped | Remove high speed reclose
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-17 | 3-phase fault on BD to AUBURNTON 230 kV Circuit 1, near BD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | No | 672321 SHAND and 672303 BD generators rotor angle unstable (first swing) and tripped | Remove high speed reclose
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-18 | 3-phase fault on BD to SHAND 230 kV Circuit 1, near BD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | No | 672321 SHAND generator rotor angle unstable (first swing) and tripped | Remove high speed reclose
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-19 | 3-phase fault on BD to KISBEY TAP 230 kV Circuit 1, near BD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | No | 672321 SHAND and 672303 BD generators rotor angle unstable (first swing) and tripped | Remove high speed reclose
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-20 | 3-phase fault on BD 230/115 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-21 | 3-phase fault on NESET to TANDE 230 kV Circuit 1, near NESET. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-22 | 3-phase fault on NESET 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-23 | 3-phase fault on TIOGA to NESET 115 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-24 | 3-phase fault on TIOGA to STANLEY 115 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-25 | 3-phase fault on TIOGA to RAY JCT 115 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-PO-1-1 | Apply 3-phase fault on G17-048-TAP to TIOGA 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-PO-1-2 | Apply 3-phase fault on TIOGA to NESET 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-PO-1-3 | Apply 3-phase fault on TIOGA to BLAISDEL 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-PO-1-4 | Apply 3-phase fault on TIOGA to BDV 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-PO-2-1 | Apply 3-phase fault on G17-048-TAP to WHEELOCK 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-PO-2-2 | Apply 3-phase fault on WHEELOCK to WILISTN 230 kV Circuit 1, near WHEELOCK. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-PO-2-3 | Apply 3-phase fault on WHEELOCK 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-PO-3-1 | Apply 3-phase fault on G17-048-TAP to TIOGA 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-PO-3-2 | Apply 3-phase fault on G17-048-TAP to WHEELOCK 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-PO-3-3 | Apply 3-phase fault on TIOGA to BLAISDEL 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-PO-3-4 | Apply 3-phase fault on TIOGA to BDV 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-SB-1 | SLG fault on G17-048-TAP 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of G17-048-TAP 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-SB-2 | SLG fault on WHEELOCK 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of WHEELOCK 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-SB-3 | SLG fault on TIOGA 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of TIOGA 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-SB-4 | SLG fault on TIOGA 115 kV, stuck breaker results delayed clearing after 16 cycles with loss of TIOGA 115 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-SB-5 | SLG fault on WILISTN 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of WILISTN 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-SB-6 | SLG fault on BLAISDEL 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of BLAISDEL 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-SB-7 | SLG fault on BD 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of BD to Regina 230 kV Circuit 1, BD to AUBURNTON 230 kV Circuit 1, BD to KISBEY 230 kV Circuit 1, BD Generator 5 and BD Generator 6. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-SB-8 | SLG fault on NESET 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of NESET 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-3PH-1 | 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-3PH-2 | 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK33-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-3PH-3 | 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 1, near BRKNGCO3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-3PH-4 | 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-3PH-5 | 3-phase fault on KEYSTON to SD.LS-KS 345 kV Circuit 1, near KEYSTON3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-3PH-6 | 3-phase fault on THEDFRD to HOLT. CO 345 kV Circuit 1, near THEDFRD3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-3PH-7 | 3-phase fault on HOLT. CO to ANTELOPE 345 kV Circuit 1, near HOLT. CO3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-3PH-8 | 3-phase fault on HOLT. CO to GR ISLD 345 kV Circuit 1, near HOLT. CO3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-3PH-9 | 3-phase fault on BOBCAT.C to STEGALL 345 kV Circuit 1, near BOBCAT.C3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-PO-1-1 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-PO-1-2 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK33-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-PO-1-3 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK33-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-PO-1-4 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-PO-2-1 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-PO-2-2 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK33-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-PO-2-3 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-PO-3-1 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-PO-3-2 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK33-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-PO-3-3 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-SB-1 | SLG fault on BRKNGCO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of BRKNGCO 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-SB-2 | SLG fault on SPLT RK3 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of SPLT RK3 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-SB-3 | SLG fault on RAUN 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of RAUN 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-SB-4 | SLG fault on KEYSTON 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of KEYSTON 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-SB-5 | SLG fault on THEDFRD 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of THEDFRD 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-SB-6 | SLG fault on BOBCAT.C 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of BOBCAT.C 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-SB-7 | SLG fault on SIOUXCY 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of SIOUXCY 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-1 | 3-phase fault on RHAME to DAGLUM 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-2 | 3-phase fault on RHAME to BOWMAN 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-3 | 3-phase fault on RHAME to BAKER 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-5 | 3-phase fault on DAGLUM to BRADYWND 230 kV Circuit 1, near DAGLUM. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-6 | 3-phase fault on BOWMAN to HERINGR 230 kV Circuit 1, near BOWMAN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-7 | 3-phase fault on BOWMAN 230/115 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-8 | 3-phase fault on BAKER to MI CTYE 230 kV Circuit 1, near BAKER. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-9 | 3-phase fault on BAKER 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-10 | 3-phase fault on BELFELD to DICKINSN 230 kV Circuit 1, near BELFELD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-11 | 3-phase fault on BELFELD to S.HEART 230 kV Circuit 1, near BELFELD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-12 | 3-phase fault on BELFELD to MEDORA 230 kV Circuit 1, near BELFELD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-13 | 3-phase fault on BELFELD 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-14 | 3-phase fault on BELFELD to CHARL_CK 345 kV Circuit 1, near BELFELD. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-15 | 3-phase fault on BOWMAN to NBURR 115 kV Circuit 1, near BOWMAN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-16 | 3-phase fault on HETINGR to BISON 230 kV Circuit 1, near HERINGR. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-17 | 3-phase fault on HETINGR 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-18 | 3-phase fault on BAKER to CABINCR 115 kV Circuit 1, near BAKER. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-19 | 3-phase fault on BAKER 115/69 kV Transformer 2. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-20 | 3-phase fault on MI CTYE to DAWSON 230 kV Circuit 1, near MI CTYE. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-21 | 3-phase fault on MI CTYE 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-PO-1-1 | Prior Outage of RHAME to DAGLUM 230 kV Circuit 1. 3-phase fault on RHAME to BOWMAN 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-PO-1-2 | Prior Outage of RHAME to DAGLUM 230 kV Circuit 1. 3-phase fault on RHAME to BAKER 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-PO-2-1 | Prior Outage of RHAME to BOWMAN 230 kV Circuit 1. 3-phase fault on RHAME to DAGLUM 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-PO-2-2 | Prior Outage of RHAME to BOWMAN 230 kV Circuit 1. 3-phase fault on RHAME to BAKER 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-PO-3-1 | Prior Outage of RHAME to BAKER 230 kV Circuit 1. 3-phase fault on RHAME to DAGLUM 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-PO-3-2 | Prior Outage of RHAME to BAKER 230 kV Circuit 1. 3-phase fault on RHAME to BOWMAN 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-SB-1 | SLG fault on RHAME 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of RHAME 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-SB-2 | SLG fault on DALGUM 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of DALGUM 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-SB-3 | SLG fault on BOWMAN 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of BOWMAN 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-SB-4 | SLG fault on BAKER 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of BAKER 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-SB-6 | SLG fault on BELFELD 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of BELFELD 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-SB-7 | SLG fault on HETINGR 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of HETINGR 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-SB-8 | SLG fault on MI CTYE 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of MI CTYE 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-1 | 3-phase fault on G17-048-TAP to WHEELOCK 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-2 | 3-phase fault on G17-048-TAP to TIOGA 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-3 | 3-phase fault on WHEELOCK 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-4 | 3-phase fault on WHEELOCK to WILISTN 230 kV Circuit 1, near WHEELOCK. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-5 | 3-phase fault on TIOGA to BLAISDEL 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-7 | 3-phase fault on TIOGA to NESET 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-8 | 3-phase fault on TIOGA 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-9 | 3-phase fault on WILISTN 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-10 | 3-phase fault on WILISTN to JUDSON 230 kV Circuit 1, near WILISTN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-11 | 3-phase fault on WILISTN to WATFORD 230 kV Circuit 1, near WILISTN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-12 | 3-phase fault on WHEELOCK to ELLISVIL 115 kV Circuit 1, near WHEELOCK. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-13 | 3-phase fault on WHEELOCK to WHEELS_T 115 kV Circuit 1, near WHEELOCK. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-14 | 3-phase fault on BLAISDEL to LOGAN 230 kV Circuit 1, near BLAISDEL. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-15 | 3-phase fault on BLAISDEL 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-16 | 3-phase fault on BD to REGINA 230 kV Circuit 1, near BD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | No | 672321 SHAND and 672303 BD generators rotor angle unstable (first swing) and tripped | Remove high speed reclose
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-17 | 3-phase fault on BD to AUBURNTON 230 kV Circuit 1, near BD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | No | 672321 SHAND generator rotor angle unstable (first swing) and tripped | Remove high speed reclose
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-18 | 3-phase fault on BD to SHAND 230 kV Circuit 1, near BD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | No | 672321 SHAND generator rotor angle unstable (first swing) and tripped | Remove high speed reclose
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-19 | 3-phase fault on BD to KISBEY TAP 230 kV Circuit 1, near BD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | No | 672321 SHAND and 672303 BD generators rotor angle unstable (first swing) and tripped | Remove high speed reclose
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-20 | 3-phase fault on BD 230/115 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-21 | 3-phase fault on NESET to TANDE 230 kV Circuit 1, near NESET. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-22 | 3-phase fault on NESET 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-23 | 3-phase fault on TIOGA to NESET 115 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-24 | 3-phase fault on TIOGA to STANLEY 115 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-25 | 3-phase fault on TIOGA to RAY JCT 115 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-PO-1-1 | Apply 3-phase fault on G17-048-TAP to TIOGA 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-PO-1-2 | Apply 3-phase fault on TIOGA to NESET 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-PO-1-3 | Apply 3-phase fault on TIOGA to BLAISDEL 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-PO-2-1 | Apply 3-phase fault on G17-048-TAP to WHEELOCK 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-PO-2-2 | Apply 3-phase fault on WHEELOCK to WILISTN 230 kV Circuit 1, near WHEELOCK. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-PO-2-3 | Apply 3-phase fault on WHEELOCK 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-PO-3-1 | Apply 3-phase fault on G17-048-TAP to TIOGA 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-PO-3-2 | Apply 3-phase fault on G17-048-TAP to WHEELOCK 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-PO-3-3 | Apply 3-phase fault on TIOGA to BLAISDEL 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-SB-1 | SLG fault on G17-048-TAP 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of G17-048-TAP 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-SB-2 | SLG fault on WHEELOCK 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of WHEELOCK 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-SB-4 | SLG fault on TIOGA 115 kV, stuck breaker results delayed clearing after 16 cycles with loss of TIOGA 115 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-SB-5 | SLG fault on WILISTN 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of WILISTN 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-SB-6 | SLG fault on BLAISDEL 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of BLAISDEL 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-SB-7 | SLG fault on BD 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of BD to Regina 230 kV Circuit 1, BD to AUBURNTON 230 kV Circuit 1, BD to KISBEY 230 kV Circuit 1, BD Generator 5 and BD Generator 6. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-SB-8 | SLG fault on NESET 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of NESET 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-3PH-1 | 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-3PH-2 | 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK33-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-3PH-3 | 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 1, near BRKNGCO3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-3PH-4 | 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-3PH-5 | 3-phase fault on KEYSTON to SD.LS-KS 345 kV Circuit 1, near KEYSTON3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-3PH-6 | 3-phase fault on THEDFRD to HOLT. CO 345 kV Circuit 1, near THEDFRD3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-3PH-7 | 3-phase fault on HOLT. CO to ANTELOPE 345 kV Circuit 1, near HOLT. CO3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-3PH-8 | 3-phase fault on HOLT. CO to GR ISLD 345 kV Circuit 1, near HOLT. CO3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-3PH-9 | 3-phase fault on BOBCAT.C to STEGALL 345 kV Circuit 1, near BOBCAT.C3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-PO-1-1 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-PO-1-2 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK33-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-PO-1-3 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK33-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-PO-1-4 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-PO-2-1 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-PO-2-2 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK33-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-PO-2-3 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-PO-3-1 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-PO-3-2 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK33-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-PO-3-3 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-SB-1 | SLG fault on BRKNGCO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of BRKNGCO 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-SB-2 | SLG fault on SPLT RK3 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of SPLT RK3 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-SB-3 | SLG fault on RAUN 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of RAUN 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-SB-4 | SLG fault on KEYSTON 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of KEYSTON 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-SB-5 | SLG fault on THEDFRD 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of THEDFRD 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-SB-6 | SLG fault on BOBCAT.C 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of BOBCAT.C 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-SB-7 | SLG fault on SIOUXCY 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of SIOUXCY 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-1 | 3-phase fault on RHAME to DAGLUM 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-2 | 3-phase fault on RHAME to BOWMAN 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-3 | 3-phase fault on RHAME to BAKER 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-4 | 3-phase fault on DAGLUM to BELFELD 230 kV Circuit 1, near DAGLUM. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-5 | 3-phase fault on DAGLUM to BRADYWND 230 kV Circuit 1, near DAGLUM. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-6 | 3-phase fault on BOWMAN to HERINGR 230 kV Circuit 1, near BOWMAN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-7 | 3-phase fault on BOWMAN 230/115 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-8 | 3-phase fault on BAKER to MI CTYE 230 kV Circuit 1, near BAKER. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-9 | 3-phase fault on BAKER 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-10 | 3-phase fault on BELFELD to DICKINSN 230 kV Circuit 1, near BELFELD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-11 | 3-phase fault on BELFELD to S.HEART 230 kV Circuit 1, near BELFELD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-12 | 3-phase fault on BELFELD to MEDORA 230 kV Circuit 1, near BELFELD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-13 | 3-phase fault on BELFELD 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-14 | 3-phase fault on BELFELD to CHARL_CK 345 kV Circuit 1, near BELFELD. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-15 | 3-phase fault on BOWMAN to NBURR 115 kV Circuit 1, near BOWMAN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-16 | 3-phase fault on HETINGR to BISON 230 kV Circuit 1, near HERINGR. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-17 | 3-phase fault on HETINGR 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-18 | 3-phase fault on BAKER to CABINCR 115 kV Circuit 1, near BAKER. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-19 | 3-phase fault on BAKER 115/69 kV Transformer 2. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-20 | 3-phase fault on MI CTYE to DAWSON 230 kV Circuit 1, near MI CTYE. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-21 | 3-phase fault on MI CTYE 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-PO-1-1 | Prior Outage of RHAME to DAGLUM 230 kV Circuit 1. 3-phase fault on RHAME to BOWMAN 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-PO-1-2 | Prior Outage of RHAME to DAGLUM 230 kV Circuit 1. 3-phase fault on RHAME to BAKER 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-PO-2-1 | Prior Outage of RHAME to BOWMAN 230 kV Circuit 1. 3-phase fault on RHAME to DAGLUM 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-PO-2-2 | Prior Outage of RHAME to BOWMAN 230 kV Circuit 1. 3-phase fault on RHAME to BAKER 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-PO-3-1 | Prior Outage of RHAME to BAKER 230 kV Circuit 1. 3-phase fault on RHAME to DAGLUM 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-PO-3-2 | Prior Outage of RHAME to BAKER 230 kV Circuit 1. 3-phase fault on RHAME to BOWMAN 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-SB-1 | SLG fault on RHAME 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of RHAME 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-SB-2 | SLG fault on DALGUM 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of DALGUM 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-SB-3 | SLG fault on BOWMAN 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of BOWMAN 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-SB-4 | SLG fault on BAKER 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of BAKER 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-SB-6 | SLG fault on BELFELD 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of BELFELD 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-SB-7 | SLG fault on HETINGR 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of HETINGR 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-SB-8 | SLG fault on MI CTYE 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of MI CTYE 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-1 | 3-phase fault on G17-048-TAP to WHEELOCK 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-2 | 3-phase fault on G17-048-TAP to TIOGA 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-3 | 3-phase fault on WHEELOCK 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-4 | 3-phase fault on WHEELOCK to WILISTN 230 kV Circuit 1, near WHEELOCK. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-5 | 3-phase fault on TIOGA to BLAISDEL 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-6 | 3-phase fault on TIOGA to BDV 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-7 | 3-phase fault on TIOGA to NESET 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-8 | 3-phase fault on TIOGA 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-9 | 3-phase fault on WILISTN 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-10 | 3-phase fault on WILISTN to JUDSON 230 kV Circuit 1, near WILISTN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-11 | 3-phase fault on WILISTN to WATFORD 230 kV Circuit 1, near WILISTN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-12 | 3-phase fault on WHEELOCK to ELLISVIL 115 kV Circuit 1, near WHEELOCK. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-13 | 3-phase fault on WHEELOCK to WHEELS_T 115 kV Circuit 1, near WHEELOCK. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-14 | 3-phase fault on BLAISDEL to LOGAN 230 kV Circuit 1, near BLAISDEL. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-15 | 3-phase fault on BLAISDEL 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-16 | 3-phase fault on BD to REGINA 230 kV Circuit 1, near BD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | No | 672321 SHAND and 672303 BD generators rotor angle unstable (first swing) and tripped | Remove high speed reclose
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-17 | 3-phase fault on BD to AUBURNTON 230 kV Circuit 1, near BD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-18 | 3-phase fault on BD to SHAND 230 kV Circuit 1, near BD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | No | 672321 SHAND generator rotor angle unstable (first swing) and tripped | Remove high speed reclose
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-19 | 3-phase fault on BD to KISBEY TAP 230 kV Circuit 1, near BD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-20 | 3-phase fault on BD 230/115 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-21 | 3-phase fault on NESET to TANDE 230 kV Circuit 1, near NESET. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-22 | 3-phase fault on NESET 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-23 | 3-phase fault on TIOGA to NESET 115 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-24 | 3-phase fault on TIOGA to STANLEY 115 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-25 | 3-phase fault on TIOGA to RAY JCT 115 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-PO-1-1 | Apply 3-phase fault on G17-048-TAP to TIOGA 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-PO-1-2 | Apply 3-phase fault on TIOGA to NESET 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-PO-1-3 | Apply 3-phase fault on TIOGA to BLAISDEL 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-PO-1-4 | Apply 3-phase fault on TIOGA to BDV 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-PO-2-1 | Apply 3-phase fault on G17-048-TAP to WHEELOCK 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-PO-2-2 | Apply 3-phase fault on WHEELOCK to WILISTN 230 kV Circuit 1, near WHEELOCK. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-PO-2-3 | Apply 3-phase fault on WHEELOCK 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-PO-3-1 | Apply 3-phase fault on G17-048-TAP to TIOGA 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-PO-3-2 | Apply 3-phase fault on G17-048-TAP to WHEELOCK 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-PO-3-3 | Apply 3-phase fault on TIOGA to BLAISDEL 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-PO-3-4 | Apply 3-phase fault on TIOGA to BDV 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-SB-1 | SLG fault on G17-048-TAP 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of G17-048-TAP 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-SB-2 | SLG fault on WHEELOCK 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of WHEELOCK 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-SB-3 | SLG fault on TIOGA 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of TIOGA 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-SB-4 | SLG fault on TIOGA 115 kV, stuck breaker results delayed clearing after 16 cycles with loss of TIOGA 115 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-SB-5 | SLG fault on WILISTN 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of WILISTN 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-SB-6 | SLG fault on BLAISDEL 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of BLAISDEL 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-SB-7 | SLG fault on BD 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of BD to Regina 230 kV Circuit 1, BD to AUBURNTON 230 kV Circuit 1, BD to KISBEY 230 kV Circuit 1, BD Generator 5 and BD Generator 6. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-SB-8 | SLG fault on NESET 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of NESET 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-3PH-1 | 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-3PH-2 | 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK33-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-3PH-3 | 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 1, near BRKNGCO3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-3PH-4 | 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-3PH-5 | 3-phase fault on KEYSTON to SD.LS-KS 345 kV Circuit 1, near KEYSTON3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-3PH-6 | 3-phase fault on THEDFRD to HOLT. CO 345 kV Circuit 1, near THEDFRD3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-3PH-7 | 3-phase fault on HOLT. CO to ANTELOPE 345 kV Circuit 1, near HOLT. CO3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-3PH-8 | 3-phase fault on HOLT. CO to GR ISLD 345 kV Circuit 1, near HOLT. CO3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-3PH-9 | 3-phase fault on BOBCAT.C to STEGALL 345 kV Circuit 1, near BOBCAT.C3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-PO-1-1 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-PO-1-2 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK33-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-PO-1-3 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK33-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-PO-1-4 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-PO-2-1 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-PO-2-2 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK33-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-PO-2-3 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-PO-3-1 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-PO-3-2 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK33-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-PO-3-3 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-SB-1 | SLG fault on BRKNGCO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of BRKNGCO 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-SB-2 | SLG fault on SPLT RK3 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of SPLT RK3 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-SB-3 | SLG fault on RAUN 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of RAUN 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-SB-4 | SLG fault on KEYSTON 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of KEYSTON 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-SB-5 | SLG fault on THEDFRD 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of THEDFRD 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-SB-6 | SLG fault on BOBCAT.C 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of BOBCAT.C 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-SB-7 | SLG fault on SIOUXCY 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of SIOUXCY 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-01 | 3-ph fault on G17-014-TAP to Underwood 230kV crt 1, near G17-014-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-03 | 3-ph fault on G17-064-TAP to Wayside 230kV crt 1, near G17-064-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-04 | 3-ph fault on G17-064-TAP to Wayside 230kV crt 1, near G17-064-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-05 | 3-ph fault on Underwood to RUSHMORE to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-06 | 3-ph fault on Underwood to ELSWRTH7 to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-07 | 3-ph fault on Underwood to WICKSVL7 to PHILIP 7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-08 | 3-ph fault on Underwood 230/115/13.8kV TF 2A, near Underwood 115kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-09 | 3-ph fault on Underwood 230/115/13.8kV TF 1A, near Underwood 115kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-10 | 3-ph fault on Underwood to G17-014-TAP 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-11 | 3-ph fault on Underwood to G17-064-TAP 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-12 | 3-ph fault on Underwood to DRYCREEK 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-13 | 3-ph fault on Underwood to MAURINE 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-14 | 3-ph fault on Philip Tap to Philip 230kV crt 1, near Philip Tap. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-15 | 3-ph fault on Philip Tap to OAHE 230kV crt 1, near Philip Tap. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-16 | 3-ph fault on Wayside to STEGALL 230kV crt 1, near Wayside. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-17 | 3-ph fault on Wayside 230/115/13.8kV TF T1, near Wayside 230kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-18 | 3-ph fault on RAPIDCY7 to DRYCREEK 115kV crt 1, near RAPIDCY7. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-19 | 3-ph fault on RAPIDCY7 to ELKCRK 7 to G14_001IST 115kV crt 1, near RAPIDCY7. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-20 | 3-ph fault on Philip to Midland to IRVSIMM7 115kV crt 1, near Philip. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-21 | 3-ph fault on Philip to WANBLEE to MARTIN 115kV crt 1, near Philip. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-22 | 3-ph fault on Philip 230/115/13.2kV TF 1A, near Philip 115kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-23 | 3-ph fault on OAHE to G16-094-TAP 230kV crt 1, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-24 | 3-ph fault on OAHE to FTTHOMP4 230kV crt 2, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-25 | 3-ph fault on OAHE to SULLYBT-ER4 230kV crt 1, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-26 | 3-ph fault on MAURINE to BISON 230kV crt 1, near MAURINE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-27 | 3-ph fault on MAURINE 230/115/13.8kV TF 1A, near MAURINE 230kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-28 | 3-ph fault on STEGALL to DH_CS_EA-TS4 230kV crt 1, near STEGALL. Clear fault after 7 cycles by tripping the faulted crt, and DH_CS_EA-TS DC line. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-29 | 3-ph fault on STEGALL to STEGALL_-MB4 230kV crt 1, near STEGALL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-30 | 3-ph fault on STEGALL to VICTRYH4 230kV crt 1, near STEGALL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-31 | 3-ph fault on DRYCREEK to RCDC 230kV crt 1, near DRYCREEK. Clear fault after 7 cycles by tripping the faulted crt, and RCDC DC line. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-32 | 3-ph fault on DRYCREEK 230/115/13.8kV TF 1A, near DRYCREEK. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-33 | 3-ph fault on G14_001IST to MAURINE7 115kV crt 1, near G14_001IST. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-34 | 3-ph fault on Martin to SHANNON 115kV crt 1, near Martin. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-35 | 3-ph fault on Martin to VETAL_TP 115kV crt 1, near Martin. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-36 | 3-ph fault on IRVSIMM7 to OAHE 115kV crt 1, near IRVSIMM7. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-37 | 3-ph fault on IRVSIMM7 to PIERRE 115kV crt 1, near IRVSIMM7. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | SLG-38 | SLG fault on G17-064-TAP to Wayside 230kV crt 1, near G17-064-TAP for 16 cycles. Clear fault by tripping the Wayside 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | SLG-39 | SLG fault on G17-064-TAP to Underwood 230kV crt 1, near G17-064-TAP for 16 cycles. Clear fault by tripping the Underwood 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | SLG-41 | SLG fault on G17-014-TAP to Underwood 230kV crt 1, near G17-014-TAP for 16 cycles. Clear fault by tripping the Underwood 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | SLG-42 | SLG fault on Underwood to RUSHMORE to RAPIDCY7 115kV crt 1, near Underwood for 16 cycles. Clear fault by tripping the RUSHMORE 115kV bus and RAPIDCY7 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | SLG-43 | SLG fault on Underwood to ELSWRTH7 to RAPIDCY7 115kV crt 1, near Underwood for 16 cycles. Clear fault by tripping the ELSWRTH7 115kV bus and RAPIDCY7 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | SLG-44 | SLG fault on Underwood to WICKSVL7 to Philip 115kV crt 1, near Underwood for 16 cycles. Clear fault by tripping the WICKSVL7 115kV bus, WALL 115kV bus and Philip 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | SLG-45 | SLG fault on Philip Tap to OAHE 230kV crt 1, near Philip Tap for 16 cycles. Clear fault by tripping the faulted crt and OAHE to G16-094-TAP 230kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | SLG-46 | SLG fault on Philip Tap to OAHE 230kV crt 1, near Philip Tap for 16 cycles. Clear fault by tripping the faulted crt and OAHE to FTTHOMP4 230kV crt 2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | SLG-47 | SLG fault on Philip Tap to OAHE 230kV crt 1, near Philip Tap for 16 cycles. Clear fault by tripping the faulted crt and OAHE to SULLYBT 230kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | SLG-48 | SLG fault on Wayside to STEGALL 230kV crt 1, near Wayside for 16 cycles. Clear fault by tripping the faulted crt and STEGALL4 230kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | SLG-49 | SLG fault on Underwood to DRYCREEK 230kV crt 1, near Underwood for 16 cycles. Clear fault by tripping the DRYCREEK 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | SLG-50 | SLG fault on Underwood to MAURINE 230kV crt 1, near Underwood for 16 cycles. Clear fault by tripping the MAURINE 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | SLG-51 | SLG fault on RAPIDCY7 to ELKCRK 7 to G14_001IST 115kV crt 1, near RAPIDCY7 for 16 cycles. Clear fault by tripping the ELKCRK 7 115kV bus, NEWELL 115kV bus, meantime trip the G14_001IST 115kV bus and G14_001IS_3 generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | SLG-52 | SLG fault on RAPIDCY7 to DRYCREEK 115kV crt 1, near RAPIDCY7 for 16 cycles. Clear fault by tripping the DRYCREEK 115kV bus and DRYCREEK 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | SLG-53 | SLG fault on Philip to Midland to IRVSIMM7 115kV crt 1, near Philip for 16 cycles. Clear fault by tripping the Midland 115kV bus and IRVSIMM7 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | SLG-54 | SLG fault on Philip to WANBLEE to Martin 115kV crt 1, near Philip for 16 cycles. Clear fault by tripping the WANBLEE 115kV bus and Martin 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-56 | Prior Outage of G17-014-TAP to Philip Tap 230kV crt 1. 3-ph fault on G17-014-TAP to Underwood 230kV crt 1, near G17-014-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. Meantime, trip G17-014 generators. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-57 | Prior Outage of G17-014-TAP to Underwood 230kV crt 1. 3-ph fault on G17-014-TAP to Philip Tap 230kV crt 1, near G17-014-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. Meantime, trip G17-014 generators. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-58 | Prior Outage of G17-064-TAP to Underwood 230kV crt 1. 3-ph fault on G17-064-TAP to Wayside 230kV crt 1, near G17-064-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. Meantime trip G17-064 generators. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-59 | Prior Outage of G17-064-TAP to Wayside 230kV crt 1. 3-ph fault on G17-064-TAP to Underwood 230kV crt 1, near G17-064-TAP. Clear fault after 7 cycles and trip G17-064 generators. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-60 | Prior Outage of Underwood to RUSHMORE 115kV crt 1. 3-ph fault on Underwood to ELSWRTH7 to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-61 | Prior Outage of Underwood to RUSHMORE 115kV crt 1. 3-ph fault on Underwood to WICKSVL7 to PHILIP 7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-62 | Prior Outage of Underwood to RUSHMORE 115kV crt 1. 3-ph fault on Underwood 230/115/13.8kV TF 1A, near Underwood 115kV. Clear fault after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-63 | Prior Outage of Underwood to ELSWRTH7 115kV crt 1. 3-ph fault on Underwood to RUSHMORE to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-64 | Prior Outage of Underwood to ELSWRTH7 115kV crt 1. 3-ph fault on Underwood to WICKSVL7 to PHILIP 7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-65 | Prior Outage of Underwood to ELSWRTH7 115kV crt 1. 3-ph fault on Underwood 230/115/13.8kV TF 1A, near Underwood 115kV. Clear fault after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-66 | Prior Outage of Underwood to WICKSVL7 115kV crt 1. 3-ph fault on Underwood to RUSHMORE to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-67 | Prior Outage of Underwood to WICKSVL7 115kV crt 1. 3-ph fault on Underwood to ELSWRTH7 to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-68 | Prior Outage of Underwood to WICKSVL7 115kV crt 1. 3-ph fault on Underwood 230/115/13.8kV TF 1A, near Underwood 115kV. Clear fault after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-69 | Prior Outage of Underwood 230/115/13.8kV TF 1A. 3-ph fault on Underwood 230/115/13.8kV TF 2A, near Underwood 115kV. Clear fault after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-70 | Prior Outage of Underwood 230/115/13.8kV TF 1A. 3-ph fault on Underwood to G17-014-TAP 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-71 | Prior Outage of Underwood 230/115/13.8kV TF 1A. 3-ph fault on Underwood to G17-064-TAP 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-72 | Prior Outage of Underwood to DRYCREEK 230kV crt 1. 3-ph fault on Underwood to MAURINE 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | 3ph-73 | Prior Outage of Underwood-LNX5 to MAURINE 230kV crt 1. 3-ph fault on Underwood to DRYCREEK 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-01 | 3-ph fault on G17-014-TAP to Underwood 230kV crt 1, near G17-014-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-03 | 3-ph fault on G17-064-TAP to Wayside 230kV crt 1, near G17-064-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-04 | 3-ph fault on G17-064-TAP to Wayside 230kV crt 1, near G17-064-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-05 | 3-ph fault on Underwood to RUSHMORE to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-06 | 3-ph fault on Underwood to ELSWRTH7 to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-07 | 3-ph fault on Underwood to WICKSVL7 to PHILIP 7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-08 | 3-ph fault on Underwood 230/115/13.8kV TF 2A, near Underwood 115kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-09 | 3-ph fault on Underwood 230/115/13.8kV TF 1A, near Underwood 115kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-10 | 3-ph fault on Underwood to G17-014-TAP 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-11 | 3-ph fault on Underwood to G17-064-TAP 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-12 | 3-ph fault on Underwood to DRYCREEK 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-13 | 3-ph fault on Underwood to MAURINE 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-14 | 3-ph fault on Philip Tap to Philip 230kV crt 1, near Philip Tap. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-15 | 3-ph fault on Philip Tap to OAHE 230kV crt 1, near Philip Tap. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-16 | 3-ph fault on Wayside to STEGALL 230kV crt 1, near Wayside. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-17 | 3-ph fault on Wayside 230/115/13.8kV TF T1, near Wayside 230kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-18 | 3-ph fault on RAPIDCY7 to DRYCREEK 115kV crt 1, near RAPIDCY7. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-19 | 3-ph fault on RAPIDCY7 to ELKCRK 7 to G14_001IST 115kV crt 1, near RAPIDCY7. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-20 | 3-ph fault on Philip to Midland to IRVSIMM7 115kV crt 1, near Philip. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-21 | 3-ph fault on Philip to WANBLEE to MARTIN 115kV crt 1, near Philip. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-22 | 3-ph fault on Philip 230/115/13.2kV TF 1A, near Philip 115kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-23 | 3-ph fault on OAHE to G16-094-TAP 230kV crt 1, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-24 | 3-ph fault on OAHE to FTTHOMP4 230kV crt 2, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-25 | 3-ph fault on OAHE to SULLYBT-ER4 230kV crt 1, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-26 | 3-ph fault on MAURINE to BISON 230kV crt 1, near MAURINE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-27 | 3-ph fault on MAURINE 230/115/13.8kV TF 1A, near MAURINE 230kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-28 | 3-ph fault on STEGALL to DH_CS_EA-TS4 230kV crt 1, near STEGALL. Clear fault after 7 cycles by tripping the faulted crt, and DH_CS_EA-TS DC line. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-29 | 3-ph fault on STEGALL to STEGALL_-MB4 230kV crt 1, near STEGALL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-30 | 3-ph fault on STEGALL to VICTRYH4 230kV crt 1, near STEGALL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-31 | 3-ph fault on DRYCREEK to RCDC 230kV crt 1, near DRYCREEK. Clear fault after 7 cycles by tripping the faulted crt, and RCDC DC line. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-32 | 3-ph fault on DRYCREEK 230/115/13.8kV TF 1A, near DRYCREEK. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-33 | 3-ph fault on G14_001IST to MAURINE7 115kV crt 1, near G14_001IST. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-34 | 3-ph fault on Martin to SHANNON 115kV crt 1, near Martin. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-35 | 3-ph fault on Martin to VETAL_TP 115kV crt 1, near Martin. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-36 | 3-ph fault on IRVSIMM7 to OAHE 115kV crt 1, near IRVSIMM7. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-37 | 3-ph fault on IRVSIMM7 to PIERRE 115kV crt 1, near IRVSIMM7. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | SLG-38 | SLG fault on G17-064-TAP to Wayside 230kV crt 1, near G17-064-TAP for 16 cycles. Clear fault by tripping the Wayside 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | SLG-39 | SLG fault on G17-064-TAP to Underwood 230kV crt 1, near G17-064-TAP for 16 cycles. Clear fault by tripping the Underwood 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | SLG-41 | SLG fault on G17-014-TAP to Underwood 230kV crt 1, near G17-014-TAP for 16 cycles. Clear fault by tripping the Underwood 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | SLG-42 | SLG fault on Underwood to RUSHMORE to RAPIDCY7 115kV crt 1, near Underwood for 16 cycles. Clear fault by tripping the RUSHMORE 115kV bus and RAPIDCY7 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | SLG-43 | SLG fault on Underwood to ELSWRTH7 to RAPIDCY7 115kV crt 1, near Underwood for 16 cycles. Clear fault by tripping the ELSWRTH7 115kV bus and RAPIDCY7 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | SLG-44 | SLG fault on Underwood to WICKSVL7 to Philip 115kV crt 1, near Underwood for 16 cycles. Clear fault by tripping the WICKSVL7 115kV bus, WALL 115kV bus and Philip 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | SLG-45 | SLG fault on Philip Tap to OAHE 230kV crt 1, near Philip Tap for 16 cycles. Clear fault by tripping the faulted crt and OAHE to G16-094-TAP 230kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | SLG-46 | SLG fault on Philip Tap to OAHE 230kV crt 1, near Philip Tap for 16 cycles. Clear fault by tripping the faulted crt and OAHE to FTTHOMP4 230kV crt 2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | SLG-47 | SLG fault on Philip Tap to OAHE 230kV crt 1, near Philip Tap for 16 cycles. Clear fault by tripping the faulted crt and OAHE to SULLYBT 230kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | SLG-48 | SLG fault on Wayside to STEGALL 230kV crt 1, near Wayside for 16 cycles. Clear fault by tripping the faulted crt and STEGALL4 230kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | SLG-49 | SLG fault on Underwood to DRYCREEK 230kV crt 1, near Underwood for 16 cycles. Clear fault by tripping the DRYCREEK 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | SLG-50 | SLG fault on Underwood to MAURINE 230kV crt 1, near Underwood for 16 cycles. Clear fault by tripping the MAURINE 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | SLG-51 | SLG fault on RAPIDCY7 to ELKCRK 7 to G14_001IST 115kV crt 1, near RAPIDCY7 for 16 cycles. Clear fault by tripping the ELKCRK 7 115kV bus, NEWELL 115kV bus, meantime trip the G14_001IST 115kV bus and G14_001IS_3 generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | SLG-52 | SLG fault on RAPIDCY7 to DRYCREEK 115kV crt 1, near RAPIDCY7 for 16 cycles. Clear fault by tripping the DRYCREEK 115kV bus and DRYCREEK 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | SLG-53 | SLG fault on Philip to Midland to IRVSIMM7 115kV crt 1, near Philip for 16 cycles. Clear fault by tripping the Midland 115kV bus and IRVSIMM7 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | SLG-54 | SLG fault on Philip to WANBLEE to Martin 115kV crt 1, near Philip for 16 cycles. Clear fault by tripping the WANBLEE 115kV bus and Martin 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-56 | Prior Outage of G17-014-TAP to Philip Tap 230kV crt 1. 3-ph fault on G17-014-TAP to Underwood 230kV crt 1, near G17-014-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. Meantime, trip G17-014 generators. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-57 | Prior Outage of G17-014-TAP to Underwood 230kV crt 1. 3-ph fault on G17-014-TAP to Philip Tap 230kV crt 1, near G17-014-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. Meantime, trip G17-014 generators. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-58 | Prior Outage of G17-064-TAP to Underwood 230kV crt 1. 3-ph fault on G17-064-TAP to Wayside 230kV crt 1, near G17-064-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. Meantime trip G17-064 generators. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-59 | Prior Outage of G17-064-TAP to Wayside 230kV crt 1. 3-ph fault on G17-064-TAP to Underwood 230kV crt 1, near G17-064-TAP. Clear fault after 7 cycles and trip G17-064 generators. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-60 | Prior Outage of Underwood to RUSHMORE 115kV crt 1. 3-ph fault on Underwood to ELSWRTH7 to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-61 | Prior Outage of Underwood to RUSHMORE 115kV crt 1. 3-ph fault on Underwood to WICKSVL7 to PHILIP 7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-62 | Prior Outage of Underwood to RUSHMORE 115kV crt 1. 3-ph fault on Underwood 230/115/13.8kV TF 1A, near Underwood 115kV. Clear fault after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-63 | Prior Outage of Underwood to ELSWRTH7 115kV crt 1. 3-ph fault on Underwood to RUSHMORE to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-64 | Prior Outage of Underwood to ELSWRTH7 115kV crt 1. 3-ph fault on Underwood to WICKSVL7 to PHILIP 7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-65 | Prior Outage of Underwood to ELSWRTH7 115kV crt 1. 3-ph fault on Underwood 230/115/13.8kV TF 1A, near Underwood 115kV. Clear fault after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-66 | Prior Outage of Underwood to WICKSVL7 115kV crt 1. 3-ph fault on Underwood to RUSHMORE to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-67 | Prior Outage of Underwood to WICKSVL7 115kV crt 1. 3-ph fault on Underwood to ELSWRTH7 to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-68 | Prior Outage of Underwood to WICKSVL7 115kV crt 1. 3-ph fault on Underwood 230/115/13.8kV TF 1A, near Underwood 115kV. Clear fault after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-69 | Prior Outage of Underwood 230/115/13.8kV TF 1A. 3-ph fault on Underwood 230/115/13.8kV TF 2A, near Underwood 115kV. Clear fault after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-70 | Prior Outage of Underwood 230/115/13.8kV TF 1A. 3-ph fault on Underwood to G17-014-TAP 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-71 | Prior Outage of Underwood 230/115/13.8kV TF 1A. 3-ph fault on Underwood to G17-064-TAP 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-72 | Prior Outage of Underwood to DRYCREEK 230kV crt 1. 3-ph fault on Underwood to MAURINE 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | 3ph-73 | Prior Outage of Underwood-LNX5 to MAURINE 230kV crt 1. 3-ph fault on Underwood to DRYCREEK 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-01 | 3-ph fault on G17-014-TAP to Underwood 230kV crt 1, near G17-014-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-03 | 3-ph fault on G17-064-TAP to Wayside 230kV crt 1, near G17-064-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-04 | 3-ph fault on G17-064-TAP to Wayside 230kV crt 1, near G17-064-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-05 | 3-ph fault on Underwood to RUSHMORE to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-06 | 3-ph fault on Underwood to ELSWRTH7 to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-07 | 3-ph fault on Underwood to WICKSVL7 to PHILIP 7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-08 | 3-ph fault on Underwood 230/115/13.8kV TF 2A, near Underwood 115kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-09 | 3-ph fault on Underwood 230/115/13.8kV TF 1A, near Underwood 115kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-10 | 3-ph fault on Underwood to G17-014-TAP 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-11 | 3-ph fault on Underwood to G17-064-TAP 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-12 | 3-ph fault on Underwood to DRYCREEK 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-13 | 3-ph fault on Underwood to MAURINE 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-14 | 3-ph fault on Philip Tap to Philip 230kV crt 1, near Philip Tap. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-15 | 3-ph fault on Philip Tap to OAHE 230kV crt 1, near Philip Tap. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-16 | 3-ph fault on Wayside to STEGALL 230kV crt 1, near Wayside. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-17 | 3-ph fault on Wayside 230/115/13.8kV TF T1, near Wayside 230kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-18 | 3-ph fault on RAPIDCY7 to DRYCREEK 115kV crt 1, near RAPIDCY7. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-19 | 3-ph fault on RAPIDCY7 to ELKCRK 7 to G14_001IST 115kV crt 1, near RAPIDCY7. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-20 | 3-ph fault on Philip to Midland to IRVSIMM7 115kV crt 1, near Philip. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-21 | 3-ph fault on Philip to WANBLEE to MARTIN 115kV crt 1, near Philip. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-22 | 3-ph fault on Philip 230/115/13.2kV TF 1A, near Philip 115kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-23 | 3-ph fault on OAHE to G16-094-TAP 230kV crt 1, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-24 | 3-ph fault on OAHE to FTTHOMP4 230kV crt 2, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-25 | 3-ph fault on OAHE to SULLYBT-ER4 230kV crt 1, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-26 | 3-ph fault on MAURINE to BISON 230kV crt 1, near MAURINE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-27 | 3-ph fault on MAURINE 230/115/13.8kV TF 1A, near MAURINE 230kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-28 | 3-ph fault on STEGALL to DH_CS_EA-TS4 230kV crt 1, near STEGALL. Clear fault after 7 cycles by tripping the faulted crt, and DH_CS_EA-TS DC line. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-29 | 3-ph fault on STEGALL to STEGALL_-MB4 230kV crt 1, near STEGALL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-30 | 3-ph fault on STEGALL to VICTRYH4 230kV crt 1, near STEGALL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-31 | 3-ph fault on DRYCREEK to RCDC 230kV crt 1, near DRYCREEK. Clear fault after 7 cycles by tripping the faulted crt, and RCDC DC line. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-32 | 3-ph fault on DRYCREEK 230/115/13.8kV TF 1A, near DRYCREEK. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-33 | 3-ph fault on G14_001IST to MAURINE7 115kV crt 1, near G14_001IST. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-34 | 3-ph fault on Martin to SHANNON 115kV crt 1, near Martin. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-35 | 3-ph fault on Martin to VETAL_TP 115kV crt 1, near Martin. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-36 | 3-ph fault on IRVSIMM7 to OAHE 115kV crt 1, near IRVSIMM7. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-37 | 3-ph fault on IRVSIMM7 to PIERRE 115kV crt 1, near IRVSIMM7. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | SLG-38 | SLG fault on G17-064-TAP to Wayside 230kV crt 1, near G17-064-TAP for 16 cycles. Clear fault by tripping the Wayside 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | SLG-39 | SLG fault on G17-064-TAP to Underwood 230kV crt 1, near G17-064-TAP for 16 cycles. Clear fault by tripping the Underwood 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | SLG-41 | SLG fault on G17-014-TAP to Underwood 230kV crt 1, near G17-014-TAP for 16 cycles. Clear fault by tripping the Underwood 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | SLG-42 | SLG fault on Underwood to RUSHMORE to RAPIDCY7 115kV crt 1, near Underwood for 16 cycles. Clear fault by tripping the RUSHMORE 115kV bus and RAPIDCY7 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | SLG-43 | SLG fault on Underwood to ELSWRTH7 to RAPIDCY7 115kV crt 1, near Underwood for 16 cycles. Clear fault by tripping the ELSWRTH7 115kV bus and RAPIDCY7 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | SLG-44 | SLG fault on Underwood to WICKSVL7 to Philip 115kV crt 1, near Underwood for 16 cycles. Clear fault by tripping the WICKSVL7 115kV bus, WALL 115kV bus and Philip 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | SLG-45 | SLG fault on Philip Tap to OAHE 230kV crt 1, near Philip Tap for 16 cycles. Clear fault by tripping the faulted crt and OAHE to G16-094-TAP 230kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | SLG-46 | SLG fault on Philip Tap to OAHE 230kV crt 1, near Philip Tap for 16 cycles. Clear fault by tripping the faulted crt and OAHE to FTTHOMP4 230kV crt 2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | SLG-47 | SLG fault on Philip Tap to OAHE 230kV crt 1, near Philip Tap for 16 cycles. Clear fault by tripping the faulted crt and OAHE to SULLYBT 230kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | SLG-48 | SLG fault on Wayside to STEGALL 230kV crt 1, near Wayside for 16 cycles. Clear fault by tripping the faulted crt and STEGALL4 230kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | SLG-49 | SLG fault on Underwood to DRYCREEK 230kV crt 1, near Underwood for 16 cycles. Clear fault by tripping the DRYCREEK 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | SLG-50 | SLG fault on Underwood to MAURINE 230kV crt 1, near Underwood for 16 cycles. Clear fault by tripping the MAURINE 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | SLG-51 | SLG fault on RAPIDCY7 to ELKCRK 7 to G14_001IST 115kV crt 1, near RAPIDCY7 for 16 cycles. Clear fault by tripping the ELKCRK 7 115kV bus, NEWELL 115kV bus, meantime trip the G14_001IST 115kV bus and G14_001IS_3 generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | SLG-52 | SLG fault on RAPIDCY7 to DRYCREEK 115kV crt 1, near RAPIDCY7 for 16 cycles. Clear fault by tripping the DRYCREEK 115kV bus and DRYCREEK 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | SLG-53 | SLG fault on Philip to Midland to IRVSIMM7 115kV crt 1, near Philip for 16 cycles. Clear fault by tripping the Midland 115kV bus and IRVSIMM7 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | SLG-54 | SLG fault on Philip to WANBLEE to Martin 115kV crt 1, near Philip for 16 cycles. Clear fault by tripping the WANBLEE 115kV bus and Martin 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-56 | Prior Outage of G17-014-TAP to Philip Tap 230kV crt 1. 3-ph fault on G17-014-TAP to Underwood 230kV crt 1, near G17-014-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. Meantime, trip G17-014 generators. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-57 | Prior Outage of G17-014-TAP to Underwood 230kV crt 1. 3-ph fault on G17-014-TAP to Philip Tap 230kV crt 1, near G17-014-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. Meantime, trip G17-014 generators. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-58 | Prior Outage of G17-064-TAP to Underwood 230kV crt 1. 3-ph fault on G17-064-TAP to Wayside 230kV crt 1, near G17-064-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. Meantime trip G17-064 generators. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-59 | Prior Outage of G17-064-TAP to Wayside 230kV crt 1. 3-ph fault on G17-064-TAP to Underwood 230kV crt 1, near G17-064-TAP. Clear fault after 7 cycles and trip G17-064 generators. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-60 | Prior Outage of Underwood to RUSHMORE 115kV crt 1. 3-ph fault on Underwood to ELSWRTH7 to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-61 | Prior Outage of Underwood to RUSHMORE 115kV crt 1. 3-ph fault on Underwood to WICKSVL7 to PHILIP 7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-62 | Prior Outage of Underwood to RUSHMORE 115kV crt 1. 3-ph fault on Underwood 230/115/13.8kV TF 1A, near Underwood 115kV. Clear fault after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-63 | Prior Outage of Underwood to ELSWRTH7 115kV crt 1. 3-ph fault on Underwood to RUSHMORE to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-64 | Prior Outage of Underwood to ELSWRTH7 115kV crt 1. 3-ph fault on Underwood to WICKSVL7 to PHILIP 7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-65 | Prior Outage of Underwood to ELSWRTH7 115kV crt 1. 3-ph fault on Underwood 230/115/13.8kV TF 1A, near Underwood 115kV. Clear fault after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-66 | Prior Outage of Underwood to WICKSVL7 115kV crt 1. 3-ph fault on Underwood to RUSHMORE to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-67 | Prior Outage of Underwood to WICKSVL7 115kV crt 1. 3-ph fault on Underwood to ELSWRTH7 to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-68 | Prior Outage of Underwood to WICKSVL7 115kV crt 1. 3-ph fault on Underwood 230/115/13.8kV TF 1A, near Underwood 115kV. Clear fault after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-69 | Prior Outage of Underwood 230/115/13.8kV TF 1A. 3-ph fault on Underwood 230/115/13.8kV TF 2A, near Underwood 115kV. Clear fault after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-70 | Prior Outage of Underwood 230/115/13.8kV TF 1A. 3-ph fault on Underwood to G17-014-TAP 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-71 | Prior Outage of Underwood 230/115/13.8kV TF 1A. 3-ph fault on Underwood to G17-064-TAP 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-72 | Prior Outage of Underwood to DRYCREEK 230kV crt 1. 3-ph fault on Underwood to MAURINE 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | 3ph-73 | Prior Outage of Underwood-LNX5 to MAURINE 230kV crt 1. 3-ph fault on Underwood to DRYCREEK 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-01 | 3-ph fault on G17-014-TAP to Underwood 230kV crt 1, near G17-014-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-03 | 3-ph fault on G17-064-TAP to Wayside 230kV crt 1, near G17-064-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-04 | 3-ph fault on G17-064-TAP to Wayside 230kV crt 1, near G17-064-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-05 | 3-ph fault on Underwood to RUSHMORE to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-06 | 3-ph fault on Underwood to ELSWRTH7 to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-07 | 3-ph fault on Underwood to WICKSVL7 to PHILIP 7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-08 | 3-ph fault on Underwood 230/115/13.8kV TF 2A, near Underwood 115kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-09 | 3-ph fault on Underwood 230/115/13.8kV TF 1A, near Underwood 115kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-10 | 3-ph fault on Underwood to G17-014-TAP 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-11 | 3-ph fault on Underwood to G17-064-TAP 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-12 | 3-ph fault on Underwood to DRYCREEK 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-13 | 3-ph fault on Underwood to MAURINE 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-14 | 3-ph fault on Philip Tap to Philip 230kV crt 1, near Philip Tap. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-15 | 3-ph fault on Philip Tap to OAHE 230kV crt 1, near Philip Tap. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-16 | 3-ph fault on Wayside to STEGALL 230kV crt 1, near Wayside. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-17 | 3-ph fault on Wayside 230/115/13.8kV TF T1, near Wayside 230kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-18 | 3-ph fault on RAPIDCY7 to DRYCREEK 115kV crt 1, near RAPIDCY7. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-19 | 3-ph fault on RAPIDCY7 to ELKCRK 7 to G14_001IST 115kV crt 1, near RAPIDCY7. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-20 | 3-ph fault on Philip to Midland to IRVSIMM7 115kV crt 1, near Philip. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-21 | 3-ph fault on Philip to WANBLEE to MARTIN 115kV crt 1, near Philip. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-22 | 3-ph fault on Philip 230/115/13.2kV TF 1A, near Philip 115kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-23 | 3-ph fault on OAHE to G16-094-TAP 230kV crt 1, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-24 | 3-ph fault on OAHE to FTTHOMP4 230kV crt 2, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-25 | 3-ph fault on OAHE to SULLYBT-ER4 230kV crt 1, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-26 | 3-ph fault on MAURINE to BISON 230kV crt 1, near MAURINE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-27 | 3-ph fault on MAURINE 230/115/13.8kV TF 1A, near MAURINE 230kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-28 | 3-ph fault on STEGALL to DH_CS_EA-TS4 230kV crt 1, near STEGALL. Clear fault after 7 cycles by tripping the faulted crt, and DH_CS_EA-TS DC line. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-29 | 3-ph fault on STEGALL to STEGALL_-MB4 230kV crt 1, near STEGALL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-30 | 3-ph fault on STEGALL to VICTRYH4 230kV crt 1, near STEGALL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-31 | 3-ph fault on DRYCREEK to RCDC 230kV crt 1, near DRYCREEK. Clear fault after 7 cycles by tripping the faulted crt, and RCDC DC line. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-32 | 3-ph fault on DRYCREEK 230/115/13.8kV TF 1A, near DRYCREEK. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-33 | 3-ph fault on G14_001IST to MAURINE7 115kV crt 1, near G14_001IST. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-34 | 3-ph fault on Martin to SHANNON 115kV crt 1, near Martin. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-35 | 3-ph fault on Martin to VETAL_TP 115kV crt 1, near Martin. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-36 | 3-ph fault on IRVSIMM7 to OAHE 115kV crt 1, near IRVSIMM7. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-37 | 3-ph fault on IRVSIMM7 to PIERRE 115kV crt 1, near IRVSIMM7. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | SLG-38 | SLG fault on G17-064-TAP to Wayside 230kV crt 1, near G17-064-TAP for 16 cycles. Clear fault by tripping the Wayside 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | SLG-39 | SLG fault on G17-064-TAP to Underwood 230kV crt 1, near G17-064-TAP for 16 cycles. Clear fault by tripping the Underwood 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | SLG-41 | SLG fault on G17-014-TAP to Underwood 230kV crt 1, near G17-014-TAP for 16 cycles. Clear fault by tripping the Underwood 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | SLG-42 | SLG fault on Underwood to RUSHMORE to RAPIDCY7 115kV crt 1, near Underwood for 16 cycles. Clear fault by tripping the RUSHMORE 115kV bus and RAPIDCY7 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | SLG-43 | SLG fault on Underwood to ELSWRTH7 to RAPIDCY7 115kV crt 1, near Underwood for 16 cycles. Clear fault by tripping the ELSWRTH7 115kV bus and RAPIDCY7 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | SLG-44 | SLG fault on Underwood to WICKSVL7 to Philip 115kV crt 1, near Underwood for 16 cycles. Clear fault by tripping the WICKSVL7 115kV bus, WALL 115kV bus and Philip 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | SLG-45 | SLG fault on Philip Tap to OAHE 230kV crt 1, near Philip Tap for 16 cycles. Clear fault by tripping the faulted crt and OAHE to G16-094-TAP 230kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | SLG-46 | SLG fault on Philip Tap to OAHE 230kV crt 1, near Philip Tap for 16 cycles. Clear fault by tripping the faulted crt and OAHE to FTTHOMP4 230kV crt 2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | SLG-47 | SLG fault on Philip Tap to OAHE 230kV crt 1, near Philip Tap for 16 cycles. Clear fault by tripping the faulted crt and OAHE to SULLYBT 230kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | SLG-48 | SLG fault on Wayside to STEGALL 230kV crt 1, near Wayside for 16 cycles. Clear fault by tripping the faulted crt and STEGALL4 230kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | SLG-49 | SLG fault on Underwood to DRYCREEK 230kV crt 1, near Underwood for 16 cycles. Clear fault by tripping the DRYCREEK 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | SLG-50 | SLG fault on Underwood to MAURINE 230kV crt 1, near Underwood for 16 cycles. Clear fault by tripping the MAURINE 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | SLG-51 | SLG fault on RAPIDCY7 to ELKCRK 7 to G14_001IST 115kV crt 1, near RAPIDCY7 for 16 cycles. Clear fault by tripping the ELKCRK 7 115kV bus, NEWELL 115kV bus, meantime trip the G14_001IST 115kV bus and G14_001IS_3 generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | SLG-52 | SLG fault on RAPIDCY7 to DRYCREEK 115kV crt 1, near RAPIDCY7 for 16 cycles. Clear fault by tripping the DRYCREEK 115kV bus and DRYCREEK 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | SLG-53 | SLG fault on Philip to Midland to IRVSIMM7 115kV crt 1, near Philip for 16 cycles. Clear fault by tripping the Midland 115kV bus and IRVSIMM7 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | SLG-54 | SLG fault on Philip to WANBLEE to Martin 115kV crt 1, near Philip for 16 cycles. Clear fault by tripping the WANBLEE 115kV bus and Martin 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-56 | Prior Outage of G17-014-TAP to Philip Tap 230kV crt 1. 3-ph fault on G17-014-TAP to Underwood 230kV crt 1, near G17-014-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. Meantime, trip G17-014 generators. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-57 | Prior Outage of G17-014-TAP to Underwood 230kV crt 1. 3-ph fault on G17-014-TAP to Philip Tap 230kV crt 1, near G17-014-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. Meantime, trip G17-014 generators. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-58 | Prior Outage of G17-064-TAP to Underwood 230kV crt 1. 3-ph fault on G17-064-TAP to Wayside 230kV crt 1, near G17-064-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. Meantime trip G17-064 generators. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-59 | Prior Outage of G17-064-TAP to Wayside 230kV crt 1. 3-ph fault on G17-064-TAP to Underwood 230kV crt 1, near G17-064-TAP. Clear fault after 7 cycles and trip G17-064 generators. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-60 | Prior Outage of Underwood to RUSHMORE 115kV crt 1. 3-ph fault on Underwood to ELSWRTH7 to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-61 | Prior Outage of Underwood to RUSHMORE 115kV crt 1. 3-ph fault on Underwood to WICKSVL7 to PHILIP 7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-62 | Prior Outage of Underwood to RUSHMORE 115kV crt 1. 3-ph fault on Underwood 230/115/13.8kV TF 1A, near Underwood 115kV. Clear fault after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-63 | Prior Outage of Underwood to ELSWRTH7 115kV crt 1. 3-ph fault on Underwood to RUSHMORE to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-64 | Prior Outage of Underwood to ELSWRTH7 115kV crt 1. 3-ph fault on Underwood to WICKSVL7 to PHILIP 7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-65 | Prior Outage of Underwood to ELSWRTH7 115kV crt 1. 3-ph fault on Underwood 230/115/13.8kV TF 1A, near Underwood 115kV. Clear fault after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-66 | Prior Outage of Underwood to WICKSVL7 115kV crt 1. 3-ph fault on Underwood to RUSHMORE to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-67 | Prior Outage of Underwood to WICKSVL7 115kV crt 1. 3-ph fault on Underwood to ELSWRTH7 to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-68 | Prior Outage of Underwood to WICKSVL7 115kV crt 1. 3-ph fault on Underwood 230/115/13.8kV TF 1A, near Underwood 115kV. Clear fault after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-69 | Prior Outage of Underwood 230/115/13.8kV TF 1A. 3-ph fault on Underwood 230/115/13.8kV TF 2A, near Underwood 115kV. Clear fault after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-70 | Prior Outage of Underwood 230/115/13.8kV TF 1A. 3-ph fault on Underwood to G17-014-TAP 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-71 | Prior Outage of Underwood 230/115/13.8kV TF 1A. 3-ph fault on Underwood to G17-064-TAP 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-72 | Prior Outage of Underwood to DRYCREEK 230kV crt 1. 3-ph fault on Underwood to MAURINE 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | 3ph-73 | Prior Outage of Underwood-LNX5 to MAURINE 230kV crt 1. 3-ph fault on Underwood to DRYCREEK 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | Tie-3ph-01 | 3-ph fault on SIOUXCY-LNX3 to SPLT RK3 345kV crt 1, near SIOUXCY-LNX3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | Tie-3ph-02 | 3-ph fault on SIOUXCY3 to RAUN 345kV crt 1, near SIOUXCY3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | Tie-3ph-03 | 3-ph fault on SD.LS-KS-MB3 to KEYSTON3 345kV crt 1, near SD.LS-KS-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | Tie-3ph-04 | 3-ph fault on SD.LS-LR-MB3 to KEYSTON3 345kV crt 1, near SD.LS-LR-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | Tie-3ph-05 | 3-ph fault on HOLT.CO3 to THEDFRD3 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | Tie-3ph-06 | 3-ph fault on HOLT.CO3 to ANTELOPE 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | Tie-3ph-07 | 3-ph fault on HOLT.CO3 to GR ISLD-LNX3 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | Tie-3ph-08 | 3-ph fault on OAHE to G16-094-TAP 230kV crt 1, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | Tie-3ph-09 | 3-ph fault on OAHE to FTTHOMP4 230kV crt 2, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | Tie-3ph-10 | 3-ph fault on OAHE 230/115/13.8kV TF OA No.5, near OAHE 230kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | Tie-3ph-11 | 3-ph fault on FTTHOMP4 345/230/13.8kV TF FT2 KU1B, near FTTHOMP4 230kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | Tie-3ph-12 | 3-ph fault on BISON to HETINGR4 230kV crt 1, near BISON. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | Tie-SLG-13 | SLG fault on HOLT.CO3 to ANTELOPE 345kV crt 1, near HOLT.CO3 for 16 cycles. Clear fault by tripping the faulted crt and HOLT.CO3 to GR ISLD-LNX3 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | Tie-SLG-14 | SLG fault on SIOUXCY3 to RAUN 345kV crt 1, near SIOUXCY3 for 16 cycles. Clear fault by tripping the SIOUXCY3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | Tie-SLG-15 | SLG fault on SD.LS-KS-MB3 to KEYSTON 345kV crt 1, near SD.LS-KS-MB3 for 16 cycles. Clear fault by tripping the SD.LS-KS-MB3 345kV and SIDNEY 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | Tie-SLG-16 | SLG fault on OAHE to G16-094-TAP 230kV crt 1, near OAHE for 16 cycles. Clear fault by tripping the faulted crt and OAHE to FTTHOMP4 230kV crt 2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | Tie-SLG-17 | SLG fault on OAHE to FTTHOMP4 230kV crt 2, near BISON for 16 cycles. Clear fault by tripping the faulted crt and OAHE to PHILIP_Tap 230kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | Tie-SLG-18 | SLG fault on BISON to HETINGR4 230kV crt 1, near BISON for 16 cycles. Clear fault by tripping the BISON 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | Tie-3ph-19 | Prior Outage of HOLT.CO3 to ANTELOPE 345kV crt 1. 3-ph fault on HOLT.CO3 to GR ISLD-LNX3 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | Tie-3ph-20 | Prior Outage of HOLT.CO3 to ANTELOPE 345kV crt 1. 3-ph fault on SD.LS-KS-MB3 to KEYSTON3 345kV crt 1, near SD.LS-KS-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | Tie-3ph-21 | Prior Outage of HOLT.CO3 to GR ISLD-LNX3 345kV crt 1. 3-ph fault on HOLT.CO3 to ANTELOPE 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | Tie-3ph-22 | Prior Outage of HOLT.CO3 to GR ISLD-LNX3 345kV crt 1. 3-ph fault on SD.LS-KS-MB3 to KEYSTON3 345kV crt 1, near SD.LS-KS-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | Tie-3ph-23 | Prior Outage of SD.LS-KS-MB3 to KEYSTON3 345kV crt 1. 3-ph fault on HOLT.CO3 to ANTELOPE 345kV crt 1, near HOLT.CO3 | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | Tie-3ph-24 | Prior Outage of SD.LS-KS-MB3 to KEYSTON3 345kV crt 1. 3-ph fault on HOLT.CO3 to GR ISLD-LNX3 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | Tie-3ph-25 | Prior Outage of OAHE to G16-094-TAP 230kV crt 1, 3-ph fault on G17-064-TAP to WAYSIDE 230kV crt 1. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 76 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | Tie-3ph-26 | Prior Outage of OAHE to G16-094-TAP 230kV crt 1. 3-ph fault on OAHE to FTTHOMP4 230kV crt 2, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | Tie-3ph-27 | Prior Outage of OAHE to FTTHOMP4 230kV crt 3. 3-ph fault on OAHE to FTTHOMP4 230kV crt 4, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | Tie-3ph-28 | Prior Outage of OAHE to FTTHOMP4 230kV crt 3. 3-ph fault on G17-064-TAP to WAYSIDE 230kV crt 1, near G17-064-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Transfer | Tie-3ph-29 | Prior Outage of BISON___-GE4 to HETINGR4 230kV crt 1. 3-ph fault on OAHE to FTTHOMP4 230kV crt 2, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | Tie-3ph-01 | 3-ph fault on SIOUXCY-LNX3 to SPLT RK3 345kV crt 1, near SIOUXCY-LNX3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | Tie-3ph-02 | 3-ph fault on SIOUXCY3 to RAUN 345kV crt 1, near SIOUXCY3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | Tie-3ph-03 | 3-ph fault on SD.LS-KS-MB3 to KEYSTON3 345kV crt 1, near SD.LS-KS-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | Tie-3ph-04 | 3-ph fault on SD.LS-LR-MB3 to KEYSTON3 345kV crt 1, near SD.LS-LR-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | Tie-3ph-05 | 3-ph fault on HOLT.CO3 to THEDFRD3 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | Tie-3ph-06 | 3-ph fault on HOLT.CO3 to ANTELOPE 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | Tie-3ph-07 | 3-ph fault on HOLT.CO3 to GR ISLD-LNX3 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | Tie-3ph-08 | 3-ph fault on OAHE to G16-094-TAP 230kV crt 1, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | Tie-3ph-09 | 3-ph fault on OAHE to FTTHOMP4 230kV crt 2, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | Tie-3ph-10 | 3-ph fault on OAHE 230/115/13.8kV TF OA No.5, near OAHE 230kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | Tie-3ph-11 | 3-ph fault on FTTHOMP4 345/230/13.8kV TF FT2 KU1B, near FTTHOMP4 230kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | Tie-3ph-12 | 3-ph fault on BISON to HETINGR4 230kV crt 1, near BISON. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | Tie-SLG-13 | SLG fault on HOLT.CO3 to ANTELOPE 345kV crt 1, near HOLT.CO3 for 16 cycles. Clear fault by tripping the faulted crt and HOLT.CO3 to GR ISLD-LNX3 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | Tie-SLG-14 | SLG fault on SIOUXCY3 to RAUN 345kV crt 1, near SIOUXCY3 for 16 cycles. Clear fault by tripping the SIOUXCY3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | Tie-SLG-15 | SLG fault on SD.LS-KS-MB3 to KEYSTON 345kV crt 1, near SD.LS-KS-MB3 for 16 cycles. Clear fault by tripping the SD.LS-KS-MB3 345kV and SIDNEY 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | Tie-SLG-16 | SLG fault on OAHE to G16-094-TAP 230kV crt 1, near OAHE for 16 cycles. Clear fault by tripping the faulted crt and OAHE to FTTHOMP4 230kV crt 2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | Tie-SLG-17 | SLG fault on OAHE to FTTHOMP4 230kV crt 2, near BISON for 16 cycles. Clear fault by tripping the faulted crt and OAHE to PHILIP_Tap 230kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | Tie-SLG-18 | SLG fault on BISON to HETINGR4 230kV crt 1, near BISON for 16 cycles. Clear fault by tripping the BISON 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | Tie-3ph-19 | Prior Outage of HOLT.CO3 to ANTELOPE 345kV crt 1. 3-ph fault on HOLT.CO3 to GR ISLD-LNX3 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | Tie-3ph-20 | Prior Outage of HOLT.CO3 to ANTELOPE 345kV crt 1. 3-ph fault on SD.LS-KS-MB3 to KEYSTON3 345kV crt 1, near SD.LS-KS-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | Tie-3ph-21 | Prior Outage of HOLT.CO3 to GR ISLD-LNX3 345kV crt 1. 3-ph fault on HOLT.CO3 to ANTELOPE 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | Tie-3ph-22 | Prior Outage of HOLT.CO3 to GR ISLD-LNX3 345kV crt 1. 3-ph fault on SD.LS-KS-MB3 to KEYSTON3 345kV crt 1, near SD.LS-KS-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | Tie-3ph-23 | Prior Outage of SD.LS-KS-MB3 to KEYSTON3 345kV crt 1. 3-ph fault on HOLT.CO3 to ANTELOPE 345kV crt 1, near HOLT.CO3 | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | Tie-3ph-24 | Prior Outage of SD.LS-KS-MB3 to KEYSTON3 345kV crt 1. 3-ph fault on HOLT.CO3 to GR ISLD-LNX3 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | Tie-3ph-25 | Prior Outage of OAHE to G16-094-TAP 230kV crt 1, 3-ph fault on G17-064-TAP to WAYSIDE 230kV crt 1. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 76 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | Tie-3ph-26 | Prior Outage of OAHE to G16-094-TAP 230kV crt 1. 3-ph fault on OAHE to FTTHOMP4 230kV crt 2, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | Tie-3ph-27 | Prior Outage of OAHE to FTTHOMP4 230kV crt 3. 3-ph fault on OAHE to FTTHOMP4 230kV crt 4, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | Tie-3ph-28 | Prior Outage of OAHE to FTTHOMP4 230kV crt 3. 3-ph fault on G17-064-TAP to WAYSIDE 230kV crt 1, near G17-064-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Transfer | Tie-3ph-29 | Prior Outage of BISON___-GE4 to HETINGR4 230kV crt 1. 3-ph fault on OAHE to FTTHOMP4 230kV crt 2, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | Tie-3ph-01 | 3-ph fault on SIOUXCY-LNX3 to SPLT RK3 345kV crt 1, near SIOUXCY-LNX3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | Tie-3ph-02 | 3-ph fault on SIOUXCY3 to RAUN 345kV crt 1, near SIOUXCY3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | Tie-3ph-03 | 3-ph fault on SD.LS-KS-MB3 to KEYSTON3 345kV crt 1, near SD.LS-KS-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | Tie-3ph-04 | 3-ph fault on SD.LS-LR-MB3 to KEYSTON3 345kV crt 1, near SD.LS-LR-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | Tie-3ph-05 | 3-ph fault on HOLT.CO3 to THEDFRD3 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | Tie-3ph-06 | 3-ph fault on HOLT.CO3 to ANTELOPE 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | Tie-3ph-07 | 3-ph fault on HOLT.CO3 to GR ISLD-LNX3 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | Tie-3ph-08 | 3-ph fault on OAHE to G16-094-TAP 230kV crt 1, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | Tie-3ph-09 | 3-ph fault on OAHE to FTTHOMP4 230kV crt 2, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | Tie-3ph-10 | 3-ph fault on OAHE 230/115/13.8kV TF OA No.5, near OAHE 230kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | Tie-3ph-11 | 3-ph fault on FTTHOMP4 345/230/13.8kV TF FT2 KU1B, near FTTHOMP4 230kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | Tie-3ph-12 | 3-ph fault on BISON to HETINGR4 230kV crt 1, near BISON. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | Tie-SLG-13 | SLG fault on HOLT.CO3 to ANTELOPE 345kV crt 1, near HOLT.CO3 for 16 cycles. Clear fault by tripping the faulted crt and HOLT.CO3 to GR ISLD-LNX3 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | Tie-SLG-14 | SLG fault on SIOUXCY3 to RAUN 345kV crt 1, near SIOUXCY3 for 16 cycles. Clear fault by tripping the SIOUXCY3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | Tie-SLG-15 | SLG fault on SD.LS-KS-MB3 to KEYSTON 345kV crt 1, near SD.LS-KS-MB3 for 16 cycles. Clear fault by tripping the SD.LS-KS-MB3 345kV and SIDNEY 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | Tie-SLG-16 | SLG fault on OAHE to G16-094-TAP 230kV crt 1, near OAHE for 16 cycles. Clear fault by tripping the faulted crt and OAHE to FTTHOMP4 230kV crt 2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | Tie-SLG-17 | SLG fault on OAHE to FTTHOMP4 230kV crt 2, near BISON for 16 cycles. Clear fault by tripping the faulted crt and OAHE to PHILIP_Tap 230kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | Tie-SLG-18 | SLG fault on BISON to HETINGR4 230kV crt 1, near BISON for 16 cycles. Clear fault by tripping the BISON 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | Tie-3ph-19 | Prior Outage of HOLT.CO3 to ANTELOPE 345kV crt 1. 3-ph fault on HOLT.CO3 to GR ISLD-LNX3 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | Tie-3ph-20 | Prior Outage of HOLT.CO3 to ANTELOPE 345kV crt 1. 3-ph fault on SD.LS-KS-MB3 to KEYSTON3 345kV crt 1, near SD.LS-KS-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | Tie-3ph-21 | Prior Outage of HOLT.CO3 to GR ISLD-LNX3 345kV crt 1. 3-ph fault on HOLT.CO3 to ANTELOPE 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | Tie-3ph-22 | Prior Outage of HOLT.CO3 to GR ISLD-LNX3 345kV crt 1. 3-ph fault on SD.LS-KS-MB3 to KEYSTON3 345kV crt 1, near SD.LS-KS-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | Tie-3ph-23 | Prior Outage of SD.LS-KS-MB3 to KEYSTON3 345kV crt 1. 3-ph fault on HOLT.CO3 to ANTELOPE 345kV crt 1, near HOLT.CO3 | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | Tie-3ph-24 | Prior Outage of SD.LS-KS-MB3 to KEYSTON3 345kV crt 1. 3-ph fault on HOLT.CO3 to GR ISLD-LNX3 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | Tie-3ph-25 | Prior Outage of OAHE to G16-094-TAP 230kV crt 1, 3-ph fault on G17-064-TAP to WAYSIDE 230kV crt 1. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 76 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | Tie-3ph-26 | Prior Outage of OAHE to G16-094-TAP 230kV crt 1. 3-ph fault on OAHE to FTTHOMP4 230kV crt 2, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | Tie-3ph-27 | Prior Outage of OAHE to FTTHOMP4 230kV crt 3. 3-ph fault on OAHE to FTTHOMP4 230kV crt 4, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | Tie-3ph-28 | Prior Outage of OAHE to FTTHOMP4 230kV crt 3. 3-ph fault on G17-064-TAP to WAYSIDE 230kV crt 1, near G17-064-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L | Transfer | Tie-3ph-29 | Prior Outage of BISON___-GE4 to HETINGR4 230kV crt 1. 3-ph fault on OAHE to FTTHOMP4 230kV crt 2, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | Tie-3ph-01 | 3-ph fault on SIOUXCY-LNX3 to SPLT RK3 345kV crt 1, near SIOUXCY-LNX3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | Tie-3ph-02 | 3-ph fault on SIOUXCY3 to RAUN 345kV crt 1, near SIOUXCY3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | Tie-3ph-03 | 3-ph fault on SD.LS-KS-MB3 to KEYSTON3 345kV crt 1, near SD.LS-KS-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | Tie-3ph-04 | 3-ph fault on SD.LS-LR-MB3 to KEYSTON3 345kV crt 1, near SD.LS-LR-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | Tie-3ph-05 | 3-ph fault on HOLT.CO3 to THEDFRD3 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | Tie-3ph-06 | 3-ph fault on HOLT.CO3 to ANTELOPE 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | Tie-3ph-07 | 3-ph fault on HOLT.CO3 to GR ISLD-LNX3 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | Tie-3ph-08 | 3-ph fault on OAHE to G16-094-TAP 230kV crt 1, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | Tie-3ph-09 | 3-ph fault on OAHE to FTTHOMP4 230kV crt 2, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | Tie-3ph-10 | 3-ph fault on OAHE 230/115/13.8kV TF OA No.5, near OAHE 230kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | Tie-3ph-11 | 3-ph fault on FTTHOMP4 345/230/13.8kV TF FT2 KU1B, near FTTHOMP4 230kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | Tie-3ph-12 | 3-ph fault on BISON to HETINGR4 230kV crt 1, near BISON. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | Tie-SLG-13 | SLG fault on HOLT.CO3 to ANTELOPE 345kV crt 1, near HOLT.CO3 for 16 cycles. Clear fault by tripping the faulted crt and HOLT.CO3 to GR ISLD-LNX3 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | Tie-SLG-14 | SLG fault on SIOUXCY3 to RAUN 345kV crt 1, near SIOUXCY3 for 16 cycles. Clear fault by tripping the SIOUXCY3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | Tie-SLG-15 | SLG fault on SD.LS-KS-MB3 to KEYSTON 345kV crt 1, near SD.LS-KS-MB3 for 16 cycles. Clear fault by tripping the SD.LS-KS-MB3 345kV and SIDNEY 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | Tie-SLG-16 | SLG fault on OAHE to G16-094-TAP 230kV crt 1, near OAHE for 16 cycles. Clear fault by tripping the faulted crt and OAHE to FTTHOMP4 230kV crt 2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | Tie-SLG-17 | SLG fault on OAHE to FTTHOMP4 230kV crt 2, near BISON for 16 cycles. Clear fault by tripping the faulted crt and OAHE to PHILIP_Tap 230kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | Tie-SLG-18 | SLG fault on BISON to HETINGR4 230kV crt 1, near BISON for 16 cycles. Clear fault by tripping the BISON 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | Tie-3ph-19 | Prior Outage of HOLT.CO3 to ANTELOPE 345kV crt 1. 3-ph fault on HOLT.CO3 to GR ISLD-LNX3 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | Tie-3ph-20 | Prior Outage of HOLT.CO3 to ANTELOPE 345kV crt 1. 3-ph fault on SD.LS-KS-MB3 to KEYSTON3 345kV crt 1, near SD.LS-KS-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | Tie-3ph-21 | Prior Outage of HOLT.CO3 to GR ISLD-LNX3 345kV crt 1. 3-ph fault on HOLT.CO3 to ANTELOPE 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | Tie-3ph-22 | Prior Outage of HOLT.CO3 to GR ISLD-LNX3 345kV crt 1. 3-ph fault on SD.LS-KS-MB3 to KEYSTON3 345kV crt 1, near SD.LS-KS-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | Tie-3ph-23 | Prior Outage of SD.LS-KS-MB3 to KEYSTON3 345kV crt 1. 3-ph fault on HOLT.CO3 to ANTELOPE 345kV crt 1, near HOLT.CO3 | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | Tie-3ph-24 | Prior Outage of SD.LS-KS-MB3 to KEYSTON3 345kV crt 1. 3-ph fault on HOLT.CO3 to GR ISLD-LNX3 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | Tie-3ph-25 | Prior Outage of OAHE to G16-094-TAP 230kV crt 1, 3-ph fault on G17-064-TAP to WAYSIDE 230kV crt 1. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 76 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | Tie-3ph-26 | Prior Outage of OAHE to G16-094-TAP 230kV crt 1. 3-ph fault on OAHE to FTTHOMP4 230kV crt 2, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | Tie-3ph-27 | Prior Outage of OAHE to FTTHOMP4 230kV crt 3. 3-ph fault on OAHE to FTTHOMP4 230kV crt 4, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | Tie-3ph-28 | Prior Outage of OAHE to FTTHOMP4 230kV crt 3. 3-ph fault on G17-064-TAP to WAYSIDE 230kV crt 1, near G17-064-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Transfer | Tie-3ph-29 | Prior Outage of BISON___-GE4 to HETINGR4 230kV crt 1. 3-ph fault on OAHE to FTTHOMP4 230kV crt 2, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 04 - Northwest Kansas | 19W | Transfer | 004-3PH-25 | 3-phase fault on JEC N to HOYT 345kVCircuit 1, near JEC N. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Unstable | No | Yes | Yes | Yes | Yes | No | JEC Units rotor angle unstable (first swing) and get tripped | Remove high speed reclose
North | 04 - Northwest Kansas | 19W | Transfer | 013-PO-1-1 | Prior Outage of MINGO to REDWILO 345kVCircuit 1, 3-phase fault on Mingo to SETAB 345 kVCircuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | Yes | Yes | Yes | Yes | No | Voltage at Mingo collapses. G15-064, G15-065, G16-067 are tripped. | reduce Gens at Mingo (G15-064, G15-065, G16-067, G17-004) to 50%, post first outage in anticipation of contingencies in the system.
North | 04 - Northwest Kansas | 19W | Transfer | 013-PO-2-1 | Prior Outage of MINGO to SETAB 345kVCircuit 1, 3-phase fault on Mingo to REDWILO 345 kVCircuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | Yes | Yes | Yes | Yes | No | Voltage at Mingo collapses. G15-065, G16-067 are tripped. | reduce Gens at Mingo (G15-064, G15-065, G16-067, G17-004) to 50%, post first outage in anticipation of contingencies in the system.
North | 04 - Northwest Kansas | 19W | Transfer | TIE-3PH-12 | 3-phase fault on WAVERLY to LACYGNE 345 kVCircuit 1, near LACYGNE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Unstable | No | Yes | Yes | Yes | Yes | No | WCGS U1 rotor angle unstable (first swing) and get tripped | Remove high speed reclose
North | 04 - Northwest Kansas | 19W | Transfer | TIE-PO-1-1 | Prior Outage of BLACKBERRY to NEOSHO 345kV Circuit 1, 3-phase fault on WAVERLY to LACYGNE 345 kV Circuit 1, near LACYGNE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Unstable | No | Yes | Yes | Yes | Yes | No | WCGS U1 rotor angle unstable (first swing) and get tripped | Remove high speed reclose
North | 04 - Northwest Kansas | 19W | Transfer | TIE-PO-3-1 | Prior Outage of 87TH to CRAIG 345kV Circuit 1, 3-phase fault on WAVERLY to LACYGNE 345 kV Circuit 1, near LACYGNE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Unstable | No | Yes | Yes | Yes | Yes | No | WCGS U1 rotor angle unstable (first swing) and get tripped | Remove high speed reclose
North | 04 - Northwest Kansas | 19W | Transfer | TIE-PO-4-1 | Prior Outage of SWISVAL to W.GRDNR 345kV Circuit 1, 3-phase fault on WAVERLY to LACYGNE 345 kV Circuit 1, near LACYGNE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Unstable | No | Yes | Yes | Yes | Yes | No | WCGS U1 rotor angle unstable (first swing) and get tripped | Remove high speed reclose
North | 04 - Northwest Kansas | 21L | Transfer | 004-3PH-25 | 3-phase fault on JEC N to HOYT 345kVCircuit 1, near JEC N. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Unstable | No | Yes | Yes | Yes | Yes | No | JEC Units rotor angle unstable (first swing) and get tripped | Remove high speed reclose
North | 04 - Northwest Kansas | 21L | Transfer | 013-PO-1-1 | Prior Outage of MINGO to REDWILO 345kVCircuit 1, 3-phase fault on Mingo to SETAB 345 kVCircuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | Yes | Yes | Yes | Yes | No | Voltage at Mingo collapses. G15-065, G16-067 are tripped. | reduce Gens at Mingo (G15-064, G15-065, G16-067, G17-004) to 40%, post first outage in anticipation of contingencies in the system.
North | 04 - Northwest Kansas | 21L | Transfer | 013-PO-2-1 | Prior Outage of MINGO to SETAB 345kVCircuit 1, 3-phase fault on Mingo to REDWILO 345 kVCircuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | Yes | Yes | Yes | Yes | No | Voltage at Mingo collapses. G15-064, G15-065, G16-067 oscillate. | reduce Gens at Mingo (G15-064, G15-065, G16-067, G17-004) to 40%, post first outage in anticipation of contingencies in the system.
North | 04 - Northwest Kansas | 21S | Transfer | 004-3PH-25 | 3-phase fault on JEC N to HOYT 345kVCircuit 1, near JEC N. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Unstable | No | Yes | Yes | Yes | Yes | No | JEC Units rotor angle unstable (first swing) and get tripped | Remove high speed reclose
North | 04 - Northwest Kansas | 21S | Transfer | 004-3PH-26 | 3-phase fault on JEC N to MORRIS 345kVCircuit 1, near JEC N. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Unstable | No | Yes | Yes | Yes | Yes | No | JEC Units rotor angle unstable (first swing) and get tripped | Remove high speed reclose
North | 04 - Northwest Kansas | 21S | Transfer | 013-PO-1-1 | Prior Outage of MINGO to REDWILO 345kVCircuit 1, 3-phase fault on Mingo to SETAB 345 kVCircuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | Yes | Yes | Yes | Yes | No | Voltage at Mingo collapses. G15-064, G15-065, G16-067 oscillate. | reduce Gens at Mingo (G15-064, G15-065, G16-067, G17-004) to 50%, post first outage in anticipation of contingencies in the system.
North | 04 - Northwest Kansas | 21S | Transfer | 013-PO-2-1 | Prior Outage of MINGO to SETAB 345kVCircuit 1, 3-phase fault on Mingo to REDWILO 345 kVCircuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | Yes | Yes | Yes | Yes | No | Voltage at Mingo collapses. G15-064, G15-065, G16-067 oscillate. | reduce Gens at Mingo (G15-064, G15-065, G16-067, G17-004) to 50%, post first outage in anticipation of contingencies in the system.
North | 04 - Northwest Kansas | 21S | Transfer | TIE-3PH-12 | 3-phase fault on WAVERLY to LACYGNE 345 kVCircuit 1, near LACYGNE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Unstable | No | Yes | Yes | Yes | Yes | No | WCGS U1 rotor angle unstable (first swing) and get tripped | Remove high speed reclose
North | 04 - Northwest Kansas | 21S | Transfer | TIE-PO-1-1 | Prior Outage of BLACKBERRY to NEOSHO 345kV Circuit 1, 3-phase fault on WAVERLY to LACYGNE 345 kV Circuit 1, near LACYGNE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Unstable | No | Yes | Yes | Yes | Yes | No | WCGS U1 rotor angle unstable (first swing) and get tripped | Remove high speed reclose
North | 04 - Northwest Kansas | 21S | Transfer | TIE-PO-3-1 | Prior Outage of 87TH to CRAIG 345kV Circuit 1, 3-phase fault on WAVERLY to LACYGNE 345 kV Circuit 1, near LACYGNE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Unstable | No | Yes | Yes | Yes | Yes | No | WCGS U1 rotor angle unstable (first swing) and get tripped | Remove high speed reclose
North | 04 - Northwest Kansas | 21S | Transfer | TIE-PO-4-1 | Prior Outage of SWISVAL to W.GRDNR 345kV Circuit 1, 3-phase fault on WAVERLY to LACYGNE 345 kV Circuit 1, near LACYGNE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Unstable | No | Yes | Yes | Yes | Yes | No | WCGS U1 rotor angle unstable (first swing) and get tripped | Remove high speed reclose
North | 04 - Northwest Kansas | 28S | Transfer | 004-3PH-25 | 3-phase fault on JEC N to HOYT 345kVCircuit 1, near JEC N. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Unstable | No | Yes | Yes | Yes | Yes | No | JEC Units rotor angle unstable (first swing) and get tripped | Remove high speed reclose
North | 04 - Northwest Kansas | 28S | Transfer | 004-3PH-26 | 3-phase fault on JEC N to MORRIS 345kVCircuit 1, near JEC N. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Unstable | No | Yes | Yes | Yes | Yes | No | JEC Units rotor angle unstable (first swing) and get tripped | Remove high speed reclose
North | 04 - Northwest Kansas | 28S | Transfer | TIE-3PH-12 | 3-phase fault on WAVERLY to LACYGNE 345 kVCircuit 1, near LACYGNE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Unstable | No | Yes | Yes | Yes | Yes | No | WCGS U1 rotor angle unstable (first swing) and get tripped | Remove high speed reclose
North | 04 - Northwest Kansas | 28S | Transfer | TIE-PO-1-1 | Prior Outage of BLACKBERRY to NEOSHO 345kV Circuit 1, 3-phase fault on WAVERLY to LACYGNE 345 kV Circuit 1, near LACYGNE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Unstable | No | Yes | Yes | Yes | Yes | No | WCGS U1 rotor angle unstable (first swing) and get tripped | Remove high speed reclose
North | 04 - Northwest Kansas | 28S | Transfer | TIE-PO-3-1 | Prior Outage of 87TH to CRAIG 345kV Circuit 1, 3-phase fault on WAVERLY to LACYGNE 345 kV Circuit 1, near LACYGNE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Unstable | No | Yes | Yes | Yes | Yes | No | WCGS U1 rotor angle unstable (first swing) and get tripped | Remove high speed reclose
North | 04 - Northwest Kansas | 28S | Transfer | TIE-PO-4-1 | Prior Outage of SWISVAL to W.GRDNR 345kV Circuit 1, 3-phase fault on WAVERLY to LACYGNE 345 kV Circuit 1, near LACYGNE. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Unstable | No | Yes | Yes | Yes | Yes | No | WCGS U1 rotor angle unstable (first swing) and get tripped | Remove high speed reclose
North | 15 - Eastern South Dakota | 21S | Transfer | 103-PO-1-2 | Prior Outage of G16-017_TAP to Fort Thompson 345kV Circuit 1. Apply 3-phase fault on Leland Olds to Antelope 345kV Circuit 2, near Leland Olds. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | Yes | Yes | Yes | Yes | No | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 21S | Transfer | 103-PO-1-3 | Prior Outage of G16-017_TAP to Fort Thompson 345kV Circuit 1. 3-phase fault on Antelope to ROUNDUP 345kV Circuit 2, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | Yes | Yes | Yes | Yes | Yes | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 21S | Transfer | 103-PO-1-5 | Prior Outage of G16-017_TAP to Fort Thompson 345kV Circuit 1. 3-phase fault on Antelope to Broadland 345kV Circuit 1, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | Yes | Yes | Yes | Yes | Yes | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 21S | Transfer | 103-SB-2 | SLG fault on Fort Thompson 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Fort Thompson 345 kV bus. | P4 | Stable | No | Yes | Yes | Yes | Yes | Yes | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 28S | Transfer | 103-PO-1-2 | Prior Outage of G16-017_TAP to Fort Thompson 345kV Circuit 1. Apply 3-phase fault on Leland Olds to Antelope 345kV Circuit 2, near Leland Olds. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | Yes | Yes | Yes | Yes | Yes | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 28S | Transfer | 103-PO-1-3 | Prior Outage of G16-017_TAP to Fort Thompson 345kV Circuit 1. 3-phase fault on Antelope to ROUNDUP 345kV Circuit 2, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | Yes | Yes | Yes | Yes | No | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 28S | Transfer | 103-PO-1-4 | Prior Outage of G16-017_TAP to Fort Thompson 345kV Circuit 1. 3-phase fault on Antelope to CHARL_CK 345kV Circuit 1, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | Yes | Yes | Yes | Yes | Yes | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 28S | Transfer | 103-PO-1-5 | Prior Outage of G16-017_TAP to Fort Thompson 345kV Circuit 1. 3-phase fault on Antelope to Broadland 345kV Circuit 1, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | Yes | Yes | Yes | Yes | Yes | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 28S | Transfer | 103-PO-1-8 | Prior Outage of G16-017_TAP to Fort Thompson 345kV Circuit 1. 3-phase fault on Leland Olds 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | No | Yes | Yes | Yes | Yes | Yes | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 28S | Transfer | 103-SB-2 | SLG fault on Fort Thompson 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Fort Thompson 345 kV bus. | P4 | Stable | No | Yes | Yes | Yes | Yes | Yes | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 28S | Transfer | 094-SB-4 | SLG fault on Fort Thompson 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Fort Thompson 345 kV bus. | P4 | Stable | No | Yes | Yes | Yes | Yes | Yes | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 16 - Western North Dakota | 19W | Transfer | 010-SB-5 | SLG fault on BELFELD 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of BELFELD 230 kV bus. | P4 | Stable | No | Yes | Yes | Yes | Yes | No | Voltage collapse at Rhame. G17-010 tripped. | Model Correction
North | 16 - Western North Dakota | 21L | Transfer | 010-SB-5 | SLG fault on BELFELD 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of BELFELD 230 kV bus. | P4 | Stable | No | Yes | Yes | Yes | Yes | No | Voltage collapse at Rhame. G17-010 tripped. | Model Correction
North | 16 - Western North Dakota | 21S | Transfer | 010-SB-5 | SLG fault on BELFELD 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of BELFELD 230 kV bus. | P4 | Stable | No | Yes | Yes | Yes | Yes | No | Voltage collapse at Rhame. G17-010 tripped. | Model Correction
North | 16 - Western North Dakota | 28S | Transfer | 010-SB-5 | SLG fault on BELFELD 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of BELFELD 230 kV bus. | P4 | Stable | No | Yes | Yes | Yes | Yes | No | Voltage collapse at Rhame. G17-010 tripped. | Model Correction
North | 04 - Northwest Kansas | 28S | Transfer | 013-PO-1-1 | Prior Outage of MINGO to REDWILO 345kVCircuit 1, 3-phase fault on Mingo to SETAB 345 kVCircuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | No | Yes | Yes | Yes | No | Voltage at Mingo collapses. G15-064, G15-065, G16-067 oscillate. | reduce Gens at Mingo (G15-064, G15-065, G16-067, G17-004) to 50%, post prior outage in anticipation of contingencies in the system.
North | 04 - Northwest Kansas | 28S | Transfer | 013-PO-2-1 | Prior Outage of MINGO to SETAB 345kVCircuit 1, 3-phase fault on Mingo to REDWILO 345 kVCircuit 1, near Mingo. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | No | Yes | Yes | Yes | No | Voltage at Mingo collapses. G15-064, G15-065, G16-067 oscillate. | reduce Gens at Mingo (G15-064, G15-065, G16-067, G17-004) to 50%, post prior outage in anticipation of contingencies in the system.
North | 15 - Eastern South Dakota | 19W | Transfer | 103-3PH-45 | 3-phase fault on G16-017_TAP to Fort Thompson 345kV Circuit 1, near G16-017_TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | No | No | Yes | Yes | Yes | Yes | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 19W | Transfer | 103-PO-1-1 | Prior Outage of G16-017_TAP to Fort Thompson 345kV Circuit 1. 3-phase fault on Leland Olds to Groton 345kV Circuit 1, near Leland Olds. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | No | Yes | Yes | Yes | Yes | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 19W | Transfer | 103-PO-1-8 | Prior Outage of G16-017_TAP to Fort Thompson 345kV Circuit 1. 3-phase fault on Leland Olds 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | No | No | Yes | Yes | Yes | Yes | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 19W | Transfer | 103-PO-2-5 | Prior Outage of Leland Olds to Groton 345kV Circuit 1. 3-phase fault on G16-017_TAP to Fort Thompson 345kV Circuit 1, near G16-017_TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | No | Yes | Yes | Yes | Yes | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 19W | Transfer | 103-PO-3-2 | Prior Outage of Leland Olds to Antelope 345kV Circuit 1. 3-phase fault on G16-017_TAP to Fort Thompson 345kV Circuit 1, near G16-017_TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | No | Yes | Yes | Yes | Yes | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 19W | Transfer | 103-PO-4-2 | Prior Outage of Leland Olds 345/230/13.8 kV Transformer 1. 3-phase fault on G16-017_TAP to Fort Thompson 345kV Circuit 1, near G16-017_TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | No | Yes | Yes | Yes | Yes | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 21L | Transfer | 103-3PH-45 | 3-phase fault on G16-017_TAP to Fort Thompson 345kV Circuit 1, near G16-017_TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | No | No | Yes | Yes | Yes | Yes | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 21L | Transfer | 103-PO-1-1 | Prior Outage of G16-017_TAP to Fort Thompson 345kV Circuit 1. 3-phase fault on Leland Olds to Groton 345kV Circuit 1, near Leland Olds. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | No | Yes | Yes | Yes | Yes | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 21L | Transfer | 103-PO-1-8 | Prior Outage of G16-017_TAP to Fort Thompson 345kV Circuit 1. 3-phase fault on Leland Olds 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | No | No | Yes | Yes | Yes | Yes | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 21L | Transfer | 103-PO-2-5 | Prior Outage of Leland Olds to Groton 345kV Circuit 1. 3-phase fault on G16-017_TAP to Fort Thompson 345kV Circuit 1, near G16-017_TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | No | Yes | Yes | Yes | Yes | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 21L | Transfer | 103-PO-3-2 | Prior Outage of Leland Olds to Antelope 345kV Circuit 1. 3-phase fault on G16-017_TAP to Fort Thompson 345kV Circuit 1, near G16-017_TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | No | Yes | Yes | Yes | Yes | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 21L | Transfer | 103-PO-4-2 | Prior Outage of Leland Olds 345/230/13.8 kV Transformer 1. 3-phase fault on G16-017_TAP to Fort Thompson 345kV Circuit 1, near G16-017_TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | No | Yes | Yes | Yes | Yes | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 21S | Transfer | 103-3PH-45 | 3-phase fault on G16-017_TAP to Fort Thompson 345kV Circuit 1, near G16-017_TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | No | No | Yes | Yes | Yes | Yes | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 21S | Transfer | 103-PO-1-1 | Prior Outage of G16-017_TAP to Fort Thompson 345kV Circuit 1. 3-phase fault on Leland Olds to Groton 345kV Circuit 1, near Leland Olds. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | No | Yes | No | Yes | Yes | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 21S | Transfer | 103-PO-1-4 | Prior Outage of G16-017_TAP to Fort Thompson 345kV Circuit 1. 3-phase fault on Antelope to CHARL_CK 345kV Circuit 1, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | No | Yes | Yes | Yes | Yes | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 21S | Transfer | 103-PO-1-8 | Prior Outage of G16-017_TAP to Fort Thompson 345kV Circuit 1. 3-phase fault on Leland Olds 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | No | No | Yes | Yes | Yes | No | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 21S | Transfer | 103-PO-2-5 | Prior Outage of Leland Olds to Groton 345kV Circuit 1. 3-phase fault on G16-017_TAP to Fort Thompson 345kV Circuit 1, near G16-017_TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | No | Yes | Yes | Yes | No | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 21S | Transfer | 103-PO-3-2 | Prior Outage of Leland Olds to Antelope 345kV Circuit 1. 3-phase fault on G16-017_TAP to Fort Thompson 345kV Circuit 1, near G16-017_TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | No | Yes | Yes | Yes | Yes | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 21S | Transfer | 103-PO-4-2 | Prior Outage of Leland Olds 345/230/13.8 kV Transformer 1. 3-phase fault on G16-017_TAP to Fort Thompson 345kV Circuit 1, near G16-017_TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | No | Yes | Yes | Yes | Yes | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 28S | Transfer | 103-3PH-45 | 3-phase fault on G16-017_TAP to Fort Thompson 345kV Circuit 1, near G16-017_TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | No | No | Yes | Yes | Yes | Yes | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 28S | Transfer | 103-PO-1-1 | Prior Outage of G16-017_TAP to Fort Thompson 345kV Circuit 1. 3-phase fault on Leland Olds to Groton 345kV Circuit 1, near Leland Olds. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | No | Yes | Yes | Yes | Yes | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 28S | Transfer | 103-PO-2-5 | Prior Outage of Leland Olds to Groton 345kV Circuit 1. 3-phase fault on G16-017_TAP to Fort Thompson 345kV Circuit 1, near G16-017_TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | No | Yes | Yes | Yes | Yes | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 28S | Transfer | 103-PO-3-2 | Prior Outage of Leland Olds to Antelope 345kV Circuit 1. 3-phase fault on G16-017_TAP to Fort Thompson 345kV Circuit 1, near G16-017_TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | No | Yes | Yes | Yes | Yes | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 28S | Transfer | 103-PO-4-2 | Prior Outage of Leland Olds 345/230/13.8 kV Transformer 1. 3-phase fault on G16-017_TAP to Fort Thompson 345kV Circuit 1, near G16-017_TAP. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | No | Yes | Yes | Yes | Yes | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-4 | 3-phase fault on DAGLUM to BELFELD 230 kV Circuit 1, near DAGLUM. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | No | No | Yes | Yes | Yes | No | Voltage collapse at Rhame. G17-010 tripped. | Model Correction
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-4 | 3-phase fault on DAGLUM to BELFELD 230 kV Circuit 1, near DAGLUM. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | No | No | Yes | Yes | Yes | No | Voltage collapse at Rhame. G17-010 tripped. BRADYWNDGN2W tripped. G15-096 tripped. | Model Correction
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-4 | 3-phase fault on DAGLUM to BELFELD 230 kV Circuit 1, near DAGLUM. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | No | No | Yes | Yes | Yes | No | Voltage collapse at Rhame. G17-010 tripped. | Model Correction
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-36 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | No | No | No | No | No | No | The power swing caused oscillation between G16-159, G15-007, G16-021 and G16-043. Voltage collapse observed from power flow analysis. | Curtail G16-159, G15-007, G16-021 and G16-043 to 75% of their maximum capacity when prior outage exists.
North | 09 - Nebraska | 19W | Transfer | G16-159-3ph-40 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | No | No | No | No | No | No | The power swing caused oscillation between G16-159, G15-007, G16-021 and G16-043. Voltage collapse observed from power flow analysis. | Curtail G16-159, G15-007, G16-021 and G16-043 to 75% of their maximum capacity when prior outage exists.
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-36 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | No | No | No | No | No | No | The power swing caused oscillation between G16-159, G15-007, G16-021 and G16-043. Voltage collapse observed from power flow analysis. | Curtail G16-159, G15-007, G16-021 and G16-043 to 75% of their maximum capacity when prior outage exists.
North | 09 - Nebraska | 21S | Transfer | G16-159-3ph-40 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | No | No | No | No | No | No | The power swing caused oscillation between G16-159, G15-007, G16-021 and G16-043. Voltage collapse observed from power flow analysis. | Curtail G16-159, G15-007, G16-021 and G16-043 to 75% of their maximum capacity when prior outage exists.
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-36 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | No | No | No | No | No | No | The power swing caused oscillation between G16-159, G15-007, G16-021 and G16-043. Voltage collapse observed from power flow analysis. | Curtail G16-159, G15-007, G16-021 and G16-043 to 75% of their maximum capacity when prior outage exists.
North | 09 - Nebraska | 21L | Transfer | G16-159-3ph-40 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | No | No | No | No | No | No | The power swing caused oscillation between G16-159, G15-007, G16-021 and G16-043. Voltage collapse observed from power flow analysis. | Curtail G16-159, G15-007, G16-021 and G16-043 to 75% of their maximum capacity when prior outage exists.
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-36 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | No | No | No | No | No | No | The power swing caused oscillation between G16-159, G15-007, G16-021 and G16-043. Voltage collapse observed from power flow analysis. | Curtail G16-159, G15-007, G16-021 and G16-043 to 75% of their maximum capacity when prior outage exists.
North | 09 - Nebraska | 28S | Transfer | G16-159-3ph-40 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | No | No | No | No | No | No | The power swing caused oscillation between G16-159, G15-007, G16-021 and G16-043. Voltage collapse observed from power flow analysis. | Curtail G16-159, G15-007, G16-021 and G16-043 to 75% of their maximum capacity when prior outage exists.
North | 09 - Nebraska | 21S | Transfer | G17-008-3ph-32 | Prior Outage of G15-088-TAP to Moore 345kV crt 1. 3-ph fault on Pauline 345/115/13.8kV TF T1, near Pauline 345kV. Clear fault after 6 cycles. | P6 | Stable | No | No | No | No | No | No | After fault cleared, the Pauline station turned very weak, the power interaction occurred between G15-088 and G17-008. | Curtail G17-008 and G15-088 by 50% of their maximum capacity post outage of G15-088 Tap – Moore. in anticipation of contingencies in the system.
North | 09 - Nebraska | 28S | Transfer | G17-008-3ph-32 | Prior Outage of G15-088-TAP to Moore 345kV crt 1. 3-ph fault on Pauline 345/115/13.8kV TF T1, near Pauline 345kV. Clear fault after 6 cycles. | P6 | Stable | No | No | No | No | No | No | After fault cleared, the Pauline area turned very weak, the power interaction occurred between G15-088 and G17-008. | Curtail G17-008 and G15-088 by 50% of their maximum capacity post outage of G15-088 Tap – Moore. in anticipation of contingencies in the system.
North | 15 - Eastern South Dakota | 19W | Transfer | 103-PO-1-2 | Prior Outage of G16-017_TAP to Fort Thompson 345kV Circuit 1. Apply 3-phase fault on Leland Olds to Antelope 345kV Circuit 2, near Leland Olds. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | No | No | No | No | No | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 19W | Transfer | 103-PO-1-3 | Prior Outage of G16-017_TAP to Fort Thompson 345kV Circuit 1. 3-phase fault on Antelope to ROUNDUP 345kV Circuit 2, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | No | No | No | No | No | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 19W | Transfer | 103-PO-1-4 | Prior Outage of G16-017_TAP to Fort Thompson 345kV Circuit 1. 3-phase fault on Antelope to CHARL_CK 345kV Circuit 1, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | No | No | No | No | No | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 19W | Transfer | 103-PO-1-5 | Prior Outage of G16-017_TAP to Fort Thompson 345kV Circuit 1. 3-phase fault on Antelope to Broadland 345kV Circuit 1, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | No | No | No | No | No | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 19W | Transfer | 103-PO-1-6 | Prior Outage of G16-017_TAP to Fort Thompson 345kV Circuit 1. 3-phase fault on Groton to G09_001IST 345kV Circuit 1, near Groton. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | No | No | No | No | No | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 19W | Transfer | 103-PO-1-7 | Prior Outage of G16-017_TAP to Fort Thompson 345kV Circuit 1. 3-phase fault on Groton 345/115/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | No | No | No | No | No | No | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 19W | Transfer | 103-PO-5-3 | Prior Outage of G16-017_TAP to Leland Olds 345kV Circuit 1. 3-phase fault on Fort Thompson 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | No | No | No | No | No | No | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 19W | Transfer | 103-SB-2 | SLG fault on Fort Thompson 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Fort Thompson 345 kV bus. | P4 | Stable | No | No | No | No | No | No | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 21L | Transfer | 103-PO-1-2 | Prior Outage of G16-017_TAP to Fort Thompson 345kV Circuit 1. Apply 3-phase fault on Leland Olds to Antelope 345kV Circuit 2, near Leland Olds. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | No | No | No | No | No | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 21L | Transfer | 103-PO-1-3 | Prior Outage of G16-017_TAP to Fort Thompson 345kV Circuit 1. 3-phase fault on Antelope to ROUNDUP 345kV Circuit 2, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | No | No | No | No | No | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 21L | Transfer | 103-PO-1-4 | Prior Outage of G16-017_TAP to Fort Thompson 345kV Circuit 1. 3-phase fault on Antelope to CHARL_CK 345kV Circuit 1, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | No | No | No | No | No | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 21L | Transfer | 103-PO-1-5 | Prior Outage of G16-017_TAP to Fort Thompson 345kV Circuit 1. 3-phase fault on Antelope to Broadland 345kV Circuit 1, near Antelope. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | No | No | No | No | No | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 21L | Transfer | 103-PO-1-6 | Prior Outage of G16-017_TAP to Fort Thompson 345kV Circuit 1. 3-phase fault on Groton to G09_001IST 345kV Circuit 1, near Groton. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | No | No | No | No | No | No | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 21L | Transfer | 103-PO-1-7 | Prior Outage of G16-017_TAP to Fort Thompson 345kV Circuit 1. 3-phase fault on Groton 345/115/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | No | No | No | No | No | No | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 21L | Transfer | 103-PO-5-3 | Prior Outage of G16-017_TAP to Leland Olds 345kV Circuit 1. 3-phase fault on Fort Thompson 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | No | No | No | No | No | No | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 21L | Transfer | 103-SB-1 | SLG fault on Leland Olds 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Leland Olds to Antelope 345 kV Circuit 1, Leland Olds to Groton 345 kV Circuit 1, Leland Olds to G16-017 TAP Circuit 1 and Leland Olds generator 2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Transfer | 103-SB-2 | SLG fault on Fort Thompson 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Fort Thompson 345 kV bus. | P4 | Stable | No | No | No | No | No | No | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 15 - Eastern South Dakota | 28S | Transfer | 103-PO-5-3 | Prior Outage of G16-017_TAP to Leland Olds 345kV Circuit 1. 3-phase fault on Fort Thompson 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P6 | Stable | No | No | No | No | No | No | Voltage collapse at Leland Olds due to loss of G16-017_TAP to Fort Thompson 345 kV circuit | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC)
North | 17 - Western South Dakota | 19W | Transfer | 3ph-02 | 3-ph fault on G17-014-TAP to Philip Tap 230kV crt 1, near G17-014-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | No | No | No | No | No | No | Power oscillation between G17-014 and G17-097 locally, switch off either of the projects will be stable. | Convert existing Philip Tap to a ring bus substation and build approximately 6 miles of new 230kV from new substation to G17-014 Tap creating a double circuit 230kV line. The 2nd Ckt can solve this issue, however, there is still a chance that losing both lines from G17-014 to Philip Tap will result in oscillatory issues due to control interactions among the G17-014, G17-097 and G17-064 requests. In addition, the area is close to the Rapid City HVDC inverter side. EMT study is required to determine if further mitigations are required.
North | 17 - Western South Dakota | 19W | Transfer | SLG-40 | SLG fault on G17-014-TAP to Philip Tap 230kV crt 1, near G17-014-TAP for 16 cycles. Clear fault by tripping the Philip Tap 230kV bus. | P4 | Stable | No | No | No | No | No | No | Power oscillation between G17-014 and G17-097 locally, switch off either of the projects will be stable. | Convert existing Philip Tap to a ring bus substation and build approximately 6 miles of new 230kV from new substation to G17-014 Tap creating a double circuit 230kV line. The 2nd Ckt can solve this issue, however, there is still a chance that losing both lines from G17-014 to Philip Tap will result in oscillatory issues due to control interactions among the G17-014, G17-097 and G17-064 requests. In addition, the area is close to the Rapid City HVDC inverter side. EMT study is required to determine if further mitigations are required.
North | 17 - Western South Dakota | 19W | Transfer | SLG-55 | SLG fault on Philip 230/115/13.2kV TF 1A, near Philip 115kV for 16 cycles. Clear fault by tripping the Philip Tap 230kV bus. | P4 | Stable | No | No | No | No | No | No | Power oscillation between G17-014 and G17-097 locally, switch off either of the projects will be stable. | Convert existing Philip Tap to a ring bus substation and build approximately 6 miles of new 230kV from new substation to G17-014 Tap creating a double circuit 230kV line. The 2nd Ckt can solve this issue, however, there is still a chance that losing both lines from G17-014 to Philip Tap will result in oscillatory issues due to control interactions among the G17-014, G17-097 and G17-064 requests. In addition, the area is close to the Rapid City HVDC inverter side. EMT study is required to determine if further mitigations are required.
North | 17 - Western South Dakota | 21S | Transfer | 3ph-02 | 3-ph fault on G17-014-TAP to Philip Tap 230kV crt 1, near G17-014-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | No | No | No | No | No | No | Power oscillation between G17-014 and G17-097 locally, switch off either of the projects will be stable. | Convert existing Philip Tap to a ring bus substation and build approximately 6 miles of new 230kV from new substation to G17-014 Tap creating a double circuit 230kV line. The 2nd Ckt can solve this issue, however, there is still a chance that losing both lines from G17-014 to Philip Tap will result in oscillatory issues due to control interactions among the G17-014, G17-097 and G17-064 requests. In addition, the area is close to the Rapid City HVDC inverter side. EMT study is required to determine if further mitigations are required.
North | 17 - Western South Dakota | 21S | Transfer | SLG-40 | SLG fault on G17-014-TAP to Philip Tap 230kV crt 1, near G17-014-TAP for 16 cycles. Clear fault by tripping the Philip Tap 230kV bus. | P4 | Stable | No | No | No | No | No | No | Power oscillation between G17-014 and G17-097 locally, switch off either of the projects will be stable. | Convert existing Philip Tap to a ring bus substation and build approximately 6 miles of new 230kV from new substation to G17-014 Tap creating a double circuit 230kV line. The 2nd Ckt can solve this issue, however, there is still a chance that losing both lines from G17-014 to Philip Tap will result in oscillatory issues due to control interactions among the G17-014, G17-097 and G17-064 requests. In addition, the area is close to the Rapid City HVDC inverter side. EMT study is required to determine if further mitigations are required.
North | 17 - Western South Dakota | 21S | Transfer | SLG-55 | SLG fault on Philip 230/115/13.2kV TF 1A, near Philip 115kV for 16 cycles. Clear fault by tripping the Philip Tap 230kV bus. | P4 | Stable | No | No | No | No | No | No | Power oscillation between G17-014 and G17-097 locally, switch off either of the projects will be stable. | Convert existing Philip Tap to a ring bus substation and build approximately 6 miles of new 230kV from new substation to G17-014 Tap creating a double circuit 230kV line. The 2nd Ckt can solve this issue, however, there is still a chance that losing both lines from G17-014 to Philip Tap will result in oscillatory issues due to control interactions among the G17-014, G17-097 and G17-064 requests. In addition, the area is close to the Rapid City HVDC inverter side. EMT study is required to determine if further mitigations are required.
North | 17 - Western South Dakota | 21L | Transfer | 3ph-02 | 3-ph fault on G17-014-TAP to Philip Tap 230kV crt 1, near G17-014-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | No | No | No | No | No | No | Power oscillation between G17-014 and G17-097 locally, switch off either of the projects will be stable. | Convert existing Philip Tap to a ring bus substation and build approximately 6 miles of new 230kV from new substation to G17-014 Tap creating a double circuit 230kV line. The 2nd Ckt can solve this issue, however, there is still a chance that losing both lines from G17-014 to Philip Tap will result in oscillatory issues due to control interactions among the G17-014, G17-097 and G17-064 requests. In addition, the area is close to the Rapid City HVDC inverter side. EMT study is required to determine if further mitigations are required.
North | 17 - Western South Dakota | 21L | Transfer | SLG-40 | SLG fault on G17-014-TAP to Philip Tap 230kV crt 1, near G17-014-TAP for 16 cycles. Clear fault by tripping the Philip Tap 230kV bus. | P4 | Stable | No | No | No | No | No | No | Power oscillation between G17-014 and G17-097 locally, switch off either of the projects will be stable. | Convert existing Philip Tap to a ring bus substation and build approximately 6 miles of new 230kV from new substation to G17-014 Tap creating a double circuit 230kV line. The 2nd Ckt can solve this issue, however, there is still a chance that losing both lines from G17-014 to Philip Tap will result in oscillatory issues due to control interactions among the G17-014, G17-097 and G17-064 requests. In addition, the area is close to the Rapid City HVDC inverter side. EMT study is required to determine if further mitigations are required.
North | 17 - Western South Dakota | 21L | Transfer | SLG-55 | SLG fault on Philip 230/115/13.2kV TF 1A, near Philip 115kV for 16 cycles. Clear fault by tripping the Philip Tap 230kV bus. | P4 | Stable | No | No | No | No | No | No | Power oscillation between G17-014 and G17-097 locally, switch off either of the projects will be stable. | Convert existing Philip Tap to a ring bus substation and build approximately 6 miles of new 230kV from new substation to G17-014 Tap creating a double circuit 230kV line. The 2nd Ckt can solve this issue, however, there is still a chance that losing both lines from G17-014 to Philip Tap will result in oscillatory issues due to control interactions among the G17-014, G17-097 and G17-064 requests. In addition, the area is close to the Rapid City HVDC inverter side. EMT study is required to determine if further mitigations are required.
North | 17 - Western South Dakota | 28S | Transfer | 3ph-02 | 3-ph fault on G17-014-TAP to Philip Tap 230kV crt 1, near G17-014-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | No | No | No | No | No | No | Power oscillation between G17-014 and G17-097 locally, switch off either of the projects will be stable. | Convert existing Philip Tap to a ring bus substation and build approximately 6 miles of new 230kV from new substation to G17-014 Tap creating a double circuit 230kV line. The 2nd Ckt can solve this issue, however, there is still a chance that losing both lines from G17-014 to Philip Tap will result in oscillatory issues due to control interactions among the G17-014, G17-097 and G17-064 requests. In addition, the area is close to the Rapid City HVDC inverter side. EMT study is required to determine if further mitigations are required.
North | 17 - Western South Dakota | 28S | Transfer | SLG-40 | SLG fault on G17-014-TAP to Philip Tap 230kV crt 1, near G17-014-TAP for 16 cycles. Clear fault by tripping the Philip Tap 230kV bus. | P4 | Stable | No | No | No | No | No | No | Power oscillation between G17-014 and G17-097 locally, switch off either of the projects will be stable. | Convert existing Philip Tap to a ring bus substation and build approximately 6 miles of new 230kV from new substation to G17-014 Tap creating a double circuit 230kV line. The 2nd Ckt can solve this issue, however, there is still a chance that losing both lines from G17-014 to Philip Tap will result in oscillatory issues due to control interactions among the G17-014, G17-097 and G17-064 requests. In addition, the area is close to the Rapid City HVDC inverter side. EMT study is required to determine if further mitigations are required.
North | 17 - Western South Dakota | 28S | Transfer | SLG-55 | SLG fault on Philip 230/115/13.2kV TF 1A, near Philip 115kV for 16 cycles. Clear fault by tripping the Philip Tap 230kV bus. | P4 | Stable | No | No | No | No | No | No | Power oscillation between G17-014 and G17-097 locally, switch off either of the projects will be stable. | Convert existing Philip Tap to a ring bus substation and build approximately 6 miles of new 230kV from new substation to G17-014 Tap creating a double circuit 230kV line. The 2nd Ckt can solve this issue, however, there is still a chance that losing both lines from G17-014 to Philip Tap will result in oscillatory issues due to control interactions among the G17-014, G17-097 and G17-064 requests. In addition, the area is close to the Rapid City HVDC inverter side. EMT study is required to determine if further mitigations are required.
North | 16 - Western North Dakota | 19W | Transfer | 048-SB-3 | SLG fault on TIOGA 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of TIOGA 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Small ripple undamped. Observed on LELAND, GARISN, GRE-STATION generators | Model Correction
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-6 | 3-phase fault on TIOGA to BDV 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Small ripple undamped. Observed on LELAND, GARISN, GRE-STATION generators | Model Correction
North | 16 - Western North Dakota | 21S | Transfer | 048-PO-1-4 | Apply 3-phase fault on TIOGA to BDV 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Small ripple undamped. Observed on LELAND, GARISN, GRE-STATION generators | Model Correction
North | 16 - Western North Dakota | 21S | Transfer | 048-PO-3-4 | Apply 3-phase fault on TIOGA to BDV 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Small ripple undamped. Observed on LELAND, GARISN, GRE-STATION generators | Model Correction
North | 16 - Western North Dakota | 21S | Transfer | 048-SB-3 | SLG fault on TIOGA 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of TIOGA 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Small ripple undamped. Observed on LELAND, GARISN, GRE-STATION generators | Model Correction
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_1_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Modeling issues consistent in the simulation results: CAPROCK_WND134.500 DVAR [#524485] showed abnormal high frequency oscillations which also impacted several other units responses nearby. This issue is potentially due to dynamic model parameters fo the DVAR. Since this oscillations does not impact the overall stability of the system, per discussion with SPP, it is only reported (Since this issue is observed in multiple contingencies it is reported once). OCEG units [#511939,511940,511942,511943] showed abnormal responses in post-fault period which is attributed to a modeling issue. Since this issue is observed in multiple contingencies in BC and TC cases it is reported once. Voltage Spike: 1.26pu, MaxDur: 0.09s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_1_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_1_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.24pu, MaxDur: 0.07s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_1_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.05s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_10_P1_BORDER | Apply 3-phase fault on BORDER shunt device , near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_10_P1_BORDER | Apply 3-phase fault on BORDER shunt device , near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_10_P1_BORDER | Apply 3-phase fault on BORDER shunt device , near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_10_P1_BORDER | Apply 3-phase fault on BORDER shunt device , near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_100_P1_SWISHER | Apply 3-phase fault on SWISHER to NEWHART 230kV line CKT 1, near SWISHER 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_100_P1_SWISHER | Apply 3-phase fault on SWISHER to NEWHART 230kV line CKT 1, near SWISHER 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_100_P1_SWISHER | Apply 3-phase fault on SWISHER to NEWHART 230kV line CKT 1, near SWISHER 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_100_P1_SWISHER | Apply 3-phase fault on SWISHER to NEWHART 230kV line CKT 1, near SWISHER 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_101_P1_COX | Apply 3-phase fault on COX to FLOYD_CNTY 3 115kV line CKT 1, near COX 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_101_P1_COX | Apply 3-phase fault on COX to FLOYD_CNTY 3 115kV line CKT 1, near COX 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_101_P1_COX | Apply 3-phase fault on COX to FLOYD_CNTY 3 115kV line CKT 1, near COX 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_101_P1_COX | Apply 3-phase fault on COX to FLOYD_CNTY 3 115kV line CKT 1, near COX 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_102_P1_LAMTON | Apply 3-phase fault on LAMTON to HALE_CNTY 115kV line CKT 1, near LAMTON 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_102_P1_LAMTON | Apply 3-phase fault on LAMTON to HALE_CNTY 115kV line CKT 1, near LAMTON 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_102_P1_LAMTON | Apply 3-phase fault on LAMTON to HALE_CNTY 115kV line CKT 1, near LAMTON 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_102_P1_LAMTON | Apply 3-phase fault on LAMTON to HALE_CNTY 115kV line CKT 1, near LAMTON 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_103_P1_LAMTON | Apply 3-phase fault on LAMTON to LC-S_OLTON+3 115kV line CKT 1, near LAMTON 115kV for 7 cycles. Open the faulted line and LC-S_OLTON+3 to PLANT_X 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and LC-S_OLTON+3 to PLANT_X 115kV line CKT 1. Re-open the faulted line after 7 cycles% LC-S_OLTON+3 to PLANT_X 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_103_P1_LAMTON | Apply 3-phase fault on LAMTON to LC-S_OLTON+3 115kV line CKT 1, near LAMTON 115kV for 7 cycles. Open the faulted line and LC-S_OLTON+3 to PLANT_X 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and LC-S_OLTON+3 to PLANT_X 115kV line CKT 1. Re-open the faulted line after 7 cycles% LC-S_OLTON+3 to PLANT_X 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_12_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Unstable | No | No | No | No | Yes | No | LVRT VIOL - - NoVUS_WND 1[1] LANoGSU10.60[W1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1]. NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disables and the simulations were repeated, these generators went unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed. Voltage Spike: 1.30pu, MaxDur: 0.02s
South | 02 - Hitchland | 21L | Transfer | FLT_12_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Unstable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1] NoVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1]. NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disables and the simulations were repeated, these generators went unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed. Voltage Spike: 1.24pu, MaxDur: 0.10s
South | 02 - Hitchland | 21S | Transfer | FLT_12_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Unstable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1] NoVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1]. NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disables and the simulations were repeated, these generators went unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed. Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 02 - Hitchland | 28S | Transfer | FLT_12_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Unstable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1] NoVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1]. NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disables and the simulations were repeated, these generators went unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed. Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 02 - Hitchland | 19W | Transfer | FLT_13_P1_HITCHLAND | Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Unstable | No | No | No | No | Yes | No | LVRT VIOL - - NoVUS_WND 1[1] LANoGSU10.60[W1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1]. NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disables and the simulations were repeated, these generators went unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed. Voltage Spike: 1.28pu, MaxDur: 0.01s
South | 02 - Hitchland | 21L | Transfer | FLT_13_P1_HITCHLAND | Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Unstable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1] NoVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1]. NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disables and the simulations were repeated, these generators went unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed. Voltage Spike: 1.23pu, MaxDur: 0.11s
South | 02 - Hitchland | 21S | Transfer | FLT_13_P1_HITCHLAND | Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Unstable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1] NoVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1]. NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disables and the simulations were repeated, these generators went unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 28S | Transfer | FLT_13_P1_HITCHLAND | Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Unstable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1] NoVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1]. NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disables and the simulations were repeated, these generators went unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 19W | Transfer | FLT_14_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to CARPENTER 345kV line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Unstable | No | No | No | No | Yes | No | LVRT VIOL - - NoVUS_WND 1[1] LANoGSU10.60[W1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1]. NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disables and the simulations were repeated, these generators went unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed. Voltage Spike: 1.25pu, MaxDur: 0.01s
South | 02 - Hitchland | 21L | Transfer | FLT_14_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to CARPENTER 345kV line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Unstable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1] NoVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1]. NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disables and the simulations were repeated, these generators went unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed. Voltage Spike: 1.23pu, MaxDur: 0.09s
South | 02 - Hitchland | 21S | Transfer | FLT_14_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to CARPENTER 345kV line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Unstable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1] NoVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1]. NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disables and the simulations were repeated, these generators went unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 28S | Transfer | FLT_14_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to CARPENTER 345kV line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Unstable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1] NoVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1]. NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disables and the simulations were repeated, these generators went unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed. Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 19W | Transfer | FLT_15_P1_COLE | Apply 3-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_15_P1_COLE | Apply 3-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_15_P1_COLE | Apply 3-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_15_P1_COLE | Apply 3-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_16_P1_COLE | Apply 3-phase fault on COLE to OCHILTREE 115kV line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 02 - Hitchland | 21L | Transfer | FLT_16_P1_COLE | Apply 3-phase fault on COLE to OCHILTREE 115kV line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 02 - Hitchland | 21S | Transfer | FLT_16_P1_COLE | Apply 3-phase fault on COLE to OCHILTREE 115kV line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_16_P1_COLE | Apply 3-phase fault on COLE to OCHILTREE 115kV line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_17_P1_COLE | Apply 3-phase fault on COLE to TC-AGGIE 115kV line CKT 1, near COLE 115kV for 7 cycles. Open the faulted line and TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1 and clear the fault. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_17_P1_COLE | Apply 3-phase fault on COLE to TC-AGGIE 115kV line CKT 1, near COLE 115kV for 7 cycles. Open the faulted line and TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1 and clear the fault. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 02 - Hitchland | 21S | Transfer | FLT_17_P1_COLE | Apply 3-phase fault on COLE to TC-AGGIE 115kV line CKT 1, near COLE 115kV for 7 cycles. Open the faulted line and TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1 and clear the fault. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_17_P1_COLE | Apply 3-phase fault on COLE to TC-AGGIE 115kV line CKT 1, near COLE 115kV for 7 cycles. Open the faulted line and TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1 and clear the fault. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_18_P1_OCHILTREE | Apply 3-phase fault on TXFARMS to OCHILTREE 115kV line CKT 1, near OCHILTREE 115kV for 7 cycles. Open the faulted line and SPEARMAN to HANSFORD 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and SPEARMAN to HANSFORD 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open SPEARMAN to HANSFORD 115kV line CKT 1 and clear the fault. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_18_P1_OCHILTREE | Apply 3-phase fault on TXFARMS to OCHILTREE 115kV line CKT 1, near OCHILTREE 115kV for 7 cycles. Open the faulted line and SPEARMAN to HANSFORD 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and SPEARMAN to HANSFORD 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open SPEARMAN to HANSFORD 115kV line CKT 1 and clear the fault. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 21S | Transfer | FLT_18_P1_OCHILTREE | Apply 3-phase fault on TXFARMS to OCHILTREE 115kV line CKT 1, near OCHILTREE 115kV for 7 cycles. Open the faulted line and SPEARMAN to HANSFORD 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and SPEARMAN to HANSFORD 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open SPEARMAN to HANSFORD 115kV line CKT 1 and clear the fault. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_18_P1_OCHILTREE | Apply 3-phase fault on TXFARMS to OCHILTREE 115kV line CKT 1, near OCHILTREE 115kV for 7 cycles. Open the faulted line and SPEARMAN to HANSFORD 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and SPEARMAN to HANSFORD 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open SPEARMAN to HANSFORD 115kV line CKT 1 and clear the fault. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_19_P1_OCHILTREE | Apply 3-phase fault on OCHILTREE 230kV/115kV/13.19kV transformer CKT 1, near OCHILTREE 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_19_P1_OCHILTREE | Apply 3-phase fault on OCHILTREE 230kV/115kV/13.19kV transformer CKT 1, near OCHILTREE 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_19_P1_OCHILTREE | Apply 3-phase fault on OCHILTREE 230kV/115kV/13.19kV transformer CKT 1, near OCHILTREE 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_19_P1_OCHILTREE | Apply 3-phase fault on OCHILTREE 230kV/115kV/13.19kV transformer CKT 1, near OCHILTREE 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_20_P1_FRISCO_WND3 | Apply 3-phase fault on FRISCO_WND 3 to LASLEY 115kV line CKT 1, near FRISCO_WND 3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - FRISCO_WND 3[1]. G59REL at FRISCO_WND 3[1] was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21L | Transfer | FLT_20_P1_FRISCO_WND3 | Apply 3-phase fault on FRISCO_WND 3 to LASLEY 115kV line CKT 1, near FRISCO_WND 3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - FRISCO_WND 3[1]. G59REL at FRISCO_WND 3[1] was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21S | Transfer | FLT_20_P1_FRISCO_WND3 | Apply 3-phase fault on FRISCO_WND 3 to LASLEY 115kV line CKT 1, near FRISCO_WND 3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - FRISCO_WND 3[1]. G59REL at FRISCO_WND 3[1] was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 28S | Transfer | FLT_20_P1_FRISCO_WND3 | Apply 3-phase fault on FRISCO_WND 3 to LASLEY 115kV line CKT 1, near FRISCO_WND 3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - FRISCO_WND 3[1]. G59REL at FRISCO_WND 3[1] was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 19W | Transfer | FLT_21_P1_MOORE_E | Apply 3-phase fault on MOORE_CNTY 6 230kV/115kV/13.19kV transformer CKT 1, near MOORE_E 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_21_P1_MOORE_E | Apply 3-phase fault on MOORE_CNTY 6 230kV/115kV/13.19kV transformer CKT 1, near MOORE_E 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_21_P1_MOORE_E | Apply 3-phase fault on MOORE_CNTY 6 230kV/115kV/13.19kV transformer CKT 1, near MOORE_E 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_21_P1_MOORE_E | Apply 3-phase fault on MOORE_CNTY 6 230kV/115kV/13.19kV transformer CKT 1, near MOORE_E 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 19W | Transfer | FLT_22_P1_MOORE_CNTY6 | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV line CKT 1, near MOORE_CNTY 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_22_P1_MOORE_CNTY6 | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV line CKT 1, near MOORE_CNTY 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_22_P1_MOORE_CNTY6 | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV line CKT 1, near MOORE_CNTY 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_22_P1_MOORE_CNTY6 | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV line CKT 1, near MOORE_CNTY 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 19W | Transfer | FLT_23_P1_CARPENTER | Apply 3-phase fault on HARBNGR3 115kV/345kV/13.8kV transformer CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_23_P1_CARPENTER | Apply 3-phase fault on HARBNGR3 115kV/345kV/13.8kV transformer CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.21pu, MaxDur: 0.10s
South | 02 - Hitchland | 21S | Transfer | FLT_23_P1_CARPENTER | Apply 3-phase fault on HARBNGR3 115kV/345kV/13.8kV transformer CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_23_P1_CARPENTER | Apply 3-phase fault on HARBNGR3 115kV/345kV/13.8kV transformer CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_24_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO 345kV/230kV/13.19kV transformer CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21L | Transfer | FLT_24_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO 345kV/230kV/13.19kV transformer CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21S | Transfer | FLT_24_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO 345kV/230kV/13.19kV transformer CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 28S | Transfer | FLT_24_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO 345kV/230kV/13.19kV transformer CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 19W | Transfer | FLT_25_P1_MANHATTAN | Apply 3-phase fault on EAST_PLANT 3 to MANHATTAN 115kV line CKT 1, near MANHATTAN 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21L | Transfer | FLT_25_P1_MANHATTAN | Apply 3-phase fault on EAST_PLANT 3 to MANHATTAN 115kV line CKT 1, near MANHATTAN 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21S | Transfer | FLT_25_P1_MANHATTAN | Apply 3-phase fault on EAST_PLANT 3 to MANHATTAN 115kV line CKT 1, near MANHATTAN 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 28S | Transfer | FLT_25_P1_MANHATTAN | Apply 3-phase fault on EAST_PLANT 3 to MANHATTAN 115kV line CKT 1, near MANHATTAN 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 19W | Transfer | FLT_26_P1_BUSHLAND | Apply 3-phase fault on BUSHLAND 230kV/115kV/13.19kV transformer CKT 1, near BUSHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed. Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 02 - Hitchland | 21L | Transfer | FLT_26_P1_BUSHLAND | Apply 3-phase fault on BUSHLAND 230kV/115kV/13.19kV transformer CKT 1, near BUSHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21S | Transfer | FLT_26_P1_BUSHLAND | Apply 3-phase fault on BUSHLAND 230kV/115kV/13.19kV transformer CKT 1, near BUSHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed. Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 02 - Hitchland | 28S | Transfer | FLT_26_P1_BUSHLAND | Apply 3-phase fault on BUSHLAND 230kV/115kV/13.19kV transformer CKT 1, near BUSHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 19W | Transfer | FLT_27_P1_BUSHLAND | Apply 3-phase fault on POTTER_CO to BUSHLAND 230kV line CKT 1, near BUSHLAND 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed. Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 21L | Transfer | FLT_27_P1_BUSHLAND | Apply 3-phase fault on POTTER_CO to BUSHLAND 230kV line CKT 1, near BUSHLAND 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21S | Transfer | FLT_27_P1_BUSHLAND | Apply 3-phase fault on POTTER_CO to BUSHLAND 230kV line CKT 1, near BUSHLAND 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed. Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 28S | Transfer | FLT_27_P1_BUSHLAND | Apply 3-phase fault on POTTER_CO to BUSHLAND 230kV line CKT 1, near BUSHLAND 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 19W | Transfer | FLT_28_P1_RANDALL | Apply 3-phase fault on RANDALL 230kV/115kV/13.19kV transformer CKT 2, near RANDALL 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21L | Transfer | FLT_28_P1_RANDALL | Apply 3-phase fault on RANDALL 230kV/115kV/13.19kV transformer CKT 2, near RANDALL 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed. Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 21S | Transfer | FLT_28_P1_RANDALL | Apply 3-phase fault on RANDALL 230kV/115kV/13.19kV transformer CKT 2, near RANDALL 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 28S | Transfer | FLT_28_P1_RANDALL | Apply 3-phase fault on RANDALL 230kV/115kV/13.19kV transformer CKT 2, near RANDALL 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 19W | Transfer | FLT_29_P1_RANDALL | Apply 3-phase fault on RANDALL to PALO_DURO 115kV line CKT 1, near RANDALL 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21L | Transfer | FLT_29_P1_RANDALL | Apply 3-phase fault on RANDALL to PALO_DURO 115kV line CKT 1, near RANDALL 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21S | Transfer | FLT_29_P1_RANDALL | Apply 3-phase fault on RANDALL to PALO_DURO 115kV line CKT 1, near RANDALL 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 28S | Transfer | FLT_29_P1_RANDALL | Apply 3-phase fault on RANDALL to PALO_DURO 115kV line CKT 1, near RANDALL 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 19W | Transfer | FLT_30_P1_RANDALL | Apply 3-phase fault on RANDALL to AMA_SOUTH 230kV line CKT 1, near RANDALL 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21L | Transfer | FLT_30_P1_RANDALL | Apply 3-phase fault on RANDALL to AMA_SOUTH 230kV line CKT 1, near RANDALL 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21S | Transfer | FLT_30_P1_RANDALL | Apply 3-phase fault on RANDALL to AMA_SOUTH 230kV line CKT 1, near RANDALL 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 28S | Transfer | FLT_30_P1_RANDALL | Apply 3-phase fault on RANDALL to AMA_SOUTH 230kV line CKT 1, near RANDALL 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 19W | Transfer | FLT_31_P1_AMA_SOUTH | Apply 3-phase fault on AMA_SOUTH to SWISHER 230kV line CKT 1, near AMA_SOUTH 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21L | Transfer | FLT_31_P1_AMA_SOUTH | Apply 3-phase fault on AMA_SOUTH to SWISHER 230kV line CKT 1, near AMA_SOUTH 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21S | Transfer | FLT_31_P1_AMA_SOUTH | Apply 3-phase fault on AMA_SOUTH to SWISHER 230kV line CKT 1, near AMA_SOUTH 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 28S | Transfer | FLT_31_P1_AMA_SOUTH | Apply 3-phase fault on AMA_SOUTH to SWISHER 230kV line CKT 1, near AMA_SOUTH 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 19W | Transfer | FLT_32_P1_NE_HEREFORD3 | Apply 3-phase fault on NE_HEREFORD3 to DEAFSMITH 115kV line CKT 1, near NE_HEREFORD3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21L | Transfer | FLT_32_P1_NE_HEREFORD3 | Apply 3-phase fault on NE_HEREFORD3 to DEAFSMITH 115kV line CKT 1, near NE_HEREFORD3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21S | Transfer | FLT_32_P1_NE_HEREFORD3 | Apply 3-phase fault on NE_HEREFORD3 to DEAFSMITH 115kV line CKT 1, near NE_HEREFORD3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 28S | Transfer | FLT_32_P1_NE_HEREFORD3 | Apply 3-phase fault on NE_HEREFORD3 to DEAFSMITH 115kV line CKT 1, near NE_HEREFORD3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 19W | Transfer | FLT_33_P1_NE_HEREFORD3 | Apply 3-phase fault on NE_HEREFORD3 to HEREFORD 115kV line CKT 1, near NE_HEREFORD3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21L | Transfer | FLT_33_P1_NE_HEREFORD3 | Apply 3-phase fault on NE_HEREFORD3 to HEREFORD 115kV line CKT 1, near NE_HEREFORD3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21S | Transfer | FLT_33_P1_NE_HEREFORD3 | Apply 3-phase fault on NE_HEREFORD3 to HEREFORD 115kV line CKT 1, near NE_HEREFORD3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 28S | Transfer | FLT_33_P1_NE_HEREFORD3 | Apply 3-phase fault on NE_HEREFORD3 to HEREFORD 115kV line CKT 1, near NE_HEREFORD3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 19W | Transfer | FLT_34_P1_HEREFORD | Apply 3-phase fault on HEREFORD to DS-#6 115kV line CKT 1, near HEREFORD 115kV for 7 cycles. Open the faulted line and DS-#20 to CURRY 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and DS-#20 to CURRY 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open DS-#20 to CURRY 115kV line CKT 1 and clear the fault. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21L | Transfer | FLT_34_P1_HEREFORD | Apply 3-phase fault on HEREFORD to DS-#6 115kV line CKT 1, near HEREFORD 115kV for 7 cycles. Open the faulted line and DS-#20 to CURRY 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and DS-#20 to CURRY 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open DS-#20 to CURRY 115kV line CKT 1 and clear the fault. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21S | Transfer | FLT_34_P1_HEREFORD | Apply 3-phase fault on HEREFORD to DS-#6 115kV line CKT 1, near HEREFORD 115kV for 7 cycles. Open the faulted line and DS-#20 to CURRY 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and DS-#20 to CURRY 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open DS-#20 to CURRY 115kV line CKT 1 and clear the fault. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 28S | Transfer | FLT_34_P1_HEREFORD | Apply 3-phase fault on HEREFORD to DS-#6 115kV line CKT 1, near HEREFORD 115kV for 7 cycles. Open the faulted line and DS-#20 to CURRY 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and DS-#20 to CURRY 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open DS-#20 to CURRY 115kV line CKT 1 and clear the fault. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 02 - Hitchland | 19W | Transfer | FLT_35_P1_HEREFORD | Apply 3-phase fault on HEREFORD to DEAFSMITH 115kV line CKT 1, near HEREFORD 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21L | Transfer | FLT_35_P1_HEREFORD | Apply 3-phase fault on HEREFORD to DEAFSMITH 115kV line CKT 1, near HEREFORD 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21S | Transfer | FLT_35_P1_HEREFORD | Apply 3-phase fault on HEREFORD to DEAFSMITH 115kV line CKT 1, near HEREFORD 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 28S | Transfer | FLT_35_P1_HEREFORD | Apply 3-phase fault on HEREFORD to DEAFSMITH 115kV line CKT 1, near HEREFORD 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 02 - Hitchland | 19W | Transfer | FLT_36_P1_DEAFSMITH | Apply 3-phase fault on DS-#25+ to DEAFSMITH 115kV line CKT 1, near DEAFSMITH 115kV for 7 cycles. Open the faulted line and RANDALL to CANYON_E_TP3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and RANDALL to CANYON_E_TP3 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open RANDALL to CANYON_E_TP3 115kV line CKT 1 and clear the fault. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21L | Transfer | FLT_36_P1_DEAFSMITH | Apply 3-phase fault on DS-#25+ to DEAFSMITH 115kV line CKT 1, near DEAFSMITH 115kV for 7 cycles. Open the faulted line and RANDALL to CANYON_E_TP3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and RANDALL to CANYON_E_TP3 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open RANDALL to CANYON_E_TP3 115kV line CKT 1 and clear the fault. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21S | Transfer | FLT_36_P1_DEAFSMITH | Apply 3-phase fault on DS-#25+ to DEAFSMITH 115kV line CKT 1, near DEAFSMITH 115kV for 7 cycles. Open the faulted line and RANDALL to CANYON_E_TP3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and RANDALL to CANYON_E_TP3 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open RANDALL to CANYON_E_TP3 115kV line CKT 1 and clear the fault. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 28S | Transfer | FLT_36_P1_DEAFSMITH | Apply 3-phase fault on DS-#25+ to DEAFSMITH 115kV line CKT 1, near DEAFSMITH 115kV for 7 cycles. Open the faulted line and RANDALL to CANYON_E_TP3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and RANDALL to CANYON_E_TP3 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open RANDALL to CANYON_E_TP3 115kV line CKT 1 and clear the fault. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 19W | Transfer | FLT_37_P1_DEAFSMITH | Apply 3-phase fault on DS-#21 to CASTRO_CNTY3 115kV line CKT 1, near DEAFSMITH 115kV for 7 cycles. Open the faulted line and DEAFSMITH to DS-#21 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and DEAFSMITH to DS-#21 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open DEAFSMITH to DS-#21 115kV line CKT 1 and clear the fault. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21L | Transfer | FLT_37_P1_DEAFSMITH | Apply 3-phase fault on DS-#21 to CASTRO_CNTY3 115kV line CKT 1, near DEAFSMITH 115kV for 7 cycles. Open the faulted line and DEAFSMITH to DS-#21 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and DEAFSMITH to DS-#21 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open DEAFSMITH to DS-#21 115kV line CKT 1 and clear the fault. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21S | Transfer | FLT_37_P1_DEAFSMITH | Apply 3-phase fault on DS-#21 to CASTRO_CNTY3 115kV line CKT 1, near DEAFSMITH 115kV for 7 cycles. Open the faulted line and DEAFSMITH to DS-#21 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and DEAFSMITH to DS-#21 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open DEAFSMITH to DS-#21 115kV line CKT 1 and clear the fault. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 28S | Transfer | FLT_37_P1_DEAFSMITH | Apply 3-phase fault on DS-#21 to CASTRO_CNTY3 115kV line CKT 1, near DEAFSMITH 115kV for 7 cycles. Open the faulted line and DEAFSMITH to DS-#21 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and DEAFSMITH to DS-#21 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open DEAFSMITH to DS-#21 115kV line CKT 1 and clear the fault. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 19W | Transfer | FLT_38_P1_DEAFSMITH | Apply 3-phase fault on DEAFSMITH 230kV/115kV/13.19kV transformer CKT 1, near DEAFSMITH 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21L | Transfer | FLT_38_P1_DEAFSMITH | Apply 3-phase fault on DEAFSMITH 230kV/115kV/13.19kV transformer CKT 1, near DEAFSMITH 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21S | Transfer | FLT_38_P1_DEAFSMITH | Apply 3-phase fault on DEAFSMITH 230kV/115kV/13.19kV transformer CKT 1, near DEAFSMITH 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 28S | Transfer | FLT_38_P1_DEAFSMITH | Apply 3-phase fault on DEAFSMITH 230kV/115kV/13.19kV transformer CKT 1, near DEAFSMITH 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 19W | Transfer | FLT_39_P1_DEAFSMITH | Apply 3-phase fault on BUSHLAND to DEAFSMITH 230kV line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 21L | Transfer | FLT_39_P1_DEAFSMITH | Apply 3-phase fault on BUSHLAND to DEAFSMITH 230kV line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_39_P1_DEAFSMITH | Apply 3-phase fault on BUSHLAND to DEAFSMITH 230kV line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 28S | Transfer | FLT_39_P1_DEAFSMITH | Apply 3-phase fault on BUSHLAND to DEAFSMITH 230kV line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed. Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 02 - Hitchland | 19W | Transfer | FLT_40_P1_DEAFSMITH | Apply 3-phase fault on DEAFSMITH to PLANT_X 230kV line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 02 - Hitchland | 21L | Transfer | FLT_40_P1_DEAFSMITH | Apply 3-phase fault on DEAFSMITH to PLANT_X 230kV line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_40_P1_DEAFSMITH | Apply 3-phase fault on DEAFSMITH to PLANT_X 230kV line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 02 - Hitchland | 28S | Transfer | FLT_40_P1_DEAFSMITH | Apply 3-phase fault on DEAFSMITH to PLANT_X 230kV line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1] G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed. Voltage Spike: 1.20pu, MaxDur: 0.05s
South | 02 - Hitchland | 19W | Transfer | FLT_41_P1_CASTRO_CNTY3 | Apply 3-phase fault on CASTRO_CNTY3 to NEWHART 115kV line CKT 1, near CASTRO_CNTY3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_41_P1_CASTRO_CNTY3 | Apply 3-phase fault on CASTRO_CNTY3 to NEWHART 115kV line CKT 1, near CASTRO_CNTY3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_41_P1_CASTRO_CNTY3 | Apply 3-phase fault on CASTRO_CNTY3 to NEWHART 115kV line CKT 1, near CASTRO_CNTY3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_41_P1_CASTRO_CNTY3 | Apply 3-phase fault on CASTRO_CNTY3 to NEWHART 115kV line CKT 1, near CASTRO_CNTY3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_42_P1_CASTRO_CNTY3 | Apply 3-phase fault on CASTRO_CNTY3 to BETHEL_COL13 115kV line CKT 1, near CASTRO_CNTY3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - G14-040-GEN1[1] G14-040-GEN2[1]. G14040GEN1[1] G14040GEN2[1] tripped on over frequency. These generators use GEWTE2 model with imbedded frequency protection and thus protection was not disabled. These trippings were observed in BC and TC
South | 02 - Hitchland | 21L | Transfer | FLT_42_P1_CASTRO_CNTY3 | Apply 3-phase fault on CASTRO_CNTY3 to BETHEL_COL13 115kV line CKT 1, near CASTRO_CNTY3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_42_P1_CASTRO_CNTY3 | Apply 3-phase fault on CASTRO_CNTY3 to BETHEL_COL13 115kV line CKT 1, near CASTRO_CNTY3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - G14-040-GEN1[1] G14-040-GEN2[1]. G14040GEN1[1] G14040GEN2[1] tripped on over frequency. These generators use GEWTE2 model with imbedded frequency protection and thus protection was not disabled. These trippings were observed in BC and TC
South | 02 - Hitchland | 28S | Transfer | FLT_42_P1_CASTRO_CNTY3 | Apply 3-phase fault on CASTRO_CNTY3 to BETHEL_COL13 115kV line CKT 1, near CASTRO_CNTY3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - G14-040-GEN1[1] G14-040-GEN2[1]. G14040GEN1[1] G14040GEN2[1] tripped on over frequency. These generators use GEWTE2 model with imbedded frequency protection and thus protection was not disabled. These trippings were observed in BC and TC
South | 02 - Hitchland | 19W | Transfer | FLT_43_P1_PLSNT_HILL3 | Apply 3-phase fault on PLSNT_HILL 6 230kV/115kV/13.19kV transformer CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_43_P1_PLSNT_HILL3 | Apply 3-phase fault on PLSNT_HILL 6 230kV/115kV/13.19kV transformer CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_43_P1_PLSNT_HILL3 | Apply 3-phase fault on PLSNT_HILL 6 230kV/115kV/13.19kV transformer CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_43_P1_PLSNT_HILL3 | Apply 3-phase fault on PLSNT_HILL 6 230kV/115kV/13.19kV transformer CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_44_P1_CURRY | Apply 3-phase fault on NORRIS_TP to CURRY 115kV line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_44_P1_CURRY | Apply 3-phase fault on NORRIS_TP to CURRY 115kV line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_44_P1_CURRY | Apply 3-phase fault on NORRIS_TP to CURRY 115kV line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_44_P1_CURRY | Apply 3-phase fault on NORRIS_TP to CURRY 115kV line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_45_P1_CURRY | Apply 3-phase fault on CURRY to ROOSEVELT 115kV line CKT 2, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_45_P1_CURRY | Apply 3-phase fault on CURRY to ROOSEVELT 115kV line CKT 2, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_45_P1_CURRY | Apply 3-phase fault on CURRY to ROOSEVELT 115kV line CKT 2, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_45_P1_CURRY | Apply 3-phase fault on CURRY to ROOSEVELT 115kV line CKT 2, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_46_P1_CURRY | Apply 3-phase fault on CURRY to BAILEYCO 115kV line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_46_P1_CURRY | Apply 3-phase fault on CURRY to BAILEYCO 115kV line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_46_P1_CURRY | Apply 3-phase fault on CURRY to BAILEYCO 115kV line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_46_P1_CURRY | Apply 3-phase fault on CURRY to BAILEYCO 115kV line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_47_P1_CURRY | Apply 3-phase fault on E_CLOVIS to CURRY 115kV line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_47_P1_CURRY | Apply 3-phase fault on E_CLOVIS to CURRY 115kV line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_47_P1_CURRY | Apply 3-phase fault on E_CLOVIS to CURRY 115kV line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_47_P1_CURRY | Apply 3-phase fault on E_CLOVIS to CURRY 115kV line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_48_P1_ROOSEVELT | Apply 3-phase fault on ROSEVELT_N 6 230kV/115kV/13.19kV transformer CKT 1, near ROOSEVELT 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_48_P1_ROOSEVELT | Apply 3-phase fault on ROSEVELT_N 6 230kV/115kV/13.19kV transformer CKT 1, near ROOSEVELT 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_48_P1_ROOSEVELT | Apply 3-phase fault on ROSEVELT_N 6 230kV/115kV/13.19kV transformer CKT 1, near ROOSEVELT 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_48_P1_ROOSEVELT | Apply 3-phase fault on ROSEVELT_N 6 230kV/115kV/13.19kV transformer CKT 1, near ROOSEVELT 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_49_P1_ROSEVELT_N6 | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_WEST 230kV line CKT 2, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_49_P1_ROSEVELT_N6 | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_WEST 230kV line CKT 2, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_49_P1_ROSEVELT_N6 | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_WEST 230kV line CKT 2, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 02 - Hitchland | 28S | Transfer | FLT_49_P1_ROSEVELT_N6 | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_WEST 230kV line CKT 2, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_50_P1_ROSEVELT_N6 | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_EAST 230kV line CKT 1, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_50_P1_ROSEVELT_N6 | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_EAST 230kV line CKT 1, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_50_P1_ROSEVELT_N6 | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_EAST 230kV line CKT 1, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 02 - Hitchland | 28S | Transfer | FLT_50_P1_ROSEVELT_N6 | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_EAST 230kV line CKT 1, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_51_P1_PLANT_X | Apply 3-phase fault on PLANT_X to TOLK_WEST 230kV line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_51_P1_PLANT_X | Apply 3-phase fault on PLANT_X to TOLK_WEST 230kV line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.04s
South | 02 - Hitchland | 21S | Transfer | FLT_51_P1_PLANT_X | Apply 3-phase fault on PLANT_X to TOLK_WEST 230kV line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.04s
South | 02 - Hitchland | 28S | Transfer | FLT_51_P1_PLANT_X | Apply 3-phase fault on PLANT_X to TOLK_WEST 230kV line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed. Voltage Spike: 1.20pu, MaxDur: 0.04s
South | 02 - Hitchland | 19W | Transfer | FLT_52_P1_PLANT_X | Apply 3-phase fault on PLANT_X to TOLK_EAST 230kV line CKT 2, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_52_P1_PLANT_X | Apply 3-phase fault on PLANT_X to TOLK_EAST 230kV line CKT 2, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.04s
South | 02 - Hitchland | 21S | Transfer | FLT_52_P1_PLANT_X | Apply 3-phase fault on PLANT_X to TOLK_EAST 230kV line CKT 2, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.04s
South | 02 - Hitchland | 28S | Transfer | FLT_52_P1_PLANT_X | Apply 3-phase fault on PLANT_X to TOLK_EAST 230kV line CKT 2, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed. Voltage Spike: 1.20pu, MaxDur: 0.04s
South | 02 - Hitchland | 19W | Transfer | FLT_53_P1_PLANT_X | Apply 3-phase fault on PLANT_X to SUNDOWN 230kV line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 21L | Transfer | FLT_53_P1_PLANT_X | Apply 3-phase fault on PLANT_X to SUNDOWN 230kV line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.04s
South | 02 - Hitchland | 21S | Transfer | FLT_53_P1_PLANT_X | Apply 3-phase fault on PLANT_X to SUNDOWN 230kV line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.04s
South | 02 - Hitchland | 28S | Transfer | FLT_53_P1_PLANT_X | Apply 3-phase fault on PLANT_X to SUNDOWN 230kV line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed. Voltage Spike: 1.20pu, MaxDur: 0.04s
South | 02 - Hitchland | 19W | Transfer | FLT_54_P1_PLANT_X | Apply 3-phase fault on NEWHART to PLANT_X 230kV line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 21L | Transfer | FLT_54_P1_PLANT_X | Apply 3-phase fault on NEWHART to PLANT_X 230kV line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.04s
South | 02 - Hitchland | 21S | Transfer | FLT_54_P1_PLANT_X | Apply 3-phase fault on NEWHART to PLANT_X 230kV line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.04s
South | 02 - Hitchland | 28S | Transfer | FLT_54_P1_PLANT_X | Apply 3-phase fault on NEWHART to PLANT_X 230kV line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed. Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 02 - Hitchland | 19W | Transfer | FLT_55_P1_TOLK_EAST | Apply 3-phase fault on TOLK_EAST to TUCO_INT 230kV line CKT 1, near TOLK_EAST 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - G17-080-GEN1[1] G17-080-GEN2[1]. G17080GEN1[1] and G17080GEN2[1] were tripping on underfrequency. Protection was disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 02 - Hitchland | 21L | Transfer | FLT_55_P1_TOLK_EAST | Apply 3-phase fault on TOLK_EAST to TUCO_INT 230kV line CKT 1, near TOLK_EAST 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_55_P1_TOLK_EAST | Apply 3-phase fault on TOLK_EAST to TUCO_INT 230kV line CKT 1, near TOLK_EAST 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - G17-080-GEN1[1] G17-080-GEN2[1]. G17080GEN1[1] and G17080GEN2[1] were tripping on underfrequency. Protection was disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 28S | Transfer | FLT_55_P1_TOLK_EAST | Apply 3-phase fault on TOLK_EAST to TUCO_INT 230kV line CKT 1, near TOLK_EAST 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1] G17-080-GEN2[1]. G17080GEN1[1] and G17080GEN2[1] were tripping on underfrequency. Protection was disabled and simulation was rerun. No further issues were observed. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 19W | Transfer | FLT_56_P1_TOLK_TAP | Apply 3-phase fault on TOLK 345kV/230kV/13.19kV transformer CKT 1, near TOLK_TAP 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - G17-080-GEN1[1] G17-080-GEN2[1]. G17080GEN1[1] and G17080GEN2[1] were tripping on underfrequency. Protection was disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.23pu, MaxDur: 0.01s
South | 02 - Hitchland | 21L | Transfer | FLT_56_P1_TOLK_TAP | Apply 3-phase fault on TOLK 345kV/230kV/13.19kV transformer CKT 1, near TOLK_TAP 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 02 - Hitchland | 21S | Transfer | FLT_56_P1_TOLK_TAP | Apply 3-phase fault on TOLK 345kV/230kV/13.19kV transformer CKT 1, near TOLK_TAP 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - G17-080-GEN1[1] G17-080-GEN2[1]. G17080GEN1[1] and G17080GEN2[1] were tripping on underfrequency. Protection was disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.20pu, MaxDur: 0.04s
South | 02 - Hitchland | 28S | Transfer | FLT_56_P1_TOLK_TAP | Apply 3-phase fault on TOLK 345kV/230kV/13.19kV transformer CKT 1, near TOLK_TAP 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1] G17-080-GEN2[1]. G17080GEN1[1] and G17080GEN2[1] were tripping on underfrequency. Protection was disabled and simulation was rerun. No further issues were observed. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed. Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 02 - Hitchland | 19W | Transfer | FLT_57_P1_E-LIBER3 | Apply 3-phase fault on CMRIVTP3 to E-LIBER3 115kV line CKT 1, near E-LIBER3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_57_P1_E-LIBER3 | Apply 3-phase fault on CMRIVTP3 to E-LIBER3 115kV line CKT 1, near E-LIBER3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_57_P1_E-LIBER3 | Apply 3-phase fault on CMRIVTP3 to E-LIBER3 115kV line CKT 1, near E-LIBER3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_57_P1_E-LIBER3 | Apply 3-phase fault on CMRIVTP3 to E-LIBER3 115kV line CKT 1, near E-LIBER3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_58_P1_E-LIBER3 | Apply 3-phase fault on E-LIBER3 to NATBEEF3 115kV line CKT 1, near E-LIBER3 115kV for 7 cycles. Open the faulted line and NLIB 3 to NATBEEF3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NLIB 3 to NATBEEF3 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open NLIB 3 to NATBEEF3 115kV line CKT 1 and clear the fault. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_58_P1_E-LIBER3 | Apply 3-phase fault on E-LIBER3 to NATBEEF3 115kV line CKT 1, near E-LIBER3 115kV for 7 cycles. Open the faulted line and NLIB 3 to NATBEEF3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NLIB 3 to NATBEEF3 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open NLIB 3 to NATBEEF3 115kV line CKT 1 and clear the fault. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_58_P1_E-LIBER3 | Apply 3-phase fault on E-LIBER3 to NATBEEF3 115kV line CKT 1, near E-LIBER3 115kV for 7 cycles. Open the faulted line and NLIB 3 to NATBEEF3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NLIB 3 to NATBEEF3 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open NLIB 3 to NATBEEF3 115kV line CKT 1 and clear the fault. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_58_P1_E-LIBER3 | Apply 3-phase fault on E-LIBER3 to NATBEEF3 115kV line CKT 1, near E-LIBER3 115kV for 7 cycles. Open the faulted line and NLIB 3 to NATBEEF3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NLIB 3 to NATBEEF3 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open NLIB 3 to NATBEEF3 115kV line CKT 1 and clear the fault. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_59_P1_NLIB3 | Apply 3-phase fault on HAYNE3 to NLIB 3 115kV line CKT 1, near NLIB 3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_59_P1_NLIB3 | Apply 3-phase fault on HAYNE3 to NLIB 3 115kV line CKT 1, near NLIB 3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_59_P1_NLIB3 | Apply 3-phase fault on HAYNE3 to NLIB 3 115kV line CKT 1, near NLIB 3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_59_P1_NLIB3 | Apply 3-phase fault on HAYNE3 to NLIB 3 115kV line CKT 1, near NLIB 3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_60_P1_POTTER_CO | Apply 3-phase fault on POTTER_TR 13.19kV/230kV/345kV transformer CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed. Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 21L | Transfer | FLT_60_P1_POTTER_CO | Apply 3-phase fault on POTTER_TR 13.19kV/230kV/345kV transformer CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed. Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 02 - Hitchland | 21S | Transfer | FLT_60_P1_POTTER_CO | Apply 3-phase fault on POTTER_TR 13.19kV/230kV/345kV transformer CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 28S | Transfer | FLT_60_P1_POTTER_CO | Apply 3-phase fault on POTTER_TR 13.19kV/230kV/345kV transformer CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 19W | Transfer | FLT_61_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.23pu, MaxDur: 0.03s
South | 02 - Hitchland | 21L | Transfer | FLT_61_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_61_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_61_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - G17-065-GEN2[1]. G17065GEN2[1] was tripping on underfrequency. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 19W | Transfer | FLT_62_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_62_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_62_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_62_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_63_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_63_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_63_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_63_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_64_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV line CKT &1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line. Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21L | Transfer | FLT_64_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV line CKT &1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line. Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21S | Transfer | FLT_64_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV line CKT &1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line. Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 28S | Transfer | FLT_64_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV line CKT &1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line. Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 19W | Transfer | FLT_65_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV line CKT &1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line. Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21L | Transfer | FLT_65_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV line CKT &1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line. Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21S | Transfer | FLT_65_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV line CKT &1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line. Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 28S | Transfer | FLT_65_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV line CKT &1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line. Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 19W | Transfer | FLT_66_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21L | Transfer | FLT_66_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21S | Transfer | FLT_66_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 28S | Transfer | FLT_66_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 19W | Transfer | FLT_67_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_67_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_67_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_67_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_68_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21L | Transfer | FLT_68_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21S | Transfer | FLT_68_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 28S | Transfer | FLT_68_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 19W | Transfer | FLT_69_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed. Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 02 - Hitchland | 21L | Transfer | FLT_69_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21S | Transfer | FLT_69_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 28S | Transfer | FLT_69_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 19W | Transfer | FLT_70_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 02 - Hitchland | 21L | Transfer | FLT_70_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.04s
South | 02 - Hitchland | 21S | Transfer | FLT_70_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_70_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed. Voltage Spike: 1.21pu, MaxDur: 0.00s
South | 02 - Hitchland | 19W | Transfer | FLT_71_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.25pu, MaxDur: 0.00s
South | 02 - Hitchland | 21L | Transfer | FLT_71_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_71_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.29pu, MaxDur: 0.00s
South | 02 - Hitchland | 28S | Transfer | FLT_71_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.26pu, MaxDur: 0.00s
South | 02 - Hitchland | 19W | Transfer | FLT_72_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_72_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_72_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_72_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_73_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_73_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_73_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_73_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_74_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 21L | Transfer | FLT_74_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_74_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 28S | Transfer | FLT_74_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 19W | Transfer | FLT_75_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.25pu, MaxDur: 0.01s
South | 02 - Hitchland | 21L | Transfer | FLT_75_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_75_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.22pu, MaxDur: 0.00s
South | 02 - Hitchland | 28S | Transfer | FLT_75_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.22pu, MaxDur: 0.00s
South | 02 - Hitchland | 19W | Transfer | FLT_76_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.21pu, MaxDur: 0.00s
South | 02 - Hitchland | 21L | Transfer | FLT_76_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.28pu, MaxDur: 0.00s
South | 02 - Hitchland | 21S | Transfer | FLT_76_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 28S | Transfer | FLT_76_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 19W | Transfer | FLT_77_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 21L | Transfer | FLT_77_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_77_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 28S | Transfer | FLT_77_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 19W | Transfer | FLT_78_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 21L | Transfer | FLT_78_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_78_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 28S | Transfer | FLT_78_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 19W | Transfer | FLT_79_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_79_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_79_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_79_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.22pu, MaxDur: 0.00s
South | 02 - Hitchland | 19W | Transfer | FLT_80_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 02 - Hitchland | 21L | Transfer | FLT_80_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_80_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 28S | Transfer | FLT_80_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_81_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 21L | Transfer | FLT_81_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_81_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.21pu, MaxDur: 0.03s
South | 02 - Hitchland | 28S | Transfer | FLT_81_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 19W | Transfer | FLT_82_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_82_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_82_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_82_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_83_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 21L | Transfer | FLT_83_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_83_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 28S | Transfer | FLT_83_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 02 - Hitchland | 19W | Transfer | FLT_84_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 21L | Transfer | FLT_84_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_84_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 28S | Transfer | FLT_84_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 19W | Transfer | FLT_85_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_85_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_85_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_85_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_86_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_86_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_86_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_86_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_87_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_87_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_87_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_87_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_88_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_88_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_88_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_88_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_89_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_89_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_89_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_89_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_90_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 21L | Transfer | FLT_90_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_90_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 28S | Transfer | FLT_90_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 19W | Transfer | FLT_91_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_91_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_91_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_91_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_92_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_92_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_92_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_92_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_93_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_93_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_93_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes | Abnormal oscillations are observed in the responses of generators OECGT1, G06-044GEN1A4. These causes oscillations in other nearby generators. These oscillations are likely caused due to modelling issues. The same response is observed in BC and TC and thus deemed existing issue.
South | 02 - Hitchland | 28S | Transfer | FLT_93_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_94_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_94_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_94_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_94_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_95_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_95_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_95_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_95_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_96_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_96_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_96_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_96_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_97_P4_TEXAS_CNTY3 | Apply single-phase fault on TXPHSF to E-LIBER3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted line and TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1 and COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_97_P4_TEXAS_CNTY3 | Apply single-phase fault on TXPHSF to E-LIBER3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted line and TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1 and COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_97_P4_TEXAS_CNTY3 | Apply single-phase fault on TXPHSF to E-LIBER3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted line and TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1 and COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_97_P4_TEXAS_CNTY3 | Apply single-phase fault on TXPHSF to E-LIBER3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted line and TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1 and COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_98_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted line and COLE to TC-AGGIE 115kV line CKT 1 and Y TAP 3 to POWELL CNR 3 115kV line CKT 1 and Y TAP 3 to TEXAS_CNTY 3 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_98_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted line and COLE to TC-AGGIE 115kV line CKT 1 and Y TAP 3 to POWELL CNR 3 115kV line CKT 1 and Y TAP 3 to TEXAS_CNTY 3 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_98_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted line and COLE to TC-AGGIE 115kV line CKT 1 and Y TAP 3 to POWELL CNR 3 115kV line CKT 1 and Y TAP 3 to TEXAS_CNTY 3 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_98_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted line and COLE to TC-AGGIE 115kV line CKT 1 and Y TAP 3 to POWELL CNR 3 115kV line CKT 1 and Y TAP 3 to TEXAS_CNTY 3 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_99_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted line and TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 2 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_99_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted line and TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 2 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_99_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted line and TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 2 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_99_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted line and TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 2 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_100_P4_TEXAS_CNTY3 | Apply single-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted line and Y TAP 3 to POWELL CNR 3 115kV line CKT 1 and TXPHSF to E-LIBER3 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_100_P4_TEXAS_CNTY3 | Apply single-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted line and Y TAP 3 to POWELL CNR 3 115kV line CKT 1 and TXPHSF to E-LIBER3 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_100_P4_TEXAS_CNTY3 | Apply single-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted line and Y TAP 3 to POWELL CNR 3 115kV line CKT 1 and TXPHSF to E-LIBER3 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_100_P4_TEXAS_CNTY3 | Apply single-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted line and Y TAP 3 to POWELL CNR 3 115kV line CKT 1 and TXPHSF to E-LIBER3 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_101_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted line and TXPHSF to E-LIBER3 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_101_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted line and TXPHSF to E-LIBER3 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_101_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted line and TXPHSF to E-LIBER3 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_101_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted line and TXPHSF to E-LIBER3 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_102_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted line and HITCHLAND to FRISCO_WND 3 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_102_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted line and HITCHLAND to FRISCO_WND 3 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_102_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted line and HITCHLAND to FRISCO_WND 3 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_102_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted line and HITCHLAND to FRISCO_WND 3 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_103_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted line and Y TAP 3 to TEXAS_CNTY 3 115kV line CKT 1 and Y TAP 3 to POWELL CNR 3 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_103_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted line and Y TAP 3 to TEXAS_CNTY 3 115kV line CKT 1 and Y TAP 3 to POWELL CNR 3 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_103_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted line and Y TAP 3 to TEXAS_CNTY 3 115kV line CKT 1 and Y TAP 3 to POWELL CNR 3 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_103_P4_TEXAS_CNTY3 | Apply single-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 16 cycles with stuck breaker at TEXAS_CNTY 3. Open the faulted line and Y TAP 3 to TEXAS_CNTY 3 115kV line CKT 1 and Y TAP 3 to POWELL CNR 3 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_104_P4_HITCHLAND | Apply single-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding and HITCHLAND 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_104_P4_HITCHLAND | Apply single-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding and HITCHLAND 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_104_P4_HITCHLAND | Apply single-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding and HITCHLAND 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_104_P4_HITCHLAND | Apply single-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding and HITCHLAND 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_105_P4_HITCHLAND | Apply single-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding and HITCHLAND 345kV/230kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_105_P4_HITCHLAND | Apply single-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding and HITCHLAND 345kV/230kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_105_P4_HITCHLAND | Apply single-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding and HITCHLAND 345kV/230kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_105_P4_HITCHLAND | Apply single-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding and HITCHLAND 345kV/230kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_106_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted line and OCHILTREE 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_106_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted line and OCHILTREE 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_106_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted line and OCHILTREE 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_106_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted line and OCHILTREE 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_107_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted line and TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1 and COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. | P4 | Unstable | No | No | No | No | Yes | Yes | The studies contingency cuts the two 115kV lines at the project POI, leaving the project connected to the 69kV system. The instability seems to be a control issue. A controller tuning or upgrade could resolve the issue. | Reduce output of GEN-2017-047 to 90MW (Curtailment permitted for HV contingencies)
South | 02 - Hitchland | 21L | Transfer | FLT_107_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted line and TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1 and COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. | P4 | Unstable | No | No | No | No | Yes | Yes | The studies contingency cuts the two 115kV lines at the project POI, leaving the project connected to the 69kV system. The instability seems to be a control issue. A controller tuning or upgrade could resolve the issue. | Reduce output of GEN-2017-047 to 80MW (Curtailment permitted for HV contingencies)
South | 02 - Hitchland | 21S | Transfer | FLT_107_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted line and TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1 and COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_107_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted line and TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1 and COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. | P4 | Unstable | No | No | No | No | Yes | Yes | The studies contingency cuts the two 115kV lines at the project POI, leaving the project connected to the 69kV system. The instability seems to be a control issue. A controller tuning or upgrade could resolve the issue. | Reduce output of GEN-2017-047 to 90MW (Curtailment permitted for HV contingencies)
South | 02 - Hitchland | 19W | Transfer | FLT_108_P4_COLE | Apply single-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Three Winding and COLE to OCHILTREE 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_108_P4_COLE | Apply single-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Three Winding and COLE to OCHILTREE 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_108_P4_COLE | Apply single-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Three Winding and COLE to OCHILTREE 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_108_P4_COLE | Apply single-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Three Winding and COLE to OCHILTREE 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_109_P4_COLE | Apply single-phase fault on COLE to TC-AGGIE 115kV line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted line and TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1 and TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_109_P4_COLE | Apply single-phase fault on COLE to TC-AGGIE 115kV line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted line and TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1 and TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_109_P4_COLE | Apply single-phase fault on COLE to TC-AGGIE 115kV line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted line and TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1 and TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_109_P4_COLE | Apply single-phase fault on COLE to TC-AGGIE 115kV line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted line and TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1 and TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_110_P4_COLE | Apply single-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Three Winding and TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1 and COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_110_P4_COLE | Apply single-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Three Winding and TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1 and COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_110_P4_COLE | Apply single-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Three Winding and TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1 and COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_110_P4_COLE | Apply single-phase fault on COLE 115kV/69kV/13.19kV transformer CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted Three Winding and TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1 and COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_111_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted line and TXFARMS to OCHILTREE 115kV line CKT 1 and SPEARMAN to HANSFORD 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_111_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted line and TXFARMS to OCHILTREE 115kV line CKT 1 and SPEARMAN to HANSFORD 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_111_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted line and TXFARMS to OCHILTREE 115kV line CKT 1 and SPEARMAN to HANSFORD 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_111_P4_COLE | Apply single-phase fault on COLE to OCHILTREE 115kV line CKT 1, near COLE 115kV for 16 cycles with stuck breaker at COLE. Open the faulted line and TXFARMS to OCHILTREE 115kV line CKT 1 and SPEARMAN to HANSFORD 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_112_P4_OCHILTREE | Apply single-phase fault on TXFARMS to OCHILTREE 115kV line CKT 1, near OCHILTREE 115kV for 16 cycles with stuck breaker at OCHILTREE. Open the faulted line and SPEARMAN to HANSFORD 115kV line CKT 1 and OCHILTREE 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 21L | Transfer | FLT_112_P4_OCHILTREE | Apply single-phase fault on TXFARMS to OCHILTREE 115kV line CKT 1, near OCHILTREE 115kV for 16 cycles with stuck breaker at OCHILTREE. Open the faulted line and SPEARMAN to HANSFORD 115kV line CKT 1 and OCHILTREE 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 21S | Transfer | FLT_112_P4_OCHILTREE | Apply single-phase fault on TXFARMS to OCHILTREE 115kV line CKT 1, near OCHILTREE 115kV for 16 cycles with stuck breaker at OCHILTREE. Open the faulted line and SPEARMAN to HANSFORD 115kV line CKT 1 and OCHILTREE 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_112_P4_OCHILTREE | Apply single-phase fault on TXFARMS to OCHILTREE 115kV line CKT 1, near OCHILTREE 115kV for 16 cycles with stuck breaker at OCHILTREE. Open the faulted line and SPEARMAN to HANSFORD 115kV line CKT 1 and OCHILTREE 230kV/115kV/13.19kV transformer CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_113_P4_NE_HEREFORD3 | Apply single-phase fault on NE_HEREFORD3 115kV/69kV/13.19kV transformer CKT 1, near NE_HEREFORD3 115kV for 16 cycles with stuck breaker at NE_HEREFORD3. Open the faulted Three Winding and NE_HEREFORD3 115kV/69kV/13.19kV transformer CKT 2 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 02 - Hitchland | 21L | Transfer | FLT_113_P4_NE_HEREFORD3 | Apply single-phase fault on NE_HEREFORD3 115kV/69kV/13.19kV transformer CKT 1, near NE_HEREFORD3 115kV for 16 cycles with stuck breaker at NE_HEREFORD3. Open the faulted Three Winding and NE_HEREFORD3 115kV/69kV/13.19kV transformer CKT 2 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 21S | Transfer | FLT_113_P4_NE_HEREFORD3 | Apply single-phase fault on NE_HEREFORD3 115kV/69kV/13.19kV transformer CKT 1, near NE_HEREFORD3 115kV for 16 cycles with stuck breaker at NE_HEREFORD3. Open the faulted Three Winding and NE_HEREFORD3 115kV/69kV/13.19kV transformer CKT 2 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 02 - Hitchland | 28S | Transfer | FLT_113_P4_NE_HEREFORD3 | Apply single-phase fault on NE_HEREFORD3 115kV/69kV/13.19kV transformer CKT 1, near NE_HEREFORD3 115kV for 16 cycles with stuck breaker at NE_HEREFORD3. Open the faulted Three Winding and NE_HEREFORD3 115kV/69kV/13.19kV transformer CKT 2 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 02 - Hitchland | 19W | Transfer | FLT_114_P4_NE_HEREFORD3 | Apply single-phase fault on NE_HEREFORD3 to DEAFSMITH 115kV line CKT 1, near NE_HEREFORD3 115kV for 16 cycles with stuck breaker at NE_HEREFORD3. Open the faulted line and DEAFSMITH to DS-#21 115kV line CKT 1 and DS-#21 to CASTRO_CNTY3 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_114_P4_NE_HEREFORD3 | Apply single-phase fault on NE_HEREFORD3 to DEAFSMITH 115kV line CKT 1, near NE_HEREFORD3 115kV for 16 cycles with stuck breaker at NE_HEREFORD3. Open the faulted line and DEAFSMITH to DS-#21 115kV line CKT 1 and DS-#21 to CASTRO_CNTY3 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 21S | Transfer | FLT_114_P4_NE_HEREFORD3 | Apply single-phase fault on NE_HEREFORD3 to DEAFSMITH 115kV line CKT 1, near NE_HEREFORD3 115kV for 16 cycles with stuck breaker at NE_HEREFORD3. Open the faulted line and DEAFSMITH to DS-#21 115kV line CKT 1 and DS-#21 to CASTRO_CNTY3 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_114_P4_NE_HEREFORD3 | Apply single-phase fault on NE_HEREFORD3 to DEAFSMITH 115kV line CKT 1, near NE_HEREFORD3 115kV for 16 cycles with stuck breaker at NE_HEREFORD3. Open the faulted line and DEAFSMITH to DS-#21 115kV line CKT 1 and DS-#21 to CASTRO_CNTY3 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_115_P4_NE_HEREFORD3 | Apply single-phase fault on NE_HEREFORD3 to DEAFSMITH 115kV line CKT 1, near NE_HEREFORD3 115kV for 16 cycles with stuck breaker at NE_HEREFORD3. Open the faulted line and NE_HEREFORD3 to HEREFORD 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_115_P4_NE_HEREFORD3 | Apply single-phase fault on NE_HEREFORD3 to DEAFSMITH 115kV line CKT 1, near NE_HEREFORD3 115kV for 16 cycles with stuck breaker at NE_HEREFORD3. Open the faulted line and NE_HEREFORD3 to HEREFORD 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_115_P4_NE_HEREFORD3 | Apply single-phase fault on NE_HEREFORD3 to DEAFSMITH 115kV line CKT 1, near NE_HEREFORD3 115kV for 16 cycles with stuck breaker at NE_HEREFORD3. Open the faulted line and NE_HEREFORD3 to HEREFORD 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_115_P4_NE_HEREFORD3 | Apply single-phase fault on NE_HEREFORD3 to DEAFSMITH 115kV line CKT 1, near NE_HEREFORD3 115kV for 16 cycles with stuck breaker at NE_HEREFORD3. Open the faulted line and NE_HEREFORD3 to HEREFORD 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_116_P4_NE_HEREFORD3 | Apply single-phase fault on NE_HEREFORD3 to DEAFSMITH 115kV line CKT 1, near NE_HEREFORD3 115kV for 16 cycles with stuck breaker at NE_HEREFORD3. Open the faulted line and HEREFORD to DEAFSMITH 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_116_P4_NE_HEREFORD3 | Apply single-phase fault on NE_HEREFORD3 to DEAFSMITH 115kV line CKT 1, near NE_HEREFORD3 115kV for 16 cycles with stuck breaker at NE_HEREFORD3. Open the faulted line and HEREFORD to DEAFSMITH 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 21S | Transfer | FLT_116_P4_NE_HEREFORD3 | Apply single-phase fault on NE_HEREFORD3 to DEAFSMITH 115kV line CKT 1, near NE_HEREFORD3 115kV for 16 cycles with stuck breaker at NE_HEREFORD3. Open the faulted line and HEREFORD to DEAFSMITH 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_116_P4_NE_HEREFORD3 | Apply single-phase fault on NE_HEREFORD3 to DEAFSMITH 115kV line CKT 1, near NE_HEREFORD3 115kV for 16 cycles with stuck breaker at NE_HEREFORD3. Open the faulted line and HEREFORD to DEAFSMITH 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_117_P4_NE_HEREFORD3 | Apply single-phase fault on NE_HEREFORD3 to DEAFSMITH 115kV line CKT 1, near NE_HEREFORD3 115kV for 16 cycles with stuck breaker at NE_HEREFORD3. Open the faulted line and DS-#25+ to DEAFSMITH 115kV line CKT 1 and RANDALL to CANYON_E_TP3 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_117_P4_NE_HEREFORD3 | Apply single-phase fault on NE_HEREFORD3 to DEAFSMITH 115kV line CKT 1, near NE_HEREFORD3 115kV for 16 cycles with stuck breaker at NE_HEREFORD3. Open the faulted line and DS-#25+ to DEAFSMITH 115kV line CKT 1 and RANDALL to CANYON_E_TP3 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_117_P4_NE_HEREFORD3 | Apply single-phase fault on NE_HEREFORD3 to DEAFSMITH 115kV line CKT 1, near NE_HEREFORD3 115kV for 16 cycles with stuck breaker at NE_HEREFORD3. Open the faulted line and DS-#25+ to DEAFSMITH 115kV line CKT 1 and RANDALL to CANYON_E_TP3 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_117_P4_NE_HEREFORD3 | Apply single-phase fault on NE_HEREFORD3 to DEAFSMITH 115kV line CKT 1, near NE_HEREFORD3 115kV for 16 cycles with stuck breaker at NE_HEREFORD3. Open the faulted line and DS-#25+ to DEAFSMITH 115kV line CKT 1 and RANDALL to CANYON_E_TP3 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 19W | Transfer | FLT_118_P4_HEREFORD | Apply single-phase fault on HEREFORD to DEAFSMITH 115kV line CKT 1, near HEREFORD 115kV for 16 cycles with stuck breaker at HEREFORD. Open the faulted line and HEREFORD to DEAFSMITH 115kV line CKT 2 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 02 - Hitchland | 21L | Transfer | FLT_118_P4_HEREFORD | Apply single-phase fault on HEREFORD to DEAFSMITH 115kV line CKT 1, near HEREFORD 115kV for 16 cycles with stuck breaker at HEREFORD. Open the faulted line and HEREFORD to DEAFSMITH 115kV line CKT 2 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 21S | Transfer | FLT_118_P4_HEREFORD | Apply single-phase fault on HEREFORD to DEAFSMITH 115kV line CKT 1, near HEREFORD 115kV for 16 cycles with stuck breaker at HEREFORD. Open the faulted line and HEREFORD to DEAFSMITH 115kV line CKT 2 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 02 - Hitchland | 28S | Transfer | FLT_118_P4_HEREFORD | Apply single-phase fault on HEREFORD to DEAFSMITH 115kV line CKT 1, near HEREFORD 115kV for 16 cycles with stuck breaker at HEREFORD. Open the faulted line and HEREFORD to DEAFSMITH 115kV line CKT 2 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 02 - Hitchland | 19W | Transfer | FLT_119_P4_HEREFORD | Apply single-phase fault on HEREFORD to DEAFSMITH 115kV line CKT 2, near HEREFORD 115kV for 16 cycles with stuck breaker at HEREFORD. Open the faulted line and HEREFORD to DS-#6 115kV line CKT 1 and DS-#20 to CURRY 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 02 - Hitchland | 21L | Transfer | FLT_119_P4_HEREFORD | Apply single-phase fault on HEREFORD to DEAFSMITH 115kV line CKT 2, near HEREFORD 115kV for 16 cycles with stuck breaker at HEREFORD. Open the faulted line and HEREFORD to DS-#6 115kV line CKT 1 and DS-#20 to CURRY 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_119_P4_HEREFORD | Apply single-phase fault on HEREFORD to DEAFSMITH 115kV line CKT 2, near HEREFORD 115kV for 16 cycles with stuck breaker at HEREFORD. Open the faulted line and HEREFORD to DS-#6 115kV line CKT 1 and DS-#20 to CURRY 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 02 - Hitchland | 28S | Transfer | FLT_119_P4_HEREFORD | Apply single-phase fault on HEREFORD to DEAFSMITH 115kV line CKT 2, near HEREFORD 115kV for 16 cycles with stuck breaker at HEREFORD. Open the faulted line and HEREFORD to DS-#6 115kV line CKT 1 and DS-#20 to CURRY 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 02 - Hitchland | 19W | Transfer | FLT_120_P4_DEAFSMITH | Apply single-phase fault on DS-#25+ to DEAFSMITH 115kV line CKT 1, near DEAFSMITH 115kV for 16 cycles with stuck breaker at DEAFSMITH. Open the faulted line and DEAFSMITH to DS-#21 115kV line CKT 1 and DS-#21 to CASTRO_CNTY3 115kV line CKT 1 and RANDALL to CANYON_E_TP3 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 21L | Transfer | FLT_120_P4_DEAFSMITH | Apply single-phase fault on DS-#25+ to DEAFSMITH 115kV line CKT 1, near DEAFSMITH 115kV for 16 cycles with stuck breaker at DEAFSMITH. Open the faulted line and DEAFSMITH to DS-#21 115kV line CKT 1 and DS-#21 to CASTRO_CNTY3 115kV line CKT 1 and RANDALL to CANYON_E_TP3 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 21S | Transfer | FLT_120_P4_DEAFSMITH | Apply single-phase fault on DS-#25+ to DEAFSMITH 115kV line CKT 1, near DEAFSMITH 115kV for 16 cycles with stuck breaker at DEAFSMITH. Open the faulted line and DEAFSMITH to DS-#21 115kV line CKT 1 and DS-#21 to CASTRO_CNTY3 115kV line CKT 1 and RANDALL to CANYON_E_TP3 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 28S | Transfer | FLT_120_P4_DEAFSMITH | Apply single-phase fault on DS-#25+ to DEAFSMITH 115kV line CKT 1, near DEAFSMITH 115kV for 16 cycles with stuck breaker at DEAFSMITH. Open the faulted line and DEAFSMITH to DS-#21 115kV line CKT 1 and DS-#21 to CASTRO_CNTY3 115kV line CKT 1 and RANDALL to CANYON_E_TP3 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 02 - Hitchland | 19W | Transfer | FLT_121_P4_DEAFSMITH | Apply single-phase fault on DEAFSMITH 230kV/115kV/13.19kV transformer CKT 1, near DEAFSMITH 115kV for 16 cycles with stuck breaker at DEAFSMITH. Open the faulted Three Winding and DEAFSMITH 230kV/115kV/13.8kV transformer CKT 2 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_121_P4_DEAFSMITH | Apply single-phase fault on DEAFSMITH 230kV/115kV/13.19kV transformer CKT 1, near DEAFSMITH 115kV for 16 cycles with stuck breaker at DEAFSMITH. Open the faulted Three Winding and DEAFSMITH 230kV/115kV/13.8kV transformer CKT 2 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_121_P4_DEAFSMITH | Apply single-phase fault on DEAFSMITH 230kV/115kV/13.19kV transformer CKT 1, near DEAFSMITH 115kV for 16 cycles with stuck breaker at DEAFSMITH. Open the faulted Three Winding and DEAFSMITH 230kV/115kV/13.8kV transformer CKT 2 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_121_P4_DEAFSMITH | Apply single-phase fault on DEAFSMITH 230kV/115kV/13.19kV transformer CKT 1, near DEAFSMITH 115kV for 16 cycles with stuck breaker at DEAFSMITH. Open the faulted Three Winding and DEAFSMITH 230kV/115kV/13.8kV transformer CKT 2 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_122_P4_HITCHLAND | Apply single-phase fault on HITCHLD_TR01 13.19kV/230kV/345kV transformer CKT 1, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding and HITCHLD_TR21 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_122_P4_HITCHLAND | Apply single-phase fault on HITCHLD_TR01 13.19kV/230kV/345kV transformer CKT 1, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding and HITCHLD_TR21 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_122_P4_HITCHLAND | Apply single-phase fault on HITCHLD_TR01 13.19kV/230kV/345kV transformer CKT 1, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding and HITCHLD_TR21 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_122_P4_HITCHLAND | Apply single-phase fault on HITCHLD_TR01 13.19kV/230kV/345kV transformer CKT 1, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding and HITCHLD_TR21 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_123_P4_POTTER_CO | Apply single-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV line CKT 1, near POTTER_CO 230kV for 16 cycles with stuck breaker at POTTER_CO. Open the faulted line and POTTER_TR 13.19kV/230kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21L | Transfer | FLT_123_P4_POTTER_CO | Apply single-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV line CKT 1, near POTTER_CO 230kV for 16 cycles with stuck breaker at POTTER_CO. Open the faulted line and POTTER_TR 13.19kV/230kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21S | Transfer | FLT_123_P4_POTTER_CO | Apply single-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV line CKT 1, near POTTER_CO 230kV for 16 cycles with stuck breaker at POTTER_CO. Open the faulted line and POTTER_TR 13.19kV/230kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 28S | Transfer | FLT_123_P4_POTTER_CO | Apply single-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV line CKT 1, near POTTER_CO 230kV for 16 cycles with stuck breaker at POTTER_CO. Open the faulted line and POTTER_TR 13.19kV/230kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 19W | Transfer | FLT_124_P4_DEAFSMITH | Apply single-phase fault on POTTER_CO to BUSHLAND 230kV line CKT 1, near DEAFSMITH 115kV for 16 cycles with stuck breaker at DEAFSMITH. Open the faulted line and BSHLND_TR1 1 13.19kV/115kV/230kV transformer CKT 1 and BUSHLAND to DEAFSMITH 230kV line CKT 1 and DS-#25+ to DEAFSMITH 115kV line CKT 1 and RANDALL to CANYON_E_TP3 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 21L | Transfer | FLT_124_P4_DEAFSMITH | Apply single-phase fault on POTTER_CO to BUSHLAND 230kV line CKT 1, near DEAFSMITH 115kV for 16 cycles with stuck breaker at DEAFSMITH. Open the faulted line and BSHLND_TR1 1 13.19kV/115kV/230kV transformer CKT 1 and BUSHLAND to DEAFSMITH 230kV line CKT 1 and DS-#25+ to DEAFSMITH 115kV line CKT 1 and RANDALL to CANYON_E_TP3 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_124_P4_DEAFSMITH | Apply single-phase fault on POTTER_CO to BUSHLAND 230kV line CKT 1, near DEAFSMITH 115kV for 16 cycles with stuck breaker at DEAFSMITH. Open the faulted line and BSHLND_TR1 1 13.19kV/115kV/230kV transformer CKT 1 and BUSHLAND to DEAFSMITH 230kV line CKT 1 and DS-#25+ to DEAFSMITH 115kV line CKT 1 and RANDALL to CANYON_E_TP3 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_124_P4_DEAFSMITH | Apply single-phase fault on POTTER_CO to BUSHLAND 230kV line CKT 1, near DEAFSMITH 115kV for 16 cycles with stuck breaker at DEAFSMITH. Open the faulted line and BSHLND_TR1 1 13.19kV/115kV/230kV transformer CKT 1 and BUSHLAND to DEAFSMITH 230kV line CKT 1 and DS-#25+ to DEAFSMITH 115kV line CKT 1 and RANDALL to CANYON_E_TP3 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 02 - Hitchland | 19W | Transfer | FLT_125_P4_CASTRO_CNTY3 | Apply single-phase fault on DEAFSMITH to DS-#21 115kV line CKT 1, near CASTRO_CNTY3 115kV for 16 cycles with stuck breaker at CASTRO_CNTY3. Open the faulted line and DS-#21 to CASTRO_CNTY3 115kV line CKT 1 and CASTRO_CNTY3 to BC-KELLEY +3 115kV line CKT 1 and BC-KELLEY +3 to BC-EARTH 115kV line CKT 1 and BC-EARTH to PLANT_X 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 21L | Transfer | FLT_125_P4_CASTRO_CNTY3 | Apply single-phase fault on DEAFSMITH to DS-#21 115kV line CKT 1, near CASTRO_CNTY3 115kV for 16 cycles with stuck breaker at CASTRO_CNTY3. Open the faulted line and DS-#21 to CASTRO_CNTY3 115kV line CKT 1 and CASTRO_CNTY3 to BC-KELLEY +3 115kV line CKT 1 and BC-KELLEY +3 to BC-EARTH 115kV line CKT 1 and BC-EARTH to PLANT_X 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_125_P4_CASTRO_CNTY3 | Apply single-phase fault on DEAFSMITH to DS-#21 115kV line CKT 1, near CASTRO_CNTY3 115kV for 16 cycles with stuck breaker at CASTRO_CNTY3. Open the faulted line and DS-#21 to CASTRO_CNTY3 115kV line CKT 1 and CASTRO_CNTY3 to BC-KELLEY +3 115kV line CKT 1 and BC-KELLEY +3 to BC-EARTH 115kV line CKT 1 and BC-EARTH to PLANT_X 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 28S | Transfer | FLT_125_P4_CASTRO_CNTY3 | Apply single-phase fault on DEAFSMITH to DS-#21 115kV line CKT 1, near CASTRO_CNTY3 115kV for 16 cycles with stuck breaker at CASTRO_CNTY3. Open the faulted line and DS-#21 to CASTRO_CNTY3 115kV line CKT 1 and CASTRO_CNTY3 to BC-KELLEY +3 115kV line CKT 1 and BC-KELLEY +3 to BC-EARTH 115kV line CKT 1 and BC-EARTH to PLANT_X 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_126_P4_CURRY | Apply single-phase fault on CURRY to BAILEYCO 115kV line CKT 1, near CURRY 115kV for 16 cycles with stuck breaker at CURRY. Open the faulted line and DS-#20 to CURRY 115kV line CKT 1 and HEREFORD to DS-#6 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 02 - Hitchland | 21L | Transfer | FLT_126_P4_CURRY | Apply single-phase fault on CURRY to BAILEYCO 115kV line CKT 1, near CURRY 115kV for 16 cycles with stuck breaker at CURRY. Open the faulted line and DS-#20 to CURRY 115kV line CKT 1 and HEREFORD to DS-#6 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_126_P4_CURRY | Apply single-phase fault on CURRY to BAILEYCO 115kV line CKT 1, near CURRY 115kV for 16 cycles with stuck breaker at CURRY. Open the faulted line and DS-#20 to CURRY 115kV line CKT 1 and HEREFORD to DS-#6 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.21pu, MaxDur: 0.02s
South | 02 - Hitchland | 28S | Transfer | FLT_126_P4_CURRY | Apply single-phase fault on CURRY to BAILEYCO 115kV line CKT 1, near CURRY 115kV for 16 cycles with stuck breaker at CURRY. Open the faulted line and DS-#20 to CURRY 115kV line CKT 1 and HEREFORD to DS-#6 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.21pu, MaxDur: 0.02s
South | 02 - Hitchland | 19W | Transfer | FLT_127_P4_PLANT_X | Apply single-phase fault on BC-EARTH to PLANT_X 115kV line CKT 1, near PLANT_X 115kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted line and CASTRO_CNTY3 to BC-KELLEY +3 115kV line CKT 1 and MULSHVLY_TP3 to PLANT_X 115kV line CKT 1 and MULSHVLY_TP3 to BAILEYCO 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_127_P4_PLANT_X | Apply single-phase fault on BC-EARTH to PLANT_X 115kV line CKT 1, near PLANT_X 115kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted line and CASTRO_CNTY3 to BC-KELLEY +3 115kV line CKT 1 and MULSHVLY_TP3 to PLANT_X 115kV line CKT 1 and MULSHVLY_TP3 to BAILEYCO 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_127_P4_PLANT_X | Apply single-phase fault on BC-EARTH to PLANT_X 115kV line CKT 1, near PLANT_X 115kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted line and CASTRO_CNTY3 to BC-KELLEY +3 115kV line CKT 1 and MULSHVLY_TP3 to PLANT_X 115kV line CKT 1 and MULSHVLY_TP3 to BAILEYCO 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_127_P4_PLANT_X | Apply single-phase fault on BC-EARTH to PLANT_X 115kV line CKT 1, near PLANT_X 115kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted line and CASTRO_CNTY3 to BC-KELLEY +3 115kV line CKT 1 and MULSHVLY_TP3 to PLANT_X 115kV line CKT 1 and MULSHVLY_TP3 to BAILEYCO 115kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_128_P4_PLANT_X | Apply single-phase fault on NEWHART to PLANT_X 230kV line CKT 1, near PLANT_X 230kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted line and DEAFSMITH to PLANT_X 230kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_128_P4_PLANT_X | Apply single-phase fault on NEWHART to PLANT_X 230kV line CKT 1, near PLANT_X 230kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted line and DEAFSMITH to PLANT_X 230kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_128_P4_PLANT_X | Apply single-phase fault on NEWHART to PLANT_X 230kV line CKT 1, near PLANT_X 230kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted line and DEAFSMITH to PLANT_X 230kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_128_P4_PLANT_X | Apply single-phase fault on NEWHART to PLANT_X 230kV line CKT 1, near PLANT_X 230kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted line and DEAFSMITH to PLANT_X 230kV line CKT 1 and clear the fault. | P4 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_129_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 2, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_129_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 2, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 02 - Hitchland | 21S | Transfer | FLT_129_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 2, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_129_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 2, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_130_P6_TEXAS_CNTY3 | Prior Outage of TXPHSF to E-LIBER3 115kV line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Open the faulted line and COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and COLE to TC-AGGIE 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. | P6 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_130_P6_TEXAS_CNTY3 | Prior Outage of TXPHSF to E-LIBER3 115kV line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Open the faulted line and COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and COLE to TC-AGGIE 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. | P6 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 02 - Hitchland | 21S | Transfer | FLT_130_P6_TEXAS_CNTY3 | Prior Outage of TXPHSF to E-LIBER3 115kV line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Open the faulted line and COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and COLE to TC-AGGIE 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. | P6 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_130_P6_TEXAS_CNTY3 | Prior Outage of TXPHSF to E-LIBER3 115kV line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Open the faulted line and COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and COLE to TC-AGGIE 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. | P6 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_131_P6_TEXAS_CNTY3 | Prior Outage of Y TAP 3 to TEXAS_CNTY 3 115kV line CKT 1Prior Outage of Y TAP 3 to POWELL CNR 3 115kV line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Open the faulted line and COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and COLE to TC-AGGIE 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. | P6 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_131_P6_TEXAS_CNTY3 | Prior Outage of Y TAP 3 to TEXAS_CNTY 3 115kV line CKT 1Prior Outage of Y TAP 3 to POWELL CNR 3 115kV line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Open the faulted line and COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and COLE to TC-AGGIE 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. | P6 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 02 - Hitchland | 21S | Transfer | FLT_131_P6_TEXAS_CNTY3 | Prior Outage of Y TAP 3 to TEXAS_CNTY 3 115kV line CKT 1Prior Outage of Y TAP 3 to POWELL CNR 3 115kV line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Open the faulted line and COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and COLE to TC-AGGIE 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. | P6 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_131_P6_TEXAS_CNTY3 | Prior Outage of Y TAP 3 to TEXAS_CNTY 3 115kV line CKT 1Prior Outage of Y TAP 3 to POWELL CNR 3 115kV line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Open the faulted line and COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and COLE to TC-AGGIE 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. | P6 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_132_P6_TEXAS_CNTY3 | Prior Outage of Y TAP 3 to TEXAS_CNTY 3 115kV line CKT 1Prior Outage of Y TAP 3 to POWELL CNR 3 115kV line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_132_P6_TEXAS_CNTY3 | Prior Outage of Y TAP 3 to TEXAS_CNTY 3 115kV line CKT 1Prior Outage of Y TAP 3 to POWELL CNR 3 115kV line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_132_P6_TEXAS_CNTY3 | Prior Outage of Y TAP 3 to TEXAS_CNTY 3 115kV line CKT 1Prior Outage of Y TAP 3 to POWELL CNR 3 115kV line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_132_P6_TEXAS_CNTY3 | Prior Outage of Y TAP 3 to TEXAS_CNTY 3 115kV line CKT 1Prior Outage of Y TAP 3 to POWELL CNR 3 115kV line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_133_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Open the faulted line and COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and COLE to TC-AGGIE 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. | P6 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_133_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Open the faulted line and COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and COLE to TC-AGGIE 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. | P6 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 02 - Hitchland | 21S | Transfer | FLT_133_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Open the faulted line and COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and COLE to TC-AGGIE 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. | P6 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_133_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Open the faulted line and COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and COLE to TC-AGGIE 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. | P6 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_134_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_134_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 02 - Hitchland | 21S | Transfer | FLT_134_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_134_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_135_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1Apply 3-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Open the faulted line and Y TAP 3 to POWELL CNR 3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and Y TAP 3 to POWELL CNR 3 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open Y TAP 3 to POWELL CNR 3 115kV line CKT 1 and clear the fault. | P6 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_135_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1Apply 3-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Open the faulted line and Y TAP 3 to POWELL CNR 3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and Y TAP 3 to POWELL CNR 3 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open Y TAP 3 to POWELL CNR 3 115kV line CKT 1 and clear the fault. | P6 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_135_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1Apply 3-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Open the faulted line and Y TAP 3 to POWELL CNR 3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and Y TAP 3 to POWELL CNR 3 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open Y TAP 3 to POWELL CNR 3 115kV line CKT 1 and clear the fault. | P6 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_135_P6_TEXAS_CNTY3 | Prior Outage of TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1Apply 3-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Open the faulted line and Y TAP 3 to POWELL CNR 3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and Y TAP 3 to POWELL CNR 3 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open Y TAP 3 to POWELL CNR 3 115kV line CKT 1 and clear the fault. | P6 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_136_P6_HITCHLAND | Prior Outage of HITCHLAND to HANSFORD 115kV line CKT 1Apply 3-phase fault on OCHILTREE 230kV/115kV/13.19kV transformer CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_136_P6_HITCHLAND | Prior Outage of HITCHLAND to HANSFORD 115kV line CKT 1Apply 3-phase fault on OCHILTREE 230kV/115kV/13.19kV transformer CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.29pu, MaxDur: 0.01s
South | 02 - Hitchland | 21S | Transfer | FLT_136_P6_HITCHLAND | Prior Outage of HITCHLAND to HANSFORD 115kV line CKT 1Apply 3-phase fault on OCHILTREE 230kV/115kV/13.19kV transformer CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_136_P6_HITCHLAND | Prior Outage of HITCHLAND to HANSFORD 115kV line CKT 1Apply 3-phase fault on OCHILTREE 230kV/115kV/13.19kV transformer CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.23pu, MaxDur: 0.01s
South | 02 - Hitchland | 19W | Transfer | FLT_137_P6_HITCHLAND | Prior Outage of HITCHLAND 230kV/115kV/13.19kV transformer CKT 2Apply 3-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_137_P6_HITCHLAND | Prior Outage of HITCHLAND 230kV/115kV/13.19kV transformer CKT 2Apply 3-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.29pu, MaxDur: 0.01s
South | 02 - Hitchland | 21S | Transfer | FLT_137_P6_HITCHLAND | Prior Outage of HITCHLAND 230kV/115kV/13.19kV transformer CKT 2Apply 3-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_137_P6_HITCHLAND | Prior Outage of HITCHLAND 230kV/115kV/13.19kV transformer CKT 2Apply 3-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_138_P6_HITCHLAND | Prior Outage of HITCHLAND to MOORE_CNTY 6 230kV line CKT 1Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV line CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_138_P6_HITCHLAND | Prior Outage of HITCHLAND to MOORE_CNTY 6 230kV line CKT 1Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV line CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | No | No | No | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.04s
South | 02 - Hitchland | 21S | Transfer | FLT_138_P6_HITCHLAND | Prior Outage of HITCHLAND to MOORE_CNTY 6 230kV line CKT 1Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV line CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_138_P6_HITCHLAND | Prior Outage of HITCHLAND to MOORE_CNTY 6 230kV line CKT 1Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV line CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 19W | Transfer | FLT_139_P6_HITCHLAND | Prior Outage of HITCHLAND 345kV/230kV/13.19kV transformer CKT 2Apply 3-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_139_P6_HITCHLAND | Prior Outage of HITCHLAND 345kV/230kV/13.19kV transformer CKT 2Apply 3-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_139_P6_HITCHLAND | Prior Outage of HITCHLAND 345kV/230kV/13.19kV transformer CKT 2Apply 3-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | No | No | No | No | Yes | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_139_P6_HITCHLAND | Prior Outage of HITCHLAND 345kV/230kV/13.19kV transformer CKT 2Apply 3-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 19W | Transfer | FLT_140_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV line CKT 1Apply 3-phase fault on HITCHLAND to CARPENTER 345kV line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Unstable | No | No | No | No | Yes | No | LVRT VIOL - - NoVUS_WND 1[1] LANoGSU10.60[W1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1]. NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disables and the simulations were repeated, these generators went unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed. Voltage Spike: 1.27pu, MaxDur: 0.02s
South | 02 - Hitchland | 21L | Transfer | FLT_140_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV line CKT 1Apply 3-phase fault on HITCHLAND to CARPENTER 345kV line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Unstable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1] NoVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1]. NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disables and the simulations were repeated, these generators went unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed. Voltage Spike: 1.23pu, MaxDur: 0.08s
South | 02 - Hitchland | 21S | Transfer | FLT_140_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV line CKT 1Apply 3-phase fault on HITCHLAND to CARPENTER 345kV line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Unstable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1] NoVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1]. NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disables and the simulations were repeated, these generators went unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 28S | Transfer | FLT_140_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV line CKT 1Apply 3-phase fault on HITCHLAND to CARPENTER 345kV line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Unstable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1] NoVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1]. NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disables and the simulations were repeated, these generators went unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 19W | Transfer | FLT_141_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV line CKT 2Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Unstable | No | No | No | No | Yes | No | LVRT VIOL - - NoVUS_WND 1[1] LANoGSU10.60[W1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1]. NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disables and the simulations were repeated, these generators went unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed. Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 21L | Transfer | FLT_141_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV line CKT 2Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Unstable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1] NoVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1]. NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disables and the simulations were repeated, these generators went unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed. Voltage Spike: 1.23pu, MaxDur: 0.10s
South | 02 - Hitchland | 21S | Transfer | FLT_141_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV line CKT 2Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Unstable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1] NoVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1]. NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disables and the simulations were repeated, these generators went unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 28S | Transfer | FLT_141_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV line CKT 2Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Unstable | No | No | No | No | Yes | No | LVRT VIOL - - LANoGSU10.60[W1] NoVUS_WND 1[1] G06-044GEN2B[1] G06-044GEN1A[1] G06-044GEN2A[1]. NOVUS_WND 1[1] LANOGSU10.60[W1] G06044GEN2B[1] G06044GEN1A[1] G06044GEN2A[1] tripped on over frequency. When the protection relays were disables and the simulations were repeated, these generators went unstable. It is noted that, even though these are Wind generators, they are modelled using GENSAL models. It is also noted that the same behavior was observed in BC and TC for all study seasons. These units were GNETed and the simulation was repeated, no further issues were observed with these generators GNETed. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_104_P1_LAMTON | Apply 3-phase fault on LAMTON to LC-S_OLTON+3 115kV line CKT 1, near LAMTON 115kV for 7 cycles. Open the faulted line and RKYFORD_TP 3 to PLANT_X 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and RKYFORD_TP 3 to PLANT_X 115kV line CKT 1. Re-open the faulted line after 7 cycles% RKYFORD_TP 3 to PLANT_X 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_104_P1_LAMTON | Apply 3-phase fault on LAMTON to LC-S_OLTON+3 115kV line CKT 1, near LAMTON 115kV for 7 cycles. Open the faulted line and RKYFORD_TP 3 to PLANT_X 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and RKYFORD_TP 3 to PLANT_X 115kV line CKT 1. Re-open the faulted line after 7 cycles% RKYFORD_TP 3 to PLANT_X 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_105_P1_HALE_CNTY | Apply 3-phase fault on COX to HALE_CNTY 115kV line CKT 1, near HALE_CNTY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_105_P1_HALE_CNTY | Apply 3-phase fault on COX to HALE_CNTY 115kV line CKT 1, near HALE_CNTY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_105_P1_HALE_CNTY | Apply 3-phase fault on COX to HALE_CNTY 115kV line CKT 1, near HALE_CNTY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_105_P1_HALE_CNTY | Apply 3-phase fault on COX to HALE_CNTY 115kV line CKT 1, near HALE_CNTY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_106_P1_HALE_CNTY | Apply 3-phase fault on HALE_CNTY to TUCO_INT 115kV line CKT 1, near HALE_CNTY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_106_P1_HALE_CNTY | Apply 3-phase fault on HALE_CNTY to TUCO_INT 115kV line CKT 1, near HALE_CNTY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_106_P1_HALE_CNTY | Apply 3-phase fault on HALE_CNTY to TUCO_INT 115kV line CKT 1, near HALE_CNTY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_106_P1_HALE_CNTY | Apply 3-phase fault on HALE_CNTY to TUCO_INT 115kV line CKT 1, near HALE_CNTY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_107_P1_HALE_CNTY | Apply 3-phase fault on HALE_CNTY to PLANT_X 115kV line CKT 1, near HALE_CNTY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_107_P1_HALE_CNTY | Apply 3-phase fault on HALE_CNTY to PLANT_X 115kV line CKT 1, near HALE_CNTY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_107_P1_HALE_CNTY | Apply 3-phase fault on HALE_CNTY to PLANT_X 115kV line CKT 1, near HALE_CNTY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_107_P1_HALE_CNTY | Apply 3-phase fault on HALE_CNTY to PLANT_X 115kV line CKT 1, near HALE_CNTY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_108_P1_HALE_CNTY | Apply 3-phase fault on LAMTON to HALE_CNTY 115kV line CKT 1, near HALE_CNTY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_108_P1_HALE_CNTY | Apply 3-phase fault on LAMTON to HALE_CNTY 115kV line CKT 1, near HALE_CNTY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_108_P1_HALE_CNTY | Apply 3-phase fault on LAMTON to HALE_CNTY 115kV line CKT 1, near HALE_CNTY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_108_P1_HALE_CNTY | Apply 3-phase fault on LAMTON to HALE_CNTY 115kV line CKT 1, near HALE_CNTY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_109_P1_NEWHART | Apply 3-phase fault on NEWHART_TR21 13.19kV/115kV/230kV transformer CKT 2, near NEWHART 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_109_P1_NEWHART | Apply 3-phase fault on NEWHART_TR21 13.19kV/115kV/230kV transformer CKT 2, near NEWHART 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_109_P1_NEWHART | Apply 3-phase fault on NEWHART_TR21 13.19kV/115kV/230kV transformer CKT 2, near NEWHART 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_109_P1_NEWHART | Apply 3-phase fault on NEWHART_TR21 13.19kV/115kV/230kV transformer CKT 2, near NEWHART 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_11_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV line CKT 1, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_11_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV line CKT 1, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_11_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV line CKT 1, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_11_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV line CKT 1, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC and TC cases. Due to the size and location of the unit no further simulations was performed. Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_110_P1_NEWHART | Apply 3-phase fault on HART_INDUST3 to NEWHART 115kV line CKT 1, near NEWHART 115kV for 7 cycles. Open the faulted line and HART_INDUST3 to LAMTON 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and HART_INDUST3 to LAMTON 115kV line CKT 1. Re-open the faulted line after 7 cycles% HART_INDUST3 to LAMTON 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_110_P1_NEWHART | Apply 3-phase fault on HART_INDUST3 to NEWHART 115kV line CKT 1, near NEWHART 115kV for 7 cycles. Open the faulted line and HART_INDUST3 to LAMTON 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and HART_INDUST3 to LAMTON 115kV line CKT 1. Re-open the faulted line after 7 cycles% HART_INDUST3 to LAMTON 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_110_P1_NEWHART | Apply 3-phase fault on HART_INDUST3 to NEWHART 115kV line CKT 1, near NEWHART 115kV for 7 cycles. Open the faulted line and HART_INDUST3 to LAMTON 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and HART_INDUST3 to LAMTON 115kV line CKT 1. Re-open the faulted line after 7 cycles% HART_INDUST3 to LAMTON 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_110_P1_NEWHART | Apply 3-phase fault on HART_INDUST3 to NEWHART 115kV line CKT 1, near NEWHART 115kV for 7 cycles. Open the faulted line and HART_INDUST3 to LAMTON 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and HART_INDUST3 to LAMTON 115kV line CKT 1. Re-open the faulted line after 7 cycles% HART_INDUST3 to LAMTON 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_111_P1_NEWHART | Apply 3-phase fault on CASTRO_CNTY3 to NEWHART 115kV line CKT 1, near NEWHART 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_111_P1_NEWHART | Apply 3-phase fault on CASTRO_CNTY3 to NEWHART 115kV line CKT 1, near NEWHART 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_111_P1_NEWHART | Apply 3-phase fault on CASTRO_CNTY3 to NEWHART 115kV line CKT 1, near NEWHART 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_111_P1_NEWHART | Apply 3-phase fault on CASTRO_CNTY3 to NEWHART 115kV line CKT 1, near NEWHART 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_112_P1_NEWHART | Apply 3-phase fault on KRESS_INT to NEWHART 115kV line CKT 1, near NEWHART 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_112_P1_NEWHART | Apply 3-phase fault on KRESS_INT to NEWHART 115kV line CKT 1, near NEWHART 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_112_P1_NEWHART | Apply 3-phase fault on KRESS_INT to NEWHART 115kV line CKT 1, near NEWHART 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_112_P1_NEWHART | Apply 3-phase fault on KRESS_INT to NEWHART 115kV line CKT 1, near NEWHART 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_113_P1_NEWHART | Apply 3-phase fault on SWISHER to NEWHART 230kV line CKT 1, near NEWHART 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_113_P1_NEWHART | Apply 3-phase fault on SWISHER to NEWHART 230kV line CKT 1, near NEWHART 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_113_P1_NEWHART | Apply 3-phase fault on SWISHER to NEWHART 230kV line CKT 1, near NEWHART 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_113_P1_NEWHART | Apply 3-phase fault on SWISHER to NEWHART 230kV line CKT 1, near NEWHART 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_114_P1_NEWHART | Apply 3-phase fault on NEWPOT_SS to NEWHART 230kV line CKT 1, near NEWHART 230kV for 7 cycles. Open the faulted line and POTTER_CO to NEWPOT_SS 230kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and POTTER_CO to NEWPOT_SS 230kV line CKT 1. Re-open the faulted line after 7 cycles% POTTER_CO to NEWPOT_SS 230kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_114_P1_NEWHART | Apply 3-phase fault on NEWPOT_SS to NEWHART 230kV line CKT 1, near NEWHART 230kV for 7 cycles. Open the faulted line and POTTER_CO to NEWPOT_SS 230kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and POTTER_CO to NEWPOT_SS 230kV line CKT 1. Re-open the faulted line after 7 cycles% POTTER_CO to NEWPOT_SS 230kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_114_P1_NEWHART | Apply 3-phase fault on NEWPOT_SS to NEWHART 230kV line CKT 1, near NEWHART 230kV for 7 cycles. Open the faulted line and POTTER_CO to NEWPOT_SS 230kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and POTTER_CO to NEWPOT_SS 230kV line CKT 1. Re-open the faulted line after 7 cycles% POTTER_CO to NEWPOT_SS 230kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_114_P1_NEWHART | Apply 3-phase fault on NEWPOT_SS to NEWHART 230kV line CKT 1, near NEWHART 230kV for 7 cycles. Open the faulted line and POTTER_CO to NEWPOT_SS 230kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and POTTER_CO to NEWPOT_SS 230kV line CKT 1. Re-open the faulted line after 7 cycles% POTTER_CO to NEWPOT_SS 230kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_115_P1_NEWHART | Apply 3-phase fault on NEWHART to PLANT_X 230kV line CKT 1, near NEWHART 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_115_P1_NEWHART | Apply 3-phase fault on NEWHART to PLANT_X 230kV line CKT 1, near NEWHART 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_115_P1_NEWHART | Apply 3-phase fault on NEWHART to PLANT_X 230kV line CKT 1, near NEWHART 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_115_P1_NEWHART | Apply 3-phase fault on NEWHART to PLANT_X 230kV line CKT 1, near NEWHART 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_116_P1_PLANT_X | Apply 3-phase fault on MULSHVLY_TP3 to PLANT_X 115kV line CKT 1, near PLANT_X 115kV for 7 cycles. Open the faulted line and MULSHVLY_TP3 to BAILEYCO 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and MULSHVLY_TP3 to BAILEYCO 115kV line CKT 1. Re-open the faulted line after 7 cycles% MULSHVLY_TP3 to BAILEYCO 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_116_P1_PLANT_X | Apply 3-phase fault on MULSHVLY_TP3 to PLANT_X 115kV line CKT 1, near PLANT_X 115kV for 7 cycles. Open the faulted line and MULSHVLY_TP3 to BAILEYCO 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and MULSHVLY_TP3 to BAILEYCO 115kV line CKT 1. Re-open the faulted line after 7 cycles% MULSHVLY_TP3 to BAILEYCO 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_116_P1_PLANT_X | Apply 3-phase fault on MULSHVLY_TP3 to PLANT_X 115kV line CKT 1, near PLANT_X 115kV for 7 cycles. Open the faulted line and MULSHVLY_TP3 to BAILEYCO 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and MULSHVLY_TP3 to BAILEYCO 115kV line CKT 1. Re-open the faulted line after 7 cycles% MULSHVLY_TP3 to BAILEYCO 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_116_P1_PLANT_X | Apply 3-phase fault on MULSHVLY_TP3 to PLANT_X 115kV line CKT 1, near PLANT_X 115kV for 7 cycles. Open the faulted line and MULSHVLY_TP3 to BAILEYCO 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and MULSHVLY_TP3 to BAILEYCO 115kV line CKT 1. Re-open the faulted line after 7 cycles% MULSHVLY_TP3 to BAILEYCO 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_117_P1_PLANT_X | Apply 3-phase fault on BC-EARTH to PLANT_X 115kV line CKT 1, near PLANT_X 115kV for 7 cycles. Open the faulted line and CASTRO_CNTY3 to BC-KELLEY +3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and CASTRO_CNTY3 to BC-KELLEY +3 115kV line CKT 1. Re-open the faulted line after 7 cycles% CASTRO_CNTY3 to BC-KELLEY +3 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_117_P1_PLANT_X | Apply 3-phase fault on BC-EARTH to PLANT_X 115kV line CKT 1, near PLANT_X 115kV for 7 cycles. Open the faulted line and CASTRO_CNTY3 to BC-KELLEY +3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and CASTRO_CNTY3 to BC-KELLEY +3 115kV line CKT 1. Re-open the faulted line after 7 cycles% CASTRO_CNTY3 to BC-KELLEY +3 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_117_P1_PLANT_X | Apply 3-phase fault on BC-EARTH to PLANT_X 115kV line CKT 1, near PLANT_X 115kV for 7 cycles. Open the faulted line and CASTRO_CNTY3 to BC-KELLEY +3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and CASTRO_CNTY3 to BC-KELLEY +3 115kV line CKT 1. Re-open the faulted line after 7 cycles% CASTRO_CNTY3 to BC-KELLEY +3 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_117_P1_PLANT_X | Apply 3-phase fault on BC-EARTH to PLANT_X 115kV line CKT 1, near PLANT_X 115kV for 7 cycles. Open the faulted line and CASTRO_CNTY3 to BC-KELLEY +3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and CASTRO_CNTY3 to BC-KELLEY +3 115kV line CKT 1. Re-open the faulted line after 7 cycles% CASTRO_CNTY3 to BC-KELLEY +3 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_118_P1_PLANT_X | Apply 3-phase fault on PLANT_X to LAMB_CNTY 115kV line CKT 1, near PLANT_X 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_118_P1_PLANT_X | Apply 3-phase fault on PLANT_X to LAMB_CNTY 115kV line CKT 1, near PLANT_X 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_118_P1_PLANT_X | Apply 3-phase fault on PLANT_X to LAMB_CNTY 115kV line CKT 1, near PLANT_X 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_119_P1_PLANT_X | Apply 3-phase fault on PLANTX_TR1 1 13.19kV/115kV/230kV transformer CKT 1, near PLANT_X 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_119_P1_PLANT_X | Apply 3-phase fault on PLANTX_TR1 1 13.19kV/115kV/230kV transformer CKT 1, near PLANT_X 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_119_P1_PLANT_X | Apply 3-phase fault on PLANTX_TR1 1 13.19kV/115kV/230kV transformer CKT 1, near PLANT_X 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_138_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on VALIANT4 to HUGO PP4 138kV line CKT 1, near HUGO PP4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Unstable | No | No | No | No | Yes | No | HUGO1 (#520947) was unstable. The simulation was rerun with reduced output for HUGO1 or recuded fault clearing time. No further issues were observed with either of the mitgation options. | Reduce the fault clearing time to 5 cycles
South | 02 - Hitchland | 19W | Transfer | FLT_1_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to BALKOW 7 345kV line CKT 1, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - BALKOWG1[1] BALKOWG2[1]. BALKOWG1[1] BALKOWG2[1] tripped on over frequency. These generators use GEWTE2 model with imbedded frequency protection and thus protection was not disabled. These trippings were observed in BC and TC for the same contingency Voltage Spike: 1.21pu, MaxDur: 0.09s
South | 02 - Hitchland | 21L | Transfer | FLT_1_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to BALKOW 7 345kV line CKT 1, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | No | No | No | LVRT VIOL - - LANoGSU10.60[W1] BALKOWG1[1] BALKOWG2[1]. BALKOWG1[1] BALKOWG2[1] tripped on over frequency. These generators use GEWTE2 model with imbedded frequency protection and thus protection was not disabled. These trippings were observed in BC and TC for the same contingency LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed. Voltage Spike: 1.21pu, MaxDur: 0.14s
South | 02 - Hitchland | 21S | Transfer | FLT_1_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to BALKOW 7 345kV line CKT 1, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1] BALKOWG1[1] BALKOWG2[1]. BALKOWG1[1] BALKOWG2[1] tripped on over frequency. These generators use GEWTE2 model with imbedded frequency protection and thus protection was not disabled. These trippings were observed in BC and TC for the same contingency LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 28S | Transfer | FLT_1_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to BALKOW 7 345kV line CKT 1, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1] BALKOWG1[1] BALKOWG2[1]. BALKOWG1[1] BALKOWG2[1] tripped on over frequency. These generators use GEWTE2 model with imbedded frequency protection and thus protection was not disabled. These trippings were observed in BC and TC for the same contingency LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 19W | Transfer | FLT_2_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to BADGER 7 345kV line CKT 1, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes | Voltage Spike: 1.21pu, MaxDur: 0.07s
South | 02 - Hitchland | 21L | Transfer | FLT_2_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to BADGER 7 345kV line CKT 1, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | No | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed. Voltage Spike: 1.21pu, MaxDur: 0.12s
South | 02 - Hitchland | 21S | Transfer | FLT_2_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to BADGER 7 345kV line CKT 1, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 28S | Transfer | FLT_2_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to BADGER 7 345kV line CKT 1, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 19W | Transfer | FLT_3_P1_POWELLCNR3 | Apply 3-phase fault on POWELL CNR 3 to TC-WHITING 3 115kV line CKT 1, near POWELL CNR 3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_3_P1_POWELLCNR3 | Apply 3-phase fault on POWELL CNR 3 to TC-WHITING 3 115kV line CKT 1, near POWELL CNR 3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No | No | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_3_P1_POWELLCNR3 | Apply 3-phase fault on POWELL CNR 3 to TC-WHITING 3 115kV line CKT 1, near POWELL CNR 3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_3_P1_POWELLCNR3 | Apply 3-phase fault on POWELL CNR 3 to TC-WHITING 3 115kV line CKT 1, near POWELL CNR 3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_4_P1_TEXAS_CNTY3 | Apply 3-phase fault on TEXAS_CNTY 3 115kV/69kV/13.19kV transformer CKT 2, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_4_P1_TEXAS_CNTY3 | Apply 3-phase fault on TEXAS_CNTY 3 115kV/69kV/13.19kV transformer CKT 2, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | No | No | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_4_P1_TEXAS_CNTY3 | Apply 3-phase fault on TEXAS_CNTY 3 115kV/69kV/13.19kV transformer CKT 2, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_4_P1_TEXAS_CNTY3 | Apply 3-phase fault on TEXAS_CNTY 3 115kV/69kV/13.19kV transformer CKT 2, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_5_P1_TEXAS_CNTY3 | Apply 3-phase fault on TXPHSF to E-LIBER3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_5_P1_TEXAS_CNTY3 | Apply 3-phase fault on TXPHSF to E-LIBER3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No | No | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_5_P1_TEXAS_CNTY3 | Apply 3-phase fault on TXPHSF to E-LIBER3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_5_P1_TEXAS_CNTY3 | Apply 3-phase fault on TXPHSF to E-LIBER3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_6_P1_TEXAS_CNTY3 | Apply 3-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Open the faulted line and Y TAP 3 to POWELL CNR 3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and Y TAP 3 to POWELL CNR 3 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open Y TAP 3 to POWELL CNR 3 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_6_P1_TEXAS_CNTY3 | Apply 3-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Open the faulted line and Y TAP 3 to POWELL CNR 3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and Y TAP 3 to POWELL CNR 3 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open Y TAP 3 to POWELL CNR 3 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_6_P1_TEXAS_CNTY3 | Apply 3-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Open the faulted line and Y TAP 3 to POWELL CNR 3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and Y TAP 3 to POWELL CNR 3 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open Y TAP 3 to POWELL CNR 3 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_6_P1_TEXAS_CNTY3 | Apply 3-phase fault on Y TAP 3 to TEXAS_CNTY 3 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Open the faulted line and Y TAP 3 to POWELL CNR 3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and Y TAP 3 to POWELL CNR 3 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open Y TAP 3 to POWELL CNR 3 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_7_P1_TEXAS_CNTY3 | Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_7_P1_TEXAS_CNTY3 | Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No | No | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_7_P1_TEXAS_CNTY3 | Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_7_P1_TEXAS_CNTY3 | Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1, near TEXAS_CNTY 3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_8_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 2, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_8_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 2, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | No | Yes | No | No | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_8_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 2, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_8_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND 230kV/115kV/13.19kV transformer CKT 2, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_9_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to HANSFORD 115kV line CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_9_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to HANSFORD 115kV line CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No | Yes | Yes | Voltage Spike: 1.32pu, MaxDur: 0.01s
South | 02 - Hitchland | 21S | Transfer | FLT_9_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to HANSFORD 115kV line CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_9_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to HANSFORD 115kV line CKT 1, near HITCHLAND 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_10_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to MOORE_CNTY 6 230kV line CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_10_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to MOORE_CNTY 6 230kV line CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | No | Yes | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 02 - Hitchland | 21S | Transfer | FLT_10_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to MOORE_CNTY 6 230kV line CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 28S | Transfer | FLT_10_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to MOORE_CNTY 6 230kV line CKT 1, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 19W | Transfer | FLT_11_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_11_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | No | No | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_11_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_11_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND 345kV/230kV/13.19kV transformer CKT 2, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 19W | Transfer | FLT_142_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_142_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 02 - Hitchland | 21S | Transfer | FLT_142_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_142_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV line CKT 1Apply 3-phase fault on TXPHSF to E-LIBER3 115kV line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_143_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_143_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 02 - Hitchland | 21S | Transfer | FLT_143_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_143_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV line CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to HITCHLAND 115kV line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_144_P6_COLE | Prior Outage of COLE 115kV/69kV/13.19kV transformer CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1, near COLE 115kV for 7 cycles. Open the faulted line and COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and COLE to TC-AGGIE 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_144_P6_COLE | Prior Outage of COLE 115kV/69kV/13.19kV transformer CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1, near COLE 115kV for 7 cycles. Open the faulted line and COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and COLE to TC-AGGIE 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | No | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 02 - Hitchland | 21S | Transfer | FLT_144_P6_COLE | Prior Outage of COLE 115kV/69kV/13.19kV transformer CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1, near COLE 115kV for 7 cycles. Open the faulted line and COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and COLE to TC-AGGIE 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_144_P6_COLE | Prior Outage of COLE 115kV/69kV/13.19kV transformer CKT 1Apply 3-phase fault on TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1, near COLE 115kV for 7 cycles. Open the faulted line and COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and COLE to TC-AGGIE 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open COLE to TC-AGGIE 115kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 02 - Hitchland | 19W | Transfer | FLT_145_P6_COLE | Prior Outage of COLE 115kV/69kV/13.19kV transformer CKT 1Apply 3-phase fault on COLE to OCHILTREE 115kV line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 02 - Hitchland | 21L | Transfer | FLT_145_P6_COLE | Prior Outage of COLE 115kV/69kV/13.19kV transformer CKT 1Apply 3-phase fault on COLE to OCHILTREE 115kV line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 02 - Hitchland | 21S | Transfer | FLT_145_P6_COLE | Prior Outage of COLE 115kV/69kV/13.19kV transformer CKT 1Apply 3-phase fault on COLE to OCHILTREE 115kV line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 02 - Hitchland | 28S | Transfer | FLT_145_P6_COLE | Prior Outage of COLE 115kV/69kV/13.19kV transformer CKT 1Apply 3-phase fault on COLE to OCHILTREE 115kV line CKT 1, near COLE 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 02 - Hitchland | 19W | Transfer | FLT_146_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV line CKT 1Apply 3-phase fault on COLE to TC-AGGIE 115kV line CKT 1, near COLE 115kV for 7 cycles. Open the faulted line and TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1 and clear the fault. | P6 | Unstable | Yes | No | Yes | Yes | No | Yes | The studies contingency cuts the two 115kV lines at the project POI, leaving the project connected to the 69kV system. The instability seems to be a control issue. A controller tuning or upgrade could resolve the issue. | Reduce output of GEN-2017-047 to 90MW
South | 02 - Hitchland | 21L | Transfer | FLT_146_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV line CKT 1Apply 3-phase fault on COLE to TC-AGGIE 115kV line CKT 1, near COLE 115kV for 7 cycles. Open the faulted line and TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1 and clear the fault. | P6 | Unstable | Yes | No | Yes | No | No | Yes | The studies contingency cuts the two 115kV lines at the project POI, leaving the project connected to the 69kV system. The instability seems to be a control issue. A controller tuning or upgrade could resolve the issue. | Reduce output of GEN-2017-047 to 80MW
South | 02 - Hitchland | 21S | Transfer | FLT_146_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV line CKT 1Apply 3-phase fault on COLE to TC-AGGIE 115kV line CKT 1, near COLE 115kV for 7 cycles. Open the faulted line and TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 02 - Hitchland | 28S | Transfer | FLT_146_P6_COLE | Prior Outage of COLE to OCHILTREE 115kV line CKT 1Apply 3-phase fault on COLE to TC-AGGIE 115kV line CKT 1, near COLE 115kV for 7 cycles. Open the faulted line and TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open TEXAS_CNTY 3 to TC-MCMURRY 3 115kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.04s
South | 02 - Hitchland | 19W | Transfer | FLT_147_P6_HEREFORD | Prior Outage of HEREFORD to DEAFSMITH 115kV line CKT 1Apply 3-phase fault on NE_HEREFORD3 to DEAFSMITH 115kV line CKT 1, near HEREFORD 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 21L | Transfer | FLT_147_P6_HEREFORD | Prior Outage of HEREFORD to DEAFSMITH 115kV line CKT 1Apply 3-phase fault on NE_HEREFORD3 to DEAFSMITH 115kV line CKT 1, near HEREFORD 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | No | No | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21S | Transfer | FLT_147_P6_HEREFORD | Prior Outage of HEREFORD to DEAFSMITH 115kV line CKT 1Apply 3-phase fault on NE_HEREFORD3 to DEAFSMITH 115kV line CKT 1, near HEREFORD 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 28S | Transfer | FLT_147_P6_HEREFORD | Prior Outage of HEREFORD to DEAFSMITH 115kV line CKT 1Apply 3-phase fault on NE_HEREFORD3 to DEAFSMITH 115kV line CKT 1, near HEREFORD 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 02 - Hitchland | 19W | Transfer | FLT_148_P6_HEREFORD | Prior Outage of HEREFORD to DEAFSMITH 115kV line CKT 1Apply 3-phase fault on HEREFORD to DEAFSMITH 115kV line CKT 2, near HEREFORD 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 02 - Hitchland | 21L | Transfer | FLT_148_P6_HEREFORD | Prior Outage of HEREFORD to DEAFSMITH 115kV line CKT 1Apply 3-phase fault on HEREFORD to DEAFSMITH 115kV line CKT 2, near HEREFORD 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | No | No | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21S | Transfer | FLT_148_P6_HEREFORD | Prior Outage of HEREFORD to DEAFSMITH 115kV line CKT 1Apply 3-phase fault on HEREFORD to DEAFSMITH 115kV line CKT 2, near HEREFORD 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 02 - Hitchland | 28S | Transfer | FLT_148_P6_HEREFORD | Prior Outage of HEREFORD to DEAFSMITH 115kV line CKT 1Apply 3-phase fault on HEREFORD to DEAFSMITH 115kV line CKT 2, near HEREFORD 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 02 - Hitchland | 19W | Transfer | FLT_149_P6_DEAFSMITH | Prior Outage of DEAFSMITH to DS-#21 115kV line CKT 1Apply 3-phase fault on NE_HEREFORD3 to HEREFORD 115kV line CKT 1, near DEAFSMITH 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21L | Transfer | FLT_149_P6_DEAFSMITH | Prior Outage of DEAFSMITH to DS-#21 115kV line CKT 1Apply 3-phase fault on NE_HEREFORD3 to HEREFORD 115kV line CKT 1, near DEAFSMITH 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | No | No | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21S | Transfer | FLT_149_P6_DEAFSMITH | Prior Outage of DEAFSMITH to DS-#21 115kV line CKT 1Apply 3-phase fault on NE_HEREFORD3 to HEREFORD 115kV line CKT 1, near DEAFSMITH 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 28S | Transfer | FLT_149_P6_DEAFSMITH | Prior Outage of DEAFSMITH to DS-#21 115kV line CKT 1Apply 3-phase fault on NE_HEREFORD3 to HEREFORD 115kV line CKT 1, near DEAFSMITH 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 19W | Transfer | FLT_150_P6_DEAFSMITH | Prior Outage of DEAFSMITH 230kV/115kV/13.19kV transformer CKT 1Apply 3-phase fault on DEAFSMITH 230kV/115kV/13.8kV transformer CKT 2, near DEAFSMITH 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21L | Transfer | FLT_150_P6_DEAFSMITH | Prior Outage of DEAFSMITH 230kV/115kV/13.19kV transformer CKT 1Apply 3-phase fault on DEAFSMITH 230kV/115kV/13.8kV transformer CKT 2, near DEAFSMITH 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | No | No | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21S | Transfer | FLT_150_P6_DEAFSMITH | Prior Outage of DEAFSMITH 230kV/115kV/13.19kV transformer CKT 1Apply 3-phase fault on DEAFSMITH 230kV/115kV/13.8kV transformer CKT 2, near DEAFSMITH 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 28S | Transfer | FLT_150_P6_DEAFSMITH | Prior Outage of DEAFSMITH 230kV/115kV/13.19kV transformer CKT 1Apply 3-phase fault on DEAFSMITH 230kV/115kV/13.8kV transformer CKT 2, near DEAFSMITH 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 19W | Transfer | FLT_151_P6_DEAFSMITH | Prior Outage of DEAFSMITH 230kV/115kV/13.19kV transformer CKT 1Apply 3-phase fault on NE_HEREFORD3 to HEREFORD 115kV line CKT 1, near DEAFSMITH 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21L | Transfer | FLT_151_P6_DEAFSMITH | Prior Outage of DEAFSMITH 230kV/115kV/13.19kV transformer CKT 1Apply 3-phase fault on NE_HEREFORD3 to HEREFORD 115kV line CKT 1, near DEAFSMITH 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | No | No | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21S | Transfer | FLT_151_P6_DEAFSMITH | Prior Outage of DEAFSMITH 230kV/115kV/13.19kV transformer CKT 1Apply 3-phase fault on NE_HEREFORD3 to HEREFORD 115kV line CKT 1, near DEAFSMITH 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 28S | Transfer | FLT_151_P6_DEAFSMITH | Prior Outage of DEAFSMITH 230kV/115kV/13.19kV transformer CKT 1Apply 3-phase fault on NE_HEREFORD3 to HEREFORD 115kV line CKT 1, near DEAFSMITH 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 19W | Transfer | FLT_152_P6_DEAFSMITH | Prior Outage of RANDALL to CANYON_E_TP3 115kV line CKT 1Prior Outage of DS-#25+ to DEAFSMITH 115kV line CKT 1Apply 3-phase fault on NE_HEREFORD3 to HEREFORD 115kV line CKT 1, near DEAFSMITH 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21L | Transfer | FLT_152_P6_DEAFSMITH | Prior Outage of RANDALL to CANYON_E_TP3 115kV line CKT 1Prior Outage of DS-#25+ to DEAFSMITH 115kV line CKT 1Apply 3-phase fault on NE_HEREFORD3 to HEREFORD 115kV line CKT 1, near DEAFSMITH 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | No | No | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 21S | Transfer | FLT_152_P6_DEAFSMITH | Prior Outage of RANDALL to CANYON_E_TP3 115kV line CKT 1Prior Outage of DS-#25+ to DEAFSMITH 115kV line CKT 1Apply 3-phase fault on NE_HEREFORD3 to HEREFORD 115kV line CKT 1, near DEAFSMITH 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 28S | Transfer | FLT_152_P6_DEAFSMITH | Prior Outage of RANDALL to CANYON_E_TP3 115kV line CKT 1Prior Outage of DS-#25+ to DEAFSMITH 115kV line CKT 1Apply 3-phase fault on NE_HEREFORD3 to HEREFORD 115kV line CKT 1, near DEAFSMITH 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed.
South | 02 - Hitchland | 19W | Transfer | FLT_153_P6_DEAFSMITH | Prior Outage of DS-#25+ to DEAFSMITH 115kV line CKT 1Prior Outage of RANDALL to CANYON_E_TP3 115kV line CKT 1Apply 3-phase fault on BUSHLAND to DEAFSMITH 230kV line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 21L | Transfer | FLT_153_P6_DEAFSMITH | Prior Outage of DS-#25+ to DEAFSMITH 115kV line CKT 1Prior Outage of RANDALL to CANYON_E_TP3 115kV line CKT 1Apply 3-phase fault on BUSHLAND to DEAFSMITH 230kV line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | No | No | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_153_P6_DEAFSMITH | Prior Outage of DS-#25+ to DEAFSMITH 115kV line CKT 1Prior Outage of RANDALL to CANYON_E_TP3 115kV line CKT 1Apply 3-phase fault on BUSHLAND to DEAFSMITH 230kV line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 02 - Hitchland | 28S | Transfer | FLT_153_P6_DEAFSMITH | Prior Outage of DS-#25+ to DEAFSMITH 115kV line CKT 1Prior Outage of RANDALL to CANYON_E_TP3 115kV line CKT 1Apply 3-phase fault on BUSHLAND to DEAFSMITH 230kV line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1] G17-058-GEN1[1]. G17058GEN1[1] is a study generator. It was tripping on a numerical underfrequency spike during fault event. Protection was disabled and simulation was rerun. No further issues were observed. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed. Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 02 - Hitchland | 19W | Transfer | FLT_154_P6_CURRY | Prior Outage of DS-#20 to CURRY 115kV line CKT 1Prior Outage of HEREFORD to DS-#6 115kV line CKT 1Apply 3-phase fault on CURRY to BAILEYCO 115kV line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 02 - Hitchland | 21L | Transfer | FLT_154_P6_CURRY | Prior Outage of DS-#20 to CURRY 115kV line CKT 1Prior Outage of HEREFORD to DS-#6 115kV line CKT 1Apply 3-phase fault on CURRY to BAILEYCO 115kV line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | No | No | Yes
South | 02 - Hitchland | 21S | Transfer | FLT_154_P6_CURRY | Prior Outage of DS-#20 to CURRY 115kV line CKT 1Prior Outage of HEREFORD to DS-#6 115kV line CKT 1Apply 3-phase fault on CURRY to BAILEYCO 115kV line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 02 - Hitchland | 28S | Transfer | FLT_154_P6_CURRY | Prior Outage of DS-#20 to CURRY 115kV line CKT 1Prior Outage of HEREFORD to DS-#6 115kV line CKT 1Apply 3-phase fault on CURRY to BAILEYCO 115kV line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_119_P1_PLANT_X | Apply 3-phase fault on PLANTX_TR1 1 13.19kV/115kV/230kV transformer CKT 1, near PLANT_X 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_12_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to BADGER 7 345kV line CKT 2, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_12_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to BADGER 7 345kV line CKT 2, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_12_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to BADGER 7 345kV line CKT 2, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_12_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to BADGER 7 345kV line CKT 2, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_120_P1_PLANT_X | Apply 3-phase fault on RKYFORD_TP 3 to PLANT_X 115kV line CKT 1, near PLANT_X 115kV for 7 cycles. Open the faulted line and LAMTON to LC-S_OLTON+3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and LAMTON to LC-S_OLTON+3 115kV line CKT 1. Re-open the faulted line after 7 cycles% LAMTON to LC-S_OLTON+3 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_120_P1_PLANT_X | Apply 3-phase fault on RKYFORD_TP 3 to PLANT_X 115kV line CKT 1, near PLANT_X 115kV for 7 cycles. Open the faulted line and LAMTON to LC-S_OLTON+3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and LAMTON to LC-S_OLTON+3 115kV line CKT 1. Re-open the faulted line after 7 cycles% LAMTON to LC-S_OLTON+3 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_121_P1_PLANT_X | Apply 3-phase fault on HALE_CNTY to PLANT_X 115kV line CKT 1, near PLANT_X 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_121_P1_PLANT_X | Apply 3-phase fault on HALE_CNTY to PLANT_X 115kV line CKT 1, near PLANT_X 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_121_P1_PLANT_X | Apply 3-phase fault on HALE_CNTY to PLANT_X 115kV line CKT 1, near PLANT_X 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_121_P1_PLANT_X | Apply 3-phase fault on HALE_CNTY to PLANT_X 115kV line CKT 1, near PLANT_X 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_122_P1_PLANT_X | Apply 3-phase fault on LC-S_OLTON+3 to PLANT_X 115kV line CKT 1, near PLANT_X 115kV for 7 cycles. Open the faulted line and LAMTON to LC-S_OLTON+3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and LAMTON to LC-S_OLTON+3 115kV line CKT 1. Re-open the faulted line after 7 cycles% LAMTON to LC-S_OLTON+3 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_122_P1_PLANT_X | Apply 3-phase fault on LC-S_OLTON+3 to PLANT_X 115kV line CKT 1, near PLANT_X 115kV for 7 cycles. Open the faulted line and LAMTON to LC-S_OLTON+3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and LAMTON to LC-S_OLTON+3 115kV line CKT 1. Re-open the faulted line after 7 cycles% LAMTON to LC-S_OLTON+3 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_123_P1_PLANT_X | Apply 3-phase fault on PLANT_X to W_LITLFLDTP3 115kV line CKT 1, near PLANT_X 115kV for 7 cycles. Open the faulted line and W_LITLFLDTP3 to LAMB_CNTY 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and W_LITLFLDTP3 to LAMB_CNTY 115kV line CKT 1. Re-open the faulted line after 7 cycles% W_LITLFLDTP3 to LAMB_CNTY 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_124_P1_PLANT_X | Apply 3-phase fault on PLANT_X to SUNDOWN 230kV line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.04s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_124_P1_PLANT_X | Apply 3-phase fault on PLANT_X to SUNDOWN 230kV line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | No | LVRT VIOL - - A11-002-GEN1[1] A11-002-GEN1[2] FRISCO_WND 3[1].
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_124_P1_PLANT_X | Apply 3-phase fault on PLANT_X to SUNDOWN 230kV line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_124_P1_PLANT_X | Apply 3-phase fault on PLANT_X to SUNDOWN 230kV line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.22pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_125_P1_PLANT_X | Apply 3-phase fault on DEAFSMITH to PLANT_X 230kV line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | No | Yes | Yes | No | LVRT VIOL - - A11-002-GEN1[1] A11-002-GEN1[2] FRISCO_WND 3[1] G1140G1204G1[1]. Undamped oscillations were observed in conventional units angles and powers, renewable units powers and system voltage responses. In addition several units tripped under this contingency: A11-002-GEN1[1], A11-002-GEN1[2], and FRISCO_WND 3[1] relays tripped on overvoltage protection under several contingencies in both BC and TC cases (due to the size and location of the unit no further simulations was performed). G1140G1204G1[1] tripped on voltage protection setting 1.20pu-0.08s (embedded in the user model). Simulation was rerun with the SVC mitigation solution and protection settings disabled. The damping issue was resolved with the SVC mitigation option. | ±600 MVAr SVC at Crossroad 765kV
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_125_P1_PLANT_X | Apply 3-phase fault on DEAFSMITH to PLANT_X 230kV line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.04s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_125_P1_PLANT_X | Apply 3-phase fault on DEAFSMITH to PLANT_X 230kV line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_125_P1_PLANT_X | Apply 3-phase fault on DEAFSMITH to PLANT_X 230kV line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.22pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_126_P1_PLANT_X | Apply 3-phase fault on NEWHART to PLANT_X 230kV line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | No | No | Yes | No | LVRT VIOL - - ROOSWND-GEN1[1] FRISCO_WND 3[1] A11-002-GEN1[1] G08-022-GEN3[1] ROOSWND-GEN2[2] A11-002-GEN1[2] G1140G1204G2[1] ARBCKL_WTG1[1] G1140G1204G1[1]. Undamped oscillations were observed in conventional units angles and powers, renewable units powers and system voltage responses. In addition, several units tripped under this contingency: ROOSWND-GEN1[1], G08-022-GEN3[1], ROOSWND-GEN2[2], G1140G1204G2[1], ARBCKL_WTG1[1], G1140G1204G1[1] tripped on voltage protection setting 1.20pu-0.08s (embedded in the user model). Simulation was rerun with the SVC mitigation solution and protection settings disabled. The damping issue was resolved with the SVC mitigation option. | ±600 MVAr SVC at Crossroad 765kV
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_126_P1_PLANT_X | Apply 3-phase fault on NEWHART to PLANT_X 230kV line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.04s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_126_P1_PLANT_X | Apply 3-phase fault on NEWHART to PLANT_X 230kV line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_126_P1_PLANT_X | Apply 3-phase fault on NEWHART to PLANT_X 230kV line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.22pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_127_P1_PLANT_X | Apply 3-phase fault on PLANT_X to TOLK_WEST 230kV line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | No | No | Yes | No | LVRT VIOL - - A11-002-GEN1[1] A11-002-GEN1[2] FRISCO_WND 3[1]. Undamped oscillations were observed in conventional units angles and powers, renewable units powers and system voltage responses. In addition several units tripped under this contingency (ignored, see comments above). Simulation was rerun with the SVC mitigation solution. No further issues were observed. | ±600 MVAr SVC at Crossroad 765kV
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_127_P1_PLANT_X | Apply 3-phase fault on PLANT_X to TOLK_WEST 230kV line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.05s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_127_P1_PLANT_X | Apply 3-phase fault on PLANT_X to TOLK_WEST 230kV line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.04s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_127_P1_PLANT_X | Apply 3-phase fault on PLANT_X to TOLK_WEST 230kV line CKT 1, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.22pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_128_P1_PLANT_X | Apply 3-phase fault on PLANT_X to TOLK_EAST 230kV line CKT 2, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | No | Yes | Yes | No | LVRT VIOL - - A11-002-GEN1[1] A11-002-GEN1[2] FRISCO_WND 3[1]. Undamped oscillations were observed in conventional units angles and powers, renewable units powers and system voltage responses. In addition several units tripped under this contingency (ignored, see comments above). Simulation was rerun with the SVC mitigation solution. No further issues were observed. | ±600 MVAr SVC at Crossroad 765kV
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_128_P1_PLANT_X | Apply 3-phase fault on PLANT_X to TOLK_EAST 230kV line CKT 2, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Note: Abnormal oscillations were observed in the generation units and system responses, which are attributed to the OECGT generation units modeling issues. When the OECGT units were GENETed these oscillations were mitigated. Voltage Spike: 1.20pu, MaxDur: 0.05s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_128_P1_PLANT_X | Apply 3-phase fault on PLANT_X to TOLK_EAST 230kV line CKT 2, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.04s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_128_P1_PLANT_X | Apply 3-phase fault on PLANT_X to TOLK_EAST 230kV line CKT 2, near PLANT_X 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.22pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_129_P1_TOLK_EAST | Apply 3-phase fault on PLANT_X to TOLK_EAST 230kV line CKT 2, near TOLK_EAST 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-080-GEN1[1] G17-080-GEN2[1]. G17-080-GEN1[1] and G17-080-GEN2[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s. The protection settings were disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.25pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_129_P1_TOLK_EAST | Apply 3-phase fault on PLANT_X to TOLK_EAST 230kV line CKT 2, near TOLK_EAST 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | No | LVRT VIOL - - G17-080-GEN1[1] G17-080-GEN2[1] FRISCO_WND 3[1]. G17-080-GEN1[1] and G17-080-GEN2[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s. The protection settings were disabled and simulation was rerun. No further issues were observed.
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_129_P1_TOLK_EAST | Apply 3-phase fault on PLANT_X to TOLK_EAST 230kV line CKT 2, near TOLK_EAST 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-080-GEN1[1] G17-080-GEN2[1]. G17-080-GEN1[1] and G17-080-GEN2[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s. The protection settings were disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.22pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_129_P1_TOLK_EAST | Apply 3-phase fault on PLANT_X to TOLK_EAST 230kV line CKT 2, near TOLK_EAST 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1] G17-080-GEN1[1] G17-080-GEN2[1]. G17-080-GEN1[1] and G17-080-GEN2[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s. The protection settings were disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.23pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_13_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV line CKT 2, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_13_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV line CKT 2, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_13_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV line CKT 2, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_13_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV line CKT 2, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_130_P1_TOLK_EAST | Apply 3-phase fault on TOLK_EAST to TUCO_INT 230kV line CKT 1, near TOLK_EAST 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-080-GEN1[1] G17-080-GEN2[1]. G17-080-GEN1[1] and G17-080-GEN2[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s. The protection settings were disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.26pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_130_P1_TOLK_EAST | Apply 3-phase fault on TOLK_EAST to TUCO_INT 230kV line CKT 1, near TOLK_EAST 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | No | LVRT VIOL - - G17-080-GEN1[1] G17-080-GEN2[1] FRISCO_WND 3[1]. G17-080-GEN1[1] and G17-080-GEN2[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s. The protection settings were disabled and simulation was rerun. Following the protection disable: Undamped oscillations were observed in conventional units angles and powers, renewable units power responses and system voltage. In addition several other units tripped due to voltage protection action (ROOSWND-GEN1[1], G08-022-GEN3[1], ROOSWND-GEN2[2], G1140G1204G2[1] ARBCKL_WTG1[1], G1140G1204G1[1]). Simulation was rerun with the SVC mitigation solution and new sets of protection settings disabled. No further issues were observed. | ±600 MVAr SVC at Crossroad 765kV
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_130_P1_TOLK_EAST | Apply 3-phase fault on TOLK_EAST to TUCO_INT 230kV line CKT 1, near TOLK_EAST 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-080-GEN1[1] G17-080-GEN2[1]. G17-080-GEN1[1] and G17-080-GEN2[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s. The protection settings were disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.24pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_130_P1_TOLK_EAST | Apply 3-phase fault on TOLK_EAST to TUCO_INT 230kV line CKT 1, near TOLK_EAST 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1] G17-080-GEN1[1] G17-080-GEN2[1]. G17-080-GEN1[1] and G17-080-GEN2[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s. The protection settings were disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.24pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_131_P1_TOLK_EAST | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_EAST 230kV line CKT 1, near TOLK_EAST 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-080-GEN1[1] G17-080-GEN2[1]. G17-080-GEN1[1] and G17-080-GEN2[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s. The protection settings were disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.25pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_131_P1_TOLK_EAST | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_EAST 230kV line CKT 1, near TOLK_EAST 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | No | LVRT VIOL - - G17-080-GEN1[1] G17-080-GEN2[1] FRISCO_WND 3[1]. G17-080-GEN1[1] and G17-080-GEN2[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s. The protection settings were disabled and simulation was rerun. No further issues were observed.
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_131_P1_TOLK_EAST | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_EAST 230kV line CKT 1, near TOLK_EAST 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-080-GEN1[1] G17-080-GEN2[1]. G17-080-GEN1[1] and G17-080-GEN2[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s. The protection settings were disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.23pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_131_P1_TOLK_EAST | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_EAST 230kV line CKT 1, near TOLK_EAST 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1] G17-080-GEN1[1] G17-080-GEN2[1]. G17-080-GEN1[1] and G17-080-GEN2[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s. The protection settings were disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.24pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_132_P1_TOLK_WEST | Apply 3-phase fault on LAMB_TR3 13.19kV/115kV/230kV transformer CKT 1, near TOLK_WEST 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-080-GEN1[1] G17-080-GEN2[1]. G17-080-GEN1[1] and G17-080-GEN2[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s. The protection settings were disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.21pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_132_P1_TOLK_WEST | Apply 3-phase fault on LAMB_TR3 13.19kV/115kV/230kV transformer CKT 1, near TOLK_WEST 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-080-GEN1[1] G17-080-GEN2[1] FRISCO_WND 3[1]. G17-080-GEN1[1] and G17-080-GEN2[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s. The protection settings were disabled and simulation was rerun. Following protection disable: Undamped oscillations were observed in conventional units angles and powers, renewable units power responses and system voltage. Simulation was rerun with the SVC mitigation solution. No further issues were observed. | ±600 MVAr SVC at Crossroad 765kV
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_132_P1_TOLK_WEST | Apply 3-phase fault on LAMB_TR3 13.19kV/115kV/230kV transformer CKT 1, near TOLK_WEST 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-080-GEN1[1] G17-080-GEN2[1]. G17-080-GEN1[1] and G17-080-GEN2[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s. The protection settings were disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_132_P1_TOLK_WEST | Apply 3-phase fault on LAMB_TR3 13.19kV/115kV/230kV transformer CKT 1, near TOLK_WEST 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1] G17-080-GEN1[1] G17-080-GEN2[1]. G17-080-GEN1[1] and G17-080-GEN2[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s. The protection settings were disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_133_P1_TOLK_WEST | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_WEST 230kV line CKT 2, near TOLK_WEST 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-080-GEN1[1] G17-080-GEN2[1]. G17-080-GEN1[1] and G17-080-GEN2[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s. The protection settings were disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.25pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_133_P1_TOLK_WEST | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_WEST 230kV line CKT 2, near TOLK_WEST 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | No | LVRT VIOL - - G17-080-GEN1[1] G17-080-GEN2[1] FRISCO_WND 3[1]. G17-080-GEN1[1] and G17-080-GEN2[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s. The protection settings were disabled and simulation was rerun. Following protection disable: Undamped oscillations were observed in conventional units angles and powers, renewable units power responses and system voltage. Simulation was rerun with the SVC mitigation solution. No further issues were observed. | ±600 MVAr SVC at Crossroad 765kV
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_133_P1_TOLK_WEST | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_WEST 230kV line CKT 2, near TOLK_WEST 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-080-GEN1[1] G17-080-GEN2[1]. G17-080-GEN1[1] and G17-080-GEN2[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s. The protection settings were disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.23pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_133_P1_TOLK_WEST | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_WEST 230kV line CKT 2, near TOLK_WEST 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1] G17-080-GEN1[1] G17-080-GEN2[1]. G17-080-GEN1[1] and G17-080-GEN2[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s. The protection settings were disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.24pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_134_P1_TOLK_WEST | Apply 3-phase fault on PLANT_X to TOLK_WEST 230kV line CKT 1, near TOLK_WEST 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-080-GEN1[1] G17-080-GEN2[1]. G17-080-GEN1[1] and G17-080-GEN2[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s. The protection settings were disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.25pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_134_P1_TOLK_WEST | Apply 3-phase fault on PLANT_X to TOLK_WEST 230kV line CKT 1, near TOLK_WEST 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | No | LVRT VIOL - - G17-080-GEN1[1] G17-080-GEN2[1] FRISCO_WND 3[1]. G17-080-GEN1[1] and G17-080-GEN2[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s. The protection settings were disabled and simulation was rerun. No further issues were observed.
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_134_P1_TOLK_WEST | Apply 3-phase fault on PLANT_X to TOLK_WEST 230kV line CKT 1, near TOLK_WEST 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-080-GEN1[1] G17-080-GEN2[1]. G17-080-GEN1[1] and G17-080-GEN2[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s. The protection settings were disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.23pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_134_P1_TOLK_WEST | Apply 3-phase fault on PLANT_X to TOLK_WEST 230kV line CKT 1, near TOLK_WEST 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1] G17-080-GEN1[1] G17-080-GEN2[1]. G17-080-GEN1[1] and G17-080-GEN2[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s. The protection settings were disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.24pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_135_P1_TOLK_WEST | Apply 3-phase fault on TOLK_WEST to NEEDMORE 230kV line CKT 1, near TOLK_WEST 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | [7 empty] | Crashing issue: This contingency led to simulation crash when the fault is cleared and the faulted line is opened at 1.1 sec. The issue is traced back to the study generator GEN-2017-039 (#588803) 'GSCOR1' Vestas user model with the POI at remote end of the faulted line. This contingency has been rerun with different simulation options such as acceleration factor, iteration limit, time step and so on, but none of these options could resolve this modeling issue. Note, when the fault is located at the POI of this unit, there is no numerical or crashing issues with stable responses (contingency 137). This issue has been observed in TC cases only and in all 4 scenarios. It is recommended that this user model be further evaluated and troubleshooted.
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_135_P1_TOLK_WEST | Apply 3-phase fault on TOLK_WEST to NEEDMORE 230kV line CKT 1, near TOLK_WEST 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | [7 empty] | See note of this contingency for 19W TC.
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_135_P1_TOLK_WEST | Apply 3-phase fault on TOLK_WEST to NEEDMORE 230kV line CKT 1, near TOLK_WEST 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | [7 empty] | See note of this contingency for 19W TC.
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_135_P1_TOLK_WEST | Apply 3-phase fault on TOLK_WEST to NEEDMORE 230kV line CKT 1, near TOLK_WEST 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | [7 empty] | See note of this contingency for 19W TC.
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_136_P1_TOLK | Apply 3-phase fault on TOLK to CROSSROADS 7 345kV line CKT 1, near TOLK 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G08-022-GEN3[1]. G08-022-GEN3[1] tripped on voltage protection setting 1.25pu-0.005s (embedded in the user model). The protection setting was disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.30pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_136_P1_TOLK | Apply 3-phase fault on TOLK to CROSSROADS 7 345kV line CKT 1, near TOLK 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.27pu, MaxDur: 0.05s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_136_P1_TOLK | Apply 3-phase fault on TOLK to CROSSROADS 7 345kV line CKT 1, near TOLK 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes | Voltage Spike: 1.22pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_136_P1_TOLK | Apply 3-phase fault on TOLK to CROSSROADS 7 345kV line CKT 1, near TOLK 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.22pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_137_P1_NEEDMORE | Apply 3-phase fault on TOLK_WEST to NEEDMORE 230kV line CKT 1, near NEEDMORE 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | No | Yes | No | Yes | Voltage Spike: 1.55pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_137_P1_NEEDMORE | Apply 3-phase fault on TOLK_WEST to NEEDMORE 230kV line CKT 1, near NEEDMORE 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | No | Yes | No | Yes | Voltage Spike: 1.54pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_137_P1_NEEDMORE | Apply 3-phase fault on TOLK_WEST to NEEDMORE 230kV line CKT 1, near NEEDMORE 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.55pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_137_P1_NEEDMORE | Apply 3-phase fault on TOLK_WEST to NEEDMORE 230kV line CKT 1, near NEEDMORE 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.56pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_138_P1_NEEDMORE | Apply 3-phase fault on NEEDMORE to DEAN_INTG 230kV line CKT 1, near NEEDMORE 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.34pu, MaxDur: 0.04s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_138_P1_NEEDMORE | Apply 3-phase fault on NEEDMORE to DEAN_INTG 230kV line CKT 1, near NEEDMORE 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.36pu, MaxDur: 0.05s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_138_P1_NEEDMORE | Apply 3-phase fault on NEEDMORE to DEAN_INTG 230kV line CKT 1, near NEEDMORE 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.33pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_138_P1_NEEDMORE | Apply 3-phase fault on NEEDMORE to DEAN_INTG 230kV line CKT 1, near NEEDMORE 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.33pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_139_P1_LAMB_CNTY | Apply 3-phase fault on LAMB_CNTY to HOCKLEY 115kV line CKT 1, near LAMB_CNTY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_139_P1_LAMB_CNTY | Apply 3-phase fault on LAMB_CNTY to HOCKLEY 115kV line CKT 1, near LAMB_CNTY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_139_P1_LAMB_CNTY | Apply 3-phase fault on LAMB_CNTY to HOCKLEY 115kV line CKT 1, near LAMB_CNTY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_139_P1_LAMB_CNTY | Apply 3-phase fault on LAMB_CNTY to HOCKLEY 115kV line CKT 1, near LAMB_CNTY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_14_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to BADGER 7 345kV line CKT 1, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_14_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to BADGER 7 345kV line CKT 1, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_14_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to BADGER 7 345kV line CKT 1, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_14_P1_BVRCNTY7 | Apply 3-phase fault on BVRCNTY7 to BADGER 7 345kV line CKT 1, near BVRCNTY7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_140_P1_LAMB_CNTY | Apply 3-phase fault on PLANT_X to LAMB_CNTY 115kV line CKT 1, near LAMB_CNTY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_140_P1_LAMB_CNTY | Apply 3-phase fault on PLANT_X to LAMB_CNTY 115kV line CKT 1, near LAMB_CNTY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_140_P1_LAMB_CNTY | Apply 3-phase fault on PLANT_X to LAMB_CNTY 115kV line CKT 1, near LAMB_CNTY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_140_P1_LAMB_CNTY | Apply 3-phase fault on PLANT_X to LAMB_CNTY 115kV line CKT 1, near LAMB_CNTY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_141_P1_BLANCO | Apply 3-phase fault on BLANCO to CROSBY 115kV line CKT 1, near BLANCO 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_141_P1_BLANCO | Apply 3-phase fault on BLANCO to CROSBY 115kV line CKT 1, near BLANCO 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_141_P1_BLANCO | Apply 3-phase fault on BLANCO to CROSBY 115kV line CKT 1, near BLANCO 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_141_P1_BLANCO | Apply 3-phase fault on BLANCO to CROSBY 115kV line CKT 1, near BLANCO 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_142_P1_TUCO_INT | Apply 3-phase fault on FLOYD_CNTY 3 to TUCO_INT 115kV line CKT 1, near TUCO_INT 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_142_P1_TUCO_INT | Apply 3-phase fault on FLOYD_CNTY 3 to TUCO_INT 115kV line CKT 1, near TUCO_INT 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_142_P1_TUCO_INT | Apply 3-phase fault on FLOYD_CNTY 3 to TUCO_INT 115kV line CKT 1, near TUCO_INT 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_142_P1_TUCO_INT | Apply 3-phase fault on FLOYD_CNTY 3 to TUCO_INT 115kV line CKT 1, near TUCO_INT 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_143_P1_TUCO_INT | Apply 3-phase fault on TUCO_TR3 13.19kV/115kV/230kV transformer CKT 2, near TUCO_INT 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_143_P1_TUCO_INT | Apply 3-phase fault on TUCO_TR3 13.19kV/115kV/230kV transformer CKT 2, near TUCO_INT 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_143_P1_TUCO_INT | Apply 3-phase fault on TUCO_TR3 13.19kV/115kV/230kV transformer CKT 2, near TUCO_INT 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_143_P1_TUCO_INT | Apply 3-phase fault on TUCO_TR3 13.19kV/115kV/230kV transformer CKT 2, near TUCO_INT 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_144_P1_TUCO_INT | Apply 3-phase fault on SP-ERSKINE 3 to CARLISLE 115kV line CKT 1, near TUCO_INT 115kV for 7 cycles. Open the faulted line and TUCO_INT to STANTON_W 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and TUCO_INT to STANTON_W 115kV line CKT 1. Re-open the faulted line after 7 cycles% TUCO_INT to STANTON_W 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_144_P1_TUCO_INT | Apply 3-phase fault on SP-ERSKINE 3 to CARLISLE 115kV line CKT 1, near TUCO_INT 115kV for 7 cycles. Open the faulted line and TUCO_INT to STANTON_W 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and TUCO_INT to STANTON_W 115kV line CKT 1. Re-open the faulted line after 7 cycles% TUCO_INT to STANTON_W 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_144_P1_TUCO_INT | Apply 3-phase fault on SP-ERSKINE 3 to CARLISLE 115kV line CKT 1, near TUCO_INT 115kV for 7 cycles. Open the faulted line and TUCO_INT to STANTON_W 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and TUCO_INT to STANTON_W 115kV line CKT 1. Re-open the faulted line after 7 cycles% TUCO_INT to STANTON_W 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_144_P1_TUCO_INT | Apply 3-phase fault on SP-ERSKINE 3 to CARLISLE 115kV line CKT 1, near TUCO_INT 115kV for 7 cycles. Open the faulted line and TUCO_INT to STANTON_W 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and TUCO_INT to STANTON_W 115kV line CKT 1. Re-open the faulted line after 7 cycles% TUCO_INT to STANTON_W 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_145_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to LUBBCK_EST 3 115kV line CKT 1, near TUCO_INT 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_145_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to LUBBCK_EST 3 115kV line CKT 1, near TUCO_INT 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_145_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to LUBBCK_EST 3 115kV line CKT 1, near TUCO_INT 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_145_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to LUBBCK_EST 3 115kV line CKT 1, near TUCO_INT 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_146_P1_TUCO_INT | Apply 3-phase fault on SWISHER to TUCO_INT 230kV line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_146_P1_TUCO_INT | Apply 3-phase fault on SWISHER to TUCO_INT 230kV line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_146_P1_TUCO_INT | Apply 3-phase fault on SWISHER to TUCO_INT 230kV line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_146_P1_TUCO_INT | Apply 3-phase fault on SWISHER to TUCO_INT 230kV line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_147_P1_TUCO_INT | Apply 3-phase fault on TOLK_EAST to TUCO_INT 230kV line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_147_P1_TUCO_INT | Apply 3-phase fault on TOLK_EAST to TUCO_INT 230kV line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_147_P1_TUCO_INT | Apply 3-phase fault on TOLK_EAST to TUCO_INT 230kV line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_147_P1_TUCO_INT | Apply 3-phase fault on TOLK_EAST to TUCO_INT 230kV line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_148_P1_TUCO_INT | Apply 3-phase fault on TUCO_TR4 13.19kV/115kV/230kV transformer CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_148_P1_TUCO_INT | Apply 3-phase fault on TUCO_TR4 13.19kV/115kV/230kV transformer CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_148_P1_TUCO_INT | Apply 3-phase fault on TUCO_TR4 13.19kV/115kV/230kV transformer CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_148_P1_TUCO_INT | Apply 3-phase fault on TUCO_TR4 13.19kV/115kV/230kV transformer CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_149_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to JONES 230kV line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Unstable | No | No | No | No | Yes | No | It was observed that ANTELOPE units A, B and C were unstable under this contingency for both 21L BC and TC cases. The instability issue in the TC case was resolved with the SVC mitigation option. | ±600 MVAr SVC at Crossroad 765kV
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_149_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to JONES 230kV line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_149_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to JONES 230kV line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_149_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to JONES 230kV line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_15_P1_BADGER7 | Apply 3-phase fault on BVRCNTY7 to BADGER 7 345kV line CKT 2, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_15_P1_BADGER7 | Apply 3-phase fault on BVRCNTY7 to BADGER 7 345kV line CKT 2, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_15_P1_BADGER7 | Apply 3-phase fault on BVRCNTY7 to BADGER 7 345kV line CKT 2, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.23pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_15_P1_BADGER7 | Apply 3-phase fault on BVRCNTY7 to BADGER 7 345kV line CKT 2, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.23pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_150_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to CARLISLE 230kV line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_150_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to CARLISLE 230kV line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_150_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to CARLISLE 230kV line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_150_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to CARLISLE 230kV line CKT 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_151_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to YOAKUM_345 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_151_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to YOAKUM_345 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | No | LVRT VIOL - - FRISCO_WND 3[1].
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_151_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to YOAKUM_345 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.06s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_151_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to YOAKUM_345 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_152_P1_TUCO_INT | Apply 3-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Unstable | No | No | No | No | Yes | No | Angular and system instability was observed in the G6 region. The stability issue was resolved with the SVC mitigation solution. | ±600 MVAr SVC at Crossroad 765kV
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_152_P1_TUCO_INT | Apply 3-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_152_P1_TUCO_INT | Apply 3-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_152_P1_TUCO_INT | Apply 3-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_153_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV line CKT 2, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes | Note: Abnormal oscillations were observed in the generation units and system responses, which are attributed to the OECGT generation units modeling issues. When the OECGT units were GENETed these oscillations were mitigated.
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_153_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV line CKT 2, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | No | LVRT VIOL - - FRISCO_WND 3[1].
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_153_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV line CKT 2, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_153_P1_TUCO_INT | Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV line CKT 2, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.05s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_154_P1_DEAN_INTG | Apply 3-phase fault on DEAN_INTG to COCHRAN 115kV line CKT 1, near DEAN_INTG 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_154_P1_DEAN_INTG | Apply 3-phase fault on DEAN_INTG to COCHRAN 115kV line CKT 1, near DEAN_INTG 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_154_P1_DEAN_INTG | Apply 3-phase fault on DEAN_INTG to COCHRAN 115kV line CKT 1, near DEAN_INTG 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_154_P1_DEAN_INTG | Apply 3-phase fault on DEAN_INTG to COCHRAN 115kV line CKT 1, near DEAN_INTG 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_155_P1_DEAN_INTG | Apply 3-phase fault on DEAN_INTTR11 13.19kV/115kV/230kV transformer CKT 1, near DEAN_INTG 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_155_P1_DEAN_INTG | Apply 3-phase fault on DEAN_INTTR11 13.19kV/115kV/230kV transformer CKT 1, near DEAN_INTG 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_155_P1_DEAN_INTG | Apply 3-phase fault on DEAN_INTTR11 13.19kV/115kV/230kV transformer CKT 1, near DEAN_INTG 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_155_P1_DEAN_INTG | Apply 3-phase fault on DEAN_INTTR11 13.19kV/115kV/230kV transformer CKT 1, near DEAN_INTG 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_156_P1_DEAN_INTG | Apply 3-phase fault on DEAN_INTG to YOAKUM 230kV line CKT 1, near DEAN_INTG 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_156_P1_DEAN_INTG | Apply 3-phase fault on DEAN_INTG to YOAKUM 230kV line CKT 1, near DEAN_INTG 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_156_P1_DEAN_INTG | Apply 3-phase fault on DEAN_INTG to YOAKUM 230kV line CKT 1, near DEAN_INTG 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_156_P1_DEAN_INTG | Apply 3-phase fault on DEAN_INTG to YOAKUM 230kV line CKT 1, near DEAN_INTG 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_157_P1_CARLISLE | Apply 3-phase fault on CRLSLE_TR1 1 13.19kV/115kV/230kV transformer CKT 1, near CARLISLE 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_157_P1_CARLISLE | Apply 3-phase fault on CRLSLE_TR1 1 13.19kV/115kV/230kV transformer CKT 1, near CARLISLE 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_157_P1_CARLISLE | Apply 3-phase fault on CRLSLE_TR1 1 13.19kV/115kV/230kV transformer CKT 1, near CARLISLE 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_157_P1_CARLISLE | Apply 3-phase fault on CRLSLE_TR1 1 13.19kV/115kV/230kV transformer CKT 1, near CARLISLE 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_158_P1_CARLISLE | Apply 3-phase fault on LP-MCDONALD6 to CARLISLE 230kV line CKT 1, near CARLISLE 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_158_P1_CARLISLE | Apply 3-phase fault on LP-MCDONALD6 to CARLISLE 230kV line CKT 1, near CARLISLE 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_158_P1_CARLISLE | Apply 3-phase fault on LP-MCDONALD6 to CARLISLE 230kV line CKT 1, near CARLISLE 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_158_P1_CARLISLE | Apply 3-phase fault on LP-MCDONALD6 to CARLISLE 230kV line CKT 1, near CARLISLE 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_159_P1_CARLISLE | Apply 3-phase fault on CARLISLE to WOLFFORTH 230kV line CKT 1, near CARLISLE 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_159_P1_CARLISLE | Apply 3-phase fault on CARLISLE to WOLFFORTH 230kV line CKT 1, near CARLISLE 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_159_P1_CARLISLE | Apply 3-phase fault on CARLISLE to WOLFFORTH 230kV line CKT 1, near CARLISLE 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_159_P1_CARLISLE | Apply 3-phase fault on CARLISLE to WOLFFORTH 230kV line CKT 1, near CARLISLE 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_16_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_16_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_16_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.22pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_16_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.21pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_160_P1_LUBBCK_STH6 | Apply 3-phase fault on LUBBCK_STH 6 to WOLFFORTH 230kV line CKT 1, near LUBBCK_STH 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_160_P1_LUBBCK_STH6 | Apply 3-phase fault on LUBBCK_STH 6 to WOLFFORTH 230kV line CKT 1, near LUBBCK_STH 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_160_P1_LUBBCK_STH6 | Apply 3-phase fault on LUBBCK_STH 6 to WOLFFORTH 230kV line CKT 1, near LUBBCK_STH 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_160_P1_LUBBCK_STH6 | Apply 3-phase fault on LUBBCK_STH 6 to WOLFFORTH 230kV line CKT 1, near LUBBCK_STH 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_161_P1_LUBBCK_STH6 | Apply 3-phase fault on LP-SOUTHEST6 to LUBBCK_STH 6 230kV line CKT 1, near LUBBCK_STH 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_161_P1_LUBBCK_STH6 | Apply 3-phase fault on LP-SOUTHEST6 to LUBBCK_STH 6 230kV line CKT 1, near LUBBCK_STH 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_161_P1_LUBBCK_STH6 | Apply 3-phase fault on LP-SOUTHEST6 to LUBBCK_STH 6 230kV line CKT 1, near LUBBCK_STH 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_161_P1_LUBBCK_STH6 | Apply 3-phase fault on LP-SOUTHEST6 to LUBBCK_STH 6 230kV line CKT 1, near LUBBCK_STH 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_162_P1_JONES | Apply 3-phase fault on LP-HOLLY to JONES 230kV line CKT 1, near JONES 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_162_P1_JONES | Apply 3-phase fault on LP-HOLLY to JONES 230kV line CKT 1, near JONES 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_162_P1_JONES | Apply 3-phase fault on LP-HOLLY to JONES 230kV line CKT 1, near JONES 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_162_P1_JONES | Apply 3-phase fault on LP-HOLLY to JONES 230kV line CKT 1, near JONES 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_163_P1_JONES | Apply 3-phase fault on JONES to GRASSLAND 230kV line CKT 1, near JONES 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_163_P1_JONES | Apply 3-phase fault on JONES to GRASSLAND 230kV line CKT 1, near JONES 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_163_P1_JONES | Apply 3-phase fault on JONES to GRASSLAND 230kV line CKT 1, near JONES 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_163_P1_JONES | Apply 3-phase fault on JONES to GRASSLAND 230kV line CKT 1, near JONES 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_164_P1_JONES | Apply 3-phase fault on LUBBCK_STH 6 to JONES 230kV line CKT 2, near JONES 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_164_P1_JONES | Apply 3-phase fault on LUBBCK_STH 6 to JONES 230kV line CKT 2, near JONES 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_164_P1_JONES | Apply 3-phase fault on LUBBCK_STH 6 to JONES 230kV line CKT 2, near JONES 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_164_P1_JONES | Apply 3-phase fault on LUBBCK_STH 6 to JONES 230kV line CKT 2, near JONES 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_165_P1_JONES | Apply 3-phase fault on LUBBCK_EST 6 to JONES 230kV line CKT 1, near JONES 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_165_P1_JONES | Apply 3-phase fault on LUBBCK_EST 6 to JONES 230kV line CKT 1, near JONES 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_165_P1_JONES | Apply 3-phase fault on LUBBCK_EST 6 to JONES 230kV line CKT 1, near JONES 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_165_P1_JONES | Apply 3-phase fault on LUBBCK_EST 6 to JONES 230kV line CKT 1, near JONES 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_166_P1_SUNDOWN | Apply 3-phase fault on SUNDOWN to WOLFFORTH 230kV line CKT 1, near SUNDOWN 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_166_P1_SUNDOWN | Apply 3-phase fault on SUNDOWN to WOLFFORTH 230kV line CKT 1, near SUNDOWN 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_166_P1_SUNDOWN | Apply 3-phase fault on SUNDOWN to WOLFFORTH 230kV line CKT 1, near SUNDOWN 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_166_P1_SUNDOWN | Apply 3-phase fault on SUNDOWN to WOLFFORTH 230kV line CKT 1, near SUNDOWN 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_167_P1_SUNDOWN | Apply 3-phase fault on SUNDOWN_TR11 13.8kV/115kV/230kV transformer CKT 1, near SUNDOWN 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_167_P1_SUNDOWN | Apply 3-phase fault on SUNDOWN_TR11 13.8kV/115kV/230kV transformer CKT 1, near SUNDOWN 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_167_P1_SUNDOWN | Apply 3-phase fault on SUNDOWN_TR11 13.8kV/115kV/230kV transformer CKT 1, near SUNDOWN 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_167_P1_SUNDOWN | Apply 3-phase fault on SUNDOWN_TR11 13.8kV/115kV/230kV transformer CKT 1, near SUNDOWN 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_168_P1_SUNDOWN | Apply 3-phase fault on SUNDOWN to AMOCO_SS 230kV line CKT 1, near SUNDOWN 230kV for 7 cycles. Open the faulted line and AMOCO_SS to YOAKUM 230kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and AMOCO_SS to YOAKUM 230kV line CKT 1. Re-open the faulted line after 7 cycles% AMOCO_SS to YOAKUM 230kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_168_P1_SUNDOWN | Apply 3-phase fault on SUNDOWN to AMOCO_SS 230kV line CKT 1, near SUNDOWN 230kV for 7 cycles. Open the faulted line and AMOCO_SS to YOAKUM 230kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and AMOCO_SS to YOAKUM 230kV line CKT 1. Re-open the faulted line after 7 cycles% AMOCO_SS to YOAKUM 230kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_168_P1_SUNDOWN | Apply 3-phase fault on SUNDOWN to AMOCO_SS 230kV line CKT 1, near SUNDOWN 230kV for 7 cycles. Open the faulted line and AMOCO_SS to YOAKUM 230kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and AMOCO_SS to YOAKUM 230kV line CKT 1. Re-open the faulted line after 7 cycles% AMOCO_SS to YOAKUM 230kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_168_P1_SUNDOWN | Apply 3-phase fault on SUNDOWN to AMOCO_SS 230kV line CKT 1, near SUNDOWN 230kV for 7 cycles. Open the faulted line and AMOCO_SS to YOAKUM 230kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and AMOCO_SS to YOAKUM 230kV line CKT 1. Re-open the faulted line after 7 cycles% AMOCO_SS to YOAKUM 230kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_169_P1_YOAKUM | Apply 3-phase fault on YOAKUM to MUSTANG 230kV line CKT 1, near YOAKUM 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_169_P1_YOAKUM | Apply 3-phase fault on YOAKUM to MUSTANG 230kV line CKT 1, near YOAKUM 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_169_P1_YOAKUM | Apply 3-phase fault on YOAKUM to MUSTANG 230kV line CKT 1, near YOAKUM 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_169_P1_YOAKUM | Apply 3-phase fault on YOAKUM to MUSTANG 230kV line CKT 1, near YOAKUM 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_17_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.33pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_17_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_17_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.33pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_17_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.32pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_170_P1_YOAKUM | Apply 3-phase fault on YOAKUM to BRU_SUB 230kV line CKT 1, near YOAKUM 230kV for 7 cycles. Open the faulted line and AMOCOWASSON6 to MUSTANG 230kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and AMOCOWASSON6 to MUSTANG 230kV line CKT 1. Re-open the faulted line after 7 cycles% AMOCOWASSON6 to MUSTANG 230kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes | Undamped and abnormal oscillations were observed in conventional units angles and powers, renewable units powers and system voltage responses. Simulation was rerun with the SVC mitigation solution. No further issues were observed. | ±600 MVAr SVC at Crossroad 765kV
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_170_P1_YOAKUM | Apply 3-phase fault on YOAKUM to BRU_SUB 230kV line CKT 1, near YOAKUM 230kV for 7 cycles. Open the faulted line and AMOCOWASSON6 to MUSTANG 230kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and AMOCOWASSON6 to MUSTANG 230kV line CKT 1. Re-open the faulted line after 7 cycles% AMOCOWASSON6 to MUSTANG 230kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.06s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_170_P1_YOAKUM | Apply 3-phase fault on YOAKUM to BRU_SUB 230kV line CKT 1, near YOAKUM 230kV for 7 cycles. Open the faulted line and AMOCOWASSON6 to MUSTANG 230kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and AMOCOWASSON6 to MUSTANG 230kV line CKT 1. Re-open the faulted line after 7 cycles% AMOCOWASSON6 to MUSTANG 230kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_170_P1_YOAKUM | Apply 3-phase fault on YOAKUM to BRU_SUB 230kV line CKT 1, near YOAKUM 230kV for 7 cycles. Open the faulted line and AMOCOWASSON6 to MUSTANG 230kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and AMOCOWASSON6 to MUSTANG 230kV line CKT 1. Re-open the faulted line after 7 cycles% AMOCOWASSON6 to MUSTANG 230kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_171_P1_YOAKUM | Apply 3-phase fault on YOAKUM_TR1 1 13.19kV/115kV/230kV transformer CKT 1, near YOAKUM 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_171_P1_YOAKUM | Apply 3-phase fault on YOAKUM_TR1 1 13.19kV/115kV/230kV transformer CKT 1, near YOAKUM 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_171_P1_YOAKUM | Apply 3-phase fault on YOAKUM_TR1 1 13.19kV/115kV/230kV transformer CKT 1, near YOAKUM 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_171_P1_YOAKUM | Apply 3-phase fault on YOAKUM_TR1 1 13.19kV/115kV/230kV transformer CKT 1, near YOAKUM 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | No | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_172_P1_YOAKUM | Apply 3-phase fault on AMOCO_SS to YOAKUM 230kV line CKT 1, near YOAKUM 230kV for 7 cycles. Open the faulted line and SUNDOWN to AMOCO_SS 230kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and SUNDOWN to AMOCO_SS 230kV line CKT 1. Re-open the faulted line after 7 cycles% SUNDOWN to AMOCO_SS 230kV line CKT 1 and clear the fault. | P1 | Unstable | No | No | No | No | Yes | No | Angular and system instability was observed in the G6 region. The stability issue was resolved with the SVC mitigation solution. | ±600 MVAr SVC at Crossroad 765kV
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_172_P1_YOAKUM | Apply 3-phase fault on AMOCO_SS to YOAKUM 230kV line CKT 1, near YOAKUM 230kV for 7 cycles. Open the faulted line and SUNDOWN to AMOCO_SS 230kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and SUNDOWN to AMOCO_SS 230kV line CKT 1. Re-open the faulted line after 7 cycles% SUNDOWN to AMOCO_SS 230kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_172_P1_YOAKUM | Apply 3-phase fault on AMOCO_SS to YOAKUM 230kV line CKT 1, near YOAKUM 230kV for 7 cycles. Open the faulted line and SUNDOWN to AMOCO_SS 230kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and SUNDOWN to AMOCO_SS 230kV line CKT 1. Re-open the faulted line after 7 cycles% SUNDOWN to AMOCO_SS 230kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_172_P1_YOAKUM | Apply 3-phase fault on AMOCO_SS to YOAKUM 230kV line CKT 1, near YOAKUM 230kV for 7 cycles. Open the faulted line and SUNDOWN to AMOCO_SS 230kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and SUNDOWN to AMOCO_SS 230kV line CKT 1. Re-open the faulted line after 7 cycles% SUNDOWN to AMOCO_SS 230kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_173_P1_YOAKUM | Apply 3-phase fault on YOAKUM to INK_BASIN 230kV line CKT 1, near YOAKUM 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_173_P1_YOAKUM | Apply 3-phase fault on YOAKUM to INK_BASIN 230kV line CKT 1, near YOAKUM 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_173_P1_YOAKUM | Apply 3-phase fault on YOAKUM to INK_BASIN 230kV line CKT 1, near YOAKUM 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_173_P1_YOAKUM | Apply 3-phase fault on YOAKUM to INK_BASIN 230kV line CKT 1, near YOAKUM 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_174_P1_YOAKUM | Apply 3-phase fault on YOAKUM 230kV/345kV/13.19kV transformer CKT 1, near YOAKUM 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_174_P1_YOAKUM | Apply 3-phase fault on YOAKUM 230kV/345kV/13.19kV transformer CKT 1, near YOAKUM 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_174_P1_YOAKUM | Apply 3-phase fault on YOAKUM 230kV/345kV/13.19kV transformer CKT 1, near YOAKUM 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_174_P1_YOAKUM | Apply 3-phase fault on YOAKUM 230kV/345kV/13.19kV transformer CKT 1, near YOAKUM 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | No | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_175_P1_INK_BASIN | Apply 3-phase fault on INK_BASIN to ALRDCRTZ_TP3 115kV line CKT 1, near INK_BASIN 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_175_P1_INK_BASIN | Apply 3-phase fault on INK_BASIN to ALRDCRTZ_TP3 115kV line CKT 1, near INK_BASIN 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_175_P1_INK_BASIN | Apply 3-phase fault on INK_BASIN to ALRDCRTZ_TP3 115kV line CKT 1, near INK_BASIN 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_175_P1_INK_BASIN | Apply 3-phase fault on INK_BASIN to ALRDCRTZ_TP3 115kV line CKT 1, near INK_BASIN 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_176_P1_INK_BASIN | Apply 3-phase fault on INKBASN_TR 1 13.19kV/115kV/230kV transformer CKT 1, near INK_BASIN 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_176_P1_INK_BASIN | Apply 3-phase fault on INKBASN_TR 1 13.19kV/115kV/230kV transformer CKT 1, near INK_BASIN 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_176_P1_INK_BASIN | Apply 3-phase fault on INKBASN_TR 1 13.19kV/115kV/230kV transformer CKT 1, near INK_BASIN 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_176_P1_INK_BASIN | Apply 3-phase fault on INKBASN_TR 1 13.19kV/115kV/230kV transformer CKT 1, near INK_BASIN 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_177_P1_INK_BASIN | Apply 3-phase fault on YOAKUM to INK_BASIN 230kV line CKT 1, near INK_BASIN 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_177_P1_INK_BASIN | Apply 3-phase fault on YOAKUM to INK_BASIN 230kV line CKT 1, near INK_BASIN 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_177_P1_INK_BASIN | Apply 3-phase fault on YOAKUM to INK_BASIN 230kV line CKT 1, near INK_BASIN 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_177_P1_INK_BASIN | Apply 3-phase fault on YOAKUM to INK_BASIN 230kV line CKT 1, near INK_BASIN 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_178_P1_MUSTANG | Apply 3-phase fault on MUSTANG to SEMINOLE 230kV line CKT 1, near MUSTANG 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_178_P1_MUSTANG | Apply 3-phase fault on MUSTANG to SEMINOLE 230kV line CKT 1, near MUSTANG 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_178_P1_MUSTANG | Apply 3-phase fault on MUSTANG to SEMINOLE 230kV line CKT 1, near MUSTANG 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_178_P1_MUSTANG | Apply 3-phase fault on MUSTANG to SEMINOLE 230kV line CKT 1, near MUSTANG 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_179_P1_CHAVES_CNTY6 | Apply 3-phase fault on CHAVES_CNTY6 to EDDY_NORTH 6 230kV line CKT 1, near CHAVES_CNTY6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_179_P1_CHAVES_CNTY6 | Apply 3-phase fault on CHAVES_CNTY6 to EDDY_NORTH 6 230kV line CKT 1, near CHAVES_CNTY6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_179_P1_CHAVES_CNTY6 | Apply 3-phase fault on CHAVES_CNTY6 to EDDY_NORTH 6 230kV line CKT 1, near CHAVES_CNTY6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G14-033-GEN2[1].
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_179_P1_CHAVES_CNTY6 | Apply 3-phase fault on CHAVES_CNTY6 to EDDY_NORTH 6 230kV line CKT 1, near CHAVES_CNTY6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G14-033-GEN2[1].
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_18_P1_LP-MCDONALD6 | Apply 3-phase fault on LP-MCDONALD6 to LP-SOUTHEST6 230kV line CKT 1, near LP-MCDONALD6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_18_P1_LP-MCDONALD6 | Apply 3-phase fault on LP-MCDONALD6 to LP-SOUTHEST6 230kV line CKT 1, near LP-MCDONALD6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_18_P1_LP-MCDONALD6 | Apply 3-phase fault on LP-MCDONALD6 to LP-SOUTHEST6 230kV line CKT 1, near LP-MCDONALD6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_18_P1_LP-MCDONALD6 | Apply 3-phase fault on LP-MCDONALD6 to LP-SOUTHEST6 230kV line CKT 1, near LP-MCDONALD6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_180_P1_CHAVES_CNTY6 | Apply 3-phase fault on SN_JUAN_TAP6 to CHAVES_CNTY6 230kV line CKT 1, near CHAVES_CNTY6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_180_P1_CHAVES_CNTY6 | Apply 3-phase fault on SN_JUAN_TAP6 to CHAVES_CNTY6 230kV line CKT 1, near CHAVES_CNTY6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_180_P1_CHAVES_CNTY6 | Apply 3-phase fault on SN_JUAN_TAP6 to CHAVES_CNTY6 230kV line CKT 1, near CHAVES_CNTY6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_180_P1_CHAVES_CNTY6 | Apply 3-phase fault on SN_JUAN_TAP6 to CHAVES_CNTY6 230kV line CKT 1, near CHAVES_CNTY6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_181_P1_CROSSROADS7 | Apply 3-phase fault on TOLK to CROSSROADS 7 345kV line CKT 1, near CROSSROADS 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes | Note: Abnormal oscillations were observed in the generation units and system responses, which are attributed to the OECGT generation units modeling issues. When the OECGT units were GENETed these oscillations were mitigated.
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_181_P1_CROSSROADS7 | Apply 3-phase fault on TOLK to CROSSROADS 7 345kV line CKT 1, near CROSSROADS 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | No | LVRT VIOL - - ROOSWND-GEN2[2] ROOSWND-GEN1[1] G08-022-GEN3[1]. ROOSWND-GEN2[2], ROOSWND-GEN1[1], and G08-022-GEN3[1] tripped on voltage protection setting 1.20pu-0.08s (embedded in the user model). The protection setting was disabled and simulation was rerun. No further issues were observed.
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_181_P1_CROSSROADS7 | Apply 3-phase fault on TOLK to CROSSROADS 7 345kV line CKT 1, near CROSSROADS 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.41pu, MaxDur: 0.08s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_181_P1_CROSSROADS7 | Apply 3-phase fault on TOLK to CROSSROADS 7 345kV line CKT 1, near CROSSROADS 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.22pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_182_P1_CROSSROADS7 | Apply 3-phase fault on CROSSROADS 7 to EDDY_CNTY 345kV line CKT 1, near CROSSROADS 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Note: Abnormal oscillations were observed in the generation units and system responses, which are attributed to the OECGT generation units modeling issues. When the OECGT units were GENETed these oscillations were mitigated. Voltage Spike: 1.21pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_182_P1_CROSSROADS7 | Apply 3-phase fault on CROSSROADS 7 to EDDY_CNTY 345kV line CKT 1, near CROSSROADS 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_182_P1_CROSSROADS7 | Apply 3-phase fault on CROSSROADS 7 to EDDY_CNTY 345kV line CKT 1, near CROSSROADS 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.22pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_182_P1_CROSSROADS7 | Apply 3-phase fault on CROSSROADS 7 to EDDY_CNTY 345kV line CKT 1, near CROSSROADS 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.23pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_183_P1_CROSSROADS7 | Apply 3-phase fault on CROSSROADS 7 345kV/765kV transformer CKT 2, near CROSSROADS 7 345kV for 6 cycles. Clear fault by tripping the faulted Two Winding. | P1 | Stable | Yes | No | No | Yes | Yes | No | LVRT VIOL - - A11-002-GEN1[1] A11-002-GEN1[2] G1140G1204G2[1] FRISCO_WND 3[1] G1140G1204G1[1]. Undamped oscillations were observed in conventional units angles and powers, renewable units powers and system voltage responses. In addition several units tripped under this contingency. Simulation was rerun with the SVC mitigation solution and the protection settings disabled. No further issues were observed. | ±600 MVAr SVC at Crossroad 765kV
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_183_P1_CROSSROADS7 | Apply 3-phase fault on CROSSROADS 7 345kV/765kV transformer CKT 2, near CROSSROADS 7 345kV for 6 cycles. Clear fault by tripping the faulted Two Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Note: Abnormal oscillations were observed in the generation units and system responses, which are attributed to the OECGT generation units modeling issues. When the OECGT units were GENETed these oscillations were mitigated. Voltage Spike: 1.23pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_183_P1_CROSSROADS7 | Apply 3-phase fault on CROSSROADS 7 345kV/765kV transformer CKT 2, near CROSSROADS 7 345kV for 6 cycles. Clear fault by tripping the faulted Two Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.22pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_183_P1_CROSSROADS7 | Apply 3-phase fault on CROSSROADS 7 345kV/765kV transformer CKT 2, near CROSSROADS 7 345kV for 6 cycles. Clear fault by tripping the faulted Two Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.27pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_184_P1_EDDY_STH | Apply 3-phase fault on EDDY_STH to CV-DAYTON +3 115kV line CKT 1, near EDDY_STH 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_184_P1_EDDY_STH | Apply 3-phase fault on EDDY_STH to CV-DAYTON +3 115kV line CKT 1, near EDDY_STH 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_184_P1_EDDY_STH | Apply 3-phase fault on EDDY_STH to CV-DAYTON +3 115kV line CKT 1, near EDDY_STH 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_184_P1_EDDY_STH | Apply 3-phase fault on EDDY_STH to CV-DAYTON +3 115kV line CKT 1, near EDDY_STH 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_185_P1_EDDY_STH | Apply 3-phase fault on EDDY_STH to PECOS 115kV line CKT 1, near EDDY_STH 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_185_P1_EDDY_STH | Apply 3-phase fault on EDDY_STH to PECOS 115kV line CKT 1, near EDDY_STH 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_185_P1_EDDY_STH | Apply 3-phase fault on EDDY_STH to PECOS 115kV line CKT 1, near EDDY_STH 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_185_P1_EDDY_STH | Apply 3-phase fault on EDDY_STH to PECOS 115kV line CKT 1, near EDDY_STH 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_186_P1_EDDY_NTH | Apply 3-phase fault on EAGLE_CREEK3 to EDDY_NTH 115kV line CKT 1, near EDDY_NTH 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_186_P1_EDDY_NTH | Apply 3-phase fault on EAGLE_CREEK3 to EDDY_NTH 115kV line CKT 1, near EDDY_NTH 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_186_P1_EDDY_NTH | Apply 3-phase fault on EAGLE_CREEK3 to EDDY_NTH 115kV line CKT 1, near EDDY_NTH 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_186_P1_EDDY_NTH | Apply 3-phase fault on EAGLE_CREEK3 to EDDY_NTH 115kV line CKT 1, near EDDY_NTH 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_187_P1_EDDY_NORTH6 | Apply 3-phase fault on CHAVES_CNTY6 to EDDY_NORTH 6 230kV line CKT 1, near EDDY_NORTH 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_187_P1_EDDY_NORTH6 | Apply 3-phase fault on CHAVES_CNTY6 to EDDY_NORTH 6 230kV line CKT 1, near EDDY_NORTH 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_187_P1_EDDY_NORTH6 | Apply 3-phase fault on CHAVES_CNTY6 to EDDY_NORTH 6 230kV line CKT 1, near EDDY_NORTH 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_187_P1_EDDY_NORTH6 | Apply 3-phase fault on CHAVES_CNTY6 to EDDY_NORTH 6 230kV line CKT 1, near EDDY_NORTH 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_188_P1_EDDY_NORTH6 | Apply 3-phase fault on EDDY_NORTH 6 to 7-RIVERS 230kV line CKT 1, near EDDY_NORTH 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_188_P1_EDDY_NORTH6 | Apply 3-phase fault on EDDY_NORTH 6 to 7-RIVERS 230kV line CKT 1, near EDDY_NORTH 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_188_P1_EDDY_NORTH6 | Apply 3-phase fault on EDDY_NORTH 6 to 7-RIVERS 230kV line CKT 1, near EDDY_NORTH 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_188_P1_EDDY_NORTH6 | Apply 3-phase fault on EDDY_NORTH 6 to 7-RIVERS 230kV line CKT 1, near EDDY_NORTH 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_189_P1_EDDY_NORTH6 | Apply 3-phase fault on EDDY_NORTH 6 to CUNNIGHM_N 6 230kV line CKT 1, near EDDY_NORTH 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_189_P1_EDDY_NORTH6 | Apply 3-phase fault on EDDY_NORTH 6 to CUNNIGHM_N 6 230kV line CKT 1, near EDDY_NORTH 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_189_P1_EDDY_NORTH6 | Apply 3-phase fault on EDDY_NORTH 6 to CUNNIGHM_N 6 230kV line CKT 1, near EDDY_NORTH 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_189_P1_EDDY_NORTH6 | Apply 3-phase fault on EDDY_NORTH 6 to CUNNIGHM_N 6 230kV line CKT 1, near EDDY_NORTH 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_19_P1_HITCHLAND | Apply 3-phase fault on HITCHLD_TR21 13.19kV/230kV/345kV transformer CKT 2, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_19_P1_HITCHLAND | Apply 3-phase fault on HITCHLD_TR21 13.19kV/230kV/345kV transformer CKT 2, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_19_P1_HITCHLAND | Apply 3-phase fault on HITCHLD_TR21 13.19kV/230kV/345kV transformer CKT 2, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_19_P1_HITCHLAND | Apply 3-phase fault on HITCHLD_TR21 13.19kV/230kV/345kV transformer CKT 2, near HITCHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.21pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_190_P1_EDDY_CNTY | Apply 3-phase fault on EDDY_TR 13.19kV/230kV/345kV transformer CKT 1, near EDDY_CNTY 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.00s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_190_P1_EDDY_CNTY | Apply 3-phase fault on EDDY_TR 13.19kV/230kV/345kV transformer CKT 1, near EDDY_CNTY 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.26pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_190_P1_EDDY_CNTY | Apply 3-phase fault on EDDY_TR 13.19kV/230kV/345kV transformer CKT 1, near EDDY_CNTY 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.24pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_190_P1_EDDY_CNTY | Apply 3-phase fault on EDDY_TR 13.19kV/230kV/345kV transformer CKT 1, near EDDY_CNTY 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | No | No | Yes | Voltage Spike: 1.25pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_191_P1_EDDY_CNTY | Apply 3-phase fault on EDDY_CNTY to KIOWA 345kV line CKT 1, near EDDY_CNTY 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_191_P1_EDDY_CNTY | Apply 3-phase fault on EDDY_CNTY to KIOWA 345kV line CKT 1, near EDDY_CNTY 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.24pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_191_P1_EDDY_CNTY | Apply 3-phase fault on EDDY_CNTY to KIOWA 345kV line CKT 1, near EDDY_CNTY 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_191_P1_EDDY_CNTY | Apply 3-phase fault on EDDY_CNTY to KIOWA 345kV line CKT 1, near EDDY_CNTY 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.25pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_192_P1_CUNNINHAM | Apply 3-phase fault on CUNNINHAM to BUCKEYE_TP 3 115kV line CKT 1, near CUNNINHAM 115kV for 7 cycles. Open the faulted line and LE-SANANDRS3 115kV/69kV transformer CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and LE-SANANDRS3 115kV/69kV transformer CKT 1. Re-open the faulted line after 7 cycles% LE-SANANDRS3 115kV/69kV transformer CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_192_P1_CUNNINHAM | Apply 3-phase fault on CUNNINHAM to BUCKEYE_TP 3 115kV line CKT 1, near CUNNINHAM 115kV for 7 cycles. Open the faulted line and LE-SANANDRS3 115kV/69kV transformer CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and LE-SANANDRS3 115kV/69kV transformer CKT 1. Re-open the faulted line after 7 cycles% LE-SANANDRS3 115kV/69kV transformer CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_192_P1_CUNNINHAM | Apply 3-phase fault on CUNNINHAM to BUCKEYE_TP 3 115kV line CKT 1, near CUNNINHAM 115kV for 7 cycles. Open the faulted line and LE-SANANDRS3 115kV/69kV transformer CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and LE-SANANDRS3 115kV/69kV transformer CKT 1. Re-open the faulted line after 7 cycles% LE-SANANDRS3 115kV/69kV transformer CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_192_P1_CUNNINHAM | Apply 3-phase fault on CUNNINHAM to BUCKEYE_TP 3 115kV line CKT 1, near CUNNINHAM 115kV for 7 cycles. Open the faulted line and LE-SANANDRS3 115kV/69kV transformer CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and LE-SANANDRS3 115kV/69kV transformer CKT 1. Re-open the faulted line after 7 cycles% LE-SANANDRS3 115kV/69kV transformer CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | No | No | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_193_P1_CUNNINHAM | Apply 3-phase fault on CUNNINHAM to MADDOX 115kV line CKT 1, near CUNNINHAM 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_193_P1_CUNNINHAM | Apply 3-phase fault on CUNNINHAM to MADDOX 115kV line CKT 1, near CUNNINHAM 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_193_P1_CUNNINHAM | Apply 3-phase fault on CUNNINHAM to MADDOX 115kV line CKT 1, near CUNNINHAM 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_193_P1_CUNNINHAM | Apply 3-phase fault on CUNNINHAM to MADDOX 115kV line CKT 1, near CUNNINHAM 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_194_P1_CUNNINHAM | Apply 3-phase fault on RDRNNER_TR11 13.19kV/115kV/345kV transformer CKT 1, near CUNNINHAM 115kV for 7 cycles. Open the faulted Three Winding and CUNNINHAM to MONUMNT_TP 3 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.28pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_194_P1_CUNNINHAM | Apply 3-phase fault on RDRNNER_TR11 13.19kV/115kV/345kV transformer CKT 1, near CUNNINHAM 115kV for 7 cycles. Open the faulted Three Winding and CUNNINHAM to MONUMNT_TP 3 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.26pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_194_P1_CUNNINHAM | Apply 3-phase fault on RDRNNER_TR11 13.19kV/115kV/345kV transformer CKT 1, near CUNNINHAM 115kV for 7 cycles. Open the faulted Three Winding and CUNNINHAM to MONUMNT_TP 3 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.28pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_194_P1_CUNNINHAM | Apply 3-phase fault on RDRNNER_TR11 13.19kV/115kV/345kV transformer CKT 1, near CUNNINHAM 115kV for 7 cycles. Open the faulted Three Winding and CUNNINHAM to MONUMNT_TP 3 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.31pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_195_P1_CUNNINHAM | Apply 3-phase fault on CUNNHM_TR1 1 13.19kV/115kV/230kV transformer CKT 1, near CUNNINHAM 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_195_P1_CUNNINHAM | Apply 3-phase fault on CUNNHM_TR1 1 13.19kV/115kV/230kV transformer CKT 1, near CUNNINHAM 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_195_P1_CUNNINHAM | Apply 3-phase fault on CUNNHM_TR1 1 13.19kV/115kV/230kV transformer CKT 1, near CUNNINHAM 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_195_P1_CUNNINHAM | Apply 3-phase fault on CUNNHM_TR1 1 13.19kV/115kV/230kV transformer CKT 1, near CUNNINHAM 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | No | No | Yes | Voltage Spike: 1.23pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_196_P1_CUNNINHAM | Apply 3-phase fault on CUNNINHAM to HOBBS_INT 115kV line CKT 1, near CUNNINHAM 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_196_P1_CUNNINHAM | Apply 3-phase fault on CUNNINHAM to HOBBS_INT 115kV line CKT 1, near CUNNINHAM 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_196_P1_CUNNINHAM | Apply 3-phase fault on CUNNINHAM to HOBBS_INT 115kV line CKT 1, near CUNNINHAM 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_196_P1_CUNNINHAM | Apply 3-phase fault on CUNNINHAM to HOBBS_INT 115kV line CKT 1, near CUNNINHAM 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_197_P1_CUNNINHAM | Apply 3-phase fault on CUNNINHAM to QUAHADA 115kV line CKT 1, near CUNNINHAM 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_197_P1_CUNNINHAM | Apply 3-phase fault on CUNNINHAM to QUAHADA 115kV line CKT 1, near CUNNINHAM 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_197_P1_CUNNINHAM | Apply 3-phase fault on CUNNINHAM to QUAHADA 115kV line CKT 1, near CUNNINHAM 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_197_P1_CUNNINHAM | Apply 3-phase fault on CUNNINHAM to QUAHADA 115kV line CKT 1, near CUNNINHAM 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_198_P1_CUNNIGHM_N6 | Apply 3-phase fault on EDDY_NORTH 6 to CUNNIGHM_N 6 230kV line CKT 1, near CUNNIGHM_N 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Unstable | No | No | No | No | Yes | No | Angular and system instability was observed in the G6 region. The stability issue was resolved with the SVC mitigation solution. | ±600 MVAr SVC at Crossroad 765kV
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_198_P1_CUNNIGHM_N6 | Apply 3-phase fault on EDDY_NORTH 6 to CUNNIGHM_N 6 230kV line CKT 1, near CUNNIGHM_N 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_198_P1_CUNNIGHM_N6 | Apply 3-phase fault on EDDY_NORTH 6 to CUNNIGHM_N 6 230kV line CKT 1, near CUNNIGHM_N 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_198_P1_CUNNIGHM_N6 | Apply 3-phase fault on EDDY_NORTH 6 to CUNNIGHM_N 6 230kV line CKT 1, near CUNNIGHM_N 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes | Voltage Spike: 1.22pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_199_P1_CUNNIGHM_N6 | Apply 3-phase fault on CUNNIGHM_N 6 to POTASH_JCT 6 230kV line CKT 1, near CUNNIGHM_N 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Unstable | No | No | No | No | Yes | No | Angular and system instability was observed in the G6 region. The stability issue was resolved with the SVC mitigation solution. | ±600 MVAr SVC at Crossroad 765kV
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_199_P1_CUNNIGHM_N6 | Apply 3-phase fault on CUNNIGHM_N 6 to POTASH_JCT 6 230kV line CKT 1, near CUNNIGHM_N 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_199_P1_CUNNIGHM_N6 | Apply 3-phase fault on CUNNIGHM_N 6 to POTASH_JCT 6 230kV line CKT 1, near CUNNIGHM_N 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_199_P1_CUNNIGHM_N6 | Apply 3-phase fault on CUNNIGHM_N 6 to POTASH_JCT 6 230kV line CKT 1, near CUNNIGHM_N 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.22pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_2_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Unstable | No | No | No | No | No | No | Angular and system instability was observed in the G6 region. Simulation was rerun with the Crossroad SVC. Initially the ±600 MVAr SVC at Crossroad 765kV option was tested. It was observed that the Crossroad 765kV SVC cannot resolve the problem even with reclosing disabled and reduced fault clearing time of 3 cycles (default 6 cycles). Next, other reactive power support options were investegated. No stability or damping issues were observed with the ±600 MVAr SVC at Crossroad and +600/-700 MVAr SVC at Seminole with fault reclosing disabled (default fault clearing time of 6 cycles). (Note: the Seminole SVC option is identical to the Crawfish SVC in terms of power flow and dynamic parameters, and it replaces the provided switched shunt/reactor at the station) max post-fault s.s. voltage: 1.11pu | Build a new Crawfish Draw 765/345kV Substation tapping the Tuco to Border 345kV Ckt 1 and Tuco to OKU 345kV Ckt 1. Both the 765kV and the 345kV Crawfish Draw switchyards shall be constructed with breaker and a half bus schemes. Furthermore, interconnected double circuit lines connected to these switchyards or transformers connecting these switchyards shall not share adjacent breakers in the switchyard(s). ±600 MVAr SVC at Crossroad 765kV & +600/-700 MVAr SVC at Seminole 765kV (w/o reclosing)
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_2_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | No | No | No | No | LVRT VIOL - - G17-065-GEN2[1]. G17-065-GEN2[1] tripped on voltage protection setting 1.22pu-0.08s. The protection setting was disabled and simulation was rerun. No further issues were observed. TOV: MaxV: 1.28pu, MaxDur: 0.10s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_2_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.25pu, MaxDur: 0.05s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_2_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.24pu, MaxDur: 0.05s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_20_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to CARPENTER 345kV line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_20_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to CARPENTER 345kV line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - FRISCO_WND 3[1].
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_20_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to CARPENTER 345kV line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_20_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to CARPENTER 345kV line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_200_P1_CUNNIGHM_S6 | Apply 3-phase fault on CUNNHM_TR1 1 13.19kV/115kV/230kV transformer CKT 1, near CUNNIGHM_S 6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_200_P1_CUNNIGHM_S6 | Apply 3-phase fault on CUNNHM_TR1 1 13.19kV/115kV/230kV transformer CKT 1, near CUNNIGHM_S 6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_200_P1_CUNNIGHM_S6 | Apply 3-phase fault on CUNNHM_TR1 1 13.19kV/115kV/230kV transformer CKT 1, near CUNNIGHM_S 6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_200_P1_CUNNIGHM_S6 | Apply 3-phase fault on CUNNHM_TR1 1 13.19kV/115kV/230kV transformer CKT 1, near CUNNIGHM_S 6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | No | No | Yes | Voltage Spike: 1.23pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_201_P1_HOBBS_INT | Apply 3-phase fault on HOBBS_INT to BENSING 115kV line CKT 1, near HOBBS_INT 115kV for 7 cycles. Open the faulted line and JOHNSON_DRW3 to HIGG 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and JOHNSON_DRW3 to HIGG 115kV line CKT 1. Re-open the faulted line after 7 cycles% JOHNSON_DRW3 to HIGG 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_201_P1_HOBBS_INT | Apply 3-phase fault on HOBBS_INT to BENSING 115kV line CKT 1, near HOBBS_INT 115kV for 7 cycles. Open the faulted line and JOHNSON_DRW3 to HIGG 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and JOHNSON_DRW3 to HIGG 115kV line CKT 1. Re-open the faulted line after 7 cycles% JOHNSON_DRW3 to HIGG 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_201_P1_HOBBS_INT | Apply 3-phase fault on HOBBS_INT to BENSING 115kV line CKT 1, near HOBBS_INT 115kV for 7 cycles. Open the faulted line and JOHNSON_DRW3 to HIGG 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and JOHNSON_DRW3 to HIGG 115kV line CKT 1. Re-open the faulted line after 7 cycles% JOHNSON_DRW3 to HIGG 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_201_P1_HOBBS_INT | Apply 3-phase fault on HOBBS_INT to BENSING 115kV line CKT 1, near HOBBS_INT 115kV for 7 cycles. Open the faulted line and JOHNSON_DRW3 to HIGG 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and JOHNSON_DRW3 to HIGG 115kV line CKT 1. Re-open the faulted line after 7 cycles% JOHNSON_DRW3 to HIGG 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_202_P1_HOBBS_INT | Apply 3-phase fault on HOBBS_INT to MADDOX 115kV line CKT 1, near HOBBS_INT 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_202_P1_HOBBS_INT | Apply 3-phase fault on HOBBS_INT to MADDOX 115kV line CKT 1, near HOBBS_INT 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_202_P1_HOBBS_INT | Apply 3-phase fault on HOBBS_INT to MADDOX 115kV line CKT 1, near HOBBS_INT 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_202_P1_HOBBS_INT | Apply 3-phase fault on HOBBS_INT to MADDOX 115kV line CKT 1, near HOBBS_INT 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_203_P1_HOBBS_INT | Apply 3-phase fault on HOBBS_INT to MILLEN 115kV line CKT 1, near HOBBS_INT 115kV for 7 cycles. Open the faulted line and TAYLOR to NE_HOBBS 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and TAYLOR to NE_HOBBS 115kV line CKT 1. Re-open the faulted line after 7 cycles% TAYLOR to NE_HOBBS 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_203_P1_HOBBS_INT | Apply 3-phase fault on HOBBS_INT to MILLEN 115kV line CKT 1, near HOBBS_INT 115kV for 7 cycles. Open the faulted line and TAYLOR to NE_HOBBS 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and TAYLOR to NE_HOBBS 115kV line CKT 1. Re-open the faulted line after 7 cycles% TAYLOR to NE_HOBBS 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_203_P1_HOBBS_INT | Apply 3-phase fault on HOBBS_INT to MILLEN 115kV line CKT 1, near HOBBS_INT 115kV for 7 cycles. Open the faulted line and TAYLOR to NE_HOBBS 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and TAYLOR to NE_HOBBS 115kV line CKT 1. Re-open the faulted line after 7 cycles% TAYLOR to NE_HOBBS 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_203_P1_HOBBS_INT | Apply 3-phase fault on HOBBS_INT to MILLEN 115kV line CKT 1, near HOBBS_INT 115kV for 7 cycles. Open the faulted line and TAYLOR to NE_HOBBS 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and TAYLOR to NE_HOBBS 115kV line CKT 1. Re-open the faulted line after 7 cycles% TAYLOR to NE_HOBBS 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_204_P1_HOBBS_INT | Apply 3-phase fault on HOBBS_INT to GAINESGENTP6 230kV line CKT 1, near HOBBS_INT 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_204_P1_HOBBS_INT | Apply 3-phase fault on HOBBS_INT to GAINESGENTP6 230kV line CKT 1, near HOBBS_INT 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | No | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_204_P1_HOBBS_INT | Apply 3-phase fault on HOBBS_INT to GAINESGENTP6 230kV line CKT 1, near HOBBS_INT 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_204_P1_HOBBS_INT | Apply 3-phase fault on HOBBS_INT to GAINESGENTP6 230kV line CKT 1, near HOBBS_INT 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | No | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_205_P1_HOBBS_INT | Apply 3-phase fault on HOBBS_INT 230kV/13.19kV/345kV transformer CKT 1, near HOBBS_INT 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_205_P1_HOBBS_INT | Apply 3-phase fault on HOBBS_INT 230kV/13.19kV/345kV transformer CKT 1, near HOBBS_INT 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_205_P1_HOBBS_INT | Apply 3-phase fault on HOBBS_INT 230kV/13.19kV/345kV transformer CKT 1, near HOBBS_INT 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_205_P1_HOBBS_INT | Apply 3-phase fault on HOBBS_INT 230kV/13.19kV/345kV transformer CKT 1, near HOBBS_INT 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.22pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_206_P1_HOBBS_INT | Apply 3-phase fault on HOBBS_TR2 13.19kV/115kV/230kV transformer CKT 2, near HOBBS_INT 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_206_P1_HOBBS_INT | Apply 3-phase fault on HOBBS_TR2 13.19kV/115kV/230kV transformer CKT 2, near HOBBS_INT 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_206_P1_HOBBS_INT | Apply 3-phase fault on HOBBS_TR2 13.19kV/115kV/230kV transformer CKT 2, near HOBBS_INT 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_206_P1_HOBBS_INT | Apply 3-phase fault on HOBBS_TR2 13.19kV/115kV/230kV transformer CKT 2, near HOBBS_INT 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | No | No | Yes | Voltage Spike: 1.22pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_207_P1_HOBBS_INT | Apply 3-phase fault on CUNNIGHM_S 6 to HOBBS_INT 230kV line CKT 1, near HOBBS_INT 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_207_P1_HOBBS_INT | Apply 3-phase fault on CUNNIGHM_S 6 to HOBBS_INT 230kV line CKT 1, near HOBBS_INT 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_207_P1_HOBBS_INT | Apply 3-phase fault on CUNNIGHM_S 6 to HOBBS_INT 230kV line CKT 1, near HOBBS_INT 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_207_P1_HOBBS_INT | Apply 3-phase fault on CUNNIGHM_S 6 to HOBBS_INT 230kV line CKT 1, near HOBBS_INT 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.08s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_208_P1_HOBBS_INT | Apply 3-phase fault on INK_BASIN to HOBBS_INT 230kV line CKT 1, near HOBBS_INT 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_208_P1_HOBBS_INT | Apply 3-phase fault on INK_BASIN to HOBBS_INT 230kV line CKT 1, near HOBBS_INT 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_208_P1_HOBBS_INT | Apply 3-phase fault on INK_BASIN to HOBBS_INT 230kV line CKT 1, near HOBBS_INT 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_208_P1_HOBBS_INT | Apply 3-phase fault on INK_BASIN to HOBBS_INT 230kV line CKT 1, near HOBBS_INT 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | No | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_209_P1_POTASH_JCT3 | Apply 3-phase fault on POTASH_JCT 3 to CARLSBAD 115kV line CKT 1, near POTASH_JCT 3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.22pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_209_P1_POTASH_JCT3 | Apply 3-phase fault on POTASH_JCT 3 to CARLSBAD 115kV line CKT 1, near POTASH_JCT 3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.23pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_209_P1_POTASH_JCT3 | Apply 3-phase fault on POTASH_JCT 3 to CARLSBAD 115kV line CKT 1, near POTASH_JCT 3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_209_P1_POTASH_JCT3 | Apply 3-phase fault on POTASH_JCT 3 to CARLSBAD 115kV line CKT 1, near POTASH_JCT 3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes | Voltage Spike: 1.26pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_21_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to NOVUS1 345kV line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_21_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to NOVUS1 345kV line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_21_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to NOVUS1 345kV line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1] G17-100-GEN1[1]. G17-100-GEN1[1] tripped on voltage protection setting 1.241pu-0.001s. The protection setting was disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_21_P1_HITCHLAND | Apply 3-phase fault on HITCHLAND to NOVUS1 345kV line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.21pu, MaxDur: 0.00s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_210_P1_POTASH_JCT3 | Apply 3-phase fault on PCA to POTASH_JCT 3 115kV line CKT 1, near POTASH_JCT 3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.22pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_210_P1_POTASH_JCT3 | Apply 3-phase fault on PCA to POTASH_JCT 3 115kV line CKT 1, near POTASH_JCT 3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.23pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_210_P1_POTASH_JCT3 | Apply 3-phase fault on PCA to POTASH_JCT 3 115kV line CKT 1, near POTASH_JCT 3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.22pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_210_P1_POTASH_JCT3 | Apply 3-phase fault on PCA to POTASH_JCT 3 115kV line CKT 1, near POTASH_JCT 3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes | Voltage Spike: 1.26pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_211_P1_POTASH_JCT3 | Apply 3-phase fault on POTASH_JCT 3 to INTREPDW_TP3 115kV line CKT 1, near POTASH_JCT 3 115kV for 7 cycles. Open the faulted line and SAGE_BRUSH 3 to CARDINAL 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and SAGE_BRUSH 3 to CARDINAL 115kV line CKT 1. Re-open the faulted line after 7 cycles% SAGE_BRUSH 3 to CARDINAL 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.24pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_211_P1_POTASH_JCT3 | Apply 3-phase fault on POTASH_JCT 3 to INTREPDW_TP3 115kV line CKT 1, near POTASH_JCT 3 115kV for 7 cycles. Open the faulted line and SAGE_BRUSH 3 to CARDINAL 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and SAGE_BRUSH 3 to CARDINAL 115kV line CKT 1. Re-open the faulted line after 7 cycles% SAGE_BRUSH 3 to CARDINAL 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.25pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_211_P1_POTASH_JCT3 | Apply 3-phase fault on POTASH_JCT 3 to INTREPDW_TP3 115kV line CKT 1, near POTASH_JCT 3 115kV for 7 cycles. Open the faulted line and SAGE_BRUSH 3 to CARDINAL 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and SAGE_BRUSH 3 to CARDINAL 115kV line CKT 1. Re-open the faulted line after 7 cycles% SAGE_BRUSH 3 to CARDINAL 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.22pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_211_P1_POTASH_JCT3 | Apply 3-phase fault on POTASH_JCT 3 to INTREPDW_TP3 115kV line CKT 1, near POTASH_JCT 3 115kV for 7 cycles. Open the faulted line and SAGE_BRUSH 3 to CARDINAL 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and SAGE_BRUSH 3 to CARDINAL 115kV line CKT 1. Re-open the faulted line after 7 cycles% SAGE_BRUSH 3 to CARDINAL 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes | Voltage Spike: 1.27pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_212_P1_POTASH_JCT6 | Apply 3-phase fault on POTASH_JCT 6 to PECOS 230kV line CKT 1, near POTASH_JCT 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_212_P1_POTASH_JCT6 | Apply 3-phase fault on POTASH_JCT 6 to PECOS 230kV line CKT 1, near POTASH_JCT 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_212_P1_POTASH_JCT6 | Apply 3-phase fault on POTASH_JCT 6 to PECOS 230kV line CKT 1, near POTASH_JCT 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_212_P1_POTASH_JCT6 | Apply 3-phase fault on POTASH_JCT 6 to PECOS 230kV line CKT 1, near POTASH_JCT 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_213_P1_POTASH_JCT6 | Apply 3-phase fault on POTASH_TR1 1 13.19kV/115kV/230kV transformer CKT 1, near POTASH_JCT 6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_213_P1_POTASH_JCT6 | Apply 3-phase fault on POTASH_TR1 1 13.19kV/115kV/230kV transformer CKT 1, near POTASH_JCT 6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_213_P1_POTASH_JCT6 | Apply 3-phase fault on POTASH_TR1 1 13.19kV/115kV/230kV transformer CKT 1, near POTASH_JCT 6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_213_P1_POTASH_JCT6 | Apply 3-phase fault on POTASH_TR1 1 13.19kV/115kV/230kV transformer CKT 1, near POTASH_JCT 6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_214_P1_KIOWA | Apply 3-phase fault on RDRNNER_TR11 13.19kV/115kV/345kV transformer CKT 1, near KIOWA 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_214_P1_KIOWA | Apply 3-phase fault on RDRNNER_TR11 13.19kV/115kV/345kV transformer CKT 1, near KIOWA 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_214_P1_KIOWA | Apply 3-phase fault on RDRNNER_TR11 13.19kV/115kV/345kV transformer CKT 1, near KIOWA 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_214_P1_KIOWA | Apply 3-phase fault on RDRNNER_TR11 13.19kV/115kV/345kV transformer CKT 1, near KIOWA 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_215_P1_KIOWA | Apply 3-phase fault on KIOWA to N_LOVING 345kV line CKT 1, near KIOWA 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_215_P1_KIOWA | Apply 3-phase fault on KIOWA to N_LOVING 345kV line CKT 1, near KIOWA 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_215_P1_KIOWA | Apply 3-phase fault on KIOWA to N_LOVING 345kV line CKT 1, near KIOWA 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_215_P1_KIOWA | Apply 3-phase fault on KIOWA to N_LOVING 345kV line CKT 1, near KIOWA 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_216_P1_KIOWA | Apply 3-phase fault on KIOWA_TR1 13.19kV/345kV/115kV transformer CKT 1, near KIOWA 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_216_P1_KIOWA | Apply 3-phase fault on KIOWA_TR1 13.19kV/345kV/115kV transformer CKT 1, near KIOWA 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_216_P1_KIOWA | Apply 3-phase fault on KIOWA_TR1 13.19kV/345kV/115kV transformer CKT 1, near KIOWA 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_216_P1_KIOWA | Apply 3-phase fault on KIOWA_TR1 13.19kV/345kV/115kV transformer CKT 1, near KIOWA 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | No | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_217_P1_KIOWA | Apply 3-phase fault on EDDY_CNTY to KIOWA 345kV line CKT 1, near KIOWA 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_217_P1_KIOWA | Apply 3-phase fault on EDDY_CNTY to KIOWA 345kV line CKT 1, near KIOWA 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_217_P1_KIOWA | Apply 3-phase fault on EDDY_CNTY to KIOWA 345kV line CKT 1, near KIOWA 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_217_P1_KIOWA | Apply 3-phase fault on EDDY_CNTY to KIOWA 345kV line CKT 1, near KIOWA 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_218_P1_7-RIVERS | Apply 3-phase fault on EDDY_NORTH 6 to 7-RIVERS 230kV line CKT 1, near 7-RIVERS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_218_P1_7-RIVERS | Apply 3-phase fault on EDDY_NORTH 6 to 7-RIVERS 230kV line CKT 1, near 7-RIVERS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_218_P1_7-RIVERS | Apply 3-phase fault on EDDY_NORTH 6 to 7-RIVERS 230kV line CKT 1, near 7-RIVERS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_218_P1_7-RIVERS | Apply 3-phase fault on EDDY_NORTH 6 to 7-RIVERS 230kV line CKT 1, near 7-RIVERS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_219_P1_7-RIVERS | Apply 3-phase fault on 7-RIVER_TR11 13.19kV/115kV/230kV transformer CKT 1, near 7-RIVERS 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_219_P1_7-RIVERS | Apply 3-phase fault on 7-RIVER_TR11 13.19kV/115kV/230kV transformer CKT 1, near 7-RIVERS 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_219_P1_7-RIVERS | Apply 3-phase fault on 7-RIVER_TR11 13.19kV/115kV/230kV transformer CKT 1, near 7-RIVERS 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_219_P1_7-RIVERS | Apply 3-phase fault on 7-RIVER_TR11 13.19kV/115kV/230kV transformer CKT 1, near 7-RIVERS 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_22_P1_HITCHLAND | Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_22_P1_HITCHLAND | Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_22_P1_HITCHLAND | Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_22_P1_HITCHLAND | Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV line CKT 1, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_220_P1_7-RIVERS | Apply 3-phase fault on 7-RIVERS to PECOS 230kV line CKT 1, near 7-RIVERS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_220_P1_7-RIVERS | Apply 3-phase fault on 7-RIVERS to PECOS 230kV line CKT 1, near 7-RIVERS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_220_P1_7-RIVERS | Apply 3-phase fault on 7-RIVERS to PECOS 230kV line CKT 1, near 7-RIVERS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_220_P1_7-RIVERS | Apply 3-phase fault on 7-RIVERS to PECOS 230kV line CKT 1, near 7-RIVERS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_221_P1_PECOS | Apply 3-phase fault on CARLSBAD to PECOS 115kV line CKT 1, near PECOS 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_221_P1_PECOS | Apply 3-phase fault on CARLSBAD to PECOS 115kV line CKT 1, near PECOS 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_221_P1_PECOS | Apply 3-phase fault on CARLSBAD to PECOS 115kV line CKT 1, near PECOS 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_221_P1_PECOS | Apply 3-phase fault on CARLSBAD to PECOS 115kV line CKT 1, near PECOS 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_222_P1_PECOS | Apply 3-phase fault on PECOS_TR1 13.19kV/115kV/230kV transformer CKT 1, near PECOS 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_222_P1_PECOS | Apply 3-phase fault on PECOS_TR1 13.19kV/115kV/230kV transformer CKT 1, near PECOS 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_222_P1_PECOS | Apply 3-phase fault on PECOS_TR1 13.19kV/115kV/230kV transformer CKT 1, near PECOS 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_222_P1_PECOS | Apply 3-phase fault on PECOS_TR1 13.19kV/115kV/230kV transformer CKT 1, near PECOS 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_223_P1_PECOS | Apply 3-phase fault on 7-RIVERS to PECOS 230kV line CKT 1, near PECOS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_223_P1_PECOS | Apply 3-phase fault on 7-RIVERS to PECOS 230kV line CKT 1, near PECOS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_223_P1_PECOS | Apply 3-phase fault on 7-RIVERS to PECOS 230kV line CKT 1, near PECOS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_223_P1_PECOS | Apply 3-phase fault on 7-RIVERS to PECOS 230kV line CKT 1, near PECOS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_224_P1_N_LOVING | Apply 3-phase fault on NORTH_LOVNG3 115kV/345kV/13.19kV transformer CKT 1, near N_LOVING 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.23pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_224_P1_N_LOVING | Apply 3-phase fault on NORTH_LOVNG3 115kV/345kV/13.19kV transformer CKT 1, near N_LOVING 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.23pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_224_P1_N_LOVING | Apply 3-phase fault on NORTH_LOVNG3 115kV/345kV/13.19kV transformer CKT 1, near N_LOVING 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.22pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_224_P1_N_LOVING | Apply 3-phase fault on NORTH_LOVNG3 115kV/345kV/13.19kV transformer CKT 1, near N_LOVING 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | No | No | Yes | Voltage Spike: 1.27pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_225_P1_N_LOVING | Apply 3-phase fault on N_LOVING to CHINA_DRAW 7 345kV line CKT 1, near N_LOVING 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.22pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_225_P1_N_LOVING | Apply 3-phase fault on N_LOVING to CHINA_DRAW 7 345kV line CKT 1, near N_LOVING 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.23pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_225_P1_N_LOVING | Apply 3-phase fault on N_LOVING to CHINA_DRAW 7 345kV line CKT 1, near N_LOVING 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes | Voltage Spike: 1.22pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_225_P1_N_LOVING | Apply 3-phase fault on N_LOVING to CHINA_DRAW 7 345kV line CKT 1, near N_LOVING 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes | Voltage Spike: 1.25pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_226_P1_LE-WEST_SUB3 | Apply 3-phase fault on LE-WEST_SUB3 to LE-NRTH_INT3 115kV line CKT 1, near LE-WEST_SUB3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | ASGI10-010 unit 1 [#528331] with Pmax of 42.1 MW found to be angular unstable for few contingencies. Since this issue occurred in both BC and TC cases and it does not impact the system overall stability, it’s not further investigated.
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_226_P1_LE-WEST_SUB3 | Apply 3-phase fault on LE-WEST_SUB3 to LE-NRTH_INT3 115kV line CKT 1, near LE-WEST_SUB3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | ASGI10-010 unit 1 [#528331] with Pmax of 42.1 MW found to be angular unstable for few contingencies. Since this issue occurred in both BC and TC cases and it does not impact the system overall stability, it’s not further investigated.
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_226_P1_LE-WEST_SUB3 | Apply 3-phase fault on LE-WEST_SUB3 to LE-NRTH_INT3 115kV line CKT 1, near LE-WEST_SUB3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | ASGI10-010 unit 1 [#528331] with Pmax of 42.1 MW found to be angular unstable for few contingencies. Since this issue occurred in both BC and TC cases and it does not impact the system overall stability, it’s not further investigated.
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_226_P1_LE-WEST_SUB3 | Apply 3-phase fault on LE-WEST_SUB3 to LE-NRTH_INT3 115kV line CKT 1, near LE-WEST_SUB3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | ASGI10-010 unit 1 [#528331] with Pmax of 42.1 MW found to be angular unstable for few contingencies. Since this issue occurred in both BC and TC cases and it does not impact the system overall stability, it’s not further investigated.
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_227_P1_LE-NRTH_INT3 | Apply 3-phase fault on LE-WAITS to LE-NRTH_INT3 115kV line CKT 1, near LE-NRTH_INT3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | ASGI10-010 unit 1 [#528331] with Pmax of 42.1 MW found to be angular unstable for few contingencies. Since this issue occurred in both BC and TC cases and it does not impact the system overall stability, it’s not further investigated.
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_227_P1_LE-NRTH_INT3 | Apply 3-phase fault on LE-WAITS to LE-NRTH_INT3 115kV line CKT 1, near LE-NRTH_INT3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | ASGI10-010 unit 1 [#528331] with Pmax of 42.1 MW found to be angular unstable for few contingencies. Since this issue occurred in both BC and TC cases and it does not impact the system overall stability, it’s not further investigated.
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_227_P1_LE-NRTH_INT3 | Apply 3-phase fault on LE-WAITS to LE-NRTH_INT3 115kV line CKT 1, near LE-NRTH_INT3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | ASGI10-010 unit 1 [#528331] with Pmax of 42.1 MW found to be angular unstable for few contingencies. Since this issue occurred in both BC and TC cases and it does not impact the system overall stability, it’s not further investigated.
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_227_P1_LE-NRTH_INT3 | Apply 3-phase fault on LE-WAITS to LE-NRTH_INT3 115kV line CKT 1, near LE-NRTH_INT3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | ASGI10-010 unit 1 [#528331] with Pmax of 42.1 MW found to be angular unstable for few contingencies. Since this issue occurred in both BC and TC cases and it does not impact the system overall stability, it’s not further investigated.
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_228_P1_MADDOX | Apply 3-phase fault on MONUMENT to W_HOBBS 115kV line CKT 1, near MADDOX 115kV for 7 cycles. Open the faulted line and TAYLOR to E_SANGER 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and TAYLOR to E_SANGER 115kV line CKT 1. Re-open the faulted line after 7 cycles% TAYLOR to E_SANGER 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_228_P1_MADDOX | Apply 3-phase fault on MONUMENT to W_HOBBS 115kV line CKT 1, near MADDOX 115kV for 7 cycles. Open the faulted line and TAYLOR to E_SANGER 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and TAYLOR to E_SANGER 115kV line CKT 1. Re-open the faulted line after 7 cycles% TAYLOR to E_SANGER 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_228_P1_MADDOX | Apply 3-phase fault on MONUMENT to W_HOBBS 115kV line CKT 1, near MADDOX 115kV for 7 cycles. Open the faulted line and TAYLOR to E_SANGER 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and TAYLOR to E_SANGER 115kV line CKT 1. Re-open the faulted line after 7 cycles% TAYLOR to E_SANGER 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_228_P1_MADDOX | Apply 3-phase fault on MONUMENT to W_HOBBS 115kV line CKT 1, near MADDOX 115kV for 7 cycles. Open the faulted line and TAYLOR to E_SANGER 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and TAYLOR to E_SANGER 115kV line CKT 1. Re-open the faulted line after 7 cycles% TAYLOR to E_SANGER 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_229_P1_MADDOX | Apply 3-phase fault on MADDOX to SANGER_SW 115kV line CKT 1, near MADDOX 115kV for 7 cycles. Open the faulted line and TAYLOR to W_BENDER 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and TAYLOR to W_BENDER 115kV line CKT 1. Re-open the faulted line after 7 cycles% TAYLOR to W_BENDER 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_229_P1_MADDOX | Apply 3-phase fault on MADDOX to SANGER_SW 115kV line CKT 1, near MADDOX 115kV for 7 cycles. Open the faulted line and TAYLOR to W_BENDER 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and TAYLOR to W_BENDER 115kV line CKT 1. Re-open the faulted line after 7 cycles% TAYLOR to W_BENDER 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_229_P1_MADDOX | Apply 3-phase fault on MADDOX to SANGER_SW 115kV line CKT 1, near MADDOX 115kV for 7 cycles. Open the faulted line and TAYLOR to W_BENDER 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and TAYLOR to W_BENDER 115kV line CKT 1. Re-open the faulted line after 7 cycles% TAYLOR to W_BENDER 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_229_P1_MADDOX | Apply 3-phase fault on MADDOX to SANGER_SW 115kV line CKT 1, near MADDOX 115kV for 7 cycles. Open the faulted line and TAYLOR to W_BENDER 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and TAYLOR to W_BENDER 115kV line CKT 1. Re-open the faulted line after 7 cycles% TAYLOR to W_BENDER 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_23_P1_HITCHLAND | Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV line CKT 2, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_23_P1_HITCHLAND | Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV line CKT 2, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_23_P1_HITCHLAND | Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV line CKT 2, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_23_P1_HITCHLAND | Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV line CKT 2, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_230_P1_MADDOX | Apply 3-phase fault on MADDOX to PEARLE 115kV line CKT 1, near MADDOX 115kV for 7 cycles. Open the faulted line and QUAHADA to LEA_NATIONL3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and QUAHADA to LEA_NATIONL3 115kV line CKT 1. Re-open the faulted line after 7 cycles% QUAHADA to LEA_NATIONL3 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_230_P1_MADDOX | Apply 3-phase fault on MADDOX to PEARLE 115kV line CKT 1, near MADDOX 115kV for 7 cycles. Open the faulted line and QUAHADA to LEA_NATIONL3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and QUAHADA to LEA_NATIONL3 115kV line CKT 1. Re-open the faulted line after 7 cycles% QUAHADA to LEA_NATIONL3 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_230_P1_MADDOX | Apply 3-phase fault on MADDOX to PEARLE 115kV line CKT 1, near MADDOX 115kV for 7 cycles. Open the faulted line and QUAHADA to LEA_NATIONL3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and QUAHADA to LEA_NATIONL3 115kV line CKT 1. Re-open the faulted line after 7 cycles% QUAHADA to LEA_NATIONL3 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_230_P1_MADDOX | Apply 3-phase fault on MADDOX to PEARLE 115kV line CKT 1, near MADDOX 115kV for 7 cycles. Open the faulted line and QUAHADA to LEA_NATIONL3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and QUAHADA to LEA_NATIONL3 115kV line CKT 1. Re-open the faulted line after 7 cycles% QUAHADA to LEA_NATIONL3 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_231_P1_QUAHADA | Apply 3-phase fault on QUAHADA to LEA_NATIONL3 115kV line CKT 1, near QUAHADA 115kV for 7 cycles. Open the faulted line and MADDOX to PEARLE 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and MADDOX to PEARLE 115kV line CKT 1. Re-open the faulted line after 7 cycles% MADDOX to PEARLE 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_231_P1_QUAHADA | Apply 3-phase fault on QUAHADA to LEA_NATIONL3 115kV line CKT 1, near QUAHADA 115kV for 7 cycles. Open the faulted line and MADDOX to PEARLE 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and MADDOX to PEARLE 115kV line CKT 1. Re-open the faulted line after 7 cycles% MADDOX to PEARLE 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_231_P1_QUAHADA | Apply 3-phase fault on QUAHADA to LEA_NATIONL3 115kV line CKT 1, near QUAHADA 115kV for 7 cycles. Open the faulted line and MADDOX to PEARLE 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and MADDOX to PEARLE 115kV line CKT 1. Re-open the faulted line after 7 cycles% MADDOX to PEARLE 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_231_P1_QUAHADA | Apply 3-phase fault on QUAHADA to LEA_NATIONL3 115kV line CKT 1, near QUAHADA 115kV for 7 cycles. Open the faulted line and MADDOX to PEARLE 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and MADDOX to PEARLE 115kV line CKT 1. Re-open the faulted line after 7 cycles% MADDOX to PEARLE 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_232_P1_QUAHADA | Apply 3-phase fault on PCA to QUAHADA 115kV line CKT 1, near QUAHADA 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_232_P1_QUAHADA | Apply 3-phase fault on PCA to QUAHADA 115kV line CKT 1, near QUAHADA 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_232_P1_QUAHADA | Apply 3-phase fault on PCA to QUAHADA 115kV line CKT 1, near QUAHADA 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_232_P1_QUAHADA | Apply 3-phase fault on PCA to QUAHADA 115kV line CKT 1, near QUAHADA 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_233_P1_QUAHADA | Apply 3-phase fault on QUAHADA to DCP_ZIA TP 3 115kV line CKT 1, near QUAHADA 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_233_P1_QUAHADA | Apply 3-phase fault on QUAHADA to DCP_ZIA TP 3 115kV line CKT 1, near QUAHADA 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_233_P1_QUAHADA | Apply 3-phase fault on QUAHADA to DCP_ZIA TP 3 115kV line CKT 1, near QUAHADA 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_233_P1_QUAHADA | Apply 3-phase fault on QUAHADA to DCP_ZIA TP 3 115kV line CKT 1, near QUAHADA 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_234_P1_ANDREWS | Apply 3-phase fault on ANDREWS to NA_ENRICH 115kV line CKT 1, near ANDREWS 115kV for 7 cycles. Open the faulted line and CARDINAL to TARGA 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and CARDINAL to TARGA 115kV line CKT 1. Re-open the faulted line after 7 cycles% CARDINAL to TARGA 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_234_P1_ANDREWS | Apply 3-phase fault on ANDREWS to NA_ENRICH 115kV line CKT 1, near ANDREWS 115kV for 7 cycles. Open the faulted line and CARDINAL to TARGA 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and CARDINAL to TARGA 115kV line CKT 1. Re-open the faulted line after 7 cycles% CARDINAL to TARGA 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_234_P1_ANDREWS | Apply 3-phase fault on ANDREWS to NA_ENRICH 115kV line CKT 1, near ANDREWS 115kV for 7 cycles. Open the faulted line and CARDINAL to TARGA 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and CARDINAL to TARGA 115kV line CKT 1. Re-open the faulted line after 7 cycles% CARDINAL to TARGA 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_234_P1_ANDREWS | Apply 3-phase fault on ANDREWS to NA_ENRICH 115kV line CKT 1, near ANDREWS 115kV for 7 cycles. Open the faulted line and CARDINAL to TARGA 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and CARDINAL to TARGA 115kV line CKT 1. Re-open the faulted line after 7 cycles% CARDINAL to TARGA 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_235_P1_CRAWFISH_DR | Apply 3-phase fault on BORDER to CRAWFISH_DR 345kV line CKT 1, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Unstable | No | No | No | No | Yes | No | Angular and system instability was observed in the G6 region. The stability issue was resolved with the SVC mitigation solution. TOV: 1.24pu, MaxDur: 0.80s | ±600 MVAr SVC at Crossroad 765kV
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_235_P1_CRAWFISH_DR | Apply 3-phase fault on BORDER to CRAWFISH_DR 345kV line CKT 1, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes | Note: Abnormal oscillations were observed in the generation units and system responses, which are attributed to the OECGT generation units modeling issues. When the OECGT units were GENETed these oscillations were mitigated.
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_235_P1_CRAWFISH_DR | Apply 3-phase fault on BORDER to CRAWFISH_DR 345kV line CKT 1, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_235_P1_CRAWFISH_DR | Apply 3-phase fault on BORDER to CRAWFISH_DR 345kV line CKT 1, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.05s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_236_P1_CRAWFISH_DR | Apply 3-phase fault on CRAWFISH_DR 345kV/765kV transformer CKT 2, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted Two Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Note: Abnormal oscillations were observed in the generation units and system responses, which are attributed to the OECGT generation units modeling issues. When the OECGT units were GENETed these oscillations were mitigated. Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_236_P1_CRAWFISH_DR | Apply 3-phase fault on CRAWFISH_DR 345kV/765kV transformer CKT 2, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted Two Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_236_P1_CRAWFISH_DR | Apply 3-phase fault on CRAWFISH_DR 345kV/765kV transformer CKT 2, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted Two Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_236_P1_CRAWFISH_DR | Apply 3-phase fault on CRAWFISH_DR 345kV/765kV transformer CKT 2, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted Two Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_237_P1_CRAWFISH_DR | Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV line CKT 2, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes | Note: Abnormal oscillations were observed in the generation units and system responses, which are attributed to the OECGT generation units modeling issues. When the OECGT units were GENETed these oscillations were mitigated.
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_237_P1_CRAWFISH_DR | Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV line CKT 2, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | No | LVRT VIOL - - FRISCO_WND 3[1].
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_237_P1_CRAWFISH_DR | Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV line CKT 2, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_237_P1_CRAWFISH_DR | Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV line CKT 2, near CRAWFISH_DR 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.05s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_238_P1_G16-037-TAP | Apply 3-phase fault on CHISHOLM7 to G16-037-TAP 345kV line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.53pu, MaxDur: 0.04s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_238_P1_G16-037-TAP | Apply 3-phase fault on CHISHOLM7 to G16-037-TAP 345kV line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_238_P1_G16-037-TAP | Apply 3-phase fault on CHISHOLM7 to G16-037-TAP 345kV line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.52pu, MaxDur: 0.04s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_238_P1_G16-037-TAP | Apply 3-phase fault on CHISHOLM7 to G16-037-TAP 345kV line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.52pu, MaxDur: 0.04s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_239_P1_CRAWFISH765 | Apply 3-phase fault on CRAWFISH765 to CROSSRDS765 765kV line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | No | LVRT VIOL - - LANOGSU10.60[W1]. Undamped and abnormal oscillations were observed in conventional units angles and powers, renewable units powers and system voltage responses. Simulation was rerun with the Crossroad SVC and different fault clearing times. The oscillations damping were improved when the fault reclosing was disabled. Furthermore, with reduced fault clearing time of 5 cycles the damping issue was resolved. min post-fault s.s. voltage: 0.89pu | Build a new Crawfish Draw 765/345kV Substation tapping the Tuco to Border 345kV Ckt 1 and Tuco to OKU 345kV Ckt 1. In addition, install a new 1000 MVar SVC for Dynamic Reactive Support at Crawfish Draw 765kV. Both the 765kV and the 345kV Crawfish Draw switchyards shall be constructed with breaker and a half bus schemes. Furthermore, interconnected double circuit lines connected to these switchyards or transformers connecting these switchyards shall not share adjacent breakers in the switchyard(s). Reduced clearing time 5 cycles w/o reclosing
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_239_P1_CRAWFISH765 | Apply 3-phase fault on CRAWFISH765 to CROSSRDS765 765kV line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Unstable | No | No | No | No | No | No | Angular and system instability was observed in the G6 region. Simulation was rerun with the Crossroad SVC. It was observed that the Crossroad 765kV SVC cannot resolve the problem even with reclosing disabled and reduced fault clearing time of 3 cycles (default 6 cycles). Next, other reactive power support options were investegated. No stability or damping issues were observed with the ±600 MVAr SVC at Crossroad 765kV, +600/-700 MVAr SVC at Seminole 765kV, increased SVC size at Crawfish 765kV from +600/-700 MVAr to +1000/-700 MVAr and with reduced fault clearing time of 3 cycles with reclosing disabled. (Note: the Seminole SVC option is identical to the Crawfish SVC in terms of power flow and dynamic parameters, and it replaces the provided switched shunt/reactor at the station) min post-fault s.s. voltage: 0.82pu | Build a new Crawfish Draw 765/345kV Substation tapping the Tuco to Border 345kV Ckt 1 and Tuco to OKU 345kV Ckt 1. In addition, install a new 1000 MVar SVC for Dynamic Reactive Support at Crawfish Draw 765kV. Both the 765kV and the 345kV Crawfish Draw switchyards shall be constructed with breaker and a half bus schemes. Furthermore, interconnected double circuit lines connected to these switchyards or transformers connecting these switchyards shall not share adjacent breakers in the switchyard(s). ±600 MVAr SVC at Crossroad 765kV & +600/-700 MVAr SVC at Seminole 765kV & Reduced clearing time 3 cycles (w/o reclosing)
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_239_P1_CRAWFISH765 | Apply 3-phase fault on CRAWFISH765 to CROSSRDS765 765kV line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_239_P1_CRAWFISH765 | Apply 3-phase fault on CRAWFISH765 to CROSSRDS765 765kV line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_24_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_24_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_24_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_24_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | No | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_240_P1_CRAWFISH765 | Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes | Undamped oscillations were observed in conventional units angles and powers, renewable units powers and system voltage responses. Simulation was rerun with the Crossroad SVC and different fault clearing times. The damping issue was resolved with the Crossroad SVC with fault reclosing disabled (default fault clearing time of 6 cycles). | Build a new Crawfish Draw 765/345kV Substation tapping the Tuco to Border 345kV Ckt 1 and Tuco to OKU 345kV Ckt 1. Both the 765kV and the 345kV Crawfish Draw switchyards shall be constructed with breaker and a half bus schemes. Furthermore, interconnected double circuit lines connected to these switchyards or transformers connecting these switchyards shall not share adjacent breakers in the switchyard(s). ±600 MVAr SVC at Crossroad 765kV (w/o reclosing)
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_240_P1_CRAWFISH765 | Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Unstable | No | No | No | No | No | No | Angular and system instability was observed in the G6 region. Simulation was rerun with the Crossroad SVC. It was observed that the Crossroad 765kV SVC cannot resolve the problem even with reclosing disabled and reduced fault clearing time of 3 cycles (default 6 cycles). Next, other reactive power support options were investegated. No stability or damping issues were observed with the following options: Primary Option: ±600 MVAr SVC at Crossroad 765kV and +600/-700 MVAr SVC at Seminole 765kV and with the reduced fault clearing time of 3 cycles without reclosing. (Note: the Seminole SVC option is identical to the Crawfish SVC in terms of power flow and dynamic parameters, and it replaces the provided switched shunt/reactor at the station) Alternative Option: ±600 MVAr SVC at Crossroad 765kV, +600/-700 MVAr SVC at Seminole 765kV and increased SVC size at the Crawfish 765kV from +600/-700 MVAr to +1000/-700 MVAr. The results are achieved with default fault clearing time of 6 cycles and reclosing disabled. | Build a new Crawfish Draw 765/345kV Substation tapping the Tuco to Border 345kV Ckt 1 and Tuco to OKU 345kV Ckt 1. Both the 765kV and the 345kV Crawfish Draw switchyards shall be constructed with breaker and a half bus schemes. Furthermore, interconnected double circuit lines connected to these switchyards or transformers connecting these switchyards shall not share adjacent breakers in the switchyard(s). ±600 MVAr SVC at Crossroad 765kV & +600/-700 MVAr SVC at Seminole 765kV (fault clearing time 3 cycles w/o reclosing) | Build a new Crawfish Draw 765/345kV Substation tapping the Tuco to Border 345kV Ckt 1 and Tuco to OKU 345kV Ckt 1. In addition, install a new 1000 MVar SVC for Dynamic Reactive Support at Crawfish Draw 765kV. Both the 765kV and the 345kV Crawfish Draw switchyards shall be constructed with breaker and a half bus schemes. Furthermore, interconnected double circuit lines connected to these switchyards or transformers connecting these switchyards shall not share adjacent breakers in the switchyard(s). ±600 MVAr SVC at Crossroad 765kV & +600/-700 MVAr SVC at Seminole 765kV & (w/o reclosing)
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_240_P1_CRAWFISH765 | Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_240_P1_CRAWFISH765 | Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_241_P1_G16-091-TAP | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.27pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_241_P1_G16-091-TAP | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_241_P1_G16-091-TAP | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.27pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_241_P1_G16-091-TAP | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.26pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_242_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV line CKT &1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line. Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | No | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_242_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV line CKT &1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line. Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_242_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV line CKT &1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line. Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_242_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV line CKT &1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line. Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_243_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV line CKT &1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line. Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | No | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_243_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV line CKT &1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line. Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_243_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV line CKT &1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line. Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_243_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV line CKT &1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line. Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_244_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.29pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_244_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_244_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.30pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_244_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.26pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_245_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_245_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_245_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_245_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_246_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_246_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_246_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_246_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_247_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.06s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_247_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | No | LVRT VIOL - - ARBCKL_WTG1[1] FRISCO_WND 3[1] A11-002-GEN1[1] A11-002-GEN1[2] G1140G1204G2[1] G1140G1204G1[1]. ARBCKL_WTG1[1], G1140G1204G2[1], and G1140G1204G1[1] tripped on voltage protection setting 1.20pu-0.08s (embedded in the user model). The protection settings were disabled and simulation was rerun. No further issues were observed.
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_247_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.04s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_247_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.06s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_248_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes | Voltage Spike: 1.25pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_248_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | No | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_248_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes | Voltage Spike: 1.27pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_248_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.27pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_249_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.04s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_249_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.06s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_249_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_249_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_25_P1_POTTER_CO | Apply 3-phase fault on CHAN+TASCOS6 to POTTER_CO 230kV line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_25_P1_POTTER_CO | Apply 3-phase fault on CHAN+TASCOS6 to POTTER_CO 230kV line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_25_P1_POTTER_CO | Apply 3-phase fault on CHAN+TASCOS6 to POTTER_CO 230kV line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_25_P1_POTTER_CO | Apply 3-phase fault on CHAN+TASCOS6 to POTTER_CO 230kV line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_250_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_250_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_250_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_250_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_251_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.05s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_251_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | No | LVRT VIOL - - ARBCKL_WTG1[1] FRISCO_WND 3[1] A11-002-GEN1[1] A11-002-GEN1[2] G1140G1204G2[1] G1140G1204G1[1]. ARBCKL_WTG1[1], G1140G1204G2[1], and G1140G1204G1[1] tripped on voltage protection settings 1.20pu-0.08s and 1.25pu-0.005s (embedded in the user model). The protection settings were disabled and simulation was rerun. No further issues were observed.
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_251_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_251_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.04s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_252_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_252_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_252_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_252_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_253_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_253_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_253_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_253_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_254_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_254_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_254_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_254_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_255_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_255_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - FRISCO_WND 3[1].
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_255_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_255_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_256_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_256_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | No | LVRT VIOL - - FRISCO_WND 3[1].
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_256_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_256_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_257_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_257_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_257_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_257_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_258_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_258_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_258_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_258_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_259_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_259_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - FRISCO_WND 3[1].
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_259_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_259_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_26_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to NEWPOT_SS 230kV line CKT 1, near POTTER_CO 230kV for 7 cycles. Open the faulted line and NEWPOT_SS to NEWHART 230kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NEWPOT_SS to NEWHART 230kV line CKT 1. Re-open the faulted line after 7 cycles% NEWPOT_SS to NEWHART 230kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_26_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to NEWPOT_SS 230kV line CKT 1, near POTTER_CO 230kV for 7 cycles. Open the faulted line and NEWPOT_SS to NEWHART 230kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NEWPOT_SS to NEWHART 230kV line CKT 1. Re-open the faulted line after 7 cycles% NEWPOT_SS to NEWHART 230kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_26_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to NEWPOT_SS 230kV line CKT 1, near POTTER_CO 230kV for 7 cycles. Open the faulted line and NEWPOT_SS to NEWHART 230kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NEWPOT_SS to NEWHART 230kV line CKT 1. Re-open the faulted line after 7 cycles% NEWPOT_SS to NEWHART 230kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_26_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to NEWPOT_SS 230kV line CKT 1, near POTTER_CO 230kV for 7 cycles. Open the faulted line and NEWPOT_SS to NEWHART 230kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NEWPOT_SS to NEWHART 230kV line CKT 1. Re-open the faulted line after 7 cycles% NEWPOT_SS to NEWHART 230kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_260_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes | Note: Abnormal oscillations were observed in the generation units and system responses, which are attributed to the OECGT generation units modeling issues. When the OECGT units were GENETed these oscillations were mitigated.
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_260_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | No | LVRT VIOL - - A11-002-GEN1[1] A11-002-GEN1[2] G1140G1204G2[1] G1140G1204G1[1] FRISCO_WND 3[1]. G1140G1204G2[1] and G1140G1204G1[1] tripped on voltage protection setting 1.20pu-0.08s (embedded in the user model). The protection settings were disabled and simulation was rerun. No further issues were observed.
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_260_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_260_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_261_P4_OKU-7 | Apply single-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV line CKT 1, near O.K.U.-7 345kV for 16 cycles with stuck breaker at O.K.U.-7. Open the faulted line and OKLAUN HVDC7 shunt device and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_261_P4_OKU-7 | Apply single-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV line CKT 1, near O.K.U.-7 345kV for 16 cycles with stuck breaker at O.K.U.-7. Open the faulted line and OKLAUN HVDC7 shunt device and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_261_P4_OKU-7 | Apply single-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV line CKT 1, near O.K.U.-7 345kV for 16 cycles with stuck breaker at O.K.U.-7. Open the faulted line and OKLAUN HVDC7 shunt device and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_261_P4_OKU-7 | Apply single-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV line CKT 1, near O.K.U.-7 345kV for 16 cycles with stuck breaker at O.K.U.-7. Open the faulted line and OKLAUN HVDC7 shunt device and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_262_P4_OKU-7 | Apply single-phase fault on O.K.U.-7 to L.E.S.-7 345kV line CKT 1, near O.K.U.-7 345kV for 16 cycles with stuck breaker at O.K.U.-7. Open the faulted line and OKLAUN HVDC7 shunt device and clear the fault. | P4 | Stable | Yes | Yes | No | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_262_P4_OKU-7 | Apply single-phase fault on O.K.U.-7 to L.E.S.-7 345kV line CKT 1, near O.K.U.-7 345kV for 16 cycles with stuck breaker at O.K.U.-7. Open the faulted line and OKLAUN HVDC7 shunt device and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_262_P4_OKU-7 | Apply single-phase fault on O.K.U.-7 to L.E.S.-7 345kV line CKT 1, near O.K.U.-7 345kV for 16 cycles with stuck breaker at O.K.U.-7. Open the faulted line and OKLAUN HVDC7 shunt device and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_263_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to G16-091-TAP 345kV line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted line and L.E.S.-7 to TERRYRD7 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_263_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to G16-091-TAP 345kV line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted line and L.E.S.-7 to TERRYRD7 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_263_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to G16-091-TAP 345kV line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted line and L.E.S.-7 to TERRYRD7 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_263_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to G16-091-TAP 345kV line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted line and L.E.S.-7 to TERRYRD7 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_264_P4_LES-7 | Apply single-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Three Winding and LES#4-1 13.8kV/138kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_264_P4_LES-7 | Apply single-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Three Winding and LES#4-1 13.8kV/138kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_264_P4_LES-7 | Apply single-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Three Winding and LES#4-1 13.8kV/138kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_264_P4_LES-7 | Apply single-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Three Winding and LES#4-1 13.8kV/138kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_265_P4_WWRDEHV7 | Apply single-phase fault on WWRDEHV7 to DGRASSE7 345kV line CKT 2, near WWRDEHV7 345kV for 16 cycles with stuck breaker at WWRDEHV7. Open the faulted line and WWRDEHV7 to DGRASSE7 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.22pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_265_P4_WWRDEHV7 | Apply single-phase fault on WWRDEHV7 to DGRASSE7 345kV line CKT 2, near WWRDEHV7 345kV for 16 cycles with stuck breaker at WWRDEHV7. Open the faulted line and WWRDEHV7 to DGRASSE7 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_265_P4_WWRDEHV7 | Apply single-phase fault on WWRDEHV7 to DGRASSE7 345kV line CKT 2, near WWRDEHV7 345kV for 16 cycles with stuck breaker at WWRDEHV7. Open the faulted line and WWRDEHV7 to DGRASSE7 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_265_P4_WWRDEHV7 | Apply single-phase fault on WWRDEHV7 to DGRASSE7 345kV line CKT 2, near WWRDEHV7 345kV for 16 cycles with stuck breaker at WWRDEHV7. Open the faulted line and WWRDEHV7 to DGRASSE7 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.23pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_266_P4_WWRDEHV7 | Apply single-phase fault on WWRDEHV7 to TATONGA7 345kV line CKT 1, near WWRDEHV7 345kV for 16 cycles with stuck breaker at WWRDEHV7. Open the faulted line and WWRDEHV7 to TATONGA7 345kV line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_266_P4_WWRDEHV7 | Apply single-phase fault on WWRDEHV7 to TATONGA7 345kV line CKT 1, near WWRDEHV7 345kV for 16 cycles with stuck breaker at WWRDEHV7. Open the faulted line and WWRDEHV7 to TATONGA7 345kV line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_266_P4_WWRDEHV7 | Apply single-phase fault on WWRDEHV7 to TATONGA7 345kV line CKT 1, near WWRDEHV7 345kV for 16 cycles with stuck breaker at WWRDEHV7. Open the faulted line and WWRDEHV7 to TATONGA7 345kV line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_266_P4_WWRDEHV7 | Apply single-phase fault on WWRDEHV7 to TATONGA7 345kV line CKT 1, near WWRDEHV7 345kV for 16 cycles with stuck breaker at WWRDEHV7. Open the faulted line and WWRDEHV7 to TATONGA7 345kV line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_267_P4_HITCHLAND | Apply single-phase fault on HITCHLD_TR01 13.19kV/230kV/345kV transformer CKT 1, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding and HITCHLD_TR21 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_267_P4_HITCHLAND | Apply single-phase fault on HITCHLD_TR01 13.19kV/230kV/345kV transformer CKT 1, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding and HITCHLD_TR21 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | No | No | Yes | FRISCO_WND 3 [#523160] with Pgen of 7.7 MW found to be angular unstable for this contingency. Since this issue occurred in both BC and TC cases and it does not impact the system overall stability it’s not further investigated.
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_267_P4_HITCHLAND | Apply single-phase fault on HITCHLD_TR01 13.19kV/230kV/345kV transformer CKT 1, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding and HITCHLD_TR21 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_267_P4_HITCHLAND | Apply single-phase fault on HITCHLD_TR01 13.19kV/230kV/345kV transformer CKT 1, near HITCHLAND 230kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted Three Winding and HITCHLD_TR21 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_268_P4_HITCHLAND | Apply single-phase fault on BVRCNTY7 to HITCHLAND 345kV line CKT 2, near HITCHLAND 345kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted line and BVRCNTY7 to HITCHLAND 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | No | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_268_P4_HITCHLAND | Apply single-phase fault on BVRCNTY7 to HITCHLAND 345kV line CKT 2, near HITCHLAND 345kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted line and BVRCNTY7 to HITCHLAND 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_268_P4_HITCHLAND | Apply single-phase fault on BVRCNTY7 to HITCHLAND 345kV line CKT 2, near HITCHLAND 345kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted line and BVRCNTY7 to HITCHLAND 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_268_P4_HITCHLAND | Apply single-phase fault on BVRCNTY7 to HITCHLAND 345kV line CKT 2, near HITCHLAND 345kV for 16 cycles with stuck breaker at HITCHLAND. Open the faulted line and BVRCNTY7 to HITCHLAND 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_269_P4_POTTER_CO | Apply single-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV line CKT 1, near POTTER_CO 230kV for 16 cycles with stuck breaker at POTTER_CO. Open the faulted line and POTTER_TR 13.19kV/230kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | No | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_269_P4_POTTER_CO | Apply single-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV line CKT 1, near POTTER_CO 230kV for 16 cycles with stuck breaker at POTTER_CO. Open the faulted line and POTTER_TR 13.19kV/230kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_269_P4_POTTER_CO | Apply single-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV line CKT 1, near POTTER_CO 230kV for 16 cycles with stuck breaker at POTTER_CO. Open the faulted line and POTTER_TR 13.19kV/230kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_269_P4_POTTER_CO | Apply single-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV line CKT 1, near POTTER_CO 230kV for 16 cycles with stuck breaker at POTTER_CO. Open the faulted line and POTTER_TR 13.19kV/230kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_27_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to BUSHLAND 230kV line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_27_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to BUSHLAND 230kV line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_27_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to BUSHLAND 230kV line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_27_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to BUSHLAND 230kV line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_270_P4_POTTER_CO | Apply single-phase fault on CHAN+TASCOS6 to POTTER_CO 230kV line CKT 1, near POTTER_CO 230kV for 16 cycles with stuck breaker at POTTER_CO. Open the faulted line and POTTER_TR 13.19kV/230kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_270_P4_POTTER_CO | Apply single-phase fault on CHAN+TASCOS6 to POTTER_CO 230kV line CKT 1, near POTTER_CO 230kV for 16 cycles with stuck breaker at POTTER_CO. Open the faulted line and POTTER_TR 13.19kV/230kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_270_P4_POTTER_CO | Apply single-phase fault on CHAN+TASCOS6 to POTTER_CO 230kV line CKT 1, near POTTER_CO 230kV for 16 cycles with stuck breaker at POTTER_CO. Open the faulted line and POTTER_TR 13.19kV/230kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_270_P4_POTTER_CO | Apply single-phase fault on CHAN+TASCOS6 to POTTER_CO 230kV line CKT 1, near POTTER_CO 230kV for 16 cycles with stuck breaker at POTTER_CO. Open the faulted line and POTTER_TR 13.19kV/230kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | No | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_271_P4_POTTER_CO | Apply single-phase fault on POTTER_CO to HARRNG_EST 6 230kV line CKT 1, near POTTER_CO 230kV for 16 cycles with stuck breaker at POTTER_CO. Open the faulted line and POTTER_CO to ROLLHILLS 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_271_P4_POTTER_CO | Apply single-phase fault on POTTER_CO to HARRNG_EST 6 230kV line CKT 1, near POTTER_CO 230kV for 16 cycles with stuck breaker at POTTER_CO. Open the faulted line and POTTER_CO to ROLLHILLS 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_271_P4_POTTER_CO | Apply single-phase fault on POTTER_CO to HARRNG_EST 6 230kV line CKT 1, near POTTER_CO 230kV for 16 cycles with stuck breaker at POTTER_CO. Open the faulted line and POTTER_CO to ROLLHILLS 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_271_P4_POTTER_CO | Apply single-phase fault on POTTER_CO to HARRNG_EST 6 230kV line CKT 1, near POTTER_CO 230kV for 16 cycles with stuck breaker at POTTER_CO. Open the faulted line and POTTER_CO to ROLLHILLS 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_272_P4_NICHOLS | Apply single-phase fault on HARRNG_WST 6 to NICHOLS 230kV line CKT 1, near NICHOLS 230kV for 16 cycles with stuck breaker at NICHOLS. Open the faulted line and HARRNG_MID 6 to NICHOLS 230kV line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_272_P4_NICHOLS | Apply single-phase fault on HARRNG_WST 6 to NICHOLS 230kV line CKT 1, near NICHOLS 230kV for 16 cycles with stuck breaker at NICHOLS. Open the faulted line and HARRNG_MID 6 to NICHOLS 230kV line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_272_P4_NICHOLS | Apply single-phase fault on HARRNG_WST 6 to NICHOLS 230kV line CKT 1, near NICHOLS 230kV for 16 cycles with stuck breaker at NICHOLS. Open the faulted line and HARRNG_MID 6 to NICHOLS 230kV line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_272_P4_NICHOLS | Apply single-phase fault on HARRNG_WST 6 to NICHOLS 230kV line CKT 1, near NICHOLS 230kV for 16 cycles with stuck breaker at NICHOLS. Open the faulted line and HARRNG_MID 6 to NICHOLS 230kV line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_273_P4_NICHOLS | Apply single-phase fault on GRAPEVINE to NICHOLS 230kV line CKT 1, near NICHOLS 230kV for 16 cycles with stuck breaker at NICHOLS. Open the faulted line and HUTCHISON to NICHOLS 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_273_P4_NICHOLS | Apply single-phase fault on GRAPEVINE to NICHOLS 230kV line CKT 1, near NICHOLS 230kV for 16 cycles with stuck breaker at NICHOLS. Open the faulted line and HUTCHISON to NICHOLS 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_273_P4_NICHOLS | Apply single-phase fault on GRAPEVINE to NICHOLS 230kV line CKT 1, near NICHOLS 230kV for 16 cycles with stuck breaker at NICHOLS. Open the faulted line and HUTCHISON to NICHOLS 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | No | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_273_P4_NICHOLS | Apply single-phase fault on GRAPEVINE to NICHOLS 230kV line CKT 1, near NICHOLS 230kV for 16 cycles with stuck breaker at NICHOLS. Open the faulted line and HUTCHISON to NICHOLS 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_274_P4_AMA_SOUTH | Apply single-phase fault on RANDALL to AMA_SOUTH 230kV line CKT 1, near AMA_SOUTH 230kV for 16 cycles with stuck breaker at AMA_SOUTH. Open the faulted line and NICHOLS to AMA_SOUTH 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_274_P4_AMA_SOUTH | Apply single-phase fault on RANDALL to AMA_SOUTH 230kV line CKT 1, near AMA_SOUTH 230kV for 16 cycles with stuck breaker at AMA_SOUTH. Open the faulted line and NICHOLS to AMA_SOUTH 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_274_P4_AMA_SOUTH | Apply single-phase fault on RANDALL to AMA_SOUTH 230kV line CKT 1, near AMA_SOUTH 230kV for 16 cycles with stuck breaker at AMA_SOUTH. Open the faulted line and NICHOLS to AMA_SOUTH 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_274_P4_AMA_SOUTH | Apply single-phase fault on RANDALL to AMA_SOUTH 230kV line CKT 1, near AMA_SOUTH 230kV for 16 cycles with stuck breaker at AMA_SOUTH. Open the faulted line and NICHOLS to AMA_SOUTH 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_275_P4_AMA_SOUTH | Apply single-phase fault on AMA_SO_TR1 1 13.19kV/115kV/230kV transformer CKT 1, near AMA_SOUTH 230kV for 16 cycles with stuck breaker at AMA_SOUTH. Open the faulted Three Winding and NICHOLS to AMA_SOUTH 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_275_P4_AMA_SOUTH | Apply single-phase fault on AMA_SO_TR1 1 13.19kV/115kV/230kV transformer CKT 1, near AMA_SOUTH 230kV for 16 cycles with stuck breaker at AMA_SOUTH. Open the faulted Three Winding and NICHOLS to AMA_SOUTH 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_275_P4_AMA_SOUTH | Apply single-phase fault on AMA_SO_TR1 1 13.19kV/115kV/230kV transformer CKT 1, near AMA_SOUTH 230kV for 16 cycles with stuck breaker at AMA_SOUTH. Open the faulted Three Winding and NICHOLS to AMA_SOUTH 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_275_P4_AMA_SOUTH | Apply single-phase fault on AMA_SO_TR1 1 13.19kV/115kV/230kV transformer CKT 1, near AMA_SOUTH 230kV for 16 cycles with stuck breaker at AMA_SOUTH. Open the faulted Three Winding and NICHOLS to AMA_SOUTH 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_276_P4_CASTRO_CNTY3 | Apply single-phase fault on DEAFSMITH to DS-#21 115kV line CKT 1, near CASTRO_CNTY3 115kV for 16 cycles with stuck breaker at CASTRO_CNTY3. Open the faulted line and DS-#21 to CASTRO_CNTY3 115kV line CKT 1 and CASTRO_CNTY3 to BC-KELLEY +3 115kV line CKT 1 and BC-KELLEY +3 to BC-EARTH 115kV line CKT 1 and BC-EARTH to PLANT_X 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_276_P4_CASTRO_CNTY3 | Apply single-phase fault on DEAFSMITH to DS-#21 115kV line CKT 1, near CASTRO_CNTY3 115kV for 16 cycles with stuck breaker at CASTRO_CNTY3. Open the faulted line and DS-#21 to CASTRO_CNTY3 115kV line CKT 1 and CASTRO_CNTY3 to BC-KELLEY +3 115kV line CKT 1 and BC-KELLEY +3 to BC-EARTH 115kV line CKT 1 and BC-EARTH to PLANT_X 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_276_P4_CASTRO_CNTY3 | Apply single-phase fault on DEAFSMITH to DS-#21 115kV line CKT 1, near CASTRO_CNTY3 115kV for 16 cycles with stuck breaker at CASTRO_CNTY3. Open the faulted line and DS-#21 to CASTRO_CNTY3 115kV line CKT 1 and CASTRO_CNTY3 to BC-KELLEY +3 115kV line CKT 1 and BC-KELLEY +3 to BC-EARTH 115kV line CKT 1 and BC-EARTH to PLANT_X 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_276_P4_CASTRO_CNTY3 | Apply single-phase fault on DEAFSMITH to DS-#21 115kV line CKT 1, near CASTRO_CNTY3 115kV for 16 cycles with stuck breaker at CASTRO_CNTY3. Open the faulted line and DS-#21 to CASTRO_CNTY3 115kV line CKT 1 and CASTRO_CNTY3 to BC-KELLEY +3 115kV line CKT 1 and BC-KELLEY +3 to BC-EARTH 115kV line CKT 1 and BC-EARTH to PLANT_X 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_277_P4_PLSNT_HILL3 | Apply single-phase fault on PLSNT_HILL 3 to FE-HOLLAND 3 115kV line CKT 1, near PLSNT_HILL 3 115kV for 16 cycles with stuck breaker at PLSNT_HILL 3. Open the faulted line and CURRY to FE-CLOVIS2+3 115kV line CKT 1 and PLSNT_HILL 3 to E_CLOVIS 115kV line CKT 1 and E_CLOVIS to CURRY 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_277_P4_PLSNT_HILL3 | Apply single-phase fault on PLSNT_HILL 3 to FE-HOLLAND 3 115kV line CKT 1, near PLSNT_HILL 3 115kV for 16 cycles with stuck breaker at PLSNT_HILL 3. Open the faulted line and CURRY to FE-CLOVIS2+3 115kV line CKT 1 and PLSNT_HILL 3 to E_CLOVIS 115kV line CKT 1 and E_CLOVIS to CURRY 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_277_P4_PLSNT_HILL3 | Apply single-phase fault on PLSNT_HILL 3 to FE-HOLLAND 3 115kV line CKT 1, near PLSNT_HILL 3 115kV for 16 cycles with stuck breaker at PLSNT_HILL 3. Open the faulted line and CURRY to FE-CLOVIS2+3 115kV line CKT 1 and PLSNT_HILL 3 to E_CLOVIS 115kV line CKT 1 and E_CLOVIS to CURRY 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_277_P4_PLSNT_HILL3 | Apply single-phase fault on PLSNT_HILL 3 to FE-HOLLAND 3 115kV line CKT 1, near PLSNT_HILL 3 115kV for 16 cycles with stuck breaker at PLSNT_HILL 3. Open the faulted line and CURRY to FE-CLOVIS2+3 115kV line CKT 1 and PLSNT_HILL 3 to E_CLOVIS 115kV line CKT 1 and E_CLOVIS to CURRY 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_278_P4_PLSNT_HILL3 | Apply single-phase fault on PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1, near PLSNT_HILL 3 115kV for 16 cycles with stuck breaker at PLSNT_HILL 3. Open the faulted line and N_CLOVIS_TP3 to FE-CLVS_INT3 115kV line CKT 1 and PLSNHIL_TR11 13.19kV/115kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_278_P4_PLSNT_HILL3 | Apply single-phase fault on PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1, near PLSNT_HILL 3 115kV for 16 cycles with stuck breaker at PLSNT_HILL 3. Open the faulted line and N_CLOVIS_TP3 to FE-CLVS_INT3 115kV line CKT 1 and PLSNHIL_TR11 13.19kV/115kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_278_P4_PLSNT_HILL3 | Apply single-phase fault on PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1, near PLSNT_HILL 3 115kV for 16 cycles with stuck breaker at PLSNT_HILL 3. Open the faulted line and N_CLOVIS_TP3 to FE-CLVS_INT3 115kV line CKT 1 and PLSNHIL_TR11 13.19kV/115kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_278_P4_PLSNT_HILL3 | Apply single-phase fault on PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1, near PLSNT_HILL 3 115kV for 16 cycles with stuck breaker at PLSNT_HILL 3. Open the faulted line and N_CLOVIS_TP3 to FE-CLVS_INT3 115kV line CKT 1 and PLSNHIL_TR11 13.19kV/115kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_279_P4_PLSNT_HILL3 | Apply single-phase fault on PLSNT_HILL 3 to FE-HOLLAND 3 115kV line CKT 1, near PLSNT_HILL 3 115kV for 16 cycles with stuck breaker at PLSNT_HILL 3. Open the faulted line and CURRY to FE-CLOVIS2+3 115kV line CKT 1 and PLSNHIL_TR11 13.19kV/115kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_279_P4_PLSNT_HILL3 | Apply single-phase fault on PLSNT_HILL 3 to FE-HOLLAND 3 115kV line CKT 1, near PLSNT_HILL 3 115kV for 16 cycles with stuck breaker at PLSNT_HILL 3. Open the faulted line and CURRY to FE-CLOVIS2+3 115kV line CKT 1 and PLSNHIL_TR11 13.19kV/115kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_279_P4_PLSNT_HILL3 | Apply single-phase fault on PLSNT_HILL 3 to FE-HOLLAND 3 115kV line CKT 1, near PLSNT_HILL 3 115kV for 16 cycles with stuck breaker at PLSNT_HILL 3. Open the faulted line and CURRY to FE-CLOVIS2+3 115kV line CKT 1 and PLSNHIL_TR11 13.19kV/115kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_279_P4_PLSNT_HILL3 | Apply single-phase fault on PLSNT_HILL 3 to FE-HOLLAND 3 115kV line CKT 1, near PLSNT_HILL 3 115kV for 16 cycles with stuck breaker at PLSNT_HILL 3. Open the faulted line and CURRY to FE-CLOVIS2+3 115kV line CKT 1 and PLSNHIL_TR11 13.19kV/115kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_28_P1_POTTER_CO | Apply 3-phase fault on POTTER_TR 13.19kV/230kV/345kV transformer CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_28_P1_POTTER_CO | Apply 3-phase fault on POTTER_TR 13.19kV/230kV/345kV transformer CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_28_P1_POTTER_CO | Apply 3-phase fault on POTTER_TR 13.19kV/230kV/345kV transformer CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_28_P1_POTTER_CO | Apply 3-phase fault on POTTER_TR 13.19kV/230kV/345kV transformer CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_280_P4_PLSNT_HILL6 | Apply single-phase fault on PLSNT_HILL 6 to OASIS 230kV line CKT 1, near PLSNT_HILL 6 230kV for 16 cycles with stuck breaker at PLSNT_HILL 6. Open the faulted line and PLSNHIL_TR11 13.19kV/115kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_280_P4_PLSNT_HILL6 | Apply single-phase fault on PLSNT_HILL 6 to OASIS 230kV line CKT 1, near PLSNT_HILL 6 230kV for 16 cycles with stuck breaker at PLSNT_HILL 6. Open the faulted line and PLSNHIL_TR11 13.19kV/115kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_280_P4_PLSNT_HILL6 | Apply single-phase fault on PLSNT_HILL 6 to OASIS 230kV line CKT 1, near PLSNT_HILL 6 230kV for 16 cycles with stuck breaker at PLSNT_HILL 6. Open the faulted line and PLSNHIL_TR11 13.19kV/115kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_280_P4_PLSNT_HILL6 | Apply single-phase fault on PLSNT_HILL 6 to OASIS 230kV line CKT 1, near PLSNT_HILL 6 230kV for 16 cycles with stuck breaker at PLSNT_HILL 6. Open the faulted line and PLSNHIL_TR11 13.19kV/115kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_281_P4_PLSNT_HILL6 | Apply single-phase fault on PLSNT_HILL 6 to OASIS 230kV line CKT 1, near PLSNT_HILL 6 230kV for 16 cycles with stuck breaker at PLSNT_HILL 6. Open the faulted line and PLSNT_HILL 6 to ROSEVELT_N 6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_281_P4_PLSNT_HILL6 | Apply single-phase fault on PLSNT_HILL 6 to OASIS 230kV line CKT 1, near PLSNT_HILL 6 230kV for 16 cycles with stuck breaker at PLSNT_HILL 6. Open the faulted line and PLSNT_HILL 6 to ROSEVELT_N 6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_281_P4_PLSNT_HILL6 | Apply single-phase fault on PLSNT_HILL 6 to OASIS 230kV line CKT 1, near PLSNT_HILL 6 230kV for 16 cycles with stuck breaker at PLSNT_HILL 6. Open the faulted line and PLSNT_HILL 6 to ROSEVELT_N 6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_281_P4_PLSNT_HILL6 | Apply single-phase fault on PLSNT_HILL 6 to OASIS 230kV line CKT 1, near PLSNT_HILL 6 230kV for 16 cycles with stuck breaker at PLSNT_HILL 6. Open the faulted line and PLSNT_HILL 6 to ROSEVELT_N 6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_282_P4_PLSNT_HILL6 | Apply single-phase fault on PLSNT_HILL 6 to ROSEVELT_N 6 230kV line CKT 1, near PLSNT_HILL 6 230kV for 16 cycles with stuck breaker at PLSNT_HILL 6. Open the faulted line and PLSNHIL_TR11 13.19kV/115kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_282_P4_PLSNT_HILL6 | Apply single-phase fault on PLSNT_HILL 6 to ROSEVELT_N 6 230kV line CKT 1, near PLSNT_HILL 6 230kV for 16 cycles with stuck breaker at PLSNT_HILL 6. Open the faulted line and PLSNHIL_TR11 13.19kV/115kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_282_P4_PLSNT_HILL6 | Apply single-phase fault on PLSNT_HILL 6 to ROSEVELT_N 6 230kV line CKT 1, near PLSNT_HILL 6 230kV for 16 cycles with stuck breaker at PLSNT_HILL 6. Open the faulted line and PLSNHIL_TR11 13.19kV/115kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_282_P4_PLSNT_HILL6 | Apply single-phase fault on PLSNT_HILL 6 to ROSEVELT_N 6 230kV line CKT 1, near PLSNT_HILL 6 230kV for 16 cycles with stuck breaker at PLSNT_HILL 6. Open the faulted line and PLSNHIL_TR11 13.19kV/115kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_283_P4_CURRY | Apply single-phase fault on CURRY to BAILEYCO 115kV line CKT 1, near CURRY 115kV for 16 cycles with stuck breaker at CURRY. Open the faulted line and DS-#20 to CURRY 115kV line CKT 1 and HEREFORD to DS-#6 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_283_P4_CURRY | Apply single-phase fault on CURRY to BAILEYCO 115kV line CKT 1, near CURRY 115kV for 16 cycles with stuck breaker at CURRY. Open the faulted line and DS-#20 to CURRY 115kV line CKT 1 and HEREFORD to DS-#6 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_283_P4_CURRY | Apply single-phase fault on CURRY to BAILEYCO 115kV line CKT 1, near CURRY 115kV for 16 cycles with stuck breaker at CURRY. Open the faulted line and DS-#20 to CURRY 115kV line CKT 1 and HEREFORD to DS-#6 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_283_P4_CURRY | Apply single-phase fault on CURRY to BAILEYCO 115kV line CKT 1, near CURRY 115kV for 16 cycles with stuck breaker at CURRY. Open the faulted line and DS-#20 to CURRY 115kV line CKT 1 and HEREFORD to DS-#6 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_284_P4_CURRY | Apply single-phase fault on E_CLOVIS to CURRY 115kV line CKT 1, near CURRY 115kV for 16 cycles with stuck breaker at CURRY. Open the faulted line and CURRY to FE-CLOVIS2+3 115kV line CKT 1 and PLSNT_HILL 3 to E_CLOVIS 115kV line CKT 1 and PLSNT_HILL 3 to FE-HOLLAND 3 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_284_P4_CURRY | Apply single-phase fault on E_CLOVIS to CURRY 115kV line CKT 1, near CURRY 115kV for 16 cycles with stuck breaker at CURRY. Open the faulted line and CURRY to FE-CLOVIS2+3 115kV line CKT 1 and PLSNT_HILL 3 to E_CLOVIS 115kV line CKT 1 and PLSNT_HILL 3 to FE-HOLLAND 3 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_284_P4_CURRY | Apply single-phase fault on E_CLOVIS to CURRY 115kV line CKT 1, near CURRY 115kV for 16 cycles with stuck breaker at CURRY. Open the faulted line and CURRY to FE-CLOVIS2+3 115kV line CKT 1 and PLSNT_HILL 3 to E_CLOVIS 115kV line CKT 1 and PLSNT_HILL 3 to FE-HOLLAND 3 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_284_P4_CURRY | Apply single-phase fault on E_CLOVIS to CURRY 115kV line CKT 1, near CURRY 115kV for 16 cycles with stuck breaker at CURRY. Open the faulted line and CURRY to FE-CLOVIS2+3 115kV line CKT 1 and PLSNT_HILL 3 to E_CLOVIS 115kV line CKT 1 and PLSNT_HILL 3 to FE-HOLLAND 3 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_285_P4_OASIS | Apply single-phase fault on OASIS_TR1 13.19kV/115kV/230kV transformer CKT 1, near OASIS 115kV for 16 cycles with stuck breaker at OASIS. Open the faulted Three Winding and OASIS to PORTALES 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_285_P4_OASIS | Apply single-phase fault on OASIS_TR1 13.19kV/115kV/230kV transformer CKT 1, near OASIS 115kV for 16 cycles with stuck breaker at OASIS. Open the faulted Three Winding and OASIS to PORTALES 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_285_P4_OASIS | Apply single-phase fault on OASIS_TR1 13.19kV/115kV/230kV transformer CKT 1, near OASIS 115kV for 16 cycles with stuck breaker at OASIS. Open the faulted Three Winding and OASIS to PORTALES 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_285_P4_OASIS | Apply single-phase fault on OASIS_TR1 13.19kV/115kV/230kV transformer CKT 1, near OASIS 115kV for 16 cycles with stuck breaker at OASIS. Open the faulted Three Winding and OASIS to PORTALES 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_286_P4_OASIS | Apply single-phase fault on OASIS to PORTALES 115kV line CKT 1, near OASIS 115kV for 16 cycles with stuck breaker at OASIS. Open the faulted line and FE-CHZPLT to OASIS 115kV line CKT 1 and NORRIS_TP to CURRY 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_286_P4_OASIS | Apply single-phase fault on OASIS to PORTALES 115kV line CKT 1, near OASIS 115kV for 16 cycles with stuck breaker at OASIS. Open the faulted line and FE-CHZPLT to OASIS 115kV line CKT 1 and NORRIS_TP to CURRY 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_286_P4_OASIS | Apply single-phase fault on OASIS to PORTALES 115kV line CKT 1, near OASIS 115kV for 16 cycles with stuck breaker at OASIS. Open the faulted line and FE-CHZPLT to OASIS 115kV line CKT 1 and NORRIS_TP to CURRY 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_286_P4_OASIS | Apply single-phase fault on OASIS to PORTALES 115kV line CKT 1, near OASIS 115kV for 16 cycles with stuck breaker at OASIS. Open the faulted line and FE-CHZPLT to OASIS 115kV line CKT 1 and NORRIS_TP to CURRY 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_287_P4_OASIS | Apply single-phase fault on PLSNT_HILL 6 to OASIS 230kV line CKT 1, near OASIS 230kV for 16 cycles with stuck breaker at OASIS. Open the faulted line and OASIS_TR1 13.19kV/115kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_287_P4_OASIS | Apply single-phase fault on PLSNT_HILL 6 to OASIS 230kV line CKT 1, near OASIS 230kV for 16 cycles with stuck breaker at OASIS. Open the faulted line and OASIS_TR1 13.19kV/115kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_287_P4_OASIS | Apply single-phase fault on PLSNT_HILL 6 to OASIS 230kV line CKT 1, near OASIS 230kV for 16 cycles with stuck breaker at OASIS. Open the faulted line and OASIS_TR1 13.19kV/115kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_287_P4_OASIS | Apply single-phase fault on PLSNT_HILL 6 to OASIS 230kV line CKT 1, near OASIS 230kV for 16 cycles with stuck breaker at OASIS. Open the faulted line and OASIS_TR1 13.19kV/115kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_288_P4_OASIS | Apply single-phase fault on OASIS to ROSEVELT_N 6 230kV line CKT 1, near OASIS 230kV for 16 cycles with stuck breaker at OASIS. Open the faulted line and PLSNT_HILL 6 to OASIS 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_288_P4_OASIS | Apply single-phase fault on OASIS to ROSEVELT_N 6 230kV line CKT 1, near OASIS 230kV for 16 cycles with stuck breaker at OASIS. Open the faulted line and PLSNT_HILL 6 to OASIS 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_288_P4_OASIS | Apply single-phase fault on OASIS to ROSEVELT_N 6 230kV line CKT 1, near OASIS 230kV for 16 cycles with stuck breaker at OASIS. Open the faulted line and PLSNT_HILL 6 to OASIS 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_288_P4_OASIS | Apply single-phase fault on OASIS to ROSEVELT_N 6 230kV line CKT 1, near OASIS 230kV for 16 cycles with stuck breaker at OASIS. Open the faulted line and PLSNT_HILL 6 to OASIS 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_289_P4_OASIS | Apply single-phase fault on OASIS to SN_JUAN_TAP6 230kV line CKT 1, near OASIS 230kV for 16 cycles with stuck breaker at OASIS. Open the faulted line and OASIS to ROSEVELT_N 6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_289_P4_OASIS | Apply single-phase fault on OASIS to SN_JUAN_TAP6 230kV line CKT 1, near OASIS 230kV for 16 cycles with stuck breaker at OASIS. Open the faulted line and OASIS to ROSEVELT_N 6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_289_P4_OASIS | Apply single-phase fault on OASIS to SN_JUAN_TAP6 230kV line CKT 1, near OASIS 230kV for 16 cycles with stuck breaker at OASIS. Open the faulted line and OASIS to ROSEVELT_N 6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_289_P4_OASIS | Apply single-phase fault on OASIS to SN_JUAN_TAP6 230kV line CKT 1, near OASIS 230kV for 16 cycles with stuck breaker at OASIS. Open the faulted line and OASIS to ROSEVELT_N 6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_29_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_29_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_29_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_29_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_290_P4_OASIS | Apply single-phase fault on OASIS_TR1 13.19kV/115kV/230kV transformer CKT 1, near OASIS 230kV for 16 cycles with stuck breaker at OASIS. Open the faulted Three Winding and OASIS to ROSEVELT_N 6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_290_P4_OASIS | Apply single-phase fault on OASIS_TR1 13.19kV/115kV/230kV transformer CKT 1, near OASIS 230kV for 16 cycles with stuck breaker at OASIS. Open the faulted Three Winding and OASIS to ROSEVELT_N 6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_290_P4_OASIS | Apply single-phase fault on OASIS_TR1 13.19kV/115kV/230kV transformer CKT 1, near OASIS 230kV for 16 cycles with stuck breaker at OASIS. Open the faulted Three Winding and OASIS to ROSEVELT_N 6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_290_P4_OASIS | Apply single-phase fault on OASIS_TR1 13.19kV/115kV/230kV transformer CKT 1, near OASIS 230kV for 16 cycles with stuck breaker at OASIS. Open the faulted Three Winding and OASIS to ROSEVELT_N 6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_291_P4_ROOSEVELT | Apply single-phase fault on CURRY to ROOSEVELT 115kV line CKT 2, near ROOSEVELT 115kV for 16 cycles with stuck breaker at ROOSEVELT. Open the faulted line and ROOSEVELT to PORTALES 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_291_P4_ROOSEVELT | Apply single-phase fault on CURRY to ROOSEVELT 115kV line CKT 2, near ROOSEVELT 115kV for 16 cycles with stuck breaker at ROOSEVELT. Open the faulted line and ROOSEVELT to PORTALES 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_291_P4_ROOSEVELT | Apply single-phase fault on CURRY to ROOSEVELT 115kV line CKT 2, near ROOSEVELT 115kV for 16 cycles with stuck breaker at ROOSEVELT. Open the faulted line and ROOSEVELT to PORTALES 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_291_P4_ROOSEVELT | Apply single-phase fault on CURRY to ROOSEVELT 115kV line CKT 2, near ROOSEVELT 115kV for 16 cycles with stuck breaker at ROOSEVELT. Open the faulted line and ROOSEVELT to PORTALES 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_292_P4_ROSEVELT_N6 | Apply single-phase fault on ROSEVELT_N 6 to TOLK_EAST 230kV line CKT 1, near ROSEVELT_N 6 230kV for 16 cycles with stuck breaker at ROSEVELT_N 6. Open the faulted line and ROSEVELT_N 6 to TOLK_WEST 230kV line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_292_P4_ROSEVELT_N6 | Apply single-phase fault on ROSEVELT_N 6 to TOLK_EAST 230kV line CKT 1, near ROSEVELT_N 6 230kV for 16 cycles with stuck breaker at ROSEVELT_N 6. Open the faulted line and ROSEVELT_N 6 to TOLK_WEST 230kV line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | No | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_292_P4_ROSEVELT_N6 | Apply single-phase fault on ROSEVELT_N 6 to TOLK_EAST 230kV line CKT 1, near ROSEVELT_N 6 230kV for 16 cycles with stuck breaker at ROSEVELT_N 6. Open the faulted line and ROSEVELT_N 6 to TOLK_WEST 230kV line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_292_P4_ROSEVELT_N6 | Apply single-phase fault on ROSEVELT_N 6 to TOLK_EAST 230kV line CKT 1, near ROSEVELT_N 6 230kV for 16 cycles with stuck breaker at ROSEVELT_N 6. Open the faulted line and ROSEVELT_N 6 to TOLK_WEST 230kV line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_293_P4_ROSEVELT_N6 | Apply single-phase fault on OASIS to ROSEVELT_N 6 230kV line CKT 1, near ROSEVELT_N 6 230kV for 16 cycles with stuck breaker at ROSEVELT_N 6. Open the faulted line and PLSNT_HILL 6 to ROSEVELT_N 6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_293_P4_ROSEVELT_N6 | Apply single-phase fault on OASIS to ROSEVELT_N 6 230kV line CKT 1, near ROSEVELT_N 6 230kV for 16 cycles with stuck breaker at ROSEVELT_N 6. Open the faulted line and PLSNT_HILL 6 to ROSEVELT_N 6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_293_P4_ROSEVELT_N6 | Apply single-phase fault on OASIS to ROSEVELT_N 6 230kV line CKT 1, near ROSEVELT_N 6 230kV for 16 cycles with stuck breaker at ROSEVELT_N 6. Open the faulted line and PLSNT_HILL 6 to ROSEVELT_N 6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_293_P4_ROSEVELT_N6 | Apply single-phase fault on OASIS to ROSEVELT_N 6 230kV line CKT 1, near ROSEVELT_N 6 230kV for 16 cycles with stuck breaker at ROSEVELT_N 6. Open the faulted line and PLSNT_HILL 6 to ROSEVELT_N 6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_294_P4_ROSEVELT_N6 | Apply single-phase fault on ROSEVLT_TR11 13.19kV/115kV/230kV transformer CKT 1, near ROSEVELT_N 6 230kV for 16 cycles with stuck breaker at ROSEVELT_N 6. Open the faulted Three Winding and PLSNT_HILL 6 to ROSEVELT_N 6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_294_P4_ROSEVELT_N6 | Apply single-phase fault on ROSEVLT_TR11 13.19kV/115kV/230kV transformer CKT 1, near ROSEVELT_N 6 230kV for 16 cycles with stuck breaker at ROSEVELT_N 6. Open the faulted Three Winding and PLSNT_HILL 6 to ROSEVELT_N 6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_294_P4_ROSEVELT_N6 | Apply single-phase fault on ROSEVLT_TR11 13.19kV/115kV/230kV transformer CKT 1, near ROSEVELT_N 6 230kV for 16 cycles with stuck breaker at ROSEVELT_N 6. Open the faulted Three Winding and PLSNT_HILL 6 to ROSEVELT_N 6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_294_P4_ROSEVELT_N6 | Apply single-phase fault on ROSEVLT_TR11 13.19kV/115kV/230kV transformer CKT 1, near ROSEVELT_N 6 230kV for 16 cycles with stuck breaker at ROSEVELT_N 6. Open the faulted Three Winding and PLSNT_HILL 6 to ROSEVELT_N 6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_295_P4_ROSEVELT_N6 | Apply single-phase fault on ROSEVLT_TR11 13.19kV/115kV/230kV transformer CKT 1, near ROSEVELT_N 6 230kV for 16 cycles with stuck breaker at ROSEVELT_N 6. Open the faulted Three Winding and OASIS to ROSEVELT_N 6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_295_P4_ROSEVELT_N6 | Apply single-phase fault on ROSEVLT_TR11 13.19kV/115kV/230kV transformer CKT 1, near ROSEVELT_N 6 230kV for 16 cycles with stuck breaker at ROSEVELT_N 6. Open the faulted Three Winding and OASIS to ROSEVELT_N 6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_295_P4_ROSEVELT_N6 | Apply single-phase fault on ROSEVLT_TR11 13.19kV/115kV/230kV transformer CKT 1, near ROSEVELT_N 6 230kV for 16 cycles with stuck breaker at ROSEVELT_N 6. Open the faulted Three Winding and OASIS to ROSEVELT_N 6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_295_P4_ROSEVELT_N6 | Apply single-phase fault on ROSEVLT_TR11 13.19kV/115kV/230kV transformer CKT 1, near ROSEVELT_N 6 230kV for 16 cycles with stuck breaker at ROSEVELT_N 6. Open the faulted Three Winding and OASIS to ROSEVELT_N 6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_296_P4_KRESS_INT | Apply single-phase fault on KRESS_INT to NEWHART 115kV line CKT 1, near KRESS_INT 115kV for 16 cycles with stuck breaker at KRESS_INT. Open the faulted line and TULIA_TP to KRESS_INT 115kV line CKT 1 and HAPPY_INT to TULIA_TP 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_296_P4_KRESS_INT | Apply single-phase fault on KRESS_INT to NEWHART 115kV line CKT 1, near KRESS_INT 115kV for 16 cycles with stuck breaker at KRESS_INT. Open the faulted line and TULIA_TP to KRESS_INT 115kV line CKT 1 and HAPPY_INT to TULIA_TP 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_296_P4_KRESS_INT | Apply single-phase fault on KRESS_INT to NEWHART 115kV line CKT 1, near KRESS_INT 115kV for 16 cycles with stuck breaker at KRESS_INT. Open the faulted line and TULIA_TP to KRESS_INT 115kV line CKT 1 and HAPPY_INT to TULIA_TP 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_296_P4_KRESS_INT | Apply single-phase fault on KRESS_INT to NEWHART 115kV line CKT 1, near KRESS_INT 115kV for 16 cycles with stuck breaker at KRESS_INT. Open the faulted line and TULIA_TP to KRESS_INT 115kV line CKT 1 and HAPPY_INT to TULIA_TP 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_297_P4_KRESS_INT | Apply single-phase fault on KRESS_INT to SWISHER 115kV line CKT 1, near KRESS_INT 115kV for 16 cycles with stuck breaker at KRESS_INT. Open the faulted line and TULIA_TP to KRESS_INT 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_297_P4_KRESS_INT | Apply single-phase fault on KRESS_INT to SWISHER 115kV line CKT 1, near KRESS_INT 115kV for 16 cycles with stuck breaker at KRESS_INT. Open the faulted line and TULIA_TP to KRESS_INT 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_297_P4_KRESS_INT | Apply single-phase fault on KRESS_INT to SWISHER 115kV line CKT 1, near KRESS_INT 115kV for 16 cycles with stuck breaker at KRESS_INT. Open the faulted line and TULIA_TP to KRESS_INT 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_297_P4_KRESS_INT | Apply single-phase fault on KRESS_INT to SWISHER 115kV line CKT 1, near KRESS_INT 115kV for 16 cycles with stuck breaker at KRESS_INT. Open the faulted line and TULIA_TP to KRESS_INT 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_298_P4_KRESS_INT | Apply single-phase fault on KRESS_INT to KRS_RURL_TP3 115kV line CKT 1, near KRESS_INT 115kV for 16 cycles with stuck breaker at KRESS_INT. Open the faulted line and KRESS_INT to HALE_CNTY 115kV line CKT 1 and KISER to COX 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_298_P4_KRESS_INT | Apply single-phase fault on KRESS_INT to KRS_RURL_TP3 115kV line CKT 1, near KRESS_INT 115kV for 16 cycles with stuck breaker at KRESS_INT. Open the faulted line and KRESS_INT to HALE_CNTY 115kV line CKT 1 and KISER to COX 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_298_P4_KRESS_INT | Apply single-phase fault on KRESS_INT to KRS_RURL_TP3 115kV line CKT 1, near KRESS_INT 115kV for 16 cycles with stuck breaker at KRESS_INT. Open the faulted line and KRESS_INT to HALE_CNTY 115kV line CKT 1 and KISER to COX 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_298_P4_KRESS_INT | Apply single-phase fault on KRESS_INT to KRS_RURL_TP3 115kV line CKT 1, near KRESS_INT 115kV for 16 cycles with stuck breaker at KRESS_INT. Open the faulted line and KRESS_INT to HALE_CNTY 115kV line CKT 1 and KISER to COX 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_299_P4_SWISHER | Apply single-phase fault on SWISHER to NEWHART 230kV line CKT 1, near SWISHER 230kV for 16 cycles with stuck breaker at SWISHER. Open the faulted line and AMA_SOUTH to SWISHER 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_299_P4_SWISHER | Apply single-phase fault on SWISHER to NEWHART 230kV line CKT 1, near SWISHER 230kV for 16 cycles with stuck breaker at SWISHER. Open the faulted line and AMA_SOUTH to SWISHER 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_299_P4_SWISHER | Apply single-phase fault on SWISHER to NEWHART 230kV line CKT 1, near SWISHER 230kV for 16 cycles with stuck breaker at SWISHER. Open the faulted line and AMA_SOUTH to SWISHER 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_299_P4_SWISHER | Apply single-phase fault on SWISHER to NEWHART 230kV line CKT 1, near SWISHER 230kV for 16 cycles with stuck breaker at SWISHER. Open the faulted line and AMA_SOUTH to SWISHER 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_3_P1_OKU-7 | Apply 3-phase fault on DC line SPP_44_OKLUN, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted DC line. | P1 | Stable | Yes | Yes | Yes | No | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_3_P1_OKU-7 | Apply 3-phase fault on DC line SPP_44_OKLUN, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted DC line. | P1 | Stable | Yes | Yes | Yes | No | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_3_P1_OKU-7 | Apply 3-phase fault on DC line SPP_44_OKLUN, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted DC line. | P1 | Stable | Yes | Yes | Yes | No | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_3_P1_OKU-7 | Apply 3-phase fault on DC line SPP_44_OKLUN, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted DC line. | P1 | Stable | Yes | Yes | Yes | No | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_30_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to ROLLHILLS 230kV line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_30_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to ROLLHILLS 230kV line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_30_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to ROLLHILLS 230kV line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_30_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to ROLLHILLS 230kV line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_300_P4_SWISHER | Apply single-phase fault on SWISHER to TUCO_INT 230kV line CKT 1, near SWISHER 230kV for 16 cycles with stuck breaker at SWISHER. Clear fault by tripping the faulted line. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_300_P4_SWISHER | Apply single-phase fault on SWISHER to TUCO_INT 230kV line CKT 1, near SWISHER 230kV for 16 cycles with stuck breaker at SWISHER. Clear fault by tripping the faulted line. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_300_P4_SWISHER | Apply single-phase fault on SWISHER to TUCO_INT 230kV line CKT 1, near SWISHER 230kV for 16 cycles with stuck breaker at SWISHER. Clear fault by tripping the faulted line. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_300_P4_SWISHER | Apply single-phase fault on SWISHER to TUCO_INT 230kV line CKT 1, near SWISHER 230kV for 16 cycles with stuck breaker at SWISHER. Clear fault by tripping the faulted line. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_301_P4_SWISHER | Apply single-phase fault on AMA_SOUTH to SWISHER 230kV line CKT 1, near SWISHER 230kV for 16 cycles with stuck breaker at SWISHER. Open the faulted line and SWISHER to TUCO_INT 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_301_P4_SWISHER | Apply single-phase fault on AMA_SOUTH to SWISHER 230kV line CKT 1, near SWISHER 230kV for 16 cycles with stuck breaker at SWISHER. Open the faulted line and SWISHER to TUCO_INT 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_301_P4_SWISHER | Apply single-phase fault on AMA_SOUTH to SWISHER 230kV line CKT 1, near SWISHER 230kV for 16 cycles with stuck breaker at SWISHER. Open the faulted line and SWISHER to TUCO_INT 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_301_P4_SWISHER | Apply single-phase fault on AMA_SOUTH to SWISHER 230kV line CKT 1, near SWISHER 230kV for 16 cycles with stuck breaker at SWISHER. Open the faulted line and SWISHER to TUCO_INT 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_302_P4_LAMTON | Apply single-phase fault on LAMTON_TR1 1 13.19kV/69kV/115kV transformer CKT 1, near LAMTON 115kV for 16 cycles with stuck breaker at LAMTON. Open the faulted Three Winding and LAMTON to HALE_CNTY 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_302_P4_LAMTON | Apply single-phase fault on LAMTON_TR1 1 13.19kV/69kV/115kV transformer CKT 1, near LAMTON 115kV for 16 cycles with stuck breaker at LAMTON. Open the faulted Three Winding and LAMTON to HALE_CNTY 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_302_P4_LAMTON | Apply single-phase fault on LAMTON_TR1 1 13.19kV/69kV/115kV transformer CKT 1, near LAMTON 115kV for 16 cycles with stuck breaker at LAMTON. Open the faulted Three Winding and LAMTON to HALE_CNTY 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_302_P4_LAMTON | Apply single-phase fault on LAMTON_TR1 1 13.19kV/69kV/115kV transformer CKT 1, near LAMTON 115kV for 16 cycles with stuck breaker at LAMTON. Open the faulted Three Winding and LAMTON to HALE_CNTY 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_303_P4_HALE_CNTY | Apply single-phase fault on HALE_CNTY to PLANT_X 115kV line CKT 1, near HALE_CNTY 115kV for 16 cycles with stuck breaker at HALE_CNTY. Open the faulted line and LAMTON to HALE_CNTY 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_303_P4_HALE_CNTY | Apply single-phase fault on HALE_CNTY to PLANT_X 115kV line CKT 1, near HALE_CNTY 115kV for 16 cycles with stuck breaker at HALE_CNTY. Open the faulted line and LAMTON to HALE_CNTY 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_303_P4_HALE_CNTY | Apply single-phase fault on HALE_CNTY to PLANT_X 115kV line CKT 1, near HALE_CNTY 115kV for 16 cycles with stuck breaker at HALE_CNTY. Open the faulted line and LAMTON to HALE_CNTY 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_303_P4_HALE_CNTY | Apply single-phase fault on HALE_CNTY to PLANT_X 115kV line CKT 1, near HALE_CNTY 115kV for 16 cycles with stuck breaker at HALE_CNTY. Open the faulted line and LAMTON to HALE_CNTY 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_304_P4_HALE_CNTY | Apply single-phase fault on HALE_CNTY to TUCO_INT 115kV line CKT 1, near HALE_CNTY 115kV for 16 cycles with stuck breaker at HALE_CNTY. Open the faulted line and COX to HALE_CNTY 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_304_P4_HALE_CNTY | Apply single-phase fault on HALE_CNTY to TUCO_INT 115kV line CKT 1, near HALE_CNTY 115kV for 16 cycles with stuck breaker at HALE_CNTY. Open the faulted line and COX to HALE_CNTY 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_304_P4_HALE_CNTY | Apply single-phase fault on HALE_CNTY to TUCO_INT 115kV line CKT 1, near HALE_CNTY 115kV for 16 cycles with stuck breaker at HALE_CNTY. Open the faulted line and COX to HALE_CNTY 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_304_P4_HALE_CNTY | Apply single-phase fault on HALE_CNTY to TUCO_INT 115kV line CKT 1, near HALE_CNTY 115kV for 16 cycles with stuck breaker at HALE_CNTY. Open the faulted line and COX to HALE_CNTY 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_305_P4_NEWHART | Apply single-phase fault on NEWHART_TR21 13.19kV/115kV/230kV transformer CKT 2, near NEWHART 115kV for 16 cycles with stuck breaker at NEWHART. Open the faulted Three Winding and NEWHART_TR11 13.19kV/115kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_305_P4_NEWHART | Apply single-phase fault on NEWHART_TR21 13.19kV/115kV/230kV transformer CKT 2, near NEWHART 115kV for 16 cycles with stuck breaker at NEWHART. Open the faulted Three Winding and NEWHART_TR11 13.19kV/115kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_305_P4_NEWHART | Apply single-phase fault on NEWHART_TR21 13.19kV/115kV/230kV transformer CKT 2, near NEWHART 115kV for 16 cycles with stuck breaker at NEWHART. Open the faulted Three Winding and NEWHART_TR11 13.19kV/115kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_305_P4_NEWHART | Apply single-phase fault on NEWHART_TR21 13.19kV/115kV/230kV transformer CKT 2, near NEWHART 115kV for 16 cycles with stuck breaker at NEWHART. Open the faulted Three Winding and NEWHART_TR11 13.19kV/115kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_306_P4_NEWHART | Apply single-phase fault on HART_INDUST3 to NEWHART 115kV line CKT 1, near NEWHART 115kV for 16 cycles with stuck breaker at NEWHART. Open the faulted line and CASTRO_CNTY3 to NEWHART 115kV line CKT 1 and HART_INDUST3 to LAMTON 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_306_P4_NEWHART | Apply single-phase fault on HART_INDUST3 to NEWHART 115kV line CKT 1, near NEWHART 115kV for 16 cycles with stuck breaker at NEWHART. Open the faulted line and CASTRO_CNTY3 to NEWHART 115kV line CKT 1 and HART_INDUST3 to LAMTON 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_306_P4_NEWHART | Apply single-phase fault on HART_INDUST3 to NEWHART 115kV line CKT 1, near NEWHART 115kV for 16 cycles with stuck breaker at NEWHART. Open the faulted line and CASTRO_CNTY3 to NEWHART 115kV line CKT 1 and HART_INDUST3 to LAMTON 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_306_P4_NEWHART | Apply single-phase fault on HART_INDUST3 to NEWHART 115kV line CKT 1, near NEWHART 115kV for 16 cycles with stuck breaker at NEWHART. Open the faulted line and CASTRO_CNTY3 to NEWHART 115kV line CKT 1 and HART_INDUST3 to LAMTON 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_307_P4_NEWHART | Apply single-phase fault on SWISHER to NEWHART 230kV line CKT 1, near NEWHART 230kV for 16 cycles with stuck breaker at NEWHART. Open the faulted line and NEWPOT_SS to NEWHART 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_307_P4_NEWHART | Apply single-phase fault on SWISHER to NEWHART 230kV line CKT 1, near NEWHART 230kV for 16 cycles with stuck breaker at NEWHART. Open the faulted line and NEWPOT_SS to NEWHART 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_307_P4_NEWHART | Apply single-phase fault on SWISHER to NEWHART 230kV line CKT 1, near NEWHART 230kV for 16 cycles with stuck breaker at NEWHART. Open the faulted line and NEWPOT_SS to NEWHART 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_307_P4_NEWHART | Apply single-phase fault on SWISHER to NEWHART 230kV line CKT 1, near NEWHART 230kV for 16 cycles with stuck breaker at NEWHART. Open the faulted line and NEWPOT_SS to NEWHART 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_308_P4_PLANT_X | Apply single-phase fault on HALE_CNTY to PLANT_X 115kV line CKT 1, near PLANT_X 115kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted line and RKYFORD_TP 3 to PLANT_X 115kV line CKT 1 and LAMTON to LC-S_OLTON+3 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_308_P4_PLANT_X | Apply single-phase fault on HALE_CNTY to PLANT_X 115kV line CKT 1, near PLANT_X 115kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted line and RKYFORD_TP 3 to PLANT_X 115kV line CKT 1 and LAMTON to LC-S_OLTON+3 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_309_P4_PLANT_X | Apply single-phase fault on LC-S_OLTON+3 to PLANT_X 115kV line CKT 1, near PLANT_X 115kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted line and HALE_CNTY to PLANT_X 115kV line CKT 1 and LAMTON to LC-S_OLTON+3 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_309_P4_PLANT_X | Apply single-phase fault on LC-S_OLTON+3 to PLANT_X 115kV line CKT 1, near PLANT_X 115kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted line and HALE_CNTY to PLANT_X 115kV line CKT 1 and LAMTON to LC-S_OLTON+3 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_31_P1_POTTER_CO | Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_31_P1_POTTER_CO | Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_31_P1_POTTER_CO | Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_31_P1_POTTER_CO | Apply 3-phase fault on HITCHLAND to POTTER_CO 345kV line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_310_P4_PLANT_X | Apply single-phase fault on PLANT_X to LAMB_CNTY 115kV line CKT 1, near PLANT_X 115kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted line and PLANTX_TR1 1 13.19kV/115kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_310_P4_PLANT_X | Apply single-phase fault on PLANT_X to LAMB_CNTY 115kV line CKT 1, near PLANT_X 115kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted line and PLANTX_TR1 1 13.19kV/115kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_310_P4_PLANT_X | Apply single-phase fault on PLANT_X to LAMB_CNTY 115kV line CKT 1, near PLANT_X 115kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted line and PLANTX_TR1 1 13.19kV/115kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_311_P4_PLANT_X | Apply single-phase fault on BC-EARTH to PLANT_X 115kV line CKT 1, near PLANT_X 115kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted line and CASTRO_CNTY3 to BC-KELLEY +3 115kV line CKT 1 and MULSHVLY_TP3 to PLANT_X 115kV line CKT 1 and MULSHVLY_TP3 to BAILEYCO 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_311_P4_PLANT_X | Apply single-phase fault on BC-EARTH to PLANT_X 115kV line CKT 1, near PLANT_X 115kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted line and CASTRO_CNTY3 to BC-KELLEY +3 115kV line CKT 1 and MULSHVLY_TP3 to PLANT_X 115kV line CKT 1 and MULSHVLY_TP3 to BAILEYCO 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_311_P4_PLANT_X | Apply single-phase fault on BC-EARTH to PLANT_X 115kV line CKT 1, near PLANT_X 115kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted line and CASTRO_CNTY3 to BC-KELLEY +3 115kV line CKT 1 and MULSHVLY_TP3 to PLANT_X 115kV line CKT 1 and MULSHVLY_TP3 to BAILEYCO 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_311_P4_PLANT_X | Apply single-phase fault on BC-EARTH to PLANT_X 115kV line CKT 1, near PLANT_X 115kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted line and CASTRO_CNTY3 to BC-KELLEY +3 115kV line CKT 1 and MULSHVLY_TP3 to PLANT_X 115kV line CKT 1 and MULSHVLY_TP3 to BAILEYCO 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_312_P4_PLANT_X | Apply single-phase fault on PLANT_X to W_LITLFLDTP3 115kV line CKT 1, near PLANT_X 115kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted line and W_LITLFLDTP3 to LAMB_CNTY 115kV line CKT 1 and PLANTX_TR1 1 13.19kV/115kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_313_P4_PLANT_X | Apply single-phase fault on PLANT_X to TOLK_WEST 230kV line CKT 1, near PLANT_X 230kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted line and PLANT_X to TOLK_EAST 230kV line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.04s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_313_P4_PLANT_X | Apply single-phase fault on PLANT_X to TOLK_WEST 230kV line CKT 1, near PLANT_X 230kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted line and PLANT_X to TOLK_EAST 230kV line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_313_P4_PLANT_X | Apply single-phase fault on PLANT_X to TOLK_WEST 230kV line CKT 1, near PLANT_X 230kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted line and PLANT_X to TOLK_EAST 230kV line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_313_P4_PLANT_X | Apply single-phase fault on PLANT_X to TOLK_WEST 230kV line CKT 1, near PLANT_X 230kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted line and PLANT_X to TOLK_EAST 230kV line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_314_P4_PLANT_X | Apply single-phase fault on NEWHART to PLANT_X 230kV line CKT 1, near PLANT_X 230kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted line and DEAFSMITH to PLANT_X 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.04s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_314_P4_PLANT_X | Apply single-phase fault on NEWHART to PLANT_X 230kV line CKT 1, near PLANT_X 230kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted line and DEAFSMITH to PLANT_X 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_314_P4_PLANT_X | Apply single-phase fault on NEWHART to PLANT_X 230kV line CKT 1, near PLANT_X 230kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted line and DEAFSMITH to PLANT_X 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_314_P4_PLANT_X | Apply single-phase fault on NEWHART to PLANT_X 230kV line CKT 1, near PLANT_X 230kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted line and DEAFSMITH to PLANT_X 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_315_P4_PLANT_X | Apply single-phase fault on PLANT_X to TOLK_WEST 230kV line CKT 1, near PLANT_X 230kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted line and PLANT_X to SUNDOWN 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.04s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_315_P4_PLANT_X | Apply single-phase fault on PLANT_X to TOLK_WEST 230kV line CKT 1, near PLANT_X 230kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted line and PLANT_X to SUNDOWN 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_315_P4_PLANT_X | Apply single-phase fault on PLANT_X to TOLK_WEST 230kV line CKT 1, near PLANT_X 230kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted line and PLANT_X to SUNDOWN 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_315_P4_PLANT_X | Apply single-phase fault on PLANT_X to TOLK_WEST 230kV line CKT 1, near PLANT_X 230kV for 16 cycles with stuck breaker at PLANT_X. Open the faulted line and PLANT_X to SUNDOWN 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_316_P4_TOLK_EAST | Apply single-phase fault on PLANT_X to TOLK_EAST 230kV line CKT 2, near TOLK_EAST 230kV for 16 cycles with stuck breaker at TOLK_EAST. Open the faulted line and TOLK_EAST to TUCO_INT 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_316_P4_TOLK_EAST | Apply single-phase fault on PLANT_X to TOLK_EAST 230kV line CKT 2, near TOLK_EAST 230kV for 16 cycles with stuck breaker at TOLK_EAST. Open the faulted line and TOLK_EAST to TUCO_INT 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_316_P4_TOLK_EAST | Apply single-phase fault on PLANT_X to TOLK_EAST 230kV line CKT 2, near TOLK_EAST 230kV for 16 cycles with stuck breaker at TOLK_EAST. Open the faulted line and TOLK_EAST to TUCO_INT 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_316_P4_TOLK_EAST | Apply single-phase fault on PLANT_X to TOLK_EAST 230kV line CKT 2, near TOLK_EAST 230kV for 16 cycles with stuck breaker at TOLK_EAST. Open the faulted line and TOLK_EAST to TUCO_INT 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_317_P4_TOLK_WEST | Apply single-phase fault on TOLK_WEST to NEEDMORE 230kV line CKT 1, near TOLK_WEST 230kV for 16 cycles with stuck breaker at TOLK_WEST. Open the faulted line and PLANT_X to TOLK_WEST 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | No | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_317_P4_TOLK_WEST | Apply single-phase fault on TOLK_WEST to NEEDMORE 230kV line CKT 1, near TOLK_WEST 230kV for 16 cycles with stuck breaker at TOLK_WEST. Open the faulted line and PLANT_X to TOLK_WEST 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | No | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_317_P4_TOLK_WEST | Apply single-phase fault on TOLK_WEST to NEEDMORE 230kV line CKT 1, near TOLK_WEST 230kV for 16 cycles with stuck breaker at TOLK_WEST. Open the faulted line and PLANT_X to TOLK_WEST 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_317_P4_TOLK_WEST | Apply single-phase fault on TOLK_WEST to NEEDMORE 230kV line CKT 1, near TOLK_WEST 230kV for 16 cycles with stuck breaker at TOLK_WEST. Open the faulted line and PLANT_X to TOLK_WEST 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_318_P4_TOLK_WEST | Apply single-phase fault on ROSEVELT_N 6 to TOLK_WEST 230kV line CKT 2, near TOLK_WEST 230kV for 16 cycles with stuck breaker at TOLK_WEST. Open the faulted line and TOLK_WEST to NEEDMORE 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | No | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_318_P4_TOLK_WEST | Apply single-phase fault on ROSEVELT_N 6 to TOLK_WEST 230kV line CKT 2, near TOLK_WEST 230kV for 16 cycles with stuck breaker at TOLK_WEST. Open the faulted line and TOLK_WEST to NEEDMORE 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | No | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_318_P4_TOLK_WEST | Apply single-phase fault on ROSEVELT_N 6 to TOLK_WEST 230kV line CKT 2, near TOLK_WEST 230kV for 16 cycles with stuck breaker at TOLK_WEST. Open the faulted line and TOLK_WEST to NEEDMORE 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_318_P4_TOLK_WEST | Apply single-phase fault on ROSEVELT_N 6 to TOLK_WEST 230kV line CKT 2, near TOLK_WEST 230kV for 16 cycles with stuck breaker at TOLK_WEST. Open the faulted line and TOLK_WEST to NEEDMORE 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_319_P4_TOLK_WEST | Apply single-phase fault on PLANT_X to TOLK_WEST 230kV line CKT 1, near TOLK_WEST 230kV for 16 cycles with stuck breaker at TOLK_WEST. Open the faulted line and LAMB_TR3 13.19kV/115kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_319_P4_TOLK_WEST | Apply single-phase fault on PLANT_X to TOLK_WEST 230kV line CKT 1, near TOLK_WEST 230kV for 16 cycles with stuck breaker at TOLK_WEST. Open the faulted line and LAMB_TR3 13.19kV/115kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_319_P4_TOLK_WEST | Apply single-phase fault on PLANT_X to TOLK_WEST 230kV line CKT 1, near TOLK_WEST 230kV for 16 cycles with stuck breaker at TOLK_WEST. Open the faulted line and LAMB_TR3 13.19kV/115kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | No | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_319_P4_TOLK_WEST | Apply single-phase fault on PLANT_X to TOLK_WEST 230kV line CKT 1, near TOLK_WEST 230kV for 16 cycles with stuck breaker at TOLK_WEST. Open the faulted line and LAMB_TR3 13.19kV/115kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_32_P1_HARRNG_WST6 | Apply 3-phase fault on HARRNG_WST 6 to ROLLHILLS 230kV line CKT 1, near HARRNG_WST 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_32_P1_HARRNG_WST6 | Apply 3-phase fault on HARRNG_WST 6 to ROLLHILLS 230kV line CKT 1, near HARRNG_WST 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_32_P1_HARRNG_WST6 | Apply 3-phase fault on HARRNG_WST 6 to ROLLHILLS 230kV line CKT 1, near HARRNG_WST 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_32_P1_HARRNG_WST6 | Apply 3-phase fault on HARRNG_WST 6 to ROLLHILLS 230kV line CKT 1, near HARRNG_WST 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_320_P4_TOLK_TAP | Apply single-phase fault on TOLK_TR 13.19kV/230kV/345kV transformer CKT 2, near TOLK_TAP 230kV for 16 cycles with stuck breaker at TOLK_TAP. Open the faulted Three Winding and TOLK_TR 13.19kV/230kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_320_P4_TOLK_TAP | Apply single-phase fault on TOLK_TR 13.19kV/230kV/345kV transformer CKT 2, near TOLK_TAP 230kV for 16 cycles with stuck breaker at TOLK_TAP. Open the faulted Three Winding and TOLK_TR 13.19kV/230kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_320_P4_TOLK_TAP | Apply single-phase fault on TOLK_TR 13.19kV/230kV/345kV transformer CKT 2, near TOLK_TAP 230kV for 16 cycles with stuck breaker at TOLK_TAP. Open the faulted Three Winding and TOLK_TR 13.19kV/230kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_320_P4_TOLK_TAP | Apply single-phase fault on TOLK_TR 13.19kV/230kV/345kV transformer CKT 2, near TOLK_TAP 230kV for 16 cycles with stuck breaker at TOLK_TAP. Open the faulted Three Winding and TOLK_TR 13.19kV/230kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_321_P4_TUCO_INT | Apply single-phase fault on TUCO_TR4 13.19kV/115kV/230kV transformer CKT 1, near TUCO_INT 115kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding and TUCO_TR3 13.19kV/115kV/230kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_321_P4_TUCO_INT | Apply single-phase fault on TUCO_TR4 13.19kV/115kV/230kV transformer CKT 1, near TUCO_INT 115kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding and TUCO_TR3 13.19kV/115kV/230kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_321_P4_TUCO_INT | Apply single-phase fault on TUCO_TR4 13.19kV/115kV/230kV transformer CKT 1, near TUCO_INT 115kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding and TUCO_TR3 13.19kV/115kV/230kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_321_P4_TUCO_INT | Apply single-phase fault on TUCO_TR4 13.19kV/115kV/230kV transformer CKT 1, near TUCO_INT 115kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding and TUCO_TR3 13.19kV/115kV/230kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_322_P4_TUCO_INT | Apply single-phase fault on TUCO_SVC generation unit 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Generator and SWISHER to TUCO_INT 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_322_P4_TUCO_INT | Apply single-phase fault on TUCO_SVC generation unit 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Generator and SWISHER to TUCO_INT 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_322_P4_TUCO_INT | Apply single-phase fault on TUCO_SVC generation unit 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Generator and SWISHER to TUCO_INT 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_322_P4_TUCO_INT | Apply single-phase fault on TUCO_SVC generation unit 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Generator and SWISHER to TUCO_INT 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_323_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding and TUCO_SVC generation unit 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_323_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding and TUCO_SVC generation unit 1 and clear the fault. | P4 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_323_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding and TUCO_SVC generation unit 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_323_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding and TUCO_SVC generation unit 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_324_P4_TUCO_INT | Apply single-phase fault on TUCO_INT to CARLISLE 230kV line CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted line and TUCO_INT to JONES 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_324_P4_TUCO_INT | Apply single-phase fault on TUCO_INT to CARLISLE 230kV line CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted line and TUCO_INT to JONES 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_324_P4_TUCO_INT | Apply single-phase fault on TUCO_INT to CARLISLE 230kV line CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted line and TUCO_INT to JONES 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_324_P4_TUCO_INT | Apply single-phase fault on TUCO_INT to CARLISLE 230kV line CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted line and TUCO_INT to JONES 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_325_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding and SWISHER to TUCO_INT 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_325_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding and SWISHER to TUCO_INT 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_325_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding and SWISHER to TUCO_INT 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_325_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding and SWISHER to TUCO_INT 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_326_P4_TUCO_INT | Apply single-phase fault on TOLK_EAST to TUCO_INT 230kV line CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted line and TUCO_INT to CARLISLE 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_326_P4_TUCO_INT | Apply single-phase fault on TOLK_EAST to TUCO_INT 230kV line CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted line and TUCO_INT to CARLISLE 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_326_P4_TUCO_INT | Apply single-phase fault on TOLK_EAST to TUCO_INT 230kV line CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted line and TUCO_INT to CARLISLE 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_326_P4_TUCO_INT | Apply single-phase fault on TOLK_EAST to TUCO_INT 230kV line CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted line and TUCO_INT to CARLISLE 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_327_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding and TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Unstable | No | No | No | No | Yes | No | Angular and system instability was observed in the G6 region. The stability issue was resolved with the SVC mitigation solution. | ±600 MVAr SVC at Crossroad 765kV
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_327_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding and TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | No | Yes | No | Yes | Voltage Spike: 1.23pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_327_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding and TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_327_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 230kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding and TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_430_P4_CRAWFISH_DR | Apply single-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near CRAWFISH_DR 345kV for 16 cycles with stuck breaker at CRAWFISH_DR . Open the faulted Transmission Circuit and BORDER to CRAWFISH_DR 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_430_P4_CRAWFISH_DR | Apply single-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near CRAWFISH_DR 345kV for 16 cycles with stuck breaker at CRAWFISH_DR . Open the faulted Transmission Circuit and BORDER to CRAWFISH_DR 345kV transmission line CKT 1 and clear the fault. | P4 | Unstable | No | No | No | No | No | No | Angular and system instability was observed in the G6 region. Simulation was rerun with the Crossroad SVC option. No stability or damping issues were observed with the Crossroad SVC. | ±600 MVAr SVC at Crossroad 765kV
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_430_P4_CRAWFISH_DR | Apply single-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near CRAWFISH_DR 345kV for 16 cycles with stuck breaker at CRAWFISH_DR . Open the faulted Transmission Circuit and BORDER to CRAWFISH_DR 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes | Voltage Spike: 1.21pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_430_P4_CRAWFISH_DR | Apply single-phase fault on TUCO_INT to CRAWFISH_DR 345kV transmission line CKT 2, near CRAWFISH_DR 345kV for 16 cycles with stuck breaker at CRAWFISH_DR . Open the faulted Transmission Circuit and BORDER to CRAWFISH_DR 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes | Voltage Spike: 1.24pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_329_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding and TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Unstable | No | No | No | No | Yes | No | Angular and system instability was observed in the G6 region. Simulation was rerun with the Crossroad SVC mitigation option and no stability or damping issues were observed. | ±600 MVAr SVC at Crossroad 765kV
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_329_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding and TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | No | Yes | No | Yes | Voltage Spike: 1.22pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_329_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding and TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_329_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding and TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_33_P1_HARRNG_WST6 | Apply 3-phase fault on HARRNG_WST 6 to NICHOLS 230kV line CKT 1, near HARRNG_WST 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_33_P1_HARRNG_WST6 | Apply 3-phase fault on HARRNG_WST 6 to NICHOLS 230kV line CKT 1, near HARRNG_WST 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_33_P1_HARRNG_WST6 | Apply 3-phase fault on HARRNG_WST 6 to NICHOLS 230kV line CKT 1, near HARRNG_WST 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_33_P1_HARRNG_WST6 | Apply 3-phase fault on HARRNG_WST 6 to NICHOLS 230kV line CKT 1, near HARRNG_WST 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_330_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding and TUCO_INT to CRAWFISH_DR 345kV line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_330_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding and TUCO_INT to CRAWFISH_DR 345kV line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_330_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding and TUCO_INT to CRAWFISH_DR 345kV line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_330_P4_TUCO_INT | Apply single-phase fault on TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1, near TUCO_INT 345kV for 16 cycles with stuck breaker at TUCO_INT. Open the faulted Three Winding and TUCO_INT to CRAWFISH_DR 345kV line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_331_P4_DEAN_INTG | Apply single-phase fault on DEAN_INTTR11 13.19kV/115kV/230kV transformer CKT 1, near DEAN_INTG 230kV for 16 cycles with stuck breaker at DEAN_INTG. Open the faulted Three Winding and DEAN_INTG to YOAKUM 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_331_P4_DEAN_INTG | Apply single-phase fault on DEAN_INTTR11 13.19kV/115kV/230kV transformer CKT 1, near DEAN_INTG 230kV for 16 cycles with stuck breaker at DEAN_INTG. Open the faulted Three Winding and DEAN_INTG to YOAKUM 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_331_P4_DEAN_INTG | Apply single-phase fault on DEAN_INTTR11 13.19kV/115kV/230kV transformer CKT 1, near DEAN_INTG 230kV for 16 cycles with stuck breaker at DEAN_INTG. Open the faulted Three Winding and DEAN_INTG to YOAKUM 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_331_P4_DEAN_INTG | Apply single-phase fault on DEAN_INTTR11 13.19kV/115kV/230kV transformer CKT 1, near DEAN_INTG 230kV for 16 cycles with stuck breaker at DEAN_INTG. Open the faulted Three Winding and DEAN_INTG to YOAKUM 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_332_P4_CARLISLE | Apply single-phase fault on CARLISLE to WOLFFORTH 230kV line CKT 1, near CARLISLE 230kV for 16 cycles with stuck breaker at CARLISLE. Open the faulted line and LP-MCDONALD6 to CARLISLE 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_332_P4_CARLISLE | Apply single-phase fault on CARLISLE to WOLFFORTH 230kV line CKT 1, near CARLISLE 230kV for 16 cycles with stuck breaker at CARLISLE. Open the faulted line and LP-MCDONALD6 to CARLISLE 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_332_P4_CARLISLE | Apply single-phase fault on CARLISLE to WOLFFORTH 230kV line CKT 1, near CARLISLE 230kV for 16 cycles with stuck breaker at CARLISLE. Open the faulted line and LP-MCDONALD6 to CARLISLE 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_332_P4_CARLISLE | Apply single-phase fault on CARLISLE to WOLFFORTH 230kV line CKT 1, near CARLISLE 230kV for 16 cycles with stuck breaker at CARLISLE. Open the faulted line and LP-MCDONALD6 to CARLISLE 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_333_P4_JONES | Apply single-phase fault on LUBBCK_STH 6 to JONES 230kV line CKT 2, near JONES 230kV for 16 cycles with stuck breaker at JONES. Open the faulted line and LUBBCK_STH 6 to JONES 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_333_P4_JONES | Apply single-phase fault on LUBBCK_STH 6 to JONES 230kV line CKT 2, near JONES 230kV for 16 cycles with stuck breaker at JONES. Open the faulted line and LUBBCK_STH 6 to JONES 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_333_P4_JONES | Apply single-phase fault on LUBBCK_STH 6 to JONES 230kV line CKT 2, near JONES 230kV for 16 cycles with stuck breaker at JONES. Open the faulted line and LUBBCK_STH 6 to JONES 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_333_P4_JONES | Apply single-phase fault on LUBBCK_STH 6 to JONES 230kV line CKT 2, near JONES 230kV for 16 cycles with stuck breaker at JONES. Open the faulted line and LUBBCK_STH 6 to JONES 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_334_P4_JONES | Apply single-phase fault on LUBBCK_EST 6 to JONES 230kV line CKT 1, near JONES 230kV for 16 cycles with stuck breaker at JONES. Open the faulted line and LP-HOLLY to JONES 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_334_P4_JONES | Apply single-phase fault on LUBBCK_EST 6 to JONES 230kV line CKT 1, near JONES 230kV for 16 cycles with stuck breaker at JONES. Open the faulted line and LP-HOLLY to JONES 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_334_P4_JONES | Apply single-phase fault on LUBBCK_EST 6 to JONES 230kV line CKT 1, near JONES 230kV for 16 cycles with stuck breaker at JONES. Open the faulted line and LP-HOLLY to JONES 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_334_P4_JONES | Apply single-phase fault on LUBBCK_EST 6 to JONES 230kV line CKT 1, near JONES 230kV for 16 cycles with stuck breaker at JONES. Open the faulted line and LP-HOLLY to JONES 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_335_P4_YOAKUM_345 | Apply single-phase fault on YOAKUM_345 to HOBBS_INT 345kV line CKT 1, near YOAKUM_345 345kV for 16 cycles with stuck breaker at YOAKUM_345. Open the faulted line and TUCO_INT to YOAKUM_345 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_335_P4_YOAKUM_345 | Apply single-phase fault on YOAKUM_345 to HOBBS_INT 345kV line CKT 1, near YOAKUM_345 345kV for 16 cycles with stuck breaker at YOAKUM_345. Open the faulted line and TUCO_INT to YOAKUM_345 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_335_P4_YOAKUM_345 | Apply single-phase fault on YOAKUM_345 to HOBBS_INT 345kV line CKT 1, near YOAKUM_345 345kV for 16 cycles with stuck breaker at YOAKUM_345. Open the faulted line and TUCO_INT to YOAKUM_345 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_335_P4_YOAKUM_345 | Apply single-phase fault on YOAKUM_345 to HOBBS_INT 345kV line CKT 1, near YOAKUM_345 345kV for 16 cycles with stuck breaker at YOAKUM_345. Open the faulted line and TUCO_INT to YOAKUM_345 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_336_P4_CROSSROADS7 | Apply single-phase fault on CROSSROADS 7 345kV/765kV transformer CKT 2, near CROSSROADS 7 345kV for 16 cycles with stuck breaker at CROSSROADS 7. Open the faulted Two Winding and TOLK to CROSSROADS 7 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.23pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_336_P4_CROSSROADS7 | Apply single-phase fault on CROSSROADS 7 345kV/765kV transformer CKT 2, near CROSSROADS 7 345kV for 16 cycles with stuck breaker at CROSSROADS 7. Open the faulted Two Winding and TOLK to CROSSROADS 7 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_336_P4_CROSSROADS7 | Apply single-phase fault on CROSSROADS 7 345kV/765kV transformer CKT 2, near CROSSROADS 7 345kV for 16 cycles with stuck breaker at CROSSROADS 7. Open the faulted Two Winding and TOLK to CROSSROADS 7 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.24pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_336_P4_CROSSROADS7 | Apply single-phase fault on CROSSROADS 7 345kV/765kV transformer CKT 2, near CROSSROADS 7 345kV for 16 cycles with stuck breaker at CROSSROADS 7. Open the faulted Two Winding and TOLK to CROSSROADS 7 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.25pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_337_P4_EDDY_NORTH6 | Apply single-phase fault on EDDY_NORTH 6 to 7-RIVERS 230kV line CKT 1, near EDDY_NORTH 6 230kV for 16 cycles with stuck breaker at EDDY_NORTH 6. Open the faulted line and EDDY_SVC generation unit 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_337_P4_EDDY_NORTH6 | Apply single-phase fault on EDDY_NORTH 6 to 7-RIVERS 230kV line CKT 1, near EDDY_NORTH 6 230kV for 16 cycles with stuck breaker at EDDY_NORTH 6. Open the faulted line and EDDY_SVC generation unit 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_337_P4_EDDY_NORTH6 | Apply single-phase fault on EDDY_NORTH 6 to 7-RIVERS 230kV line CKT 1, near EDDY_NORTH 6 230kV for 16 cycles with stuck breaker at EDDY_NORTH 6. Open the faulted line and EDDY_SVC generation unit 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_337_P4_EDDY_NORTH6 | Apply single-phase fault on EDDY_NORTH 6 to 7-RIVERS 230kV line CKT 1, near EDDY_NORTH 6 230kV for 16 cycles with stuck breaker at EDDY_NORTH 6. Open the faulted line and EDDY_SVC generation unit 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_338_P4_EDDY_NORTH6 | Apply single-phase fault on EDDY_SVC generation unit 1, near EDDY_NORTH 6 230kV for 16 cycles with stuck breaker at EDDY_NORTH 6. Open the faulted Generator and EDDY_TR 13.19kV/230kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_338_P4_EDDY_NORTH6 | Apply single-phase fault on EDDY_SVC generation unit 1, near EDDY_NORTH 6 230kV for 16 cycles with stuck breaker at EDDY_NORTH 6. Open the faulted Generator and EDDY_TR 13.19kV/230kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_338_P4_EDDY_NORTH6 | Apply single-phase fault on EDDY_SVC generation unit 1, near EDDY_NORTH 6 230kV for 16 cycles with stuck breaker at EDDY_NORTH 6. Open the faulted Generator and EDDY_TR 13.19kV/230kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_338_P4_EDDY_NORTH6 | Apply single-phase fault on EDDY_SVC generation unit 1, near EDDY_NORTH 6 230kV for 16 cycles with stuck breaker at EDDY_NORTH 6. Open the faulted Generator and EDDY_TR 13.19kV/230kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_339_P4_EDDY_NORTH6 | Apply single-phase fault on EDDY_NORTH 6 to 7-RIVERS 230kV line CKT 1, near EDDY_NORTH 6 230kV for 16 cycles with stuck breaker at EDDY_NORTH 6. Open the faulted line and EDDY_NORTH 6 to CUNNIGHM_N 6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_339_P4_EDDY_NORTH6 | Apply single-phase fault on EDDY_NORTH 6 to 7-RIVERS 230kV line CKT 1, near EDDY_NORTH 6 230kV for 16 cycles with stuck breaker at EDDY_NORTH 6. Open the faulted line and EDDY_NORTH 6 to CUNNIGHM_N 6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_339_P4_EDDY_NORTH6 | Apply single-phase fault on EDDY_NORTH 6 to 7-RIVERS 230kV line CKT 1, near EDDY_NORTH 6 230kV for 16 cycles with stuck breaker at EDDY_NORTH 6. Open the faulted line and EDDY_NORTH 6 to CUNNIGHM_N 6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_339_P4_EDDY_NORTH6 | Apply single-phase fault on EDDY_NORTH 6 to 7-RIVERS 230kV line CKT 1, near EDDY_NORTH 6 230kV for 16 cycles with stuck breaker at EDDY_NORTH 6. Open the faulted line and EDDY_NORTH 6 to CUNNIGHM_N 6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_34_P1_HARRNG_WST6 | Apply 3-phase fault on HARRNG_WST 6 to EAST_PLANT 6 230kV line CKT 1, near HARRNG_WST 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_34_P1_HARRNG_WST6 | Apply 3-phase fault on HARRNG_WST 6 to EAST_PLANT 6 230kV line CKT 1, near HARRNG_WST 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_34_P1_HARRNG_WST6 | Apply 3-phase fault on HARRNG_WST 6 to EAST_PLANT 6 230kV line CKT 1, near HARRNG_WST 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_34_P1_HARRNG_WST6 | Apply 3-phase fault on HARRNG_WST 6 to EAST_PLANT 6 230kV line CKT 1, near HARRNG_WST 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_340_P4_EDDY_NORTH6 | Apply single-phase fault on EDDY_TR 13.19kV/230kV/345kV transformer CKT 1, near EDDY_NORTH 6 230kV for 16 cycles with stuck breaker at EDDY_NORTH 6. Open the faulted Three Winding and CHAVES_CNTY6 to EDDY_NORTH 6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_340_P4_EDDY_NORTH6 | Apply single-phase fault on EDDY_TR 13.19kV/230kV/345kV transformer CKT 1, near EDDY_NORTH 6 230kV for 16 cycles with stuck breaker at EDDY_NORTH 6. Open the faulted Three Winding and CHAVES_CNTY6 to EDDY_NORTH 6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_340_P4_EDDY_NORTH6 | Apply single-phase fault on EDDY_TR 13.19kV/230kV/345kV transformer CKT 1, near EDDY_NORTH 6 230kV for 16 cycles with stuck breaker at EDDY_NORTH 6. Open the faulted Three Winding and CHAVES_CNTY6 to EDDY_NORTH 6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_340_P4_EDDY_NORTH6 | Apply single-phase fault on EDDY_TR 13.19kV/230kV/345kV transformer CKT 1, near EDDY_NORTH 6 230kV for 16 cycles with stuck breaker at EDDY_NORTH 6. Open the faulted Three Winding and CHAVES_CNTY6 to EDDY_NORTH 6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_341_P4_EDDY_NORTH6 | Apply single-phase fault on EDDY_STH 115kV/13.19kV/230kV transformer CKT 2, near EDDY_NORTH 6 230kV for 16 cycles with stuck breaker at EDDY_NORTH 6. Open the faulted Three Winding and EDDY_TR2 13.19kV/115kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_341_P4_EDDY_NORTH6 | Apply single-phase fault on EDDY_STH 115kV/13.19kV/230kV transformer CKT 2, near EDDY_NORTH 6 230kV for 16 cycles with stuck breaker at EDDY_NORTH 6. Open the faulted Three Winding and EDDY_TR2 13.19kV/115kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_341_P4_EDDY_NORTH6 | Apply single-phase fault on EDDY_STH 115kV/13.19kV/230kV transformer CKT 2, near EDDY_NORTH 6 230kV for 16 cycles with stuck breaker at EDDY_NORTH 6. Open the faulted Three Winding and EDDY_TR2 13.19kV/115kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_341_P4_EDDY_NORTH6 | Apply single-phase fault on EDDY_STH 115kV/13.19kV/230kV transformer CKT 2, near EDDY_NORTH 6 230kV for 16 cycles with stuck breaker at EDDY_NORTH 6. Open the faulted Three Winding and EDDY_TR2 13.19kV/115kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_342_P4_EDDY_CNTY | Apply single-phase fault on EDDY_TR 13.19kV/230kV/345kV transformer CKT 1, near EDDY_CNTY 345kV for 16 cycles with stuck breaker at EDDY_CNTY. Open the faulted Three Winding and EDDY_CNTY to KIOWA 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_342_P4_EDDY_CNTY | Apply single-phase fault on EDDY_TR 13.19kV/230kV/345kV transformer CKT 1, near EDDY_CNTY 345kV for 16 cycles with stuck breaker at EDDY_CNTY. Open the faulted Three Winding and EDDY_CNTY to KIOWA 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_342_P4_EDDY_CNTY | Apply single-phase fault on EDDY_TR 13.19kV/230kV/345kV transformer CKT 1, near EDDY_CNTY 345kV for 16 cycles with stuck breaker at EDDY_CNTY. Open the faulted Three Winding and EDDY_CNTY to KIOWA 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_342_P4_EDDY_CNTY | Apply single-phase fault on EDDY_TR 13.19kV/230kV/345kV transformer CKT 1, near EDDY_CNTY 345kV for 16 cycles with stuck breaker at EDDY_CNTY. Open the faulted Three Winding and EDDY_CNTY to KIOWA 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_343_P4_CUNNINHAM | Apply single-phase fault on CUNNINHAM to MADDOX 115kV line CKT 1, near CUNNINHAM 115kV for 16 cycles with stuck breaker at CUNNINHAM. Open the faulted line and CUNNINHAM to QUAHADA 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_343_P4_CUNNINHAM | Apply single-phase fault on CUNNINHAM to MADDOX 115kV line CKT 1, near CUNNINHAM 115kV for 16 cycles with stuck breaker at CUNNINHAM. Open the faulted line and CUNNINHAM to QUAHADA 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_343_P4_CUNNINHAM | Apply single-phase fault on CUNNINHAM to MADDOX 115kV line CKT 1, near CUNNINHAM 115kV for 16 cycles with stuck breaker at CUNNINHAM. Open the faulted line and CUNNINHAM to QUAHADA 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_343_P4_CUNNINHAM | Apply single-phase fault on CUNNINHAM to MADDOX 115kV line CKT 1, near CUNNINHAM 115kV for 16 cycles with stuck breaker at CUNNINHAM. Open the faulted line and CUNNINHAM to QUAHADA 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_344_P4_CUNNINHAM | Apply single-phase fault on CUNNINHAM to BUCKEYE_TP 3 115kV line CKT 1, near CUNNINHAM 115kV for 16 cycles with stuck breaker at CUNNINHAM. Open the faulted line and LE-SANANDRS3 115kV/69kV transformer CKT 1 and CUNNINHAM to MONUMNT_TP 3 115kV line CKT 1 and RDRNNER_TR11 13.19kV/115kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_344_P4_CUNNINHAM | Apply single-phase fault on CUNNINHAM to BUCKEYE_TP 3 115kV line CKT 1, near CUNNINHAM 115kV for 16 cycles with stuck breaker at CUNNINHAM. Open the faulted line and LE-SANANDRS3 115kV/69kV transformer CKT 1 and CUNNINHAM to MONUMNT_TP 3 115kV line CKT 1 and RDRNNER_TR11 13.19kV/115kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_344_P4_CUNNINHAM | Apply single-phase fault on CUNNINHAM to BUCKEYE_TP 3 115kV line CKT 1, near CUNNINHAM 115kV for 16 cycles with stuck breaker at CUNNINHAM. Open the faulted line and LE-SANANDRS3 115kV/69kV transformer CKT 1 and CUNNINHAM to MONUMNT_TP 3 115kV line CKT 1 and RDRNNER_TR11 13.19kV/115kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_344_P4_CUNNINHAM | Apply single-phase fault on CUNNINHAM to BUCKEYE_TP 3 115kV line CKT 1, near CUNNINHAM 115kV for 16 cycles with stuck breaker at CUNNINHAM. Open the faulted line and LE-SANANDRS3 115kV/69kV transformer CKT 1 and CUNNINHAM to MONUMNT_TP 3 115kV line CKT 1 and RDRNNER_TR11 13.19kV/115kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | No | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_345_P4_CUNNIGHM_N6 | Apply single-phase fault on EDDY_NORTH 6 to CUNNIGHM_N 6 230kV line CKT 1, near CUNNIGHM_N 6 230kV for 16 cycles with stuck breaker at CUNNIGHM_N 6. Open the faulted line and CUNNIGHM_N 6 to POTASH_JCT 6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_345_P4_CUNNIGHM_N6 | Apply single-phase fault on EDDY_NORTH 6 to CUNNIGHM_N 6 230kV line CKT 1, near CUNNIGHM_N 6 230kV for 16 cycles with stuck breaker at CUNNIGHM_N 6. Open the faulted line and CUNNIGHM_N 6 to POTASH_JCT 6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_345_P4_CUNNIGHM_N6 | Apply single-phase fault on EDDY_NORTH 6 to CUNNIGHM_N 6 230kV line CKT 1, near CUNNIGHM_N 6 230kV for 16 cycles with stuck breaker at CUNNIGHM_N 6. Open the faulted line and CUNNIGHM_N 6 to POTASH_JCT 6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_345_P4_CUNNIGHM_N6 | Apply single-phase fault on EDDY_NORTH 6 to CUNNIGHM_N 6 230kV line CKT 1, near CUNNIGHM_N 6 230kV for 16 cycles with stuck breaker at CUNNIGHM_N 6. Open the faulted line and CUNNIGHM_N 6 to POTASH_JCT 6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_346_P4_HOBBS_INT | Apply single-phase fault on HOBBS_INT to MADDOX 115kV line CKT 1, near HOBBS_INT 115kV for 16 cycles with stuck breaker at HOBBS_INT. Open the faulted line and HOBBS_INT to MILLEN 115kV line CKT 1 and TAYLOR to NE_HOBBS 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_346_P4_HOBBS_INT | Apply single-phase fault on HOBBS_INT to MADDOX 115kV line CKT 1, near HOBBS_INT 115kV for 16 cycles with stuck breaker at HOBBS_INT. Open the faulted line and HOBBS_INT to MILLEN 115kV line CKT 1 and TAYLOR to NE_HOBBS 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_346_P4_HOBBS_INT | Apply single-phase fault on HOBBS_INT to MADDOX 115kV line CKT 1, near HOBBS_INT 115kV for 16 cycles with stuck breaker at HOBBS_INT. Open the faulted line and HOBBS_INT to MILLEN 115kV line CKT 1 and TAYLOR to NE_HOBBS 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_346_P4_HOBBS_INT | Apply single-phase fault on HOBBS_INT to MADDOX 115kV line CKT 1, near HOBBS_INT 115kV for 16 cycles with stuck breaker at HOBBS_INT. Open the faulted line and HOBBS_INT to MILLEN 115kV line CKT 1 and TAYLOR to NE_HOBBS 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_347_P4_HOBBS_INT | Apply single-phase fault on HOBBS_INT to BENSING 115kV line CKT 1, near HOBBS_INT 115kV for 16 cycles with stuck breaker at HOBBS_INT. Open the faulted line and JOHNSON_DRW3 to HIGG 115kV line CKT 1 and TAYLOR to NE_HOBBS 115kV line CKT 1 and HOBBS_INT to MILLEN 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_347_P4_HOBBS_INT | Apply single-phase fault on HOBBS_INT to BENSING 115kV line CKT 1, near HOBBS_INT 115kV for 16 cycles with stuck breaker at HOBBS_INT. Open the faulted line and JOHNSON_DRW3 to HIGG 115kV line CKT 1 and TAYLOR to NE_HOBBS 115kV line CKT 1 and HOBBS_INT to MILLEN 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_347_P4_HOBBS_INT | Apply single-phase fault on HOBBS_INT to BENSING 115kV line CKT 1, near HOBBS_INT 115kV for 16 cycles with stuck breaker at HOBBS_INT. Open the faulted line and JOHNSON_DRW3 to HIGG 115kV line CKT 1 and TAYLOR to NE_HOBBS 115kV line CKT 1 and HOBBS_INT to MILLEN 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_347_P4_HOBBS_INT | Apply single-phase fault on HOBBS_INT to BENSING 115kV line CKT 1, near HOBBS_INT 115kV for 16 cycles with stuck breaker at HOBBS_INT. Open the faulted line and JOHNSON_DRW3 to HIGG 115kV line CKT 1 and TAYLOR to NE_HOBBS 115kV line CKT 1 and HOBBS_INT to MILLEN 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_348_P4_HOBBS_INT | Apply single-phase fault on CUNNINHAM to HOBBS_INT 115kV line CKT 2, near HOBBS_INT 115kV for 16 cycles with stuck breaker at HOBBS_INT. Open the faulted line and CUNNINHAM to HOBBS_INT 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_348_P4_HOBBS_INT | Apply single-phase fault on CUNNINHAM to HOBBS_INT 115kV line CKT 2, near HOBBS_INT 115kV for 16 cycles with stuck breaker at HOBBS_INT. Open the faulted line and CUNNINHAM to HOBBS_INT 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_348_P4_HOBBS_INT | Apply single-phase fault on CUNNINHAM to HOBBS_INT 115kV line CKT 2, near HOBBS_INT 115kV for 16 cycles with stuck breaker at HOBBS_INT. Open the faulted line and CUNNINHAM to HOBBS_INT 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_348_P4_HOBBS_INT | Apply single-phase fault on CUNNINHAM to HOBBS_INT 115kV line CKT 2, near HOBBS_INT 115kV for 16 cycles with stuck breaker at HOBBS_INT. Open the faulted line and CUNNINHAM to HOBBS_INT 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_349_P4_HOBBS_INT | Apply single-phase fault on HOBBS_INT 230kV/13.19kV/345kV transformer CKT 1, near HOBBS_INT 230kV for 16 cycles with stuck breaker at HOBBS_INT. Open the faulted Three Winding and CUNNIGHM_S 6 to HOBBS_INT 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_349_P4_HOBBS_INT | Apply single-phase fault on HOBBS_INT 230kV/13.19kV/345kV transformer CKT 1, near HOBBS_INT 230kV for 16 cycles with stuck breaker at HOBBS_INT. Open the faulted Three Winding and CUNNIGHM_S 6 to HOBBS_INT 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_349_P4_HOBBS_INT | Apply single-phase fault on HOBBS_INT 230kV/13.19kV/345kV transformer CKT 1, near HOBBS_INT 230kV for 16 cycles with stuck breaker at HOBBS_INT. Open the faulted Three Winding and CUNNIGHM_S 6 to HOBBS_INT 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_349_P4_HOBBS_INT | Apply single-phase fault on HOBBS_INT 230kV/13.19kV/345kV transformer CKT 1, near HOBBS_INT 230kV for 16 cycles with stuck breaker at HOBBS_INT. Open the faulted Three Winding and CUNNIGHM_S 6 to HOBBS_INT 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_35_P1_HARRNG_MID6 | Apply 3-phase fault on HARRNG_MID 6 to NICHOLS 230kV line CKT 2, near HARRNG_MID 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_35_P1_HARRNG_MID6 | Apply 3-phase fault on HARRNG_MID 6 to NICHOLS 230kV line CKT 2, near HARRNG_MID 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_35_P1_HARRNG_MID6 | Apply 3-phase fault on HARRNG_MID 6 to NICHOLS 230kV line CKT 2, near HARRNG_MID 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_35_P1_HARRNG_MID6 | Apply 3-phase fault on HARRNG_MID 6 to NICHOLS 230kV line CKT 2, near HARRNG_MID 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_350_P4_HOBBS_INT | Apply single-phase fault on HOBBS_INT 230kV/13.19kV/345kV transformer CKT 1, near HOBBS_INT 230kV for 16 cycles with stuck breaker at HOBBS_INT. Open the faulted Three Winding and HOBBS_INT to GAINESGENTP6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_350_P4_HOBBS_INT | Apply single-phase fault on HOBBS_INT 230kV/13.19kV/345kV transformer CKT 1, near HOBBS_INT 230kV for 16 cycles with stuck breaker at HOBBS_INT. Open the faulted Three Winding and HOBBS_INT to GAINESGENTP6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_350_P4_HOBBS_INT | Apply single-phase fault on HOBBS_INT 230kV/13.19kV/345kV transformer CKT 1, near HOBBS_INT 230kV for 16 cycles with stuck breaker at HOBBS_INT. Open the faulted Three Winding and HOBBS_INT to GAINESGENTP6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_350_P4_HOBBS_INT | Apply single-phase fault on HOBBS_INT 230kV/13.19kV/345kV transformer CKT 1, near HOBBS_INT 230kV for 16 cycles with stuck breaker at HOBBS_INT. Open the faulted Three Winding and HOBBS_INT to GAINESGENTP6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_351_P4_HOBBS_INT | Apply single-phase fault on HOBBS_TR2 13.19kV/115kV/230kV transformer CKT 2, near HOBBS_INT 230kV for 16 cycles with stuck breaker at HOBBS_INT. Open the faulted Three Winding and HOBBS_TR1 13.19kV/115kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_351_P4_HOBBS_INT | Apply single-phase fault on HOBBS_TR2 13.19kV/115kV/230kV transformer CKT 2, near HOBBS_INT 230kV for 16 cycles with stuck breaker at HOBBS_INT. Open the faulted Three Winding and HOBBS_TR1 13.19kV/115kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_351_P4_HOBBS_INT | Apply single-phase fault on HOBBS_TR2 13.19kV/115kV/230kV transformer CKT 2, near HOBBS_INT 230kV for 16 cycles with stuck breaker at HOBBS_INT. Open the faulted Three Winding and HOBBS_TR1 13.19kV/115kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_351_P4_HOBBS_INT | Apply single-phase fault on HOBBS_TR2 13.19kV/115kV/230kV transformer CKT 2, near HOBBS_INT 230kV for 16 cycles with stuck breaker at HOBBS_INT. Open the faulted Three Winding and HOBBS_TR1 13.19kV/115kV/230kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_352_P4_HOBBS_INT | Apply single-phase fault on CUNNIGHM_S 6 to HOBBS_INT 230kV line CKT 1, near HOBBS_INT 230kV for 16 cycles with stuck breaker at HOBBS_INT. Open the faulted line and INK_BASIN to HOBBS_INT 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_352_P4_HOBBS_INT | Apply single-phase fault on CUNNIGHM_S 6 to HOBBS_INT 230kV line CKT 1, near HOBBS_INT 230kV for 16 cycles with stuck breaker at HOBBS_INT. Open the faulted line and INK_BASIN to HOBBS_INT 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_352_P4_HOBBS_INT | Apply single-phase fault on CUNNIGHM_S 6 to HOBBS_INT 230kV line CKT 1, near HOBBS_INT 230kV for 16 cycles with stuck breaker at HOBBS_INT. Open the faulted line and INK_BASIN to HOBBS_INT 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_352_P4_HOBBS_INT | Apply single-phase fault on CUNNIGHM_S 6 to HOBBS_INT 230kV line CKT 1, near HOBBS_INT 230kV for 16 cycles with stuck breaker at HOBBS_INT. Open the faulted line and INK_BASIN to HOBBS_INT 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_353_P4_HOBBS_INT | Apply single-phase fault on HOBBS_INT to KIOWA 345kV line CKT 1, near HOBBS_INT 345kV for 16 cycles with stuck breaker at HOBBS_INT. Open the faulted line and YOAKUM_345 to HOBBS_INT 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_353_P4_HOBBS_INT | Apply single-phase fault on HOBBS_INT to KIOWA 345kV line CKT 1, near HOBBS_INT 345kV for 16 cycles with stuck breaker at HOBBS_INT. Open the faulted line and YOAKUM_345 to HOBBS_INT 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_353_P4_HOBBS_INT | Apply single-phase fault on HOBBS_INT to KIOWA 345kV line CKT 1, near HOBBS_INT 345kV for 16 cycles with stuck breaker at HOBBS_INT. Open the faulted line and YOAKUM_345 to HOBBS_INT 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_353_P4_HOBBS_INT | Apply single-phase fault on HOBBS_INT to KIOWA 345kV line CKT 1, near HOBBS_INT 345kV for 16 cycles with stuck breaker at HOBBS_INT. Open the faulted line and YOAKUM_345 to HOBBS_INT 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_354_P4_POTASH_JCT6 | Apply single-phase fault on POTASH_TR1 1 13.19kV/115kV/230kV transformer CKT 1, near POTASH_JCT 6 230kV for 16 cycles with stuck breaker at POTASH_JCT 6. Open the faulted Three Winding and POTASH_JCT 6 to PECOS 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_354_P4_POTASH_JCT6 | Apply single-phase fault on POTASH_TR1 1 13.19kV/115kV/230kV transformer CKT 1, near POTASH_JCT 6 230kV for 16 cycles with stuck breaker at POTASH_JCT 6. Open the faulted Three Winding and POTASH_JCT 6 to PECOS 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_354_P4_POTASH_JCT6 | Apply single-phase fault on POTASH_TR1 1 13.19kV/115kV/230kV transformer CKT 1, near POTASH_JCT 6 230kV for 16 cycles with stuck breaker at POTASH_JCT 6. Open the faulted Three Winding and POTASH_JCT 6 to PECOS 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_354_P4_POTASH_JCT6 | Apply single-phase fault on POTASH_TR1 1 13.19kV/115kV/230kV transformer CKT 1, near POTASH_JCT 6 230kV for 16 cycles with stuck breaker at POTASH_JCT 6. Open the faulted Three Winding and POTASH_JCT 6 to PECOS 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_355_P4_KIOWA | Apply single-phase fault on KIOWA to N_LOVING 345kV line CKT 1, near KIOWA 345kV for 16 cycles with stuck breaker at KIOWA. Open the faulted line and KIOWA to RDRUNNER 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_355_P4_KIOWA | Apply single-phase fault on KIOWA to N_LOVING 345kV line CKT 1, near KIOWA 345kV for 16 cycles with stuck breaker at KIOWA. Open the faulted line and KIOWA to RDRUNNER 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_355_P4_KIOWA | Apply single-phase fault on KIOWA to N_LOVING 345kV line CKT 1, near KIOWA 345kV for 16 cycles with stuck breaker at KIOWA. Open the faulted line and KIOWA to RDRUNNER 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_355_P4_KIOWA | Apply single-phase fault on KIOWA to N_LOVING 345kV line CKT 1, near KIOWA 345kV for 16 cycles with stuck breaker at KIOWA. Open the faulted line and KIOWA to RDRUNNER 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_356_P4_KIOWA | Apply single-phase fault on HOBBS_INT to KIOWA 345kV line CKT 1, near KIOWA 345kV for 16 cycles with stuck breaker at KIOWA. Open the faulted line and EDDY_CNTY to KIOWA 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_356_P4_KIOWA | Apply single-phase fault on HOBBS_INT to KIOWA 345kV line CKT 1, near KIOWA 345kV for 16 cycles with stuck breaker at KIOWA. Open the faulted line and EDDY_CNTY to KIOWA 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_356_P4_KIOWA | Apply single-phase fault on HOBBS_INT to KIOWA 345kV line CKT 1, near KIOWA 345kV for 16 cycles with stuck breaker at KIOWA. Open the faulted line and EDDY_CNTY to KIOWA 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_356_P4_KIOWA | Apply single-phase fault on HOBBS_INT to KIOWA 345kV line CKT 1, near KIOWA 345kV for 16 cycles with stuck breaker at KIOWA. Open the faulted line and EDDY_CNTY to KIOWA 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_357_P4_MADDOX | Apply single-phase fault on OXY_S_HOBBS3 to SW_4J44 115kV line CKT 1, near MADDOX 115kV for 16 cycles with stuck breaker at MADDOX. Open the faulted line and MONUMENT to W_HOBBS 115kV line CKT 1 and MADDOX to SANGER_SW 115kV line CKT 1 and W_BENDER to OXYPERMIAN 3 115kV line CKT 1 and TAYLOR to W_BENDER 115kV line CKT 1 and TAYLOR to E_SANGER 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_357_P4_MADDOX | Apply single-phase fault on OXY_S_HOBBS3 to SW_4J44 115kV line CKT 1, near MADDOX 115kV for 16 cycles with stuck breaker at MADDOX. Open the faulted line and MONUMENT to W_HOBBS 115kV line CKT 1 and MADDOX to SANGER_SW 115kV line CKT 1 and W_BENDER to OXYPERMIAN 3 115kV line CKT 1 and TAYLOR to W_BENDER 115kV line CKT 1 and TAYLOR to E_SANGER 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_357_P4_MADDOX | Apply single-phase fault on OXY_S_HOBBS3 to SW_4J44 115kV line CKT 1, near MADDOX 115kV for 16 cycles with stuck breaker at MADDOX. Open the faulted line and MONUMENT to W_HOBBS 115kV line CKT 1 and MADDOX to SANGER_SW 115kV line CKT 1 and W_BENDER to OXYPERMIAN 3 115kV line CKT 1 and TAYLOR to W_BENDER 115kV line CKT 1 and TAYLOR to E_SANGER 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_357_P4_MADDOX | Apply single-phase fault on OXY_S_HOBBS3 to SW_4J44 115kV line CKT 1, near MADDOX 115kV for 16 cycles with stuck breaker at MADDOX. Open the faulted line and MONUMENT to W_HOBBS 115kV line CKT 1 and MADDOX to SANGER_SW 115kV line CKT 1 and W_BENDER to OXYPERMIAN 3 115kV line CKT 1 and TAYLOR to W_BENDER 115kV line CKT 1 and TAYLOR to E_SANGER 115kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_36_P1_HARRNG_MID6 | Apply 3-phase fault on HARRNG_MID 6 to RANDALL 230kV line CKT 1, near HARRNG_MID 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_36_P1_HARRNG_MID6 | Apply 3-phase fault on HARRNG_MID 6 to RANDALL 230kV line CKT 1, near HARRNG_MID 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_36_P1_HARRNG_MID6 | Apply 3-phase fault on HARRNG_MID 6 to RANDALL 230kV line CKT 1, near HARRNG_MID 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_36_P1_HARRNG_MID6 | Apply 3-phase fault on HARRNG_MID 6 to RANDALL 230kV line CKT 1, near HARRNG_MID 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_361_P6_OKU-7 | Prior Outage of OKLAUN HVDC7 shunt device and DC line SPP_44_OKLUN. Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Unstable | No | No | No | No | Yes | No | Angular and system instability was observed in the G6 region. Simulation was rerun with the Crossroad SVC and different G6 dispatch options. No stability or damping issues were observed with the Crossroad SVC and G6 study generators dispatched at 90%. | ±600 MVAr SVC at Crossroad 765kV & G6 Study Generators Dispatched @ 90%
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_361_P6_OKU-7 | Prior Outage of OKLAUN HVDC7 shunt device and DC line SPP_44_OKLUN. Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | No | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_361_P6_OKU-7 | Prior Outage of OKLAUN HVDC7 shunt device and DC line SPP_44_OKLUN. Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.23pu, MaxDur: 0.04s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_361_P6_OKU-7 | Prior Outage of OKLAUN HVDC7 shunt device and DC line SPP_44_OKLUN. Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.24pu, MaxDur: 0.05s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_362_P6_OKU-7 | Prior Outage of BORDER to CRAWFISH_DR 345kV line CKT 1. Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | No | No | Yes | Yes | No | LVRT VIOL - - LANoGSU10.60[W1] G17-065-GEN2[1]. Undamped oscillations were observed in conventional units angles and powers, renewable units powers and system voltage responses. In addition, following unit tripped under this contingency: G17-065-GEN2[1] tripped on voltage protection setting 1.22pu-0.08s. The protection setting was disabled and simulation was rerun. Following protection disable: Angular and system instability was observed in the G6 region. The stability issue was resolved with the SVC mitigation solution. | ±600 MVAr SVC at Crossroad 765kV
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_362_P6_OKU-7 | Prior Outage of BORDER to CRAWFISH_DR 345kV line CKT 1. Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Unstable | No | No | No | No | Yes | No | Angular and system instability was observed in the G6 region. Simulation was rerun with the Crossroad SVC and different G6 dispatch options. No stability or damping issues were observed with the Crossroad SVC and G6 study generators dispatched at 70%. (TOV: 1.29pu, MaxDur: 0.10s) | ±600 MVAr SVC at Crossroad 765kV & G6 Study Generators Dispatched @ 70%
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_362_P6_OKU-7 | Prior Outage of BORDER to CRAWFISH_DR 345kV line CKT 1. Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.26pu, MaxDur: 0.06s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_362_P6_OKU-7 | Prior Outage of BORDER to CRAWFISH_DR 345kV line CKT 1. Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.24pu, MaxDur: 0.05s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_363_P6_OKU-7 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV line CKT 1. Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P6 | Unstable | No | No | No | No | Yes | No | Angular and system instability was observed in the G6 region. The stability issue was resolved with the SVC mitigation solution. | ±600 MVAr SVC at Crossroad 765kV
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_363_P6_OKU-7 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV line CKT 1. Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_363_P6_OKU-7 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV line CKT 1. Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_363_P6_OKU-7 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV line CKT 1. Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.22pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_364_P6_OKU-7 | Prior Outage of GRACMNT7 to G16-091-TAP 345kV line CKT 1. Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | No | Yes | No | No | No | LVRT VIOL - - G17-065-GEN2[1]. G17-065-GEN2[1] tripped on voltage protection setting 1.22pu-0.08s. The protection setting was disabled and simulation was rerun. No further issues were observed.
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_364_P6_OKU-7 | Prior Outage of GRACMNT7 to G16-091-TAP 345kV line CKT 1. Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | No | Yes | No | No | No | LVRT VIOL - - G17-065-GEN2[1]. G17-065-GEN2[1] tripped on voltage protection setting 1.22pu-0.08s and . The protection setting was disabled and simulation was rerun. No further issues were observed.
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_364_P6_OKU-7 | Prior Outage of GRACMNT7 to G16-091-TAP 345kV line CKT 1. Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.26pu, MaxDur: 0.08s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_364_P6_OKU-7 | Prior Outage of GRACMNT7 to G16-091-TAP 345kV line CKT 1. Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.24pu, MaxDur: 0.06s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_365_P6_CRAWFISH765 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV line CKT 1. Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Unstable | No | No | No | No | Yes | No | Angular and system instability was observed in the G6 region. Simulation was rerun with the Crossroad SVC and different G6 dispatch options. No stability or damping issues were observed with the Crossroad SVC and G6 study generators dispatched at 70%. (min post-fault s.s voltage: 0.86pu) | ±600 MVAr SVC at Crossroad 765kV & G6 Study Generators Dispatched @ 70%
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_365_P6_CRAWFISH765 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV line CKT 1. Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Unstable | No | No | No | No | Yes | No | Angular and system instability was observed in the G6 region. Simulation was rerun with the Crossroad SVC and different G6 dispatch options. No stability or damping issues were observed with the Crossroad SVC and G6 study generators dispatched at 40%. | ±600 MVAr SVC at Crossroad 765kV & G6 Study Generators Dispatched @ 40%
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_365_P6_CRAWFISH765 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV line CKT 1. Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | No | No | Yes | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. Undamped oscillations were observed in conventional units angles and powers, renewable units powers and system voltage responses. Simulation was rerun with the Crossroad SVC and different G6 dispatch options. Damping issues were resolved with the Crossroad SVC and G6 study generators dispatched at 90%. | ±600 MVAr SVC at Crossroad 765kV & G6 Study Generators Dispatched @ 90%
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_365_P6_CRAWFISH765 | Prior Outage of O.K.U.-7 to L.E.S.-7 345kV line CKT 1. Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | LVRT VIOL - - LANoGSU10.60[W1]. Undamped oscillations were observed in conventional units angles and powers, renewable units powers and system voltage responses. The damping issue was resolved with the SVC mitigation option. | ±600 MVAr SVC at Crossroad 765kV
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_366_P6_OKU-7 | Prior Outage of O.K.U.-7 to CRAWFISH_DR 345kV line CKT 1. Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_366_P6_OKU-7 | Prior Outage of O.K.U.-7 to CRAWFISH_DR 345kV line CKT 1. Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_366_P6_OKU-7 | Prior Outage of O.K.U.-7 to CRAWFISH_DR 345kV line CKT 1. Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_366_P6_OKU-7 | Prior Outage of O.K.U.-7 to CRAWFISH_DR 345kV line CKT 1. Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_367_P6_OKU-7 | Prior Outage of TERRYRD7 to SUNNYSD7 345kV line CKT 1. Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.22pu, MaxDur: 0.06s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_367_P6_OKU-7 | Prior Outage of TERRYRD7 to SUNNYSD7 345kV line CKT 1. Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | No | No | Yes | Voltage Spike: 1.22pu, MaxDur: 0.08s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_367_P6_OKU-7 | Prior Outage of TERRYRD7 to SUNNYSD7 345kV line CKT 1. Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.26pu, MaxDur: 0.07s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_367_P6_OKU-7 | Prior Outage of TERRYRD7 to SUNNYSD7 345kV line CKT 1. Apply 3-phase fault on O.K.U.-7 to CRAWFISH_DR 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.22pu, MaxDur: 0.04s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_368_P6_OKU-7 | Prior Outage of CRAWFISH765 to CDSEMMID 765kV line CKT 1. Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Unstable | No | No | No | No | Yes | No | Angular and system instability was observed in the G6 region. Simulation was rerun with the Crossroad SVC and different G6 dispatch options. No stability or damping issues were observed with the Crossroad SVC and G6 study generators dispatched at 80%. (min post-fault s.s voltage: 0.86pu and TOV: 1.28pu, MaxDur: 0.11s) | ±600 MVAr SVC at Crossroad 765kV & G6 Study Generators Dispatched @ 80%
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_368_P6_OKU-7 | Prior Outage of CRAWFISH765 to CDSEMMID 765kV line CKT 1. Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Unstable | No | No | No | No | Yes | No | Angular and system instability was observed in the G6 region. Simulation was rerun with the Crossroad SVC and different G6 dispatch options. No stability or damping issues were observed with the Crossroad SVC and G6 study generators dispatched at 40%. | ±600 MVAr SVC at Crossroad 765kV & G6 Study Generators Dispatched @ 40%
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_368_P6_OKU-7 | Prior Outage of CRAWFISH765 to CDSEMMID 765kV line CKT 1. Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes | Undamped oscillations were observed in conventional units angles and powers, renewable units powers and system voltage responses. The damping issue was resolved with the SVC mitigation option. (min post-fault s.s voltage: 0.89pu) | ±600 MVAr SVC at Crossroad 765kV
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_368_P6_OKU-7 | Prior Outage of CRAWFISH765 to CDSEMMID 765kV line CKT 1. Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes | Undamped oscillations were observed in conventional units angles and powers, renewable units powers and system voltage responses. The damping issue was resolved with the SVC mitigation option. (min post-fault s.s voltage: 0.89pu) | ±600 MVAr SVC at Crossroad 765kV
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_369_P6_OKU-7 | Prior Outage of BORDER shunt device . Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Unstable | No | No | No | No | Yes | No | Angular and system instability was observed in the G6 region. Simulation was rerun with the Crossroad SVC and different G6 dispatch options. No stability or damping issues were observed with the Crossroad SVC and G6 study generators dispatched at 90%. | ±600 MVAr SVC at Crossroad 765kV & G6 Study Generators Dispatched @ 90%
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_369_P6_OKU-7 | Prior Outage of BORDER shunt device . Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | No | No | No | No | LVRT VIOL - - G17-065-GEN2[1]. G17-065-GEN2[1] tripped on voltage protection setting 1.22pu-0.08s. The protection setting was disabled and simulation was rerun. No further issues were observed Voltage Spike: 1.29pu, MaxDur: 0.10s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_369_P6_OKU-7 | Prior Outage of BORDER shunt device . Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.25pu, MaxDur: 0.05s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_369_P6_OKU-7 | Prior Outage of BORDER shunt device . Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.25pu, MaxDur: 0.05s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_37_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_37_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_37_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_37_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_370_P6_LES-7 | Prior Outage of GRACMNT7 to G16-091-TAP 345kV line CKT 1. Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_370_P6_LES-7 | Prior Outage of GRACMNT7 to G16-091-TAP 345kV line CKT 1. Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_370_P6_LES-7 | Prior Outage of GRACMNT7 to G16-091-TAP 345kV line CKT 1. Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_370_P6_LES-7 | Prior Outage of GRACMNT7 to G16-091-TAP 345kV line CKT 1. Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_371_P6_WWRDEHV7 | Prior Outage of WWRDEHV7 to DGRASSE7 345kV line CKT 2. Apply 3-phase fault on WWRDEHV7 to DGRASSE7 345kV line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.27pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_371_P6_WWRDEHV7 | Prior Outage of WWRDEHV7 to DGRASSE7 345kV line CKT 2. Apply 3-phase fault on WWRDEHV7 to DGRASSE7 345kV line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | No | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_371_P6_WWRDEHV7 | Prior Outage of WWRDEHV7 to DGRASSE7 345kV line CKT 2. Apply 3-phase fault on WWRDEHV7 to DGRASSE7 345kV line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.29pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_371_P6_WWRDEHV7 | Prior Outage of WWRDEHV7 to DGRASSE7 345kV line CKT 2. Apply 3-phase fault on WWRDEHV7 to DGRASSE7 345kV line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.29pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_372_P6_WWRDEHV7 | Prior Outage of WWRDEHV7 to TATONGA7 345kV line CKT 1. Apply 3-phase fault on WWRDEHV7 to TATONGA7 345kV line CKT 2, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.23pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_372_P6_WWRDEHV7 | Prior Outage of WWRDEHV7 to TATONGA7 345kV line CKT 1. Apply 3-phase fault on WWRDEHV7 to TATONGA7 345kV line CKT 2, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_372_P6_WWRDEHV7 | Prior Outage of WWRDEHV7 to TATONGA7 345kV line CKT 1. Apply 3-phase fault on WWRDEHV7 to TATONGA7 345kV line CKT 2, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.26pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_372_P6_WWRDEHV7 | Prior Outage of WWRDEHV7 to TATONGA7 345kV line CKT 1. Apply 3-phase fault on WWRDEHV7 to TATONGA7 345kV line CKT 2, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.26pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_373_P6_BADGER7 | Prior Outage of BVRCNTY7 to BADGER 7 345kV line CKT 2. Apply 3-phase fault on BVRCNTY7 to BADGER 7 345kV line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | No | Yes | No | Yes | Voltage Spike: 1.27pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_373_P6_BADGER7 | Prior Outage of BVRCNTY7 to BADGER 7 345kV line CKT 2. Apply 3-phase fault on BVRCNTY7 to BADGER 7 345kV line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | No | No | No | LVRT VIOL - - FRISCO_WND 3[1].
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_373_P6_BADGER7 | Prior Outage of BVRCNTY7 to BADGER 7 345kV line CKT 2. Apply 3-phase fault on BVRCNTY7 to BADGER 7 345kV line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.28pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_373_P6_BADGER7 | Prior Outage of BVRCNTY7 to BADGER 7 345kV line CKT 2. Apply 3-phase fault on BVRCNTY7 to BADGER 7 345kV line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.25pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_374_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV line CKT 1. Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV line CKT 2, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Unstable | No | No | No | No | Yes | No | Angular and system instability was observed in the G6 region. The stability issue was resolved with the SVC mitigation solution. | ±600 MVAr SVC at Crossroad 765kV
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_374_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV line CKT 1. Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV line CKT 2, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | No | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_374_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV line CKT 1. Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV line CKT 2, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_374_P6_HITCHLAND | Prior Outage of BVRCNTY7 to HITCHLAND 345kV line CKT 1. Apply 3-phase fault on BVRCNTY7 to HITCHLAND 345kV line CKT 2, near HITCHLAND 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_375_P6_PLSNT_HILL3 | Prior Outage of PLSNHIL_TR11 13.19kV/115kV/230kV transformer CKT 1. Apply 3-phase fault on PLSNT_HILL 3 to FE-HOLLAND 3 115kV line CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Open the faulted line and CURRY to FE-CLOVIS2+3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and CURRY to FE-CLOVIS2+3 115kV line CKT 1. Re-open the faulted line after 7 cycles% CURRY to FE-CLOVIS2+3 115kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_375_P6_PLSNT_HILL3 | Prior Outage of PLSNHIL_TR11 13.19kV/115kV/230kV transformer CKT 1. Apply 3-phase fault on PLSNT_HILL 3 to FE-HOLLAND 3 115kV line CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Open the faulted line and CURRY to FE-CLOVIS2+3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and CURRY to FE-CLOVIS2+3 115kV line CKT 1. Re-open the faulted line after 7 cycles% CURRY to FE-CLOVIS2+3 115kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_375_P6_PLSNT_HILL3 | Prior Outage of PLSNHIL_TR11 13.19kV/115kV/230kV transformer CKT 1. Apply 3-phase fault on PLSNT_HILL 3 to FE-HOLLAND 3 115kV line CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Open the faulted line and CURRY to FE-CLOVIS2+3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and CURRY to FE-CLOVIS2+3 115kV line CKT 1. Re-open the faulted line after 7 cycles% CURRY to FE-CLOVIS2+3 115kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_375_P6_PLSNT_HILL3 | Prior Outage of PLSNHIL_TR11 13.19kV/115kV/230kV transformer CKT 1. Apply 3-phase fault on PLSNT_HILL 3 to FE-HOLLAND 3 115kV line CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Open the faulted line and CURRY to FE-CLOVIS2+3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and CURRY to FE-CLOVIS2+3 115kV line CKT 1. Re-open the faulted line after 7 cycles% CURRY to FE-CLOVIS2+3 115kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_376_P6_PLSNT_HILL3 | Prior Outage of PLSNT_HILL 3 to E_CLOVIS 115kV line CKT 1Prior Outage of E_CLOVIS to CURRY 115kV line CKT 1. Apply 3-phase fault on PLSNT_HILL 3 to FE-HOLLAND 3 115kV line CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Open the faulted line and CURRY to FE-CLOVIS2+3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and CURRY to FE-CLOVIS2+3 115kV line CKT 1. Re-open the faulted line after 7 cycles% CURRY to FE-CLOVIS2+3 115kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_376_P6_PLSNT_HILL3 | Prior Outage of PLSNT_HILL 3 to E_CLOVIS 115kV line CKT 1Prior Outage of E_CLOVIS to CURRY 115kV line CKT 1. Apply 3-phase fault on PLSNT_HILL 3 to FE-HOLLAND 3 115kV line CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Open the faulted line and CURRY to FE-CLOVIS2+3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and CURRY to FE-CLOVIS2+3 115kV line CKT 1. Re-open the faulted line after 7 cycles% CURRY to FE-CLOVIS2+3 115kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_376_P6_PLSNT_HILL3 | Prior Outage of PLSNT_HILL 3 to E_CLOVIS 115kV line CKT 1Prior Outage of E_CLOVIS to CURRY 115kV line CKT 1. Apply 3-phase fault on PLSNT_HILL 3 to FE-HOLLAND 3 115kV line CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Open the faulted line and CURRY to FE-CLOVIS2+3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and CURRY to FE-CLOVIS2+3 115kV line CKT 1. Re-open the faulted line after 7 cycles% CURRY to FE-CLOVIS2+3 115kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_376_P6_PLSNT_HILL3 | Prior Outage of PLSNT_HILL 3 to E_CLOVIS 115kV line CKT 1Prior Outage of E_CLOVIS to CURRY 115kV line CKT 1. Apply 3-phase fault on PLSNT_HILL 3 to FE-HOLLAND 3 115kV line CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Open the faulted line and CURRY to FE-CLOVIS2+3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and CURRY to FE-CLOVIS2+3 115kV line CKT 1. Re-open the faulted line after 7 cycles% CURRY to FE-CLOVIS2+3 115kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_377_P6_PLSNT_HILL3 | Prior Outage of OASIS_TR1 13.19kV/115kV/230kV transformer CKT 1. Apply 3-phase fault on PLSNHIL_TR11 13.19kV/115kV/230kV transformer CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_377_P6_PLSNT_HILL3 | Prior Outage of OASIS_TR1 13.19kV/115kV/230kV transformer CKT 1. Apply 3-phase fault on PLSNHIL_TR11 13.19kV/115kV/230kV transformer CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_377_P6_PLSNT_HILL3 | Prior Outage of OASIS_TR1 13.19kV/115kV/230kV transformer CKT 1. Apply 3-phase fault on PLSNHIL_TR11 13.19kV/115kV/230kV transformer CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_377_P6_PLSNT_HILL3 | Prior Outage of OASIS_TR1 13.19kV/115kV/230kV transformer CKT 1. Apply 3-phase fault on PLSNHIL_TR11 13.19kV/115kV/230kV transformer CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_378_P6_PLSNT_HILL6 | Prior Outage of PLSNT_HILL 6 to ROSEVELT_N 6 230kV line CKT 1. Apply 3-phase fault on PLSNT_HILL 6 to OASIS 230kV line CKT 1, near PLSNT_HILL 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_378_P6_PLSNT_HILL6 | Prior Outage of PLSNT_HILL 6 to ROSEVELT_N 6 230kV line CKT 1. Apply 3-phase fault on PLSNT_HILL 6 to OASIS 230kV line CKT 1, near PLSNT_HILL 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_378_P6_PLSNT_HILL6 | Prior Outage of PLSNT_HILL 6 to ROSEVELT_N 6 230kV line CKT 1. Apply 3-phase fault on PLSNT_HILL 6 to OASIS 230kV line CKT 1, near PLSNT_HILL 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_378_P6_PLSNT_HILL6 | Prior Outage of PLSNT_HILL 6 to ROSEVELT_N 6 230kV line CKT 1. Apply 3-phase fault on PLSNT_HILL 6 to OASIS 230kV line CKT 1, near PLSNT_HILL 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_379_P6_PLSNT_HILL6 | Prior Outage of PLSNT_HILL 6 to ROSEVELT_N 6 230kV line CKT 1. Apply 3-phase fault on PLSNHIL_TR11 13.19kV/115kV/230kV transformer CKT 1, near PLSNT_HILL 6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_379_P6_PLSNT_HILL6 | Prior Outage of PLSNT_HILL 6 to ROSEVELT_N 6 230kV line CKT 1. Apply 3-phase fault on PLSNHIL_TR11 13.19kV/115kV/230kV transformer CKT 1, near PLSNT_HILL 6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_379_P6_PLSNT_HILL6 | Prior Outage of PLSNT_HILL 6 to ROSEVELT_N 6 230kV line CKT 1. Apply 3-phase fault on PLSNHIL_TR11 13.19kV/115kV/230kV transformer CKT 1, near PLSNT_HILL 6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_379_P6_PLSNT_HILL6 | Prior Outage of PLSNT_HILL 6 to ROSEVELT_N 6 230kV line CKT 1. Apply 3-phase fault on PLSNHIL_TR11 13.19kV/115kV/230kV transformer CKT 1, near PLSNT_HILL 6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_38_P1_ROLLHILLS | Apply 3-phase fault on HARRNG_WST 6 to ROLLHILLS 230kV line CKT 1, near ROLLHILLS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_38_P1_ROLLHILLS | Apply 3-phase fault on HARRNG_WST 6 to ROLLHILLS 230kV line CKT 1, near ROLLHILLS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_38_P1_ROLLHILLS | Apply 3-phase fault on HARRNG_WST 6 to ROLLHILLS 230kV line CKT 1, near ROLLHILLS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_38_P1_ROLLHILLS | Apply 3-phase fault on HARRNG_WST 6 to ROLLHILLS 230kV line CKT 1, near ROLLHILLS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_380_P6_PLSNT_HILL6 | Prior Outage of SN_JUAN_TAP6 to CHAVES_CNTY6 230kV line CKT 1. Apply 3-phase fault on PLSNT_HILL 6 to ROSEVELT_N 6 230kV line CKT 1, near PLSNT_HILL 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_380_P6_PLSNT_HILL6 | Prior Outage of SN_JUAN_TAP6 to CHAVES_CNTY6 230kV line CKT 1. Apply 3-phase fault on PLSNT_HILL 6 to ROSEVELT_N 6 230kV line CKT 1, near PLSNT_HILL 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_380_P6_PLSNT_HILL6 | Prior Outage of SN_JUAN_TAP6 to CHAVES_CNTY6 230kV line CKT 1. Apply 3-phase fault on PLSNT_HILL 6 to ROSEVELT_N 6 230kV line CKT 1, near PLSNT_HILL 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_380_P6_PLSNT_HILL6 | Prior Outage of SN_JUAN_TAP6 to CHAVES_CNTY6 230kV line CKT 1. Apply 3-phase fault on PLSNT_HILL 6 to ROSEVELT_N 6 230kV line CKT 1, near PLSNT_HILL 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_381_P6_FE-CLVS_INT3 | Prior Outage of PLSNHIL_TR11 13.19kV/115kV/230kV transformer CKT 1. Apply 3-phase fault on W_CLOVIS to FE-CLVS_INT3 115kV line CKT 1, near FE-CLVS_INT3 115kV for 7 cycles. Open the faulted line and PERIMETER to OASIS 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and PERIMETER to OASIS 115kV line CKT 1. Re-open the faulted line after 7 cycles% PERIMETER to OASIS 115kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_381_P6_FE-CLVS_INT3 | Prior Outage of PLSNHIL_TR11 13.19kV/115kV/230kV transformer CKT 1. Apply 3-phase fault on W_CLOVIS to FE-CLVS_INT3 115kV line CKT 1, near FE-CLVS_INT3 115kV for 7 cycles. Open the faulted line and PERIMETER to OASIS 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and PERIMETER to OASIS 115kV line CKT 1. Re-open the faulted line after 7 cycles% PERIMETER to OASIS 115kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_381_P6_FE-CLVS_INT3 | Prior Outage of PLSNHIL_TR11 13.19kV/115kV/230kV transformer CKT 1. Apply 3-phase fault on W_CLOVIS to FE-CLVS_INT3 115kV line CKT 1, near FE-CLVS_INT3 115kV for 7 cycles. Open the faulted line and PERIMETER to OASIS 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and PERIMETER to OASIS 115kV line CKT 1. Re-open the faulted line after 7 cycles% PERIMETER to OASIS 115kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_381_P6_FE-CLVS_INT3 | Prior Outage of PLSNHIL_TR11 13.19kV/115kV/230kV transformer CKT 1. Apply 3-phase fault on W_CLOVIS to FE-CLVS_INT3 115kV line CKT 1, near FE-CLVS_INT3 115kV for 7 cycles. Open the faulted line and PERIMETER to OASIS 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and PERIMETER to OASIS 115kV line CKT 1. Re-open the faulted line after 7 cycles% PERIMETER to OASIS 115kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_382_P6_FE-CLVS_INT3 | Prior Outage of OASIS to PORTALES 115kV line CKT 1. Apply 3-phase fault on N_CLOVIS_TP3 to FE-CLVS_INT3 115kV line CKT 1, near FE-CLVS_INT3 115kV for 7 cycles. Open the faulted line and PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1. Re-open the faulted line after 7 cycles% PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_382_P6_FE-CLVS_INT3 | Prior Outage of OASIS to PORTALES 115kV line CKT 1. Apply 3-phase fault on N_CLOVIS_TP3 to FE-CLVS_INT3 115kV line CKT 1, near FE-CLVS_INT3 115kV for 7 cycles. Open the faulted line and PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1. Re-open the faulted line after 7 cycles% PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_382_P6_FE-CLVS_INT3 | Prior Outage of OASIS to PORTALES 115kV line CKT 1. Apply 3-phase fault on N_CLOVIS_TP3 to FE-CLVS_INT3 115kV line CKT 1, near FE-CLVS_INT3 115kV for 7 cycles. Open the faulted line and PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1. Re-open the faulted line after 7 cycles% PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_382_P6_FE-CLVS_INT3 | Prior Outage of OASIS to PORTALES 115kV line CKT 1. Apply 3-phase fault on N_CLOVIS_TP3 to FE-CLVS_INT3 115kV line CKT 1, near FE-CLVS_INT3 115kV for 7 cycles. Open the faulted line and PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1. Re-open the faulted line after 7 cycles% PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_383_P6_FE-CLVS_INT3 | Prior Outage of OASIS_TR1 13.19kV/115kV/230kV transformer CKT 1. Apply 3-phase fault on N_CLOVIS_TP3 to FE-CLVS_INT3 115kV line CKT 1, near FE-CLVS_INT3 115kV for 7 cycles. Open the faulted line and PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1. Re-open the faulted line after 7 cycles% PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_383_P6_FE-CLVS_INT3 | Prior Outage of OASIS_TR1 13.19kV/115kV/230kV transformer CKT 1. Apply 3-phase fault on N_CLOVIS_TP3 to FE-CLVS_INT3 115kV line CKT 1, near FE-CLVS_INT3 115kV for 7 cycles. Open the faulted line and PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1. Re-open the faulted line after 7 cycles% PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_383_P6_FE-CLVS_INT3 | Prior Outage of OASIS_TR1 13.19kV/115kV/230kV transformer CKT 1. Apply 3-phase fault on N_CLOVIS_TP3 to FE-CLVS_INT3 115kV line CKT 1, near FE-CLVS_INT3 115kV for 7 cycles. Open the faulted line and PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1. Re-open the faulted line after 7 cycles% PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_383_P6_FE-CLVS_INT3 | Prior Outage of OASIS_TR1 13.19kV/115kV/230kV transformer CKT 1. Apply 3-phase fault on N_CLOVIS_TP3 to FE-CLVS_INT3 115kV line CKT 1, near FE-CLVS_INT3 115kV for 7 cycles. Open the faulted line and PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1. Re-open the faulted line after 7 cycles% PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_384_P6_CURRY | Prior Outage of DS-#20 to CURRY 115kV line CKT 1Prior Outage of HEREFORD to DS-#6 115kV line CKT 1. Apply 3-phase fault on CURRY to BAILEYCO 115kV line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_384_P6_CURRY | Prior Outage of DS-#20 to CURRY 115kV line CKT 1Prior Outage of HEREFORD to DS-#6 115kV line CKT 1. Apply 3-phase fault on CURRY to BAILEYCO 115kV line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_384_P6_CURRY | Prior Outage of DS-#20 to CURRY 115kV line CKT 1Prior Outage of HEREFORD to DS-#6 115kV line CKT 1. Apply 3-phase fault on CURRY to BAILEYCO 115kV line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_384_P6_CURRY | Prior Outage of DS-#20 to CURRY 115kV line CKT 1Prior Outage of HEREFORD to DS-#6 115kV line CKT 1. Apply 3-phase fault on CURRY to BAILEYCO 115kV line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_385_P6_OASIS | Prior Outage of ROSEVLT_TR11 13.19kV/115kV/230kV transformer CKT 1. Apply 3-phase fault on OASIS_TR1 13.19kV/115kV/230kV transformer CKT 1, near OASIS 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_385_P6_OASIS | Prior Outage of ROSEVLT_TR11 13.19kV/115kV/230kV transformer CKT 1. Apply 3-phase fault on OASIS_TR1 13.19kV/115kV/230kV transformer CKT 1, near OASIS 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_385_P6_OASIS | Prior Outage of ROSEVLT_TR11 13.19kV/115kV/230kV transformer CKT 1. Apply 3-phase fault on OASIS_TR1 13.19kV/115kV/230kV transformer CKT 1, near OASIS 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_385_P6_OASIS | Prior Outage of ROSEVLT_TR11 13.19kV/115kV/230kV transformer CKT 1. Apply 3-phase fault on OASIS_TR1 13.19kV/115kV/230kV transformer CKT 1, near OASIS 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_386_P6_OASIS | Prior Outage of N_CLOVIS_TP3 to FE-CLVS_INT3 115kV line CKT 1Prior Outage of PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1. Apply 3-phase fault on OASIS to PORTALES 115kV line CKT 1, near OASIS 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_386_P6_OASIS | Prior Outage of N_CLOVIS_TP3 to FE-CLVS_INT3 115kV line CKT 1Prior Outage of PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1. Apply 3-phase fault on OASIS to PORTALES 115kV line CKT 1, near OASIS 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_386_P6_OASIS | Prior Outage of N_CLOVIS_TP3 to FE-CLVS_INT3 115kV line CKT 1Prior Outage of PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1. Apply 3-phase fault on OASIS to PORTALES 115kV line CKT 1, near OASIS 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_386_P6_OASIS | Prior Outage of N_CLOVIS_TP3 to FE-CLVS_INT3 115kV line CKT 1Prior Outage of PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1. Apply 3-phase fault on OASIS to PORTALES 115kV line CKT 1, near OASIS 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_387_P6_OASIS | Prior Outage of TOLK to CROSSROADS 7 345kV line CKT 1. Apply 3-phase fault on OASIS to ROSEVELT_N 6 230kV line CKT 1, near OASIS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_387_P6_OASIS | Prior Outage of TOLK to CROSSROADS 7 345kV line CKT 1. Apply 3-phase fault on OASIS to ROSEVELT_N 6 230kV line CKT 1, near OASIS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_387_P6_OASIS | Prior Outage of TOLK to CROSSROADS 7 345kV line CKT 1. Apply 3-phase fault on OASIS to ROSEVELT_N 6 230kV line CKT 1, near OASIS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_387_P6_OASIS | Prior Outage of TOLK to CROSSROADS 7 345kV line CKT 1. Apply 3-phase fault on OASIS to ROSEVELT_N 6 230kV line CKT 1, near OASIS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_388_P6_ROSEVELT_N6 | Prior Outage of ROSEVELT_N 6 to TOLK_WEST 230kV line CKT 2. Apply 3-phase fault on ROSEVELT_N 6 to TOLK_EAST 230kV line CKT 1, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Unstable | No | No | No | No | Yes | No | Angular and system instability, voltage collapse, and generation tripping was observed in the SPS-CLHF Zone (#1504). The stability issue is attributed to the export limit of the region and is caused by tripping the two outgoing transmission lines from ROSEVELT_N 6 station (#524909) to TOLK station as a part of P6 contingency. Following the N-1-1 contingency all the power of the region is exported from the OASIS bus (#524875) to SN_JUAN_TAP6 (#524885). Two mitigation options were tested: 1) Crossroad SVC & G6 Study Generators Scaled Down The stability issue was resolved with the SVC and all the G6 study generators dispatched at 90%. 2) SPS-CLHF Zone Study Generators Scaled Down As an alternative mitigation option, since this issue is related to this specific region, only the study generators in this region (GEN-2017-007, GEN-2017-016, GEN-2017-069, and GEN-2017-087) have been scaled down. The stability issue was resolved with the aforementioned study generators in the zone dispatched at 80%. | ±600 MVAr SVC at Crossroad 765kV & G6 Study Generators Dispatched @ 90% | SPS-CLHF Zone Study Generators Dispatched @ 80%
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_388_P6_ROSEVELT_N6 | Prior Outage of ROSEVELT_N 6 to TOLK_WEST 230kV line CKT 2. Apply 3-phase fault on ROSEVELT_N 6 to TOLK_EAST 230kV line CKT 1, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_388_P6_ROSEVELT_N6 | Prior Outage of ROSEVELT_N 6 to TOLK_WEST 230kV line CKT 2. Apply 3-phase fault on ROSEVELT_N 6 to TOLK_EAST 230kV line CKT 1, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_388_P6_ROSEVELT_N6 | Prior Outage of ROSEVELT_N 6 to TOLK_WEST 230kV line CKT 2. Apply 3-phase fault on ROSEVELT_N 6 to TOLK_EAST 230kV line CKT 1, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_389_P6_KRESS_INT | Prior Outage of AMA_SOUTH to SWISHER 230kV line CKT 1. Apply 3-phase fault on TULIA_TP to KRESS_INT 115kV line CKT 1, near KRESS_INT 115kV for 7 cycles. Open the faulted line and HAPPY_INT to TULIA_TP 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and HAPPY_INT to TULIA_TP 115kV line CKT 1. Re-open the faulted line after 7 cycles% HAPPY_INT to TULIA_TP 115kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_389_P6_KRESS_INT | Prior Outage of AMA_SOUTH to SWISHER 230kV line CKT 1. Apply 3-phase fault on TULIA_TP to KRESS_INT 115kV line CKT 1, near KRESS_INT 115kV for 7 cycles. Open the faulted line and HAPPY_INT to TULIA_TP 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and HAPPY_INT to TULIA_TP 115kV line CKT 1. Re-open the faulted line after 7 cycles% HAPPY_INT to TULIA_TP 115kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_389_P6_KRESS_INT | Prior Outage of AMA_SOUTH to SWISHER 230kV line CKT 1. Apply 3-phase fault on TULIA_TP to KRESS_INT 115kV line CKT 1, near KRESS_INT 115kV for 7 cycles. Open the faulted line and HAPPY_INT to TULIA_TP 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and HAPPY_INT to TULIA_TP 115kV line CKT 1. Re-open the faulted line after 7 cycles% HAPPY_INT to TULIA_TP 115kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_389_P6_KRESS_INT | Prior Outage of AMA_SOUTH to SWISHER 230kV line CKT 1. Apply 3-phase fault on TULIA_TP to KRESS_INT 115kV line CKT 1, near KRESS_INT 115kV for 7 cycles. Open the faulted line and HAPPY_INT to TULIA_TP 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and HAPPY_INT to TULIA_TP 115kV line CKT 1. Re-open the faulted line after 7 cycles% HAPPY_INT to TULIA_TP 115kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_39_P1_ROLLHILLS | Apply 3-phase fault on ROLLHILLS 115kV/13.19kV/230kV transformer CKT 1, near ROLLHILLS 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_39_P1_ROLLHILLS | Apply 3-phase fault on ROLLHILLS 115kV/13.19kV/230kV transformer CKT 1, near ROLLHILLS 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_39_P1_ROLLHILLS | Apply 3-phase fault on ROLLHILLS 115kV/13.19kV/230kV transformer CKT 1, near ROLLHILLS 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_39_P1_ROLLHILLS | Apply 3-phase fault on ROLLHILLS 115kV/13.19kV/230kV transformer CKT 1, near ROLLHILLS 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_390_P6_KRESS_INT | Prior Outage of NEWPOT_SS to NEWHART 230kV line CKT 1Prior Outage of POTTER_CO to NEWPOT_SS 230kV line CKT 1. Apply 3-phase fault on TULIA_TP to KRESS_INT 115kV line CKT 1, near KRESS_INT 115kV for 7 cycles. Open the faulted line and HAPPY_INT to TULIA_TP 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and HAPPY_INT to TULIA_TP 115kV line CKT 1. Re-open the faulted line after 7 cycles% HAPPY_INT to TULIA_TP 115kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_390_P6_KRESS_INT | Prior Outage of NEWPOT_SS to NEWHART 230kV line CKT 1Prior Outage of POTTER_CO to NEWPOT_SS 230kV line CKT 1. Apply 3-phase fault on TULIA_TP to KRESS_INT 115kV line CKT 1, near KRESS_INT 115kV for 7 cycles. Open the faulted line and HAPPY_INT to TULIA_TP 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and HAPPY_INT to TULIA_TP 115kV line CKT 1. Re-open the faulted line after 7 cycles% HAPPY_INT to TULIA_TP 115kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | No | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_390_P6_KRESS_INT | Prior Outage of NEWPOT_SS to NEWHART 230kV line CKT 1Prior Outage of POTTER_CO to NEWPOT_SS 230kV line CKT 1. Apply 3-phase fault on TULIA_TP to KRESS_INT 115kV line CKT 1, near KRESS_INT 115kV for 7 cycles. Open the faulted line and HAPPY_INT to TULIA_TP 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and HAPPY_INT to TULIA_TP 115kV line CKT 1. Re-open the faulted line after 7 cycles% HAPPY_INT to TULIA_TP 115kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_390_P6_KRESS_INT | Prior Outage of NEWPOT_SS to NEWHART 230kV line CKT 1Prior Outage of POTTER_CO to NEWPOT_SS 230kV line CKT 1. Apply 3-phase fault on TULIA_TP to KRESS_INT 115kV line CKT 1, near KRESS_INT 115kV for 7 cycles. Open the faulted line and HAPPY_INT to TULIA_TP 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and HAPPY_INT to TULIA_TP 115kV line CKT 1. Re-open the faulted line after 7 cycles% HAPPY_INT to TULIA_TP 115kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_391_P6_SWISHER | Prior Outage of AMA_SOUTH to SWISHER 230kV line CKT 1. Apply 3-phase fault on KRESS_INT to SWISHER 115kV line CKT 1, near SWISHER 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_391_P6_SWISHER | Prior Outage of AMA_SOUTH to SWISHER 230kV line CKT 1. Apply 3-phase fault on KRESS_INT to SWISHER 115kV line CKT 1, near SWISHER 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_391_P6_SWISHER | Prior Outage of AMA_SOUTH to SWISHER 230kV line CKT 1. Apply 3-phase fault on KRESS_INT to SWISHER 115kV line CKT 1, near SWISHER 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_391_P6_SWISHER | Prior Outage of AMA_SOUTH to SWISHER 230kV line CKT 1. Apply 3-phase fault on KRESS_INT to SWISHER 115kV line CKT 1, near SWISHER 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_392_P6_SWISHER | Prior Outage of TULIA_TP to KRESS_INT 115kV line CKT 1Prior Outage of HAPPY_INT to TULIA_TP 115kV line CKT 1. Apply 3-phase fault on KRESS_INT to SWISHER 115kV line CKT 1, near SWISHER 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_392_P6_SWISHER | Prior Outage of TULIA_TP to KRESS_INT 115kV line CKT 1Prior Outage of HAPPY_INT to TULIA_TP 115kV line CKT 1. Apply 3-phase fault on KRESS_INT to SWISHER 115kV line CKT 1, near SWISHER 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_392_P6_SWISHER | Prior Outage of TULIA_TP to KRESS_INT 115kV line CKT 1Prior Outage of HAPPY_INT to TULIA_TP 115kV line CKT 1. Apply 3-phase fault on KRESS_INT to SWISHER 115kV line CKT 1, near SWISHER 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_392_P6_SWISHER | Prior Outage of TULIA_TP to KRESS_INT 115kV line CKT 1Prior Outage of HAPPY_INT to TULIA_TP 115kV line CKT 1. Apply 3-phase fault on KRESS_INT to SWISHER 115kV line CKT 1, near SWISHER 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_393_P6_SWISHER | Prior Outage of AMA_SOUTH to SWISHER 230kV line CKT 1. Apply 3-phase fault on SWISHER to NEWHART 230kV line CKT 1, near SWISHER 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_393_P6_SWISHER | Prior Outage of AMA_SOUTH to SWISHER 230kV line CKT 1. Apply 3-phase fault on SWISHER to NEWHART 230kV line CKT 1, near SWISHER 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_393_P6_SWISHER | Prior Outage of AMA_SOUTH to SWISHER 230kV line CKT 1. Apply 3-phase fault on SWISHER to NEWHART 230kV line CKT 1, near SWISHER 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_393_P6_SWISHER | Prior Outage of AMA_SOUTH to SWISHER 230kV line CKT 1. Apply 3-phase fault on SWISHER to NEWHART 230kV line CKT 1, near SWISHER 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_394_P6_SWISHER | Prior Outage of SWISHER shunt device . Apply 3-phase fault on AMA_SOUTH to SWISHER 230kV line CKT 1, near SWISHER 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_394_P6_SWISHER | Prior Outage of SWISHER shunt device . Apply 3-phase fault on AMA_SOUTH to SWISHER 230kV line CKT 1, near SWISHER 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.22pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_394_P6_SWISHER | Prior Outage of SWISHER shunt device . Apply 3-phase fault on AMA_SOUTH to SWISHER 230kV line CKT 1, near SWISHER 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_394_P6_SWISHER | Prior Outage of SWISHER shunt device . Apply 3-phase fault on AMA_SOUTH to SWISHER 230kV line CKT 1, near SWISHER 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.21pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_395_P6_SWISHER | Prior Outage of AMA_SOUTH to SWISHER 230kV line CKT 1. Apply 3-phase fault on SWISHER to TUCO_INT 230kV line CKT 1, near SWISHER 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_395_P6_SWISHER | Prior Outage of AMA_SOUTH to SWISHER 230kV line CKT 1. Apply 3-phase fault on SWISHER to TUCO_INT 230kV line CKT 1, near SWISHER 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_395_P6_SWISHER | Prior Outage of AMA_SOUTH to SWISHER 230kV line CKT 1. Apply 3-phase fault on SWISHER to TUCO_INT 230kV line CKT 1, near SWISHER 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_395_P6_SWISHER | Prior Outage of AMA_SOUTH to SWISHER 230kV line CKT 1. Apply 3-phase fault on SWISHER to TUCO_INT 230kV line CKT 1, near SWISHER 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_396_P6_SWISHER | Prior Outage of NEWPOT_SS to NEWHART 230kV line CKT 1Prior Outage of POTTER_CO to NEWPOT_SS 230kV line CKT 1. Apply 3-phase fault on AMA_SOUTH to SWISHER 230kV line CKT 1, near SWISHER 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_396_P6_SWISHER | Prior Outage of NEWPOT_SS to NEWHART 230kV line CKT 1Prior Outage of POTTER_CO to NEWPOT_SS 230kV line CKT 1. Apply 3-phase fault on AMA_SOUTH to SWISHER 230kV line CKT 1, near SWISHER 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | No | No | Yes | Voltage Spike: 1.22pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_396_P6_SWISHER | Prior Outage of NEWPOT_SS to NEWHART 230kV line CKT 1Prior Outage of POTTER_CO to NEWPOT_SS 230kV line CKT 1. Apply 3-phase fault on AMA_SOUTH to SWISHER 230kV line CKT 1, near SWISHER 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_396_P6_SWISHER | Prior Outage of NEWPOT_SS to NEWHART 230kV line CKT 1Prior Outage of POTTER_CO to NEWPOT_SS 230kV line CKT 1. Apply 3-phase fault on AMA_SOUTH to SWISHER 230kV line CKT 1, near SWISHER 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.21pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_397_P6_SWISHER | Prior Outage of TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1. Apply 3-phase fault on AMA_SOUTH to SWISHER 230kV line CKT 1, near SWISHER 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_397_P6_SWISHER | Prior Outage of TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1. Apply 3-phase fault on AMA_SOUTH to SWISHER 230kV line CKT 1, near SWISHER 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.22pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_397_P6_SWISHER | Prior Outage of TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1. Apply 3-phase fault on AMA_SOUTH to SWISHER 230kV line CKT 1, near SWISHER 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_397_P6_SWISHER | Prior Outage of TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1. Apply 3-phase fault on AMA_SOUTH to SWISHER 230kV line CKT 1, near SWISHER 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.21pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_398_P6_NEWHART | Prior Outage of NEWHART_TR11 13.19kV/115kV/230kV transformer CKT 1. Apply 3-phase fault on NEWHART_TR21 13.19kV/115kV/230kV transformer CKT 2, near NEWHART 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_398_P6_NEWHART | Prior Outage of NEWHART_TR11 13.19kV/115kV/230kV transformer CKT 1. Apply 3-phase fault on NEWHART_TR21 13.19kV/115kV/230kV transformer CKT 2, near NEWHART 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_398_P6_NEWHART | Prior Outage of NEWHART_TR11 13.19kV/115kV/230kV transformer CKT 1. Apply 3-phase fault on NEWHART_TR21 13.19kV/115kV/230kV transformer CKT 2, near NEWHART 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_398_P6_NEWHART | Prior Outage of NEWHART_TR11 13.19kV/115kV/230kV transformer CKT 1. Apply 3-phase fault on NEWHART_TR21 13.19kV/115kV/230kV transformer CKT 2, near NEWHART 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_399_P6_NEWHART | Prior Outage of NEWPOT_SS to NEWHART 230kV line CKT 1Prior Outage of POTTER_CO to NEWPOT_SS 230kV line CKT 1. Apply 3-phase fault on KRESS_INT to NEWHART 115kV line CKT 1, near NEWHART 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_399_P6_NEWHART | Prior Outage of NEWPOT_SS to NEWHART 230kV line CKT 1Prior Outage of POTTER_CO to NEWPOT_SS 230kV line CKT 1. Apply 3-phase fault on KRESS_INT to NEWHART 115kV line CKT 1, near NEWHART 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_399_P6_NEWHART | Prior Outage of NEWPOT_SS to NEWHART 230kV line CKT 1Prior Outage of POTTER_CO to NEWPOT_SS 230kV line CKT 1. Apply 3-phase fault on KRESS_INT to NEWHART 115kV line CKT 1, near NEWHART 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_399_P6_NEWHART | Prior Outage of NEWPOT_SS to NEWHART 230kV line CKT 1Prior Outage of POTTER_CO to NEWPOT_SS 230kV line CKT 1. Apply 3-phase fault on KRESS_INT to NEWHART 115kV line CKT 1, near NEWHART 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_4_P1_OKU-7 | Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_4_P1_OKU-7 | Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_4_P1_OKU-7 | Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_4_P1_OKU-7 | Apply 3-phase fault on OKLAUN HVDC7 shunt device , near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Switched Shunt Device. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_40_P1_NICHOLS | Apply 3-phase fault on HUTCHISON to NICHOLS 230kV line CKT 1, near NICHOLS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_40_P1_NICHOLS | Apply 3-phase fault on HUTCHISON to NICHOLS 230kV line CKT 1, near NICHOLS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_40_P1_NICHOLS | Apply 3-phase fault on HUTCHISON to NICHOLS 230kV line CKT 1, near NICHOLS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_40_P1_NICHOLS | Apply 3-phase fault on HUTCHISON to NICHOLS 230kV line CKT 1, near NICHOLS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_400_P6_NEWHART | Prior Outage of SWISHER to NEWHART 230kV line CKT 1. Apply 3-phase fault on KRESS_INT to NEWHART 115kV line CKT 1, near NEWHART 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_400_P6_NEWHART | Prior Outage of SWISHER to NEWHART 230kV line CKT 1. Apply 3-phase fault on KRESS_INT to NEWHART 115kV line CKT 1, near NEWHART 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_400_P6_NEWHART | Prior Outage of SWISHER to NEWHART 230kV line CKT 1. Apply 3-phase fault on KRESS_INT to NEWHART 115kV line CKT 1, near NEWHART 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_400_P6_NEWHART | Prior Outage of SWISHER to NEWHART 230kV line CKT 1. Apply 3-phase fault on KRESS_INT to NEWHART 115kV line CKT 1, near NEWHART 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_401_P6_NEWHART | Prior Outage of AMA_SOUTH to SWISHER 230kV line CKT 1. Apply 3-phase fault on NEWPOT_SS to NEWHART 230kV line CKT 1, near NEWHART 230kV for 7 cycles. Open the faulted line and POTTER_CO to NEWPOT_SS 230kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and POTTER_CO to NEWPOT_SS 230kV line CKT 1. Re-open the faulted line after 7 cycles% POTTER_CO to NEWPOT_SS 230kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_401_P6_NEWHART | Prior Outage of AMA_SOUTH to SWISHER 230kV line CKT 1. Apply 3-phase fault on NEWPOT_SS to NEWHART 230kV line CKT 1, near NEWHART 230kV for 7 cycles. Open the faulted line and POTTER_CO to NEWPOT_SS 230kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and POTTER_CO to NEWPOT_SS 230kV line CKT 1. Re-open the faulted line after 7 cycles% POTTER_CO to NEWPOT_SS 230kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | No | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_401_P6_NEWHART | Prior Outage of AMA_SOUTH to SWISHER 230kV line CKT 1. Apply 3-phase fault on NEWPOT_SS to NEWHART 230kV line CKT 1, near NEWHART 230kV for 7 cycles. Open the faulted line and POTTER_CO to NEWPOT_SS 230kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and POTTER_CO to NEWPOT_SS 230kV line CKT 1. Re-open the faulted line after 7 cycles% POTTER_CO to NEWPOT_SS 230kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_401_P6_NEWHART | Prior Outage of AMA_SOUTH to SWISHER 230kV line CKT 1. Apply 3-phase fault on NEWPOT_SS to NEWHART 230kV line CKT 1, near NEWHART 230kV for 7 cycles. Open the faulted line and POTTER_CO to NEWPOT_SS 230kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and POTTER_CO to NEWPOT_SS 230kV line CKT 1. Re-open the faulted line after 7 cycles% POTTER_CO to NEWPOT_SS 230kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_402_P6_NEWHART | Prior Outage of DEAFSMITH to PLANT_X 230kV line CKT 1. Apply 3-phase fault on SWISHER to NEWHART 230kV line CKT 1, near NEWHART 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_402_P6_NEWHART | Prior Outage of DEAFSMITH to PLANT_X 230kV line CKT 1. Apply 3-phase fault on SWISHER to NEWHART 230kV line CKT 1, near NEWHART 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_402_P6_NEWHART | Prior Outage of DEAFSMITH to PLANT_X 230kV line CKT 1. Apply 3-phase fault on SWISHER to NEWHART 230kV line CKT 1, near NEWHART 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_402_P6_NEWHART | Prior Outage of DEAFSMITH to PLANT_X 230kV line CKT 1. Apply 3-phase fault on SWISHER to NEWHART 230kV line CKT 1, near NEWHART 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_403_P6_NEWHART | Prior Outage of DEAFSMITH to PLANT_X 230kV line CKT 1. Apply 3-phase fault on NEWPOT_SS to NEWHART 230kV line CKT 1, near NEWHART 230kV for 7 cycles. Open the faulted line and POTTER_CO to NEWPOT_SS 230kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and POTTER_CO to NEWPOT_SS 230kV line CKT 1. Re-open the faulted line after 7 cycles% POTTER_CO to NEWPOT_SS 230kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_403_P6_NEWHART | Prior Outage of DEAFSMITH to PLANT_X 230kV line CKT 1. Apply 3-phase fault on NEWPOT_SS to NEWHART 230kV line CKT 1, near NEWHART 230kV for 7 cycles. Open the faulted line and POTTER_CO to NEWPOT_SS 230kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and POTTER_CO to NEWPOT_SS 230kV line CKT 1. Re-open the faulted line after 7 cycles% POTTER_CO to NEWPOT_SS 230kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | No | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_403_P6_NEWHART | Prior Outage of DEAFSMITH to PLANT_X 230kV line CKT 1. Apply 3-phase fault on NEWPOT_SS to NEWHART 230kV line CKT 1, near NEWHART 230kV for 7 cycles. Open the faulted line and POTTER_CO to NEWPOT_SS 230kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and POTTER_CO to NEWPOT_SS 230kV line CKT 1. Re-open the faulted line after 7 cycles% POTTER_CO to NEWPOT_SS 230kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_403_P6_NEWHART | Prior Outage of DEAFSMITH to PLANT_X 230kV line CKT 1. Apply 3-phase fault on NEWPOT_SS to NEWHART 230kV line CKT 1, near NEWHART 230kV for 7 cycles. Open the faulted line and POTTER_CO to NEWPOT_SS 230kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and POTTER_CO to NEWPOT_SS 230kV line CKT 1. Re-open the faulted line after 7 cycles% POTTER_CO to NEWPOT_SS 230kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_404_P6_NEWHART | Prior Outage of NEWPOT_SS to NEWHART 230kV line CKT 1Prior Outage of POTTER_CO to NEWPOT_SS 230kV line CKT 1. Apply 3-phase fault on SWISHER to NEWHART 230kV line CKT 1, near NEWHART 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_404_P6_NEWHART | Prior Outage of NEWPOT_SS to NEWHART 230kV line CKT 1Prior Outage of POTTER_CO to NEWPOT_SS 230kV line CKT 1. Apply 3-phase fault on SWISHER to NEWHART 230kV line CKT 1, near NEWHART 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.22pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_404_P6_NEWHART | Prior Outage of NEWPOT_SS to NEWHART 230kV line CKT 1Prior Outage of POTTER_CO to NEWPOT_SS 230kV line CKT 1. Apply 3-phase fault on SWISHER to NEWHART 230kV line CKT 1, near NEWHART 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_404_P6_NEWHART | Prior Outage of NEWPOT_SS to NEWHART 230kV line CKT 1Prior Outage of POTTER_CO to NEWPOT_SS 230kV line CKT 1. Apply 3-phase fault on SWISHER to NEWHART 230kV line CKT 1, near NEWHART 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_405_P6_TOLK_WEST | Prior Outage of PLANT_X to TOLK_EAST 230kV line CKT 2. Apply 3-phase fault on PLANT_X to TOLK_WEST 230kV line CKT 1, near TOLK_WEST 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-080-GEN1[1] G17-080-GEN2[1]. G17-080-GEN1[1] and G17-080-GEN2[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s. The protection settings were disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.25pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_405_P6_TOLK_WEST | Prior Outage of PLANT_X to TOLK_EAST 230kV line CKT 2. Apply 3-phase fault on PLANT_X to TOLK_WEST 230kV line CKT 1, near TOLK_WEST 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | No | Yes | No | No | No | LVRT VIOL - - G17-080-GEN1[1] G17-080-GEN2[1] FRISCO_WND 3[1]. G17-080-GEN1[1] and G17-080-GEN2[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s. The protection settings were disabled and simulation was rerun. Following protection disable: Angular and system instability was observed in the G6 region. The stability issue was resolved with the SVC mitigation solution. (TOV: 1.31pu, MaxDur: 0.10s) | ±600 MVAr SVC at Crossroad 765kV
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_405_P6_TOLK_WEST | Prior Outage of PLANT_X to TOLK_EAST 230kV line CKT 2. Apply 3-phase fault on PLANT_X to TOLK_WEST 230kV line CKT 1, near TOLK_WEST 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-080-GEN1[1] G17-080-GEN2[1]. G17-080-GEN1[1] and G17-080-GEN2[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s. The protection settings were disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.22pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_405_P6_TOLK_WEST | Prior Outage of PLANT_X to TOLK_EAST 230kV line CKT 2. Apply 3-phase fault on PLANT_X to TOLK_WEST 230kV line CKT 1, near TOLK_WEST 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1] G17-080-GEN1[1] G17-080-GEN2[1]. G17-080-GEN1[1] and G17-080-GEN2[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s. The protection settings were disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.22pu, MaxDur: 0.04s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_406_P6_TOLK_WEST | Prior Outage of TOLK to CROSSROADS 7 345kV line CKT 1. Apply 3-phase fault on TOLK_2 generation unit 1, near TOLK_WEST 230kV for 7 cycles. Clear fault by tripping the faulted Generator. | P6 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-080-GEN1[1] G17-080-GEN2[1]. G17-080-GEN1[1] and G17-080-GEN2[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s. The protection settings were disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.23pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_406_P6_TOLK_WEST | Prior Outage of TOLK to CROSSROADS 7 345kV line CKT 1. Apply 3-phase fault on TOLK_2 generation unit 1, near TOLK_WEST 230kV for 7 cycles. Clear fault by tripping the faulted Generator. | P6 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-080-GEN1[1] G17-080-GEN2[1]. G17-080-GEN1[1] and G17-080-GEN2[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s. The protection settings were disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.23pu, MaxDur: 0.05s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_406_P6_TOLK_WEST | Prior Outage of TOLK to CROSSROADS 7 345kV line CKT 1. Apply 3-phase fault on TOLK_2 generation unit 1, near TOLK_WEST 230kV for 7 cycles. Clear fault by tripping the faulted Generator. | P6 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-080-GEN1[1] G17-080-GEN2[1]. G17-080-GEN1[1] and G17-080-GEN2[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s. The protection settings were disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.23pu, MaxDur: 0.04s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_406_P6_TOLK_WEST | Prior Outage of TOLK to CROSSROADS 7 345kV line CKT 1. Apply 3-phase fault on TOLK_2 generation unit 1, near TOLK_WEST 230kV for 7 cycles. Clear fault by tripping the faulted Generator. | P6 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1] G17-080-GEN1[1] G17-080-GEN2[1]. G17-080-GEN1[1] and G17-080-GEN2[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s. The protection settings were disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.25pu, MaxDur: 0.04s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_407_P6_TOLK_WEST | Prior Outage of NEEDMORE to DEAN_INTG 230kV line CKT 1. Apply 3-phase fault on PLANT_X to TOLK_WEST 230kV line CKT 1, near TOLK_WEST 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-080-GEN1[1] G17-080-GEN2[1]. G17-080-GEN1[1] and G17-080-GEN2[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s. The protection settings were disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.29pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_407_P6_TOLK_WEST | Prior Outage of NEEDMORE to DEAN_INTG 230kV line CKT 1. Apply 3-phase fault on PLANT_X to TOLK_WEST 230kV line CKT 1, near TOLK_WEST 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | No | Yes | Yes | No | No | LVRT VIOL - - G17-080-GEN1[1] G17-080-GEN2[1] FRISCO_WND 3[1]. G17-080-GEN1[1] and G17-080-GEN2[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s. The protection settings were disabled and simulation was rerun. No further issues were observed. TOV: 1.32pu, MaxDur: 0.28s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_407_P6_TOLK_WEST | Prior Outage of NEEDMORE to DEAN_INTG 230kV line CKT 1. Apply 3-phase fault on PLANT_X to TOLK_WEST 230kV line CKT 1, near TOLK_WEST 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-080-GEN1[1] G17-080-GEN2[1]. G17-080-GEN1[1] and G17-080-GEN2[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s. The protection settings were disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.31pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_407_P6_TOLK_WEST | Prior Outage of NEEDMORE to DEAN_INTG 230kV line CKT 1. Apply 3-phase fault on PLANT_X to TOLK_WEST 230kV line CKT 1, near TOLK_WEST 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1] G17-080-GEN1[1] G17-080-GEN2[1]. G17-080-GEN1[1] and G17-080-GEN2[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s. The protection settings were disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.36pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_408_P6_NEEDMORE | Prior Outage of PLANT_X to TOLK_WEST 230kV line CKT 1. Apply 3-phase fault on NEEDMORE to DEAN_INTG 230kV line CKT 1, near NEEDMORE 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.35pu, MaxDur: 0.04s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_408_P6_NEEDMORE | Prior Outage of PLANT_X to TOLK_WEST 230kV line CKT 1. Apply 3-phase fault on NEEDMORE to DEAN_INTG 230kV line CKT 1, near NEEDMORE 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.36pu, MaxDur: 0.05s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_408_P6_NEEDMORE | Prior Outage of PLANT_X to TOLK_WEST 230kV line CKT 1. Apply 3-phase fault on NEEDMORE to DEAN_INTG 230kV line CKT 1, near NEEDMORE 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.33pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_408_P6_NEEDMORE | Prior Outage of PLANT_X to TOLK_WEST 230kV line CKT 1. Apply 3-phase fault on NEEDMORE to DEAN_INTG 230kV line CKT 1, near NEEDMORE 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.33pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_409_P6_NEEDMORE | Prior Outage of DEAN_INTG to YOAKUM 230kV line CKT 1. Apply 3-phase fault on TOLK_WEST to NEEDMORE 230kV line CKT 1, near NEEDMORE 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Unstable | No | No | No | No | Yes | No | Power export issue: Instability has been observed for GEN-2017-039 study generator and several other prior qeued generators nearby. Following the trip of NEEDMORE-TOLK 230kV line with the prior outage of DEAN_INTG-YOAKUM 230kV line as a part this P6 contingency, all the powers of the GEN-2017-039 study generator and G13-027-GEN1 prior qeued generator (total power: 348.5MW) is pushed through the DEAN_INTG 230/115kV transformer, which is also POI of another prior qeued generator with 150MW dispatch. In order, to mitigate this instability issue the dispatch of GEN-2017-039 study generator is decreased incrementally untill acceptable response is achieved. This power export issue is observed in all four TCs and in none of the BCs. The stability issue was resolved with the GEN-2017-039 study generator being dispatched at 100MW (50%). Voltage Spike: 1.72pu, MaxDur: 0.02s | GEN-2017-039 study generator dispatch at 50%
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_409_P6_NEEDMORE | Prior Outage of DEAN_INTG to YOAKUM 230kV line CKT 1. Apply 3-phase fault on TOLK_WEST to NEEDMORE 230kV line CKT 1, near NEEDMORE 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Unstable | No | No | No | No | Yes | No | Power export issue: Please refer to notes in the 19WTC. Voltage Spike: 1.72pu, MaxDur: 0.02s | GEN-2017-039 study generator dispatch at 50%
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_409_P6_NEEDMORE | Prior Outage of DEAN_INTG to YOAKUM 230kV line CKT 1. Apply 3-phase fault on TOLK_WEST to NEEDMORE 230kV line CKT 1, near NEEDMORE 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Unstable | No | No | No | No | Yes | No | Power export issue: Please refer to notes in the 19WTC. Voltage Spike: 1.71pu, MaxDur: 0.02s | GEN-2017-039 study generator dispatch at 50%
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_409_P6_NEEDMORE | Prior Outage of DEAN_INTG to YOAKUM 230kV line CKT 1. Apply 3-phase fault on TOLK_WEST to NEEDMORE 230kV line CKT 1, near NEEDMORE 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Unstable | No | No | No | No | Yes | No | Power export issue: Please refer to notes in the 19WTC. Voltage Spike: 1.73pu, MaxDur: 0.02s | GEN-2017-039 study generator dispatch at 50%
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_41_P1_NICHOLS | Apply 3-phase fault on HARRNG_WST 6 to NICHOLS 230kV line CKT 1, near NICHOLS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_41_P1_NICHOLS | Apply 3-phase fault on HARRNG_WST 6 to NICHOLS 230kV line CKT 1, near NICHOLS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_41_P1_NICHOLS | Apply 3-phase fault on HARRNG_WST 6 to NICHOLS 230kV line CKT 1, near NICHOLS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_41_P1_NICHOLS | Apply 3-phase fault on HARRNG_WST 6 to NICHOLS 230kV line CKT 1, near NICHOLS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_410_P6_NEEDMORE | Prior Outage of TOLK_EAST to TUCO_INT 230kV line CKT 1. Apply 3-phase fault on NEEDMORE to DEAN_INTG 230kV line CKT 1, near NEEDMORE 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.34pu, MaxDur: 0.04s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_410_P6_NEEDMORE | Prior Outage of TOLK_EAST to TUCO_INT 230kV line CKT 1. Apply 3-phase fault on NEEDMORE to DEAN_INTG 230kV line CKT 1, near NEEDMORE 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.35pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_410_P6_NEEDMORE | Prior Outage of TOLK_EAST to TUCO_INT 230kV line CKT 1. Apply 3-phase fault on NEEDMORE to DEAN_INTG 230kV line CKT 1, near NEEDMORE 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.32pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_410_P6_NEEDMORE | Prior Outage of TOLK_EAST to TUCO_INT 230kV line CKT 1. Apply 3-phase fault on NEEDMORE to DEAN_INTG 230kV line CKT 1, near NEEDMORE 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.32pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_411_P6_TUCO_INT | Prior Outage of TUCO_INT shunt device . Apply 3-phase fault on TUCO_SVC generation unit 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Generator. | P6 | Unstable | No | No | No | No | Yes | No | Angular and system instability was observed in the G6 region. The stability issue was resolved with the SVC mitigation solution. | ±600 MVAr SVC at Crossroad 765kV
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_411_P6_TUCO_INT | Prior Outage of TUCO_INT shunt device . Apply 3-phase fault on TUCO_SVC generation unit 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Generator. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_411_P6_TUCO_INT | Prior Outage of TUCO_INT shunt device . Apply 3-phase fault on TUCO_SVC generation unit 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Generator. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_411_P6_TUCO_INT | Prior Outage of TUCO_INT shunt device . Apply 3-phase fault on TUCO_SVC generation unit 1, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Generator. | P6 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_412_P6_TUCO_INT | Prior Outage of TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1. Apply 3-phase fault on TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Unstable | No | No | No | No | Yes | No | Angular and system instability was observed in the G6 region. The stability issue was resolved with the SVC mitigation solution. | ±600 MVAr SVC at Crossroad 765kV
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_412_P6_TUCO_INT | Prior Outage of TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1. Apply 3-phase fault on TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | No | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_412_P6_TUCO_INT | Prior Outage of TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1. Apply 3-phase fault on TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_412_P6_TUCO_INT | Prior Outage of TUCO_TR1 13.19kV/230kV/345kV transformer CKT 1. Apply 3-phase fault on TUCO_TR2 13.19kV/230kV/345kV transformer CKT 2, near TUCO_INT 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_413_P6_CARLISLE | Prior Outage of LUBBCK_STH 6 to WOLFFORTH 230kV line CKT 1. Apply 3-phase fault on CARLISLE to WOLFFORTH 230kV line CKT 1, near CARLISLE 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_413_P6_CARLISLE | Prior Outage of LUBBCK_STH 6 to WOLFFORTH 230kV line CKT 1. Apply 3-phase fault on CARLISLE to WOLFFORTH 230kV line CKT 1, near CARLISLE 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_413_P6_CARLISLE | Prior Outage of LUBBCK_STH 6 to WOLFFORTH 230kV line CKT 1. Apply 3-phase fault on CARLISLE to WOLFFORTH 230kV line CKT 1, near CARLISLE 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_413_P6_CARLISLE | Prior Outage of LUBBCK_STH 6 to WOLFFORTH 230kV line CKT 1. Apply 3-phase fault on CARLISLE to WOLFFORTH 230kV line CKT 1, near CARLISLE 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_414_P6_LUBBCK_STH6 | Prior Outage of LP-SOUTHEST6 to LUBBCK_STH 6 230kV line CKT 1. Apply 3-phase fault on LUBBCK_STH 6 to WOLFFORTH 230kV line CKT 1, near LUBBCK_STH 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_414_P6_LUBBCK_STH6 | Prior Outage of LP-SOUTHEST6 to LUBBCK_STH 6 230kV line CKT 1. Apply 3-phase fault on LUBBCK_STH 6 to WOLFFORTH 230kV line CKT 1, near LUBBCK_STH 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_414_P6_LUBBCK_STH6 | Prior Outage of LP-SOUTHEST6 to LUBBCK_STH 6 230kV line CKT 1. Apply 3-phase fault on LUBBCK_STH 6 to WOLFFORTH 230kV line CKT 1, near LUBBCK_STH 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_414_P6_LUBBCK_STH6 | Prior Outage of LP-SOUTHEST6 to LUBBCK_STH 6 230kV line CKT 1. Apply 3-phase fault on LUBBCK_STH 6 to WOLFFORTH 230kV line CKT 1, near LUBBCK_STH 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_415_P6_JONES | Prior Outage of LUBBCK_STH 6 to JONES 230kV line CKT 2. Apply 3-phase fault on LUBBCK_STH 6 to JONES 230kV line CKT 1, near JONES 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_415_P6_JONES | Prior Outage of LUBBCK_STH 6 to JONES 230kV line CKT 2. Apply 3-phase fault on LUBBCK_STH 6 to JONES 230kV line CKT 1, near JONES 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_415_P6_JONES | Prior Outage of LUBBCK_STH 6 to JONES 230kV line CKT 2. Apply 3-phase fault on LUBBCK_STH 6 to JONES 230kV line CKT 1, near JONES 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_415_P6_JONES | Prior Outage of LUBBCK_STH 6 to JONES 230kV line CKT 2. Apply 3-phase fault on LUBBCK_STH 6 to JONES 230kV line CKT 1, near JONES 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_416_P6_JONES | Prior Outage of LP-HOLLY to JONES 230kV line CKT 1. Apply 3-phase fault on LUBBCK_EST 6 to JONES 230kV line CKT 1, near JONES 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_416_P6_JONES | Prior Outage of LP-HOLLY to JONES 230kV line CKT 1. Apply 3-phase fault on LUBBCK_EST 6 to JONES 230kV line CKT 1, near JONES 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_416_P6_JONES | Prior Outage of LP-HOLLY to JONES 230kV line CKT 1. Apply 3-phase fault on LUBBCK_EST 6 to JONES 230kV line CKT 1, near JONES 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_416_P6_JONES | Prior Outage of LP-HOLLY to JONES 230kV line CKT 1. Apply 3-phase fault on LUBBCK_EST 6 to JONES 230kV line CKT 1, near JONES 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_417_P6_CROSSROADS7 | Prior Outage of CROSSROADS 7 345kV/765kV transformer CKT 2. Apply 3-phase fault on CROSSROADS 7 345kV/765kV transformer CKT 1, near CROSSROADS 7 345kV for 6 cycles. Clear fault by tripping the faulted Two Winding. | P6 | Unstable | No | No | No | No | Yes | No | Angular and system instability was observed in the G6 region. Simulation was rerun with the Crossroad SVC and different G6 dispatch options. No stability or damping issues were observed with the Crossroad SVC and G6 study generators dispatched at 50%. Voltage Spike: 1.42pu, MaxDur: 0.09s | ±600 MVAr SVC at Crossroad 765kV & G6 Study Generators Dispatched @ 50%
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_417_P6_CROSSROADS7 | Prior Outage of CROSSROADS 7 345kV/765kV transformer CKT 2. Apply 3-phase fault on CROSSROADS 7 345kV/765kV transformer CKT 1, near CROSSROADS 7 345kV for 6 cycles. Clear fault by tripping the faulted Two Winding. | P6 | Stable | Yes | Yes | No | Yes | No | Yes | Note: Abnormal oscillations were observed in the generation units and system responses, which are attributed to the OECGT generation units modeling issues. When the OECGT units were GENETed these oscillations were mitigated. Voltage Spike: 1.25pu, MaxDur: 0.04s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_417_P6_CROSSROADS7 | Prior Outage of CROSSROADS 7 345kV/765kV transformer CKT 2. Apply 3-phase fault on CROSSROADS 7 345kV/765kV transformer CKT 1, near CROSSROADS 7 345kV for 6 cycles. Clear fault by tripping the faulted Two Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.23pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_417_P6_CROSSROADS7 | Prior Outage of CROSSROADS 7 345kV/765kV transformer CKT 2. Apply 3-phase fault on CROSSROADS 7 345kV/765kV transformer CKT 1, near CROSSROADS 7 345kV for 6 cycles. Clear fault by tripping the faulted Two Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.25pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_418_P6_CROSSROADS7 | Prior Outage of TOLK_TR 13.19kV/230kV/345kV transformer CKT 1. Apply 3-phase fault on CROSSROADS 7 to EDDY_CNTY 345kV line CKT 1, near CROSSROADS 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | No | Yes | Yes | No | Yes | Note: Abnormal oscillations were observed in the generation units and system responses, which are attributed to the OECGT generation units modeling issues. When the OECGT units were GENETed these oscillations were mitigated.
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_418_P6_CROSSROADS7 | Prior Outage of TOLK_TR 13.19kV/230kV/345kV transformer CKT 1. Apply 3-phase fault on CROSSROADS 7 to EDDY_CNTY 345kV line CKT 1, near CROSSROADS 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_418_P6_CROSSROADS7 | Prior Outage of TOLK_TR 13.19kV/230kV/345kV transformer CKT 1. Apply 3-phase fault on CROSSROADS 7 to EDDY_CNTY 345kV line CKT 1, near CROSSROADS 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.23pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_418_P6_CROSSROADS7 | Prior Outage of TOLK_TR 13.19kV/230kV/345kV transformer CKT 1. Apply 3-phase fault on CROSSROADS 7 to EDDY_CNTY 345kV line CKT 1, near CROSSROADS 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.23pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_419_P6_CROSSROADS7 | Prior Outage of OASIS to SN_JUAN_TAP6 230kV line CKT 1. Apply 3-phase fault on TOLK to CROSSROADS 7 345kV line CKT 1, near CROSSROADS 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_419_P6_CROSSROADS7 | Prior Outage of OASIS to SN_JUAN_TAP6 230kV line CKT 1. Apply 3-phase fault on TOLK to CROSSROADS 7 345kV line CKT 1, near CROSSROADS 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | No | Yes | Yes | No | No | LVRT VIOL - - ROOSWND-GEN2[2] ROOSWND-GEN1[1] G08-022-GEN3[1]. ROOSWND-GEN2[2], ROOSWND-GEN1[1], and G08-022-GEN3[1] tripped on voltage protection setting 1.20pu-0.08s (embedded in the user model). The protection setting was disabled and simulation was rerun. No further issues were observed.
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_419_P6_CROSSROADS7 | Prior Outage of OASIS to SN_JUAN_TAP6 230kV line CKT 1. Apply 3-phase fault on TOLK to CROSSROADS 7 345kV line CKT 1, near CROSSROADS 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_419_P6_CROSSROADS7 | Prior Outage of OASIS to SN_JUAN_TAP6 230kV line CKT 1. Apply 3-phase fault on TOLK to CROSSROADS 7 345kV line CKT 1, near CROSSROADS 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.39pu, MaxDur: 0.06s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_42_P1_NICHOLS | Apply 3-phase fault on GRAPEVINE to NICHOLS 230kV line CKT 1, near NICHOLS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_42_P1_NICHOLS | Apply 3-phase fault on GRAPEVINE to NICHOLS 230kV line CKT 1, near NICHOLS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_42_P1_NICHOLS | Apply 3-phase fault on GRAPEVINE to NICHOLS 230kV line CKT 1, near NICHOLS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_42_P1_NICHOLS | Apply 3-phase fault on GRAPEVINE to NICHOLS 230kV line CKT 1, near NICHOLS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_420_P6_EDDY_NORTH6 | Prior Outage of EDDY_NORTH 6 to CUNNIGHM_N 6 230kV line CKT 1. Apply 3-phase fault on EDDY_NORTH 6 to 7-RIVERS 230kV line CKT 1, near EDDY_NORTH 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_420_P6_EDDY_NORTH6 | Prior Outage of EDDY_NORTH 6 to CUNNIGHM_N 6 230kV line CKT 1. Apply 3-phase fault on EDDY_NORTH 6 to 7-RIVERS 230kV line CKT 1, near EDDY_NORTH 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_420_P6_EDDY_NORTH6 | Prior Outage of EDDY_NORTH 6 to CUNNIGHM_N 6 230kV line CKT 1. Apply 3-phase fault on EDDY_NORTH 6 to 7-RIVERS 230kV line CKT 1, near EDDY_NORTH 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_420_P6_EDDY_NORTH6 | Prior Outage of EDDY_NORTH 6 to CUNNIGHM_N 6 230kV line CKT 1. Apply 3-phase fault on EDDY_NORTH 6 to 7-RIVERS 230kV line CKT 1, near EDDY_NORTH 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_421_P6_CUNNIGHM_N6 | Prior Outage of CUNNIGHM_N 6 to POTASH_JCT 6 230kV line CKT 1. Apply 3-phase fault on EDDY_NORTH 6 to CUNNIGHM_N 6 230kV line CKT 1, near CUNNIGHM_N 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_421_P6_CUNNIGHM_N6 | Prior Outage of CUNNIGHM_N 6 to POTASH_JCT 6 230kV line CKT 1. Apply 3-phase fault on EDDY_NORTH 6 to CUNNIGHM_N 6 230kV line CKT 1, near CUNNIGHM_N 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_421_P6_CUNNIGHM_N6 | Prior Outage of CUNNIGHM_N 6 to POTASH_JCT 6 230kV line CKT 1. Apply 3-phase fault on EDDY_NORTH 6 to CUNNIGHM_N 6 230kV line CKT 1, near CUNNIGHM_N 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_421_P6_CUNNIGHM_N6 | Prior Outage of CUNNIGHM_N 6 to POTASH_JCT 6 230kV line CKT 1. Apply 3-phase fault on EDDY_NORTH 6 to CUNNIGHM_N 6 230kV line CKT 1, near CUNNIGHM_N 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.22pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_422_P6_HOBBS_INT | Prior Outage of HOBBS_INT to GAINESGENTP6 230kV line CKT 1. Apply 3-phase fault on HOBBS_INT 230kV/13.19kV/345kV transformer CKT 1, near HOBBS_INT 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_422_P6_HOBBS_INT | Prior Outage of HOBBS_INT to GAINESGENTP6 230kV line CKT 1. Apply 3-phase fault on HOBBS_INT 230kV/13.19kV/345kV transformer CKT 1, near HOBBS_INT 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | No | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_422_P6_HOBBS_INT | Prior Outage of HOBBS_INT to GAINESGENTP6 230kV line CKT 1. Apply 3-phase fault on HOBBS_INT 230kV/13.19kV/345kV transformer CKT 1, near HOBBS_INT 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_422_P6_HOBBS_INT | Prior Outage of HOBBS_INT to GAINESGENTP6 230kV line CKT 1. Apply 3-phase fault on HOBBS_INT 230kV/13.19kV/345kV transformer CKT 1, near HOBBS_INT 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | No | No | Yes | Voltage Spike: 1.23pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_423_P6_HOBBS_INT | Prior Outage of HOBBS_INT 230kV/13.19kV/345kV transformer CKT 1Prior Outage of CUNNIGHM_S 6 to HOBBS_INT 230kV line CKT 1. Apply 3-phase fault on HOBBS_INT to GAINESGENTP6 230kV line CKT 1, near HOBBS_INT 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_423_P6_HOBBS_INT | Prior Outage of HOBBS_INT 230kV/13.19kV/345kV transformer CKT 1Prior Outage of CUNNIGHM_S 6 to HOBBS_INT 230kV line CKT 1. Apply 3-phase fault on HOBBS_INT to GAINESGENTP6 230kV line CKT 1, near HOBBS_INT 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_423_P6_HOBBS_INT | Prior Outage of HOBBS_INT 230kV/13.19kV/345kV transformer CKT 1Prior Outage of CUNNIGHM_S 6 to HOBBS_INT 230kV line CKT 1. Apply 3-phase fault on HOBBS_INT to GAINESGENTP6 230kV line CKT 1, near HOBBS_INT 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_423_P6_HOBBS_INT | Prior Outage of HOBBS_INT 230kV/13.19kV/345kV transformer CKT 1Prior Outage of CUNNIGHM_S 6 to HOBBS_INT 230kV line CKT 1. Apply 3-phase fault on HOBBS_INT to GAINESGENTP6 230kV line CKT 1, near HOBBS_INT 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_424_P6_CRAWFISH765 | Prior Outage of CRAWFISH765 to CDSEMMID 765kV line CKT 1. Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV line CKT 2, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Unstable | No | No | No | No | Yes | No | Angular and system instability was observed in the G6 region. Simulation was rerun with the Crossroad SVC and different G6 dispatch options. No stability or damping issues were observed with the Crossroad SVC and G6 study generators dispatched at 30%. (min post-fault s.s voltage: 0.83pu) | ±600 MVAr SVC at Crossroad 765kV & G6 Study Generators Dispatched @ 30%
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_424_P6_CRAWFISH765 | Prior Outage of CRAWFISH765 to CDSEMMID 765kV line CKT 1. Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV line CKT 2, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Unstable | No | No | No | No | Yes | No | Angular and system instability was observed in the G6 region. Simulation was rerun with the Crossroad SVC and different G6 dispatch options. No stability or damping issues were observed with the Crossroad SVC and G6 study generators dispatched at 40%. (min post-fault s.s voltage: 0.85pu, Voltage Spike: 1.24pu, MaxDur: 0.03s) Note: The simulation result was stable for the option of SVC and Dispatch at 50%; However, very suppressed system voltages were observed and the study generation unit G17-065-GEN2[1] tripped due to undervoltage protection setting of 0.80pu-2.0sec. | ±600 MVAr SVC at Crossroad 765kV & G6 Study Generators Dispatched @ 40%
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_425_P6_CRAWFISH765 | Prior Outage of BORDER to CRAWFISH_DR 345kV line CKT 1. Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Unstable | No | No | No | No | Yes | No | Angular and system instability was observed in the G6 region. Simulation was rerun with the Crossroad SVC and different G6 dispatch options. No stability or damping issues were observed with the Crossroad SVC and G6 study generators dispatched at 90%. (TOV: 1.22pu, MaxDur: 0.67s) | ±600 MVAr SVC at Crossroad 765kV & G6 Study Generators Dispatched @ 90%
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_425_P6_CRAWFISH765 | Prior Outage of BORDER to CRAWFISH_DR 345kV line CKT 1. Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Unstable | No | No | No | No | Yes | No | Angular and system instability was observed in the G6 region. Simulation was rerun with the Crossroad SVC and different G6 dispatch options. No stability or damping issues were observed with the Crossroad SVC and G6 study generators dispatched at 60%. | ±600 MVAr SVC at Crossroad 765kV & G6 Study Generators Dispatched @ 60%
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_425_P6_CRAWFISH765 | Prior Outage of BORDER to CRAWFISH_DR 345kV line CKT 1. Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_425_P6_CRAWFISH765 | Prior Outage of BORDER to CRAWFISH_DR 345kV line CKT 1. Apply 3-phase fault on CRAWFISH765 to CDSEMMID 765kV line CKT 1, near CRAWFISH765 765kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_426_P6_TUCO_INT | Prior Outage of TUCO_INT to CRAWFISH_DR 345kV line CKT 1. Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV line CKT 2, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Unstable | No | No | No | No | Yes | No | Angular and system instability was observed in the G6 region. Simulation was rerun with the Crossroad SVC and different G6 dispatch options. No stability or damping issues were observed with the Crossroad SVC and G6 study generators dispatched at 70%. (TOV: 1.25pu, MaxDur: 1.59s, min post-fault s.s voltage: 0.88pu) | ±600 MVAr SVC at Crossroad 765kV & G6 Study Generators Dispatched @ 70%
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_426_P6_TUCO_INT | Prior Outage of TUCO_INT to CRAWFISH_DR 345kV line CKT 1. Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV line CKT 2, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Unstable | No | No | No | No | Yes | No | Angular and system instability was observed in the G6 region. Simulation was rerun with the Crossroad SVC and different G6 dispatch options. No stability or damping issues were observed with the Crossroad SVC and G6 study generators dispatched at 40%. (TOV: 1.23pu, MaxDur: 0.92s, min post-fault s.s voltage: 0.89pu) | ±600 MVAr SVC at Crossroad 765kV & G6 Study Generators Dispatched @ 40%
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_426_P6_TUCO_INT | Prior Outage of TUCO_INT to CRAWFISH_DR 345kV line CKT 1. Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV line CKT 2, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Unstable | No | No | No | No | Yes | No | Angular and system instability was observed in the G6 region. The stability issue was resolved with the SVC mitigation solution. (TOV: 1.22pu, MaxDur: 0.23s, min post-fault s.s voltage: 0.89pu) | ±600 MVAr SVC at Crossroad 765kV
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_426_P6_TUCO_INT | Prior Outage of TUCO_INT to CRAWFISH_DR 345kV line CKT 1. Apply 3-phase fault on TUCO_INT to CRAWFISH_DR 345kV line CKT 2, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | No | No | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_427_P6_CROSSRDS765 | Prior Outage of CROSSROADS 7 to TOLK 345kV line CKT 1. Apply 3-phase fault on CROSSRDS765 to CRAWFISH765 765kV line CKT 1, near CROSSRDS765 765kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes | Undamped oscillations were observed in renewable units voltage and power responses. Simulation was rerun with the Crossroad SVC and different G6 dispatch options. The damping issue was resolved with the Crossroad SVC and G6 study generators dispatched at 90%. (Voltage Spike: 0.29pu, MaxDur: 0.05s) | ±600 MVAr SVC at Crossroad 765kV & G6 Study Generators Dispatched @ 90%
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_427_P6_CROSSRDS765 | Prior Outage of CROSSROADS 7 to TOLK 345kV line CKT 1. Apply 3-phase fault on CROSSRDS765 to CRAWFISH765 765kV line CKT 1, near CROSSRDS765 765kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Unstable | No | No | No | No | Yes | No | Angular and system instability was observed in the G6 region. Simulation was rerun with the Crossroad SVC and different G6 dispatch options. No stability or damping issues were observed with the Crossroad SVC and G6 study generators dispatched at 70%. | ±600 MVAr SVC at Crossroad 765kV & G6 Study Generators Dispatched @ 70%
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_427_P6_CROSSRDS765 | Prior Outage of CROSSROADS 7 to TOLK 345kV line CKT 1. Apply 3-phase fault on CROSSRDS765 to CRAWFISH765 765kV line CKT 1, near CROSSRDS765 765kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes | Undamped oscillations were observed in renewable units voltage and power responses. Simulation was rerun with the Crossroad SVC and different G6 dispatch options. The damping issue was resolved with the Crossroad SVC. | ±600 MVAr SVC at Crossroad 765kV
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_427_P6_CROSSRDS765 | Prior Outage of CROSSROADS 7 to TOLK 345kV line CKT 1. Apply 3-phase fault on CROSSRDS765 to CRAWFISH765 765kV line CKT 1, near CROSSRDS765 765kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes | Undamped oscillations were observed in renewable units voltage and power responses. Simulation was rerun with the Crossroad SVC and different G6 dispatch options. The damping issue was resolved with the Crossroad SVC. | ±600 MVAr SVC at Crossroad 765kV
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_428_P6_TUCO_INT | Prior Outage of CROSSRDS765 to CRAWFISH765 765kV line CKT 1. Apply 3-phase fault on TUCO_INT to YOAKUM_345 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | [7 empty] | Non-Convergence issue: The power flow case could not be solved under N-1 condition (prior outage of CROSSRDS765 to CRAWFISH765 765kV line CKT 1). Addition of the SVC mitigation option at Crossroad765 bus could not help. However, when the G6 study generators were scaled down to 90% power flow solution could be achieved for the N-1 condition. Angular and system instability was observed in the G6 region for the SVC+90% case. Simulation was rerun with the SVC and lower G6 dispatch options. No stability or damping issues were observed with the SVC and G6 study generators dispatched at 40%.(TOV: 1.24pu, MaxDur: 0.81s) | ±600 MVAr SVC at Crossroad 765kV & G6 Study Generators Dispatched @ 40%
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_428_P6_TUCO_INT | Prior Outage of CROSSRDS765 to CRAWFISH765 765kV line CKT 1. Apply 3-phase fault on TUCO_INT to YOAKUM_345 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Unstable | No | No | No | No | Yes | No | Angular and system instability was observed in the G6 region. Simulation was rerun with the Crossroad SVC and different G6 dispatch options. No stability or damping issues were observed with the Crossroad SVC and G6 study generators dispatched at 70%. (TOV: 1.28pu, MaxDur: 0.90s) | ±600 MVAr SVC at Crossroad 765kV & G6 Study Generators Dispatched @ 70%
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_428_P6_TUCO_INT | Prior Outage of CROSSRDS765 to CRAWFISH765 765kV line CKT 1. Apply 3-phase fault on TUCO_INT to YOAKUM_345 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Unstable | No | No | No | No | Yes | No | Angular and system instability was observed in the G6 region. Simulation was rerun with the Crossroad SVC and different G6 dispatch options. No stability or damping issues were observed with the Crossroad SVC and G6 study generators dispatched at 80%. (TOV: 1.23pu, MaxDur: 0.34s) | ±600 MVAr SVC at Crossroad 765kV & G6 Study Generators Dispatched @ 80%
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_428_P6_TUCO_INT | Prior Outage of CROSSRDS765 to CRAWFISH765 765kV line CKT 1. Apply 3-phase fault on TUCO_INT to YOAKUM_345 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | No | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_429_P6_EDDY_CNTY | Prior Outage of CROSSRDS765 to CRAWFISH765 765kV line CKT 1. Apply 3-phase fault on EDDY_CNTY to KIOWA 345kV line CKT 1, near EDDY_CNTY 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | [7 empty] | Non-Convergence issue: The power flow case could not be solved under N-1 condition (prior outage of CROSSRDS765 to CRAWFISH765 765kV line CKT 1). Addition of the SVC mitigation option at Crossroad765 bus could not help. However, when the G6 study generators were scaled down to 90% power flow solution could be achieved for the N-1 condition. Angular and system instability was observed in the G6 region for the SVC+90% case. Simulation was rerun with the SVC and lower G6 dispatch options. No stability or damping issues were observed with the SVC and G6 study generators dispatched at 80%.(Voltage Spike: 1.28pu, MaxDur: 0.02s) | ±600 MVAr SVC at Crossroad 765kV & G6 Study Generators Dispatched @ 80%
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_429_P6_EDDY_CNTY | Prior Outage of CROSSRDS765 to CRAWFISH765 765kV line CKT 1. Apply 3-phase fault on EDDY_CNTY to KIOWA 345kV line CKT 1, near EDDY_CNTY 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | No | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_429_P6_EDDY_CNTY | Prior Outage of CROSSRDS765 to CRAWFISH765 765kV line CKT 1. Apply 3-phase fault on EDDY_CNTY to KIOWA 345kV line CKT 1, near EDDY_CNTY 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | No | No | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_429_P6_EDDY_CNTY | Prior Outage of CROSSRDS765 to CRAWFISH765 765kV line CKT 1. Apply 3-phase fault on EDDY_CNTY to KIOWA 345kV line CKT 1, near EDDY_CNTY 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P6 | Stable | Yes | Yes | No | Yes | No | Yes | Voltage Spike: 1.23pu, MaxDur: 0.07s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_43_P1_BUSHLAND | Apply 3-phase fault on BUSHLAND to DEAFSMITH 230kV line CKT 1, near BUSHLAND 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_43_P1_BUSHLAND | Apply 3-phase fault on BUSHLAND to DEAFSMITH 230kV line CKT 1, near BUSHLAND 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_43_P1_BUSHLAND | Apply 3-phase fault on BUSHLAND to DEAFSMITH 230kV line CKT 1, near BUSHLAND 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_43_P1_BUSHLAND | Apply 3-phase fault on BUSHLAND to DEAFSMITH 230kV line CKT 1, near BUSHLAND 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_44_P1_BUSHLAND | Apply 3-phase fault on BSHLND_TR1 1 13.19kV/115kV/230kV transformer CKT 1, near BUSHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_44_P1_BUSHLAND | Apply 3-phase fault on BSHLND_TR1 1 13.19kV/115kV/230kV transformer CKT 1, near BUSHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_44_P1_BUSHLAND | Apply 3-phase fault on BSHLND_TR1 1 13.19kV/115kV/230kV transformer CKT 1, near BUSHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_44_P1_BUSHLAND | Apply 3-phase fault on BSHLND_TR1 1 13.19kV/115kV/230kV transformer CKT 1, near BUSHLAND 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_45_P1_RANDALL | Apply 3-phase fault on MANHATTAN to RANDALL 115kV line CKT 1, near RANDALL 115kV for 7 cycles. Open the faulted line and EAST_PLANT 3 to MANHATTAN 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and EAST_PLANT 3 to MANHATTAN 115kV line CKT 1. Re-open the faulted line after 7 cycles% EAST_PLANT 3 to MANHATTAN 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_45_P1_RANDALL | Apply 3-phase fault on MANHATTAN to RANDALL 115kV line CKT 1, near RANDALL 115kV for 7 cycles. Open the faulted line and EAST_PLANT 3 to MANHATTAN 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and EAST_PLANT 3 to MANHATTAN 115kV line CKT 1. Re-open the faulted line after 7 cycles% EAST_PLANT 3 to MANHATTAN 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_45_P1_RANDALL | Apply 3-phase fault on MANHATTAN to RANDALL 115kV line CKT 1, near RANDALL 115kV for 7 cycles. Open the faulted line and EAST_PLANT 3 to MANHATTAN 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and EAST_PLANT 3 to MANHATTAN 115kV line CKT 1. Re-open the faulted line after 7 cycles% EAST_PLANT 3 to MANHATTAN 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_45_P1_RANDALL | Apply 3-phase fault on MANHATTAN to RANDALL 115kV line CKT 1, near RANDALL 115kV for 7 cycles. Open the faulted line and EAST_PLANT 3 to MANHATTAN 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and EAST_PLANT 3 to MANHATTAN 115kV line CKT 1. Re-open the faulted line after 7 cycles% EAST_PLANT 3 to MANHATTAN 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_46_P1_RANDALL | Apply 3-phase fault on GEORGIA to RANDALL 115kV line CKT 1, near RANDALL 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_46_P1_RANDALL | Apply 3-phase fault on GEORGIA to RANDALL 115kV line CKT 1, near RANDALL 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_46_P1_RANDALL | Apply 3-phase fault on GEORGIA to RANDALL 115kV line CKT 1, near RANDALL 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_46_P1_RANDALL | Apply 3-phase fault on GEORGIA to RANDALL 115kV line CKT 1, near RANDALL 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_47_P1_RANDALL | Apply 3-phase fault on RANDALL to CANYON_E_TP3 115kV line CKT 1, near RANDALL 115kV for 7 cycles. Open the faulted line and DS-#25+ to DEAFSMITH 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and DS-#25+ to DEAFSMITH 115kV line CKT 1. Re-open the faulted line after 7 cycles% DS-#25+ to DEAFSMITH 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_47_P1_RANDALL | Apply 3-phase fault on RANDALL to CANYON_E_TP3 115kV line CKT 1, near RANDALL 115kV for 7 cycles. Open the faulted line and DS-#25+ to DEAFSMITH 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and DS-#25+ to DEAFSMITH 115kV line CKT 1. Re-open the faulted line after 7 cycles% DS-#25+ to DEAFSMITH 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_47_P1_RANDALL | Apply 3-phase fault on RANDALL to CANYON_E_TP3 115kV line CKT 1, near RANDALL 115kV for 7 cycles. Open the faulted line and DS-#25+ to DEAFSMITH 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and DS-#25+ to DEAFSMITH 115kV line CKT 1. Re-open the faulted line after 7 cycles% DS-#25+ to DEAFSMITH 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_47_P1_RANDALL | Apply 3-phase fault on RANDALL to CANYON_E_TP3 115kV line CKT 1, near RANDALL 115kV for 7 cycles. Open the faulted line and DS-#25+ to DEAFSMITH 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and DS-#25+ to DEAFSMITH 115kV line CKT 1. Re-open the faulted line after 7 cycles% DS-#25+ to DEAFSMITH 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_48_P1_AMA_SOUTH | Apply 3-phase fault on AMA_SO_TR1 1 13.19kV/115kV/230kV transformer CKT 1, near AMA_SOUTH 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_48_P1_AMA_SOUTH | Apply 3-phase fault on AMA_SO_TR1 1 13.19kV/115kV/230kV transformer CKT 1, near AMA_SOUTH 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_48_P1_AMA_SOUTH | Apply 3-phase fault on AMA_SO_TR1 1 13.19kV/115kV/230kV transformer CKT 1, near AMA_SOUTH 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_48_P1_AMA_SOUTH | Apply 3-phase fault on AMA_SO_TR1 1 13.19kV/115kV/230kV transformer CKT 1, near AMA_SOUTH 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_49_P1_AMA_SOUTH | Apply 3-phase fault on NICHOLS to AMA_SOUTH 230kV line CKT 1, near AMA_SOUTH 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_49_P1_AMA_SOUTH | Apply 3-phase fault on NICHOLS to AMA_SOUTH 230kV line CKT 1, near AMA_SOUTH 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_49_P1_AMA_SOUTH | Apply 3-phase fault on NICHOLS to AMA_SOUTH 230kV line CKT 1, near AMA_SOUTH 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_49_P1_AMA_SOUTH | Apply 3-phase fault on NICHOLS to AMA_SOUTH 230kV line CKT 1, near AMA_SOUTH 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_5_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_5_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_5_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_5_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_50_P1_AMA_SOUTH | Apply 3-phase fault on RANDALL to AMA_SOUTH 230kV line CKT 1, near AMA_SOUTH 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_50_P1_AMA_SOUTH | Apply 3-phase fault on RANDALL to AMA_SOUTH 230kV line CKT 1, near AMA_SOUTH 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_50_P1_AMA_SOUTH | Apply 3-phase fault on RANDALL to AMA_SOUTH 230kV line CKT 1, near AMA_SOUTH 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_50_P1_AMA_SOUTH | Apply 3-phase fault on RANDALL to AMA_SOUTH 230kV line CKT 1, near AMA_SOUTH 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_51_P1_PALO_DURO | Apply 3-phase fault on RANDALL to PALO_DURO 115kV line CKT 1, near PALO_DURO 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_51_P1_PALO_DURO | Apply 3-phase fault on RANDALL to PALO_DURO 115kV line CKT 1, near PALO_DURO 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_51_P1_PALO_DURO | Apply 3-phase fault on RANDALL to PALO_DURO 115kV line CKT 1, near PALO_DURO 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_51_P1_PALO_DURO | Apply 3-phase fault on RANDALL to PALO_DURO 115kV line CKT 1, near PALO_DURO 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_52_P1_NE_HEREFORD3 | Apply 3-phase fault on NE_HEREFORD3 to HEREFORD 115kV line CKT 1, near NE_HEREFORD3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-058-GEN1[1]. G17-058-GEN1[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s (Similar to the BC). The protection setting was disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_52_P1_NE_HEREFORD3 | Apply 3-phase fault on NE_HEREFORD3 to HEREFORD 115kV line CKT 1, near NE_HEREFORD3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_52_P1_NE_HEREFORD3 | Apply 3-phase fault on NE_HEREFORD3 to HEREFORD 115kV line CKT 1, near NE_HEREFORD3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-058-GEN1[1]. G17-058-GEN1[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s (Similar to the BC). The protection setting was disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_52_P1_NE_HEREFORD3 | Apply 3-phase fault on NE_HEREFORD3 to HEREFORD 115kV line CKT 1, near NE_HEREFORD3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-058-GEN1[1]. G17-058-GEN1[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s (Similar to the BC). The protection setting was disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_53_P1_NE_HEREFORD3 | Apply 3-phase fault on NE_HEREFORD3 to DEAFSMITH 115kV line CKT 1, near NE_HEREFORD3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-058-GEN1[1]. G17-058-GEN1[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s (Similar to the BC). The protection setting was disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_53_P1_NE_HEREFORD3 | Apply 3-phase fault on NE_HEREFORD3 to DEAFSMITH 115kV line CKT 1, near NE_HEREFORD3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_53_P1_NE_HEREFORD3 | Apply 3-phase fault on NE_HEREFORD3 to DEAFSMITH 115kV line CKT 1, near NE_HEREFORD3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-058-GEN1[1]. G17-058-GEN1[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s (Similar to the BC). The protection setting was disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_53_P1_NE_HEREFORD3 | Apply 3-phase fault on NE_HEREFORD3 to DEAFSMITH 115kV line CKT 1, near NE_HEREFORD3 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-058-GEN1[1]. G17-058-GEN1[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s (Similar to the BC). The protection setting was disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_54_P1_HEREFORD | Apply 3-phase fault on HEREFORD to DS-#6 115kV line CKT 1, near HEREFORD 115kV for 7 cycles. Open the faulted line and DS-#20 to CURRY 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and DS-#20 to CURRY 115kV line CKT 1. Re-open the faulted line after 7 cycles% DS-#20 to CURRY 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_54_P1_HEREFORD | Apply 3-phase fault on HEREFORD to DS-#6 115kV line CKT 1, near HEREFORD 115kV for 7 cycles. Open the faulted line and DS-#20 to CURRY 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and DS-#20 to CURRY 115kV line CKT 1. Re-open the faulted line after 7 cycles% DS-#20 to CURRY 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_54_P1_HEREFORD | Apply 3-phase fault on HEREFORD to DS-#6 115kV line CKT 1, near HEREFORD 115kV for 7 cycles. Open the faulted line and DS-#20 to CURRY 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and DS-#20 to CURRY 115kV line CKT 1. Re-open the faulted line after 7 cycles% DS-#20 to CURRY 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_54_P1_HEREFORD | Apply 3-phase fault on HEREFORD to DS-#6 115kV line CKT 1, near HEREFORD 115kV for 7 cycles. Open the faulted line and DS-#20 to CURRY 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and DS-#20 to CURRY 115kV line CKT 1. Re-open the faulted line after 7 cycles% DS-#20 to CURRY 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_55_P1_DEAFSMITH | Apply 3-phase fault on DS-#25+ to DEAFSMITH 115kV line CKT 1, near DEAFSMITH 115kV for 7 cycles. Open the faulted line and RANDALL to CANYON_E_TP3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and RANDALL to CANYON_E_TP3 115kV line CKT 1. Re-open the faulted line after 7 cycles% RANDALL to CANYON_E_TP3 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-058-GEN1[1]. G17-058-GEN1[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s (Similar to the BC). The protection setting was disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_55_P1_DEAFSMITH | Apply 3-phase fault on DS-#25+ to DEAFSMITH 115kV line CKT 1, near DEAFSMITH 115kV for 7 cycles. Open the faulted line and RANDALL to CANYON_E_TP3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and RANDALL to CANYON_E_TP3 115kV line CKT 1. Re-open the faulted line after 7 cycles% RANDALL to CANYON_E_TP3 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_55_P1_DEAFSMITH | Apply 3-phase fault on DS-#25+ to DEAFSMITH 115kV line CKT 1, near DEAFSMITH 115kV for 7 cycles. Open the faulted line and RANDALL to CANYON_E_TP3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and RANDALL to CANYON_E_TP3 115kV line CKT 1. Re-open the faulted line after 7 cycles% RANDALL to CANYON_E_TP3 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-058-GEN1[1]. G17-058-GEN1[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s (Similar to the BC). The protection setting was disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_55_P1_DEAFSMITH | Apply 3-phase fault on DS-#25+ to DEAFSMITH 115kV line CKT 1, near DEAFSMITH 115kV for 7 cycles. Open the faulted line and RANDALL to CANYON_E_TP3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and RANDALL to CANYON_E_TP3 115kV line CKT 1. Re-open the faulted line after 7 cycles% RANDALL to CANYON_E_TP3 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-058-GEN1[1]. G17-058-GEN1[1] tripped on frequency protection setting 57.0/63.5Hz-0.001s (Similar to the BC). The protection setting was disabled and simulation was rerun. No further issues were observed. Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_56_P1_DEAFSMITH | Apply 3-phase fault on DEAFSMITH to PLANT_X 230kV line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_56_P1_DEAFSMITH | Apply 3-phase fault on DEAFSMITH to PLANT_X 230kV line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_56_P1_DEAFSMITH | Apply 3-phase fault on DEAFSMITH to PLANT_X 230kV line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_56_P1_DEAFSMITH | Apply 3-phase fault on DEAFSMITH to PLANT_X 230kV line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.22pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_57_P1_DEAFSMITH | Apply 3-phase fault on BUSHLAND to DEAFSMITH 230kV line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_57_P1_DEAFSMITH | Apply 3-phase fault on BUSHLAND to DEAFSMITH 230kV line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_57_P1_DEAFSMITH | Apply 3-phase fault on BUSHLAND to DEAFSMITH 230kV line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_57_P1_DEAFSMITH | Apply 3-phase fault on BUSHLAND to DEAFSMITH 230kV line CKT 1, near DEAFSMITH 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.22pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_58_P1_CASTRO_CNTY3 | Apply 3-phase fault on CASTRO_CNTY3 to BC-KELLEY +3 115kV line CKT 1, near CASTRO_CNTY3 115kV for 7 cycles. Open the faulted line and BC-EARTH to PLANT_X 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BC-EARTH to PLANT_X 115kV line CKT 1. Re-open the faulted line after 7 cycles% BC-EARTH to PLANT_X 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_58_P1_CASTRO_CNTY3 | Apply 3-phase fault on CASTRO_CNTY3 to BC-KELLEY +3 115kV line CKT 1, near CASTRO_CNTY3 115kV for 7 cycles. Open the faulted line and BC-EARTH to PLANT_X 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BC-EARTH to PLANT_X 115kV line CKT 1. Re-open the faulted line after 7 cycles% BC-EARTH to PLANT_X 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_58_P1_CASTRO_CNTY3 | Apply 3-phase fault on CASTRO_CNTY3 to BC-KELLEY +3 115kV line CKT 1, near CASTRO_CNTY3 115kV for 7 cycles. Open the faulted line and BC-EARTH to PLANT_X 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BC-EARTH to PLANT_X 115kV line CKT 1. Re-open the faulted line after 7 cycles% BC-EARTH to PLANT_X 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_58_P1_CASTRO_CNTY3 | Apply 3-phase fault on CASTRO_CNTY3 to BC-KELLEY +3 115kV line CKT 1, near CASTRO_CNTY3 115kV for 7 cycles. Open the faulted line and BC-EARTH to PLANT_X 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BC-EARTH to PLANT_X 115kV line CKT 1. Re-open the faulted line after 7 cycles% BC-EARTH to PLANT_X 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_59_P1_CASTRO_CNTY3 | Apply 3-phase fault on DS-#21 to CASTRO_CNTY3 115kV line CKT 1, near CASTRO_CNTY3 115kV for 7 cycles. Open the faulted line and DEAFSMITH to DS-#21 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and DEAFSMITH to DS-#21 115kV line CKT 1. Re-open the faulted line after 7 cycles% DEAFSMITH to DS-#21 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_59_P1_CASTRO_CNTY3 | Apply 3-phase fault on DS-#21 to CASTRO_CNTY3 115kV line CKT 1, near CASTRO_CNTY3 115kV for 7 cycles. Open the faulted line and DEAFSMITH to DS-#21 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and DEAFSMITH to DS-#21 115kV line CKT 1. Re-open the faulted line after 7 cycles% DEAFSMITH to DS-#21 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_59_P1_CASTRO_CNTY3 | Apply 3-phase fault on DS-#21 to CASTRO_CNTY3 115kV line CKT 1, near CASTRO_CNTY3 115kV for 7 cycles. Open the faulted line and DEAFSMITH to DS-#21 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and DEAFSMITH to DS-#21 115kV line CKT 1. Re-open the faulted line after 7 cycles% DEAFSMITH to DS-#21 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_59_P1_CASTRO_CNTY3 | Apply 3-phase fault on DS-#21 to CASTRO_CNTY3 115kV line CKT 1, near CASTRO_CNTY3 115kV for 7 cycles. Open the faulted line and DEAFSMITH to DS-#21 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and DEAFSMITH to DS-#21 115kV line CKT 1. Re-open the faulted line after 7 cycles% DEAFSMITH to DS-#21 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_6_P1_LES-7 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.25pu, MaxDur: 0.00s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_6_P1_LES-7 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_6_P1_LES-7 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.24pu, MaxDur: 0.00s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_6_P1_LES-7 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.22pu, MaxDur: 0.00s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_60_P1_PLSNT_HILL3 | Apply 3-phase fault on PLSNHIL_TR11 13.19kV/115kV/230kV transformer CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_60_P1_PLSNT_HILL3 | Apply 3-phase fault on PLSNHIL_TR11 13.19kV/115kV/230kV transformer CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_60_P1_PLSNT_HILL3 | Apply 3-phase fault on PLSNHIL_TR11 13.19kV/115kV/230kV transformer CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_60_P1_PLSNT_HILL3 | Apply 3-phase fault on PLSNHIL_TR11 13.19kV/115kV/230kV transformer CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_61_P1_PLSNT_HILL3 | Apply 3-phase fault on PLSNT_HILL 3 to E_CLOVIS 115kV line CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Open the faulted line and E_CLOVIS to CURRY 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and E_CLOVIS to CURRY 115kV line CKT 1. Re-open the faulted line after 7 cycles% E_CLOVIS to CURRY 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_61_P1_PLSNT_HILL3 | Apply 3-phase fault on PLSNT_HILL 3 to E_CLOVIS 115kV line CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Open the faulted line and E_CLOVIS to CURRY 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and E_CLOVIS to CURRY 115kV line CKT 1. Re-open the faulted line after 7 cycles% E_CLOVIS to CURRY 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_61_P1_PLSNT_HILL3 | Apply 3-phase fault on PLSNT_HILL 3 to E_CLOVIS 115kV line CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Open the faulted line and E_CLOVIS to CURRY 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and E_CLOVIS to CURRY 115kV line CKT 1. Re-open the faulted line after 7 cycles% E_CLOVIS to CURRY 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_61_P1_PLSNT_HILL3 | Apply 3-phase fault on PLSNT_HILL 3 to E_CLOVIS 115kV line CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Open the faulted line and E_CLOVIS to CURRY 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and E_CLOVIS to CURRY 115kV line CKT 1. Re-open the faulted line after 7 cycles% E_CLOVIS to CURRY 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_62_P1_PLSNT_HILL3 | Apply 3-phase fault on PLSNT_HILL 3 to FE-HOLLAND 3 115kV line CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Open the faulted line and CURRY to FE-CLOVIS2+3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and CURRY to FE-CLOVIS2+3 115kV line CKT 1. Re-open the faulted line after 7 cycles% CURRY to FE-CLOVIS2+3 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_62_P1_PLSNT_HILL3 | Apply 3-phase fault on PLSNT_HILL 3 to FE-HOLLAND 3 115kV line CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Open the faulted line and CURRY to FE-CLOVIS2+3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and CURRY to FE-CLOVIS2+3 115kV line CKT 1. Re-open the faulted line after 7 cycles% CURRY to FE-CLOVIS2+3 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_62_P1_PLSNT_HILL3 | Apply 3-phase fault on PLSNT_HILL 3 to FE-HOLLAND 3 115kV line CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Open the faulted line and CURRY to FE-CLOVIS2+3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and CURRY to FE-CLOVIS2+3 115kV line CKT 1. Re-open the faulted line after 7 cycles% CURRY to FE-CLOVIS2+3 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_62_P1_PLSNT_HILL3 | Apply 3-phase fault on PLSNT_HILL 3 to FE-HOLLAND 3 115kV line CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Open the faulted line and CURRY to FE-CLOVIS2+3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and CURRY to FE-CLOVIS2+3 115kV line CKT 1. Re-open the faulted line after 7 cycles% CURRY to FE-CLOVIS2+3 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_63_P1_PLSNT_HILL3 | Apply 3-phase fault on PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Open the faulted line and N_CLOVIS_TP3 to FE-CLVS_INT3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and N_CLOVIS_TP3 to FE-CLVS_INT3 115kV line CKT 1. Re-open the faulted line after 7 cycles% N_CLOVIS_TP3 to FE-CLVS_INT3 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_63_P1_PLSNT_HILL3 | Apply 3-phase fault on PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Open the faulted line and N_CLOVIS_TP3 to FE-CLVS_INT3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and N_CLOVIS_TP3 to FE-CLVS_INT3 115kV line CKT 1. Re-open the faulted line after 7 cycles% N_CLOVIS_TP3 to FE-CLVS_INT3 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_63_P1_PLSNT_HILL3 | Apply 3-phase fault on PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Open the faulted line and N_CLOVIS_TP3 to FE-CLVS_INT3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and N_CLOVIS_TP3 to FE-CLVS_INT3 115kV line CKT 1. Re-open the faulted line after 7 cycles% N_CLOVIS_TP3 to FE-CLVS_INT3 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_63_P1_PLSNT_HILL3 | Apply 3-phase fault on PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1, near PLSNT_HILL 3 115kV for 7 cycles. Open the faulted line and N_CLOVIS_TP3 to FE-CLVS_INT3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and N_CLOVIS_TP3 to FE-CLVS_INT3 115kV line CKT 1. Re-open the faulted line after 7 cycles% N_CLOVIS_TP3 to FE-CLVS_INT3 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_64_P1_PLSNT_HILL6 | Apply 3-phase fault on PLSNT_HILL 6 to ROSEVELT_N 6 230kV line CKT 1, near PLSNT_HILL 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_64_P1_PLSNT_HILL6 | Apply 3-phase fault on PLSNT_HILL 6 to ROSEVELT_N 6 230kV line CKT 1, near PLSNT_HILL 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_64_P1_PLSNT_HILL6 | Apply 3-phase fault on PLSNT_HILL 6 to ROSEVELT_N 6 230kV line CKT 1, near PLSNT_HILL 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_64_P1_PLSNT_HILL6 | Apply 3-phase fault on PLSNT_HILL 6 to ROSEVELT_N 6 230kV line CKT 1, near PLSNT_HILL 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_65_P1_PLSNT_HILL6 | Apply 3-phase fault on PLSNT_HILL 6 to OASIS 230kV line CKT 1, near PLSNT_HILL 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_65_P1_PLSNT_HILL6 | Apply 3-phase fault on PLSNT_HILL 6 to OASIS 230kV line CKT 1, near PLSNT_HILL 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_65_P1_PLSNT_HILL6 | Apply 3-phase fault on PLSNT_HILL 6 to OASIS 230kV line CKT 1, near PLSNT_HILL 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_65_P1_PLSNT_HILL6 | Apply 3-phase fault on PLSNT_HILL 6 to OASIS 230kV line CKT 1, near PLSNT_HILL 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_66_P1_FE-CLVS_INT3 | Apply 3-phase fault on W_CLOVIS to FE-CLVS_INT3 115kV line CKT 1, near FE-CLVS_INT3 115kV for 7 cycles. Open the faulted line and PERIMETER to OASIS 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and PERIMETER to OASIS 115kV line CKT 1. Re-open the faulted line after 7 cycles% PERIMETER to OASIS 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_66_P1_FE-CLVS_INT3 | Apply 3-phase fault on W_CLOVIS to FE-CLVS_INT3 115kV line CKT 1, near FE-CLVS_INT3 115kV for 7 cycles. Open the faulted line and PERIMETER to OASIS 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and PERIMETER to OASIS 115kV line CKT 1. Re-open the faulted line after 7 cycles% PERIMETER to OASIS 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_66_P1_FE-CLVS_INT3 | Apply 3-phase fault on W_CLOVIS to FE-CLVS_INT3 115kV line CKT 1, near FE-CLVS_INT3 115kV for 7 cycles. Open the faulted line and PERIMETER to OASIS 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and PERIMETER to OASIS 115kV line CKT 1. Re-open the faulted line after 7 cycles% PERIMETER to OASIS 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_66_P1_FE-CLVS_INT3 | Apply 3-phase fault on W_CLOVIS to FE-CLVS_INT3 115kV line CKT 1, near FE-CLVS_INT3 115kV for 7 cycles. Open the faulted line and PERIMETER to OASIS 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and PERIMETER to OASIS 115kV line CKT 1. Re-open the faulted line after 7 cycles% PERIMETER to OASIS 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_67_P1_FE-CLVS_INT3 | Apply 3-phase fault on N_CLOVIS_TP3 to FE-CLVS_INT3 115kV line CKT 1, near FE-CLVS_INT3 115kV for 7 cycles. Open the faulted line and PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1. Re-open the faulted line after 7 cycles% PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_67_P1_FE-CLVS_INT3 | Apply 3-phase fault on N_CLOVIS_TP3 to FE-CLVS_INT3 115kV line CKT 1, near FE-CLVS_INT3 115kV for 7 cycles. Open the faulted line and PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1. Re-open the faulted line after 7 cycles% PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_67_P1_FE-CLVS_INT3 | Apply 3-phase fault on N_CLOVIS_TP3 to FE-CLVS_INT3 115kV line CKT 1, near FE-CLVS_INT3 115kV for 7 cycles. Open the faulted line and PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1. Re-open the faulted line after 7 cycles% PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_67_P1_FE-CLVS_INT3 | Apply 3-phase fault on N_CLOVIS_TP3 to FE-CLVS_INT3 115kV line CKT 1, near FE-CLVS_INT3 115kV for 7 cycles. Open the faulted line and PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1. Re-open the faulted line after 7 cycles% PLSNT_HILL 3 to N_CLOVIS_TP3 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_68_P1_CURRY | Apply 3-phase fault on DS-#20 to CURRY 115kV line CKT 1, near CURRY 115kV for 7 cycles. Open the faulted line and HEREFORD to DS-#6 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and HEREFORD to DS-#6 115kV line CKT 1. Re-open the faulted line after 7 cycles% HEREFORD to DS-#6 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_68_P1_CURRY | Apply 3-phase fault on DS-#20 to CURRY 115kV line CKT 1, near CURRY 115kV for 7 cycles. Open the faulted line and HEREFORD to DS-#6 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and HEREFORD to DS-#6 115kV line CKT 1. Re-open the faulted line after 7 cycles% HEREFORD to DS-#6 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_68_P1_CURRY | Apply 3-phase fault on DS-#20 to CURRY 115kV line CKT 1, near CURRY 115kV for 7 cycles. Open the faulted line and HEREFORD to DS-#6 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and HEREFORD to DS-#6 115kV line CKT 1. Re-open the faulted line after 7 cycles% HEREFORD to DS-#6 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_68_P1_CURRY | Apply 3-phase fault on DS-#20 to CURRY 115kV line CKT 1, near CURRY 115kV for 7 cycles. Open the faulted line and HEREFORD to DS-#6 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and HEREFORD to DS-#6 115kV line CKT 1. Re-open the faulted line after 7 cycles% HEREFORD to DS-#6 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_69_P1_CURRY | Apply 3-phase fault on CURRY to BAILEYCO 115kV line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_69_P1_CURRY | Apply 3-phase fault on CURRY to BAILEYCO 115kV line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_69_P1_CURRY | Apply 3-phase fault on CURRY to BAILEYCO 115kV line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_69_P1_CURRY | Apply 3-phase fault on CURRY to BAILEYCO 115kV line CKT 1, near CURRY 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_7_P1_TERRYRD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_7_P1_TERRYRD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_7_P1_TERRYRD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_7_P1_TERRYRD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_70_P1_OASIS | Apply 3-phase fault on OASIS_TR1 13.19kV/115kV/230kV transformer CKT 1, near OASIS 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_70_P1_OASIS | Apply 3-phase fault on OASIS_TR1 13.19kV/115kV/230kV transformer CKT 1, near OASIS 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_70_P1_OASIS | Apply 3-phase fault on OASIS_TR1 13.19kV/115kV/230kV transformer CKT 1, near OASIS 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_70_P1_OASIS | Apply 3-phase fault on OASIS_TR1 13.19kV/115kV/230kV transformer CKT 1, near OASIS 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_71_P1_OASIS | Apply 3-phase fault on FE-CHZPLT to OASIS 115kV line CKT 1, near OASIS 115kV for 7 cycles. Open the faulted line and NORRIS_TP to CURRY 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NORRIS_TP to CURRY 115kV line CKT 1. Re-open the faulted line after 7 cycles% NORRIS_TP to CURRY 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_71_P1_OASIS | Apply 3-phase fault on FE-CHZPLT to OASIS 115kV line CKT 1, near OASIS 115kV for 7 cycles. Open the faulted line and NORRIS_TP to CURRY 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NORRIS_TP to CURRY 115kV line CKT 1. Re-open the faulted line after 7 cycles% NORRIS_TP to CURRY 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_71_P1_OASIS | Apply 3-phase fault on FE-CHZPLT to OASIS 115kV line CKT 1, near OASIS 115kV for 7 cycles. Open the faulted line and NORRIS_TP to CURRY 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NORRIS_TP to CURRY 115kV line CKT 1. Re-open the faulted line after 7 cycles% NORRIS_TP to CURRY 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_71_P1_OASIS | Apply 3-phase fault on FE-CHZPLT to OASIS 115kV line CKT 1, near OASIS 115kV for 7 cycles. Open the faulted line and NORRIS_TP to CURRY 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NORRIS_TP to CURRY 115kV line CKT 1. Re-open the faulted line after 7 cycles% NORRIS_TP to CURRY 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_72_P1_OASIS | Apply 3-phase fault on PERIMETER to OASIS 115kV line CKT 1, near OASIS 115kV for 7 cycles. Open the faulted line and W_CLOVIS to FE-CLVS_INT3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and W_CLOVIS to FE-CLVS_INT3 115kV line CKT 1. Re-open the faulted line after 7 cycles% W_CLOVIS to FE-CLVS_INT3 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_72_P1_OASIS | Apply 3-phase fault on PERIMETER to OASIS 115kV line CKT 1, near OASIS 115kV for 7 cycles. Open the faulted line and W_CLOVIS to FE-CLVS_INT3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and W_CLOVIS to FE-CLVS_INT3 115kV line CKT 1. Re-open the faulted line after 7 cycles% W_CLOVIS to FE-CLVS_INT3 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_72_P1_OASIS | Apply 3-phase fault on PERIMETER to OASIS 115kV line CKT 1, near OASIS 115kV for 7 cycles. Open the faulted line and W_CLOVIS to FE-CLVS_INT3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and W_CLOVIS to FE-CLVS_INT3 115kV line CKT 1. Re-open the faulted line after 7 cycles% W_CLOVIS to FE-CLVS_INT3 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_72_P1_OASIS | Apply 3-phase fault on PERIMETER to OASIS 115kV line CKT 1, near OASIS 115kV for 7 cycles. Open the faulted line and W_CLOVIS to FE-CLVS_INT3 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and W_CLOVIS to FE-CLVS_INT3 115kV line CKT 1. Re-open the faulted line after 7 cycles% W_CLOVIS to FE-CLVS_INT3 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_73_P1_OASIS | Apply 3-phase fault on OASIS to PORTALES 115kV line CKT 1, near OASIS 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_73_P1_OASIS | Apply 3-phase fault on OASIS to PORTALES 115kV line CKT 1, near OASIS 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_73_P1_OASIS | Apply 3-phase fault on OASIS to PORTALES 115kV line CKT 1, near OASIS 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_73_P1_OASIS | Apply 3-phase fault on OASIS to PORTALES 115kV line CKT 1, near OASIS 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_74_P1_OASIS | Apply 3-phase fault on OASIS to ROSEVELT_N 6 230kV line CKT 1, near OASIS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_74_P1_OASIS | Apply 3-phase fault on OASIS to ROSEVELT_N 6 230kV line CKT 1, near OASIS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_74_P1_OASIS | Apply 3-phase fault on OASIS to ROSEVELT_N 6 230kV line CKT 1, near OASIS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_74_P1_OASIS | Apply 3-phase fault on OASIS to ROSEVELT_N 6 230kV line CKT 1, near OASIS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_75_P1_OASIS | Apply 3-phase fault on PLSNT_HILL 6 to OASIS 230kV line CKT 1, near OASIS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_75_P1_OASIS | Apply 3-phase fault on PLSNT_HILL 6 to OASIS 230kV line CKT 1, near OASIS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_75_P1_OASIS | Apply 3-phase fault on PLSNT_HILL 6 to OASIS 230kV line CKT 1, near OASIS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_75_P1_OASIS | Apply 3-phase fault on PLSNT_HILL 6 to OASIS 230kV line CKT 1, near OASIS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_76_P1_OASIS | Apply 3-phase fault on OASIS to SN_JUAN_TAP6 230kV line CKT 1, near OASIS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_76_P1_OASIS | Apply 3-phase fault on OASIS to SN_JUAN_TAP6 230kV line CKT 1, near OASIS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_76_P1_OASIS | Apply 3-phase fault on OASIS to SN_JUAN_TAP6 230kV line CKT 1, near OASIS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_76_P1_OASIS | Apply 3-phase fault on OASIS to SN_JUAN_TAP6 230kV line CKT 1, near OASIS 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_77_P1_SN_JUAN_TAP6 | Apply 3-phase fault on OASIS to SN_JUAN_TAP6 230kV line CKT 1, near SN_JUAN_TAP6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_77_P1_SN_JUAN_TAP6 | Apply 3-phase fault on OASIS to SN_JUAN_TAP6 230kV line CKT 1, near SN_JUAN_TAP6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_77_P1_SN_JUAN_TAP6 | Apply 3-phase fault on OASIS to SN_JUAN_TAP6 230kV line CKT 1, near SN_JUAN_TAP6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_77_P1_SN_JUAN_TAP6 | Apply 3-phase fault on OASIS to SN_JUAN_TAP6 230kV line CKT 1, near SN_JUAN_TAP6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_78_P1_SN_JUAN_TAP6 | Apply 3-phase fault on SN_JUAN_TAP6 to CHAVES_CNTY6 230kV line CKT 1, near SN_JUAN_TAP6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_78_P1_SN_JUAN_TAP6 | Apply 3-phase fault on SN_JUAN_TAP6 to CHAVES_CNTY6 230kV line CKT 1, near SN_JUAN_TAP6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_78_P1_SN_JUAN_TAP6 | Apply 3-phase fault on SN_JUAN_TAP6 to CHAVES_CNTY6 230kV line CKT 1, near SN_JUAN_TAP6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_78_P1_SN_JUAN_TAP6 | Apply 3-phase fault on SN_JUAN_TAP6 to CHAVES_CNTY6 230kV line CKT 1, near SN_JUAN_TAP6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_79_P1_ROOSEVELT | Apply 3-phase fault on ROSEVLT_TR11 13.19kV/115kV/230kV transformer CKT 1, near ROOSEVELT 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_79_P1_ROOSEVELT | Apply 3-phase fault on ROSEVLT_TR11 13.19kV/115kV/230kV transformer CKT 1, near ROOSEVELT 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_79_P1_ROOSEVELT | Apply 3-phase fault on ROSEVLT_TR11 13.19kV/115kV/230kV transformer CKT 1, near ROOSEVELT 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_79_P1_ROOSEVELT | Apply 3-phase fault on ROSEVLT_TR11 13.19kV/115kV/230kV transformer CKT 1, near ROOSEVELT 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_8_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.27pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_8_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_8_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.26pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_8_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.26pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_80_P1_ROOSEVELT | Apply 3-phase fault on ROOSEVELT to PORTALES 115kV line CKT 1, near ROOSEVELT 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_80_P1_ROOSEVELT | Apply 3-phase fault on ROOSEVELT to PORTALES 115kV line CKT 1, near ROOSEVELT 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_80_P1_ROOSEVELT | Apply 3-phase fault on ROOSEVELT to PORTALES 115kV line CKT 1, near ROOSEVELT 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_80_P1_ROOSEVELT | Apply 3-phase fault on ROOSEVELT to PORTALES 115kV line CKT 1, near ROOSEVELT 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_81_P1_ROOSEVELT | Apply 3-phase fault on CURRY to ROOSEVELT 115kV line CKT 2, near ROOSEVELT 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_81_P1_ROOSEVELT | Apply 3-phase fault on CURRY to ROOSEVELT 115kV line CKT 2, near ROOSEVELT 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_81_P1_ROOSEVELT | Apply 3-phase fault on CURRY to ROOSEVELT 115kV line CKT 2, near ROOSEVELT 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_81_P1_ROOSEVELT | Apply 3-phase fault on CURRY to ROOSEVELT 115kV line CKT 2, near ROOSEVELT 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_82_P1_ROSEVELT_N6 | Apply 3-phase fault on OASIS to ROSEVELT_N 6 230kV line CKT 1, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_82_P1_ROSEVELT_N6 | Apply 3-phase fault on OASIS to ROSEVELT_N 6 230kV line CKT 1, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_82_P1_ROSEVELT_N6 | Apply 3-phase fault on OASIS to ROSEVELT_N 6 230kV line CKT 1, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_82_P1_ROSEVELT_N6 | Apply 3-phase fault on OASIS to ROSEVELT_N 6 230kV line CKT 1, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_83_P1_ROSEVELT_N6 | Apply 3-phase fault on PLSNT_HILL 6 to ROSEVELT_N 6 230kV line CKT 1, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_83_P1_ROSEVELT_N6 | Apply 3-phase fault on PLSNT_HILL 6 to ROSEVELT_N 6 230kV line CKT 1, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_83_P1_ROSEVELT_N6 | Apply 3-phase fault on PLSNT_HILL 6 to ROSEVELT_N 6 230kV line CKT 1, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_83_P1_ROSEVELT_N6 | Apply 3-phase fault on PLSNT_HILL 6 to ROSEVELT_N 6 230kV line CKT 1, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_84_P1_ROSEVELT_N6 | Apply 3-phase fault on DC line SPP_41_BLKWT, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted DC line. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_84_P1_ROSEVELT_N6 | Apply 3-phase fault on DC line SPP_41_BLKWT, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted DC line. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_84_P1_ROSEVELT_N6 | Apply 3-phase fault on DC line SPP_41_BLKWT, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted DC line. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_84_P1_ROSEVELT_N6 | Apply 3-phase fault on DC line SPP_41_BLKWT, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted DC line. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_85_P1_ROSEVELT_N6 | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_EAST 230kV line CKT 1, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_85_P1_ROSEVELT_N6 | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_EAST 230kV line CKT 1, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_85_P1_ROSEVELT_N6 | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_EAST 230kV line CKT 1, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_85_P1_ROSEVELT_N6 | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_EAST 230kV line CKT 1, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_86_P1_ROSEVELT_N6 | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_WEST 230kV line CKT 2, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_86_P1_ROSEVELT_N6 | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_WEST 230kV line CKT 2, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_86_P1_ROSEVELT_N6 | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_WEST 230kV line CKT 2, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_86_P1_ROSEVELT_N6 | Apply 3-phase fault on ROSEVELT_N 6 to TOLK_WEST 230kV line CKT 2, near ROSEVELT_N 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_87_P1_PORTALES | Apply 3-phase fault on S_PORTALES 3 Load 1, near PORTALES 115kV for 7 cycles. Open the faulted Load and KILGORE to S_PORTALES 3 115kV line CKT 1 and PORTALES to KILGORE 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_87_P1_PORTALES | Apply 3-phase fault on S_PORTALES 3 Load 1, near PORTALES 115kV for 7 cycles. Open the faulted Load and KILGORE to S_PORTALES 3 115kV line CKT 1 and PORTALES to KILGORE 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_87_P1_PORTALES | Apply 3-phase fault on S_PORTALES 3 Load 1, near PORTALES 115kV for 7 cycles. Open the faulted Load and KILGORE to S_PORTALES 3 115kV line CKT 1 and PORTALES to KILGORE 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_87_P1_PORTALES | Apply 3-phase fault on S_PORTALES 3 Load 1, near PORTALES 115kV for 7 cycles. Open the faulted Load and KILGORE to S_PORTALES 3 115kV line CKT 1 and PORTALES to KILGORE 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_88_P1_PORTALES | Apply 3-phase fault on OASIS to PORTALES 115kV line CKT 1, near PORTALES 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_88_P1_PORTALES | Apply 3-phase fault on OASIS to PORTALES 115kV line CKT 1, near PORTALES 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_88_P1_PORTALES | Apply 3-phase fault on OASIS to PORTALES 115kV line CKT 1, near PORTALES 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_88_P1_PORTALES | Apply 3-phase fault on OASIS to PORTALES 115kV line CKT 1, near PORTALES 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_89_P1_BAILEYCO | Apply 3-phase fault on MULSHVLY_TP3 to BAILEYCO 115kV line CKT 1, near BAILEYCO 115kV for 7 cycles. Open the faulted line and MULSHVLY_TP3 to PLANT_X 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and MULSHVLY_TP3 to PLANT_X 115kV line CKT 1. Re-open the faulted line after 7 cycles% MULSHVLY_TP3 to PLANT_X 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_89_P1_BAILEYCO | Apply 3-phase fault on MULSHVLY_TP3 to BAILEYCO 115kV line CKT 1, near BAILEYCO 115kV for 7 cycles. Open the faulted line and MULSHVLY_TP3 to PLANT_X 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and MULSHVLY_TP3 to PLANT_X 115kV line CKT 1. Re-open the faulted line after 7 cycles% MULSHVLY_TP3 to PLANT_X 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_89_P1_BAILEYCO | Apply 3-phase fault on MULSHVLY_TP3 to BAILEYCO 115kV line CKT 1, near BAILEYCO 115kV for 7 cycles. Open the faulted line and MULSHVLY_TP3 to PLANT_X 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and MULSHVLY_TP3 to PLANT_X 115kV line CKT 1. Re-open the faulted line after 7 cycles% MULSHVLY_TP3 to PLANT_X 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_89_P1_BAILEYCO | Apply 3-phase fault on MULSHVLY_TP3 to BAILEYCO 115kV line CKT 1, near BAILEYCO 115kV for 7 cycles. Open the faulted line and MULSHVLY_TP3 to PLANT_X 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and MULSHVLY_TP3 to PLANT_X 115kV line CKT 1. Re-open the faulted line after 7 cycles% MULSHVLY_TP3 to PLANT_X 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_9_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes | Voltage Spike: 1.25pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_9_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | No | Yes | No | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_9_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | No | No | Yes | Voltage Spike: 1.27pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_9_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 6 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.27pu, MaxDur: 0.03s
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_90_P1_HAPPY_INT | Apply 3-phase fault on PALO_DURO to HAPPY_INT 115kV line CKT 1, near HAPPY_INT 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_90_P1_HAPPY_INT | Apply 3-phase fault on PALO_DURO to HAPPY_INT 115kV line CKT 1, near HAPPY_INT 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_90_P1_HAPPY_INT | Apply 3-phase fault on PALO_DURO to HAPPY_INT 115kV line CKT 1, near HAPPY_INT 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_90_P1_HAPPY_INT | Apply 3-phase fault on PALO_DURO to HAPPY_INT 115kV line CKT 1, near HAPPY_INT 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_91_P1_KRESS_INT | Apply 3-phase fault on KRESS_TR1 13.19kV/69kV/115kV transformer CKT 1, near KRESS_INT 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_91_P1_KRESS_INT | Apply 3-phase fault on KRESS_TR1 13.19kV/69kV/115kV transformer CKT 1, near KRESS_INT 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_91_P1_KRESS_INT | Apply 3-phase fault on KRESS_TR1 13.19kV/69kV/115kV transformer CKT 1, near KRESS_INT 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_91_P1_KRESS_INT | Apply 3-phase fault on KRESS_TR1 13.19kV/69kV/115kV transformer CKT 1, near KRESS_INT 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_92_P1_KRESS_INT | Apply 3-phase fault on KRESS_INT to NEWHART 115kV line CKT 1, near KRESS_INT 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_92_P1_KRESS_INT | Apply 3-phase fault on KRESS_INT to NEWHART 115kV line CKT 1, near KRESS_INT 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_92_P1_KRESS_INT | Apply 3-phase fault on KRESS_INT to NEWHART 115kV line CKT 1, near KRESS_INT 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_92_P1_KRESS_INT | Apply 3-phase fault on KRESS_INT to NEWHART 115kV line CKT 1, near KRESS_INT 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_93_P1_KRESS_INT | Apply 3-phase fault on KRESS_INT to HALE_CNTY 115kV line CKT 1, near KRESS_INT 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_93_P1_KRESS_INT | Apply 3-phase fault on KRESS_INT to HALE_CNTY 115kV line CKT 1, near KRESS_INT 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_93_P1_KRESS_INT | Apply 3-phase fault on KRESS_INT to HALE_CNTY 115kV line CKT 1, near KRESS_INT 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_93_P1_KRESS_INT | Apply 3-phase fault on KRESS_INT to HALE_CNTY 115kV line CKT 1, near KRESS_INT 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_94_P1_KRESS_INT | Apply 3-phase fault on KRESS_INT to KRS_RURL_TP3 115kV line CKT 1, near KRESS_INT 115kV for 7 cycles. Open the faulted line and KISER to COX 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and KISER to COX 115kV line CKT 1. Re-open the faulted line after 7 cycles% KISER to COX 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_94_P1_KRESS_INT | Apply 3-phase fault on KRESS_INT to KRS_RURL_TP3 115kV line CKT 1, near KRESS_INT 115kV for 7 cycles. Open the faulted line and KISER to COX 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and KISER to COX 115kV line CKT 1. Re-open the faulted line after 7 cycles% KISER to COX 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_94_P1_KRESS_INT | Apply 3-phase fault on KRESS_INT to KRS_RURL_TP3 115kV line CKT 1, near KRESS_INT 115kV for 7 cycles. Open the faulted line and KISER to COX 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and KISER to COX 115kV line CKT 1. Re-open the faulted line after 7 cycles% KISER to COX 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_94_P1_KRESS_INT | Apply 3-phase fault on KRESS_INT to KRS_RURL_TP3 115kV line CKT 1, near KRESS_INT 115kV for 7 cycles. Open the faulted line and KISER to COX 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and KISER to COX 115kV line CKT 1. Re-open the faulted line after 7 cycles% KISER to COX 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_95_P1_KRESS_INT | Apply 3-phase fault on TULIA_TP to KRESS_INT 115kV line CKT 1, near KRESS_INT 115kV for 7 cycles. Open the faulted line and HAPPY_INT to TULIA_TP 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and HAPPY_INT to TULIA_TP 115kV line CKT 1. Re-open the faulted line after 7 cycles% HAPPY_INT to TULIA_TP 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_95_P1_KRESS_INT | Apply 3-phase fault on TULIA_TP to KRESS_INT 115kV line CKT 1, near KRESS_INT 115kV for 7 cycles. Open the faulted line and HAPPY_INT to TULIA_TP 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and HAPPY_INT to TULIA_TP 115kV line CKT 1. Re-open the faulted line after 7 cycles% HAPPY_INT to TULIA_TP 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_95_P1_KRESS_INT | Apply 3-phase fault on TULIA_TP to KRESS_INT 115kV line CKT 1, near KRESS_INT 115kV for 7 cycles. Open the faulted line and HAPPY_INT to TULIA_TP 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and HAPPY_INT to TULIA_TP 115kV line CKT 1. Re-open the faulted line after 7 cycles% HAPPY_INT to TULIA_TP 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_95_P1_KRESS_INT | Apply 3-phase fault on TULIA_TP to KRESS_INT 115kV line CKT 1, near KRESS_INT 115kV for 7 cycles. Open the faulted line and HAPPY_INT to TULIA_TP 115kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and HAPPY_INT to TULIA_TP 115kV line CKT 1. Re-open the faulted line after 7 cycles% HAPPY_INT to TULIA_TP 115kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_96_P1_SWISHER | Apply 3-phase fault on SWISHER_TR11 13.19kV/115kV/230kV transformer CKT 1, near SWISHER 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_96_P1_SWISHER | Apply 3-phase fault on SWISHER_TR11 13.19kV/115kV/230kV transformer CKT 1, near SWISHER 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_96_P1_SWISHER | Apply 3-phase fault on SWISHER_TR11 13.19kV/115kV/230kV transformer CKT 1, near SWISHER 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_96_P1_SWISHER | Apply 3-phase fault on SWISHER_TR11 13.19kV/115kV/230kV transformer CKT 1, near SWISHER 115kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_97_P1_SWISHER | Apply 3-phase fault on KRESS_INT to SWISHER 115kV line CKT 1, near SWISHER 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_97_P1_SWISHER | Apply 3-phase fault on KRESS_INT to SWISHER 115kV line CKT 1, near SWISHER 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_97_P1_SWISHER | Apply 3-phase fault on KRESS_INT to SWISHER 115kV line CKT 1, near SWISHER 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_97_P1_SWISHER | Apply 3-phase fault on KRESS_INT to SWISHER 115kV line CKT 1, near SWISHER 115kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_98_P1_SWISHER | Apply 3-phase fault on AMA_SOUTH to SWISHER 230kV line CKT 1, near SWISHER 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_98_P1_SWISHER | Apply 3-phase fault on AMA_SOUTH to SWISHER 230kV line CKT 1, near SWISHER 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_98_P1_SWISHER | Apply 3-phase fault on AMA_SOUTH to SWISHER 230kV line CKT 1, near SWISHER 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_98_P1_SWISHER | Apply 3-phase fault on AMA_SOUTH to SWISHER 230kV line CKT 1, near SWISHER 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 19W | Transfer | FLT_99_P1_SWISHER | Apply 3-phase fault on SWISHER to TUCO_INT 230kV line CKT 1, near SWISHER 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 06 - South Texas Panhandle/New Mexico | 21L | Transfer | FLT_99_P1_SWISHER | Apply 3-phase fault on SWISHER to TUCO_INT 230kV line CKT 1, near SWISHER 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.02s
South | 06 - South Texas Panhandle/New Mexico | 21S | Transfer | FLT_99_P1_SWISHER | Apply 3-phase fault on SWISHER to TUCO_INT 230kV line CKT 1, near SWISHER 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1].
South | 06 - South Texas Panhandle/New Mexico | 28S | Transfer | FLT_99_P1_SWISHER | Apply 3-phase fault on SWISHER to TUCO_INT 230kV line CKT 1, near SWISHER 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line and re-open after 7 cycles. Clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.02s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_1_P1_ALTUSJT4 | Apply 3-phase fault on ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1, near ALTUSJT4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | 520519[BCI WTG, 520520[BCII WTG & 520522[BCVI_WTG1 caused abnormal oscillationss in numerous contingencies across all cases. When these units were GNETed and the simulation were repeated, the oscillations subsided. OECGT1-1 unit 1 (511939) has shown abnormal fluctuations in the post-contingency period in BC and TC for several contingencies accross all cases.
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_1_P1_ALTUSJT4 | Apply 3-phase fault on ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1, near ALTUSJT4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.02s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_1_P1_ALTUSJT4 | Apply 3-phase fault on ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1, near ALTUSJT4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_1_P1_ALTUSJT4 | Apply 3-phase fault on ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1, near ALTUSJT4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_2_P1_SNYDER-4 | Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.29pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_2_P1_SNYDER-4 | Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.34pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_2_P1_SNYDER-4 | Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.27pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_2_P1_SNYDER-4 | Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed :MaxV: 1.28pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_3_P1_SNYDER-4 | Apply 3-phase fault on SNYDER-4 to SNYDER 4 138kV line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed MaxV: 1.28pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_3_P1_SNYDER-4 | Apply 3-phase fault on SNYDER-4 to SNYDER 4 138kV line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.30pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_3_P1_SNYDER-4 | Apply 3-phase fault on SNYDER-4 to SNYDER 4 138kV line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.29pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_3_P1_SNYDER-4 | Apply 3-phase fault on SNYDER-4 to SNYDER 4 138kV line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.25pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_4_P1_SNYDER-4 | Apply 3-phase fault on SNYDER-4 to ALTUSJT4 138kV line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.29pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_4_P1_SNYDER-4 | Apply 3-phase fault on SNYDER-4 to ALTUSJT4 138kV line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.31pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_4_P1_SNYDER-4 | Apply 3-phase fault on SNYDER-4 to ALTUSJT4 138kV line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.30pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_4_P1_SNYDER-4 | Apply 3-phase fault on SNYDER-4 to ALTUSJT4 138kV line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.29pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_5_P1_SNYDER-4 | Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.29pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_5_P1_SNYDER-4 | Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.34pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_5_P1_SNYDER-4 | Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.27pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_5_P1_SNYDER-4 | Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.28pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_6_P1_COMANC-4 | Apply 3-phase fault on COMANC-4 to L.E.S.-4 138kV line CKT 1, near COMANC-4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_6_P1_COMANC-4 | Apply 3-phase fault on COMANC-4 to L.E.S.-4 138kV line CKT 1, near COMANC-4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_6_P1_COMANC-4 | Apply 3-phase fault on COMANC-4 to L.E.S.-4 138kV line CKT 1, near COMANC-4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_6_P1_COMANC-4 | Apply 3-phase fault on COMANC-4 to L.E.S.-4 138kV line CKT 1, near COMANC-4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_7_P1_COMANC-4 | Apply 3-phase fault on COMANC-4 to COMMTAP4 138kV line CKT 1, near COMANC-4 138kV for 7 cycles. Open the faulted line and L.E.S.-4 to COMMTAP4 138kV line CKT 1 and DUNCAN-4 to OMDUNCN4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and L.E.S.-4 to COMMTAP4 138kV line CKT 1 and DUNCAN-4 to OMDUNCN4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open L.E.S.-4 to COMMTAP4 138kV line CKT 1. Simultaneously re-open DUNCAN-4 to OMDUNCN4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_7_P1_COMANC-4 | Apply 3-phase fault on COMANC-4 to COMMTAP4 138kV line CKT 1, near COMANC-4 138kV for 7 cycles. Open the faulted line and L.E.S.-4 to COMMTAP4 138kV line CKT 1 and DUNCAN-4 to OMDUNCN4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and L.E.S.-4 to COMMTAP4 138kV line CKT 1 and DUNCAN-4 to OMDUNCN4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open L.E.S.-4 to COMMTAP4 138kV line CKT 1. Simultaneously re-open DUNCAN-4 to OMDUNCN4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_7_P1_COMANC-4 | Apply 3-phase fault on COMANC-4 to COMMTAP4 138kV line CKT 1, near COMANC-4 138kV for 7 cycles. Open the faulted line and L.E.S.-4 to COMMTAP4 138kV line CKT 1 and DUNCAN-4 to OMDUNCN4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and L.E.S.-4 to COMMTAP4 138kV line CKT 1 and DUNCAN-4 to OMDUNCN4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open L.E.S.-4 to COMMTAP4 138kV line CKT 1. Simultaneously re-open DUNCAN-4 to OMDUNCN4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_7_P1_COMANC-4 | Apply 3-phase fault on COMANC-4 to COMMTAP4 138kV line CKT 1, near COMANC-4 138kV for 7 cycles. Open the faulted line and L.E.S.-4 to COMMTAP4 138kV line CKT 1 and DUNCAN-4 to OMDUNCN4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and L.E.S.-4 to COMMTAP4 138kV line CKT 1 and DUNCAN-4 to OMDUNCN4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open L.E.S.-4 to COMMTAP4 138kV line CKT 1. Simultaneously re-open DUNCAN-4 to OMDUNCN4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_8_P1_ALTUSJT4 | Apply 3-phase fault on ALTUSJT4 to OMPARK-4 138kV line CKT 1, near ALTUSJT4 138kV for 7 cycles. Open the faulted line and HOB-JCT4 to MARTHA 4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and HOB-JCT4 to MARTHA 4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open HOB-JCT4 to MARTHA 4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_8_P1_ALTUSJT4 | Apply 3-phase fault on ALTUSJT4 to OMPARK-4 138kV line CKT 1, near ALTUSJT4 138kV for 7 cycles. Open the faulted line and HOB-JCT4 to MARTHA 4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and HOB-JCT4 to MARTHA 4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open HOB-JCT4 to MARTHA 4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.02s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_8_P1_ALTUSJT4 | Apply 3-phase fault on ALTUSJT4 to OMPARK-4 138kV line CKT 1, near ALTUSJT4 138kV for 7 cycles. Open the faulted line and HOB-JCT4 to MARTHA 4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and HOB-JCT4 to MARTHA 4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open HOB-JCT4 to MARTHA 4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_8_P1_ALTUSJT4 | Apply 3-phase fault on ALTUSJT4 to OMPARK-4 138kV line CKT 1, near ALTUSJT4 138kV for 7 cycles. Open the faulted line and HOB-JCT4 to MARTHA 4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and HOB-JCT4 to MARTHA 4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open HOB-JCT4 to MARTHA 4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_9_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-065-GEN2[1]. G17-065-GEN2[1] tripped on overfrequency. When the protection relay is disabled and the simulation is repeated, the unit becomes stable. The tripping is observed in TC for this contingency.
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_9_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_9_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_9_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-065-GEN2[1]. G17-065-GEN2[1] tripped on overfrequency. When the protection relay is disabled and the simulation is repeated, the unit becomes stable. The tripping is observed in TC for this contingency.
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_10_P1_ELKCTY-2 | Apply 3-phase fault on ELKCTY-4 138kV/69kV/13.8kV transformer CKT 1, near ELKCTY-2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | No | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_10_P1_ELKCTY-2 | Apply 3-phase fault on ELKCTY-4 138kV/69kV/13.8kV transformer CKT 1, near ELKCTY-2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_10_P1_ELKCTY-2 | Apply 3-phase fault on ELKCTY-4 138kV/69kV/13.8kV transformer CKT 1, near ELKCTY-2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | No | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_10_P1_ELKCTY-2 | Apply 3-phase fault on ELKCTY-4 138kV/69kV/13.8kV transformer CKT 1, near ELKCTY-2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | No | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_11_P1_HOB-JCT4 | Apply 3-phase fault on CARNEG-4 to HOB-JCT4 138kV line CKT 1, near HOB-JCT4 138kV for 7 cycles. Open the faulted line and CARNEG-4 to S.W.S.-4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and CARNEG-4 to S.W.S.-4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open CARNEG-4 to S.W.S.-4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_11_P1_HOB-JCT4 | Apply 3-phase fault on CARNEG-4 to HOB-JCT4 138kV line CKT 1, near HOB-JCT4 138kV for 7 cycles. Open the faulted line and CARNEG-4 to S.W.S.-4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and CARNEG-4 to S.W.S.-4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open CARNEG-4 to S.W.S.-4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_11_P1_HOB-JCT4 | Apply 3-phase fault on CARNEG-4 to HOB-JCT4 138kV line CKT 1, near HOB-JCT4 138kV for 7 cycles. Open the faulted line and CARNEG-4 to S.W.S.-4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and CARNEG-4 to S.W.S.-4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open CARNEG-4 to S.W.S.-4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_11_P1_HOB-JCT4 | Apply 3-phase fault on CARNEG-4 to HOB-JCT4 138kV line CKT 1, near HOB-JCT4 138kV for 7 cycles. Open the faulted line and CARNEG-4 to S.W.S.-4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and CARNEG-4 to S.W.S.-4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open CARNEG-4 to S.W.S.-4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_12_P1_HOB-JCT4 | Apply 3-phase fault on HOB-JCT4 to RKY_RDG4 138kV line CKT 1, near HOB-JCT4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_12_P1_HOB-JCT4 | Apply 3-phase fault on HOB-JCT4 to RKY_RDG4 138kV line CKT 1, near HOB-JCT4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_12_P1_HOB-JCT4 | Apply 3-phase fault on HOB-JCT4 to RKY_RDG4 138kV line CKT 1, near HOB-JCT4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_12_P1_HOB-JCT4 | Apply 3-phase fault on HOB-JCT4 to RKY_RDG4 138kV line CKT 1, near HOB-JCT4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_13_P1_HOB-JCT4 | Apply 3-phase fault on CL-AFTP4 to HOB-JCT4 138kV line CKT 1, near HOB-JCT4 138kV for 7 cycles. Open the faulted line and CL-AFTP4 to ELKCTY-4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and CL-AFTP4 to ELKCTY-4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open CL-AFTP4 to ELKCTY-4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_13_P1_HOB-JCT4 | Apply 3-phase fault on CL-AFTP4 to HOB-JCT4 138kV line CKT 1, near HOB-JCT4 138kV for 7 cycles. Open the faulted line and CL-AFTP4 to ELKCTY-4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and CL-AFTP4 to ELKCTY-4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open CL-AFTP4 to ELKCTY-4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_13_P1_HOB-JCT4 | Apply 3-phase fault on CL-AFTP4 to HOB-JCT4 138kV line CKT 1, near HOB-JCT4 138kV for 7 cycles. Open the faulted line and CL-AFTP4 to ELKCTY-4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and CL-AFTP4 to ELKCTY-4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open CL-AFTP4 to ELKCTY-4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_13_P1_HOB-JCT4 | Apply 3-phase fault on CL-AFTP4 to HOB-JCT4 138kV line CKT 1, near HOB-JCT4 138kV for 7 cycles. Open the faulted line and CL-AFTP4 to ELKCTY-4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and CL-AFTP4 to ELKCTY-4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open CL-AFTP4 to ELKCTY-4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_14_P1_LES-4 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_14_P1_LES-4 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_14_P1_LES-4 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_14_P1_LES-4 | Apply 3-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_15_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_15_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_15_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_15_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.00s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_16_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.00s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_16_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.21pu, MaxDur: 0.02s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_16_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_16_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_17_P1_SNYDER-2 | Apply 3-phase fault on SNYDER-2 to TOMSTEED2 69kV line CKT 1, near SNYDER-2 69kV for 7 cycles. Open the faulted line and HOB-JCT2 to HOBART-2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and HOB-JCT2 to HOBART-2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open HOB-JCT2 to HOBART-2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_17_P1_SNYDER-2 | Apply 3-phase fault on SNYDER-2 to TOMSTEED2 69kV line CKT 1, near SNYDER-2 69kV for 7 cycles. Open the faulted line and HOB-JCT2 to HOBART-2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and HOB-JCT2 to HOBART-2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open HOB-JCT2 to HOBART-2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_17_P1_SNYDER-2 | Apply 3-phase fault on SNYDER-2 to TOMSTEED2 69kV line CKT 1, near SNYDER-2 69kV for 7 cycles. Open the faulted line and HOB-JCT2 to HOBART-2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and HOB-JCT2 to HOBART-2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open HOB-JCT2 to HOBART-2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_17_P1_SNYDER-2 | Apply 3-phase fault on SNYDER-2 to TOMSTEED2 69kV line CKT 1, near SNYDER-2 69kV for 7 cycles. Open the faulted line and HOB-JCT2 to HOBART-2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and HOB-JCT2 to HOBART-2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open HOB-JCT2 to HOBART-2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_18_P1_SNYDER-2 | Apply 3-phase fault on TIPTE T2 to SNYDER-2 69kV line CKT 1, near SNYDER-2 69kV for 7 cycles. Open the faulted line and VRNMTAP2 to VERNON 2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and VRNMTAP2 to VERNON 2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open VRNMTAP2 to VERNON 2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_18_P1_SNYDER-2 | Apply 3-phase fault on TIPTE T2 to SNYDER-2 69kV line CKT 1, near SNYDER-2 69kV for 7 cycles. Open the faulted line and VRNMTAP2 to VERNON 2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and VRNMTAP2 to VERNON 2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open VRNMTAP2 to VERNON 2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_18_P1_SNYDER-2 | Apply 3-phase fault on TIPTE T2 to SNYDER-2 69kV line CKT 1, near SNYDER-2 69kV for 7 cycles. Open the faulted line and VRNMTAP2 to VERNON 2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and VRNMTAP2 to VERNON 2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open VRNMTAP2 to VERNON 2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_18_P1_SNYDER-2 | Apply 3-phase fault on TIPTE T2 to SNYDER-2 69kV line CKT 1, near SNYDER-2 69kV for 7 cycles. Open the faulted line and VRNMTAP2 to VERNON 2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and VRNMTAP2 to VERNON 2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open VRNMTAP2 to VERNON 2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_19_P1_112GORE4 | Apply 3-phase fault on COMANC-4 to 112GORE4 138kV line CKT 1, near 112GORE4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.21pu, MaxDur: 0.02s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_19_P1_112GORE4 | Apply 3-phase fault on COMANC-4 to 112GORE4 138kV line CKT 1, near 112GORE4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.21pu, MaxDur: 0.02s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_19_P1_112GORE4 | Apply 3-phase fault on COMANC-4 to 112GORE4 138kV line CKT 1, near 112GORE4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_19_P1_112GORE4 | Apply 3-phase fault on COMANC-4 to 112GORE4 138kV line CKT 1, near 112GORE4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_20_P1_112GORE4 | Apply 3-phase fault on LWS-NTP4 to 112GORE4 138kV line CKT 1, near 112GORE4 138kV for 7 cycles. Open the faulted line and L.E.S.-4 to SHERID4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and L.E.S.-4 to SHERID4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open L.E.S.-4 to SHERID4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.21pu, MaxDur: 0.02s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_20_P1_112GORE4 | Apply 3-phase fault on LWS-NTP4 to 112GORE4 138kV line CKT 1, near 112GORE4 138kV for 7 cycles. Open the faulted line and L.E.S.-4 to SHERID4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and L.E.S.-4 to SHERID4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open L.E.S.-4 to SHERID4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.21pu, MaxDur: 0.02s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_20_P1_112GORE4 | Apply 3-phase fault on LWS-NTP4 to 112GORE4 138kV line CKT 1, near 112GORE4 138kV for 7 cycles. Open the faulted line and L.E.S.-4 to SHERID4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and L.E.S.-4 to SHERID4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open L.E.S.-4 to SHERID4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.02s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_20_P1_112GORE4 | Apply 3-phase fault on LWS-NTP4 to 112GORE4 138kV line CKT 1, near 112GORE4 138kV for 7 cycles. Open the faulted line and L.E.S.-4 to SHERID4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and L.E.S.-4 to SHERID4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open L.E.S.-4 to SHERID4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_21_P1_112GORE4 | Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV line CKT 1, near 112GORE4 138kV for 7 cycles. Open the faulted line and LWSTAP 4 to L.E.S.-4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and LWSTAP 4 to L.E.S.-4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.21pu, MaxDur: 0.02s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_21_P1_112GORE4 | Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV line CKT 1, near 112GORE4 138kV for 7 cycles. Open the faulted line and LWSTAP 4 to L.E.S.-4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and LWSTAP 4 to L.E.S.-4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.21pu, MaxDur: 0.02s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_21_P1_112GORE4 | Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV line CKT 1, near 112GORE4 138kV for 7 cycles. Open the faulted line and LWSTAP 4 to L.E.S.-4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and LWSTAP 4 to L.E.S.-4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.02s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_21_P1_112GORE4 | Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV line CKT 1, near 112GORE4 138kV for 7 cycles. Open the faulted line and LWSTAP 4 to L.E.S.-4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and LWSTAP 4 to L.E.S.-4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_22_P1_ELKCITY6 | Apply 3-phase fault on ELKCTY-4 138kV/13.8kV/230kV transformer CKT 1, near ELKCITY6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_22_P1_ELKCITY6 | Apply 3-phase fault on ELKCTY-4 138kV/13.8kV/230kV transformer CKT 1, near ELKCITY6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_22_P1_ELKCITY6 | Apply 3-phase fault on ELKCTY-4 138kV/13.8kV/230kV transformer CKT 1, near ELKCITY6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_22_P1_ELKCITY6 | Apply 3-phase fault on ELKCTY-4 138kV/13.8kV/230kV transformer CKT 1, near ELKCITY6 230kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_23_P1_CHISHOLM7 | Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.37pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_23_P1_CHISHOLM7 | Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | No | Yes | No | Yes | Voltage spike observed : MaxV: 1.36pu, MaxDur: 0.07s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_23_P1_CHISHOLM7 | Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.36pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_23_P1_CHISHOLM7 | Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.35pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_24_P1_CHISHOLM6 | Apply 3-phase fault on SWEETWT6 to CHISHOLM6 230kV line CKT 1, near CHISHOLM6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.24pu, MaxDur: 0.02s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_24_P1_CHISHOLM6 | Apply 3-phase fault on SWEETWT6 to CHISHOLM6 230kV line CKT 1, near CHISHOLM6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.24pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_24_P1_CHISHOLM6 | Apply 3-phase fault on SWEETWT6 to CHISHOLM6 230kV line CKT 1, near CHISHOLM6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection (due to size and location of the unit. No further simulation was peroformed) Voltage spike observed : MaxV: 1.23pu, MaxDur: 0.02s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_24_P1_CHISHOLM6 | Apply 3-phase fault on SWEETWT6 to CHISHOLM6 230kV line CKT 1, near CHISHOLM6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection (due to size and location of the unit. No further simulation was peroformed) Voltage spike observed : MaxV: 1.22pu, MaxDur: 0.02s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_25_P1_CHISHOLM6 | Apply 3-phase fault on ELKCITY6 to CHISHOLM6 230kV line CKT 1, near CHISHOLM6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.26pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_25_P1_CHISHOLM6 | Apply 3-phase fault on ELKCITY6 to CHISHOLM6 230kV line CKT 1, near CHISHOLM6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.27pu, MaxDur: 0.07s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_25_P1_CHISHOLM6 | Apply 3-phase fault on ELKCITY6 to CHISHOLM6 230kV line CKT 1, near CHISHOLM6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection (due to size and location of the unit. No further simulation was peroformed) Voltage spike observed : MaxV: 1.25pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_25_P1_CHISHOLM6 | Apply 3-phase fault on ELKCITY6 to CHISHOLM6 230kV line CKT 1, near CHISHOLM6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection (due to size and location of the unit. No further simulation was peroformed) Voltage spike observed : MaxV: 1.24pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_26_P1_TERRYRD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.21pu, MaxDur: 0.07s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_26_P1_TERRYRD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_26_P1_TERRYRD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_26_P1_TERRYRD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_27_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed :MaxV: 1.27pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_27_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_27_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.27pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_27_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | No | Yes | No | Yes | Voltage spike observed : MaxV: 1.26pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_28_P1_CIMARON7 | Apply 3-phase fault on CIMARON7 to MATHWSN7 345kV line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.21pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_28_P1_CIMARON7 | Apply 3-phase fault on CIMARON7 to MATHWSN7 345kV line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_28_P1_CIMARON7 | Apply 3-phase fault on CIMARON7 to MATHWSN7 345kV line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.02s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_28_P1_CIMARON7 | Apply 3-phase fault on CIMARON7 to MATHWSN7 345kV line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_29_P1_CIMARON7 | Apply 3-phase fault on CIMARON7 to DRAPER 7 345kV line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.21pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_29_P1_CIMARON7 | Apply 3-phase fault on CIMARON7 to DRAPER 7 345kV line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_29_P1_CIMARON7 | Apply 3-phase fault on CIMARON7 to DRAPER 7 345kV line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_29_P1_CIMARON7 | Apply 3-phase fault on CIMARON7 to DRAPER 7 345kV line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_30_P1_CIMARON7 | Apply 3-phase fault on NORTWST7 to CIMARON7 345kV line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.21pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_30_P1_CIMARON7 | Apply 3-phase fault on NORTWST7 to CIMARON7 345kV line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_30_P1_CIMARON7 | Apply 3-phase fault on NORTWST7 to CIMARON7 345kV line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_30_P1_CIMARON7 | Apply 3-phase fault on NORTWST7 to CIMARON7 345kV line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_31_P1_CIMARON7 | Apply 3-phase fault on CIMARON4 138kV/345kV/13.8kV transformer CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.04s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_31_P1_CIMARON7 | Apply 3-phase fault on CIMARON4 138kV/345kV/13.8kV transformer CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_31_P1_CIMARON7 | Apply 3-phase fault on CIMARON4 138kV/345kV/13.8kV transformer CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.04s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_31_P1_CIMARON7 | Apply 3-phase fault on CIMARON4 138kV/345kV/13.8kV transformer CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_32_P1_GRACMNT7 | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_32_P1_GRACMNT7 | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_32_P1_GRACMNT7 | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.36pu, MaxDur: 0.07s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_32_P1_GRACMNT7 | Apply 3-phase fault on GRACMNT7 to G16-091-TAP 345kV line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.35pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_33_P1_GRACMNT7 | Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.39pu, MaxDur: 0.04s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_33_P1_GRACMNT7 | Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_33_P1_GRACMNT7 | Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.39pu, MaxDur: 0.05s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_33_P1_GRACMNT7 | Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.38pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_34_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_34_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_34_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.35pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_34_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.34pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_35_P1_GRACMNT4 | Apply 3-phase fault on GRACMNT4 to ANADARK4 138kV line CKT 1, near GRACMNT4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_35_P1_GRACMNT4 | Apply 3-phase fault on GRACMNT4 to ANADARK4 138kV line CKT 1, near GRACMNT4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_35_P1_GRACMNT4 | Apply 3-phase fault on GRACMNT4 to ANADARK4 138kV line CKT 1, near GRACMNT4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_35_P1_GRACMNT4 | Apply 3-phase fault on GRACMNT4 to ANADARK4 138kV line CKT 1, near GRACMNT4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_36_P1_ANADARK4 | Apply 3-phase fault on ANADARK4 to CHERRYRD 4 138kV line CKT 1, near ANADARK4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_36_P1_ANADARK4 | Apply 3-phase fault on ANADARK4 to CHERRYRD 4 138kV line CKT 1, near ANADARK4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_36_P1_ANADARK4 | Apply 3-phase fault on ANADARK4 to CHERRYRD 4 138kV line CKT 1, near ANADARK4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_36_P1_ANADARK4 | Apply 3-phase fault on ANADARK4 to CHERRYRD 4 138kV line CKT 1, near ANADARK4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_37_P1_ANADARK4 | Apply 3-phase fault on SEQUOYAHJ4 to ANADARK4 138kV line CKT 1, near ANADARK4 138kV for 7 cycles. Open the faulted line and NAPLSTP4 to CORN TP4 138kV line CKT 1 and CORNVIL4 to CORN TP4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NAPLSTP4 to CORN TP4 138kV line CKT 1 and CORNVIL4 to CORN TP4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open NAPLSTP4 to CORN TP4 138kV line CKT 1. Simultaneously re-open CORNVIL4 to CORN TP4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_37_P1_ANADARK4 | Apply 3-phase fault on SEQUOYAHJ4 to ANADARK4 138kV line CKT 1, near ANADARK4 138kV for 7 cycles. Open the faulted line and NAPLSTP4 to CORN TP4 138kV line CKT 1 and CORNVIL4 to CORN TP4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NAPLSTP4 to CORN TP4 138kV line CKT 1 and CORNVIL4 to CORN TP4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open NAPLSTP4 to CORN TP4 138kV line CKT 1. Simultaneously re-open CORNVIL4 to CORN TP4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_37_P1_ANADARK4 | Apply 3-phase fault on SEQUOYAHJ4 to ANADARK4 138kV line CKT 1, near ANADARK4 138kV for 7 cycles. Open the faulted line and NAPLSTP4 to CORN TP4 138kV line CKT 1 and CORNVIL4 to CORN TP4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NAPLSTP4 to CORN TP4 138kV line CKT 1 and CORNVIL4 to CORN TP4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open NAPLSTP4 to CORN TP4 138kV line CKT 1. Simultaneously re-open CORNVIL4 to CORN TP4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_37_P1_ANADARK4 | Apply 3-phase fault on SEQUOYAHJ4 to ANADARK4 138kV line CKT 1, near ANADARK4 138kV for 7 cycles. Open the faulted line and NAPLSTP4 to CORN TP4 138kV line CKT 1 and CORNVIL4 to CORN TP4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NAPLSTP4 to CORN TP4 138kV line CKT 1 and CORNVIL4 to CORN TP4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open NAPLSTP4 to CORN TP4 138kV line CKT 1. Simultaneously re-open CORNVIL4 to CORN TP4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.05s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_38_P1_GOTEBO2 | Apply 3-phase fault on PINERDG2 to WASHITA2 69kV line CKT 1, near GOTEBO 2 69kV for 7 cycles. Open the faulted line and GOTEBO 2 to MTNVWTP2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and GOTEBO 2 to MTNVWTP2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open GOTEBO 2 to MTNVWTP2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.24pu, MaxDur: 0.01s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_38_P1_GOTEBO2 | Apply 3-phase fault on PINERDG2 to WASHITA2 69kV line CKT 1, near GOTEBO 2 69kV for 7 cycles. Open the faulted line and GOTEBO 2 to MTNVWTP2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and GOTEBO 2 to MTNVWTP2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open GOTEBO 2 to MTNVWTP2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes | Voltage Spike: 1.26pu, MaxDur: 0.01s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_38_P1_GOTEBO2 | Apply 3-phase fault on PINERDG2 to WASHITA2 69kV line CKT 1, near GOTEBO 2 69kV for 7 cycles. Open the faulted line and GOTEBO 2 to MTNVWTP2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and GOTEBO 2 to MTNVWTP2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open GOTEBO 2 to MTNVWTP2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.23pu, MaxDur: 0.01s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_38_P1_GOTEBO2 | Apply 3-phase fault on PINERDG2 to WASHITA2 69kV line CKT 1, near GOTEBO 2 69kV for 7 cycles. Open the faulted line and GOTEBO 2 to MTNVWTP2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and GOTEBO 2 to MTNVWTP2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open GOTEBO 2 to MTNVWTP2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.24pu, MaxDur: 0.01s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_39_P1_HOLLSTR2 | Apply 3-phase fault on GRANFLD2 to HOLLSTR2 69kV line CKT 1, near HOLLSTR2 69kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_39_P1_HOLLSTR2 | Apply 3-phase fault on GRANFLD2 to HOLLSTR2 69kV line CKT 1, near HOLLSTR2 69kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_39_P1_HOLLSTR2 | Apply 3-phase fault on GRANFLD2 to HOLLSTR2 69kV line CKT 1, near HOLLSTR2 69kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_39_P1_HOLLSTR2 | Apply 3-phase fault on GRANFLD2 to HOLLSTR2 69kV line CKT 1, near HOLLSTR2 69kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_40_P1_LKCREEK2 | Apply 3-phase fault on CARTERJ2 to LKCREEK2 69kV line CKT 1, near LKCREEK2 69kV for 7 cycles. Open the faulted line and ELKCTY-2 to ELKCITY2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and ELKCTY-2 to ELKCITY2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open ELKCTY-2 to ELKCITY2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_40_P1_LKCREEK2 | Apply 3-phase fault on CARTERJ2 to LKCREEK2 69kV line CKT 1, near LKCREEK2 69kV for 7 cycles. Open the faulted line and ELKCTY-2 to ELKCITY2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and ELKCTY-2 to ELKCITY2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open ELKCTY-2 to ELKCITY2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.25pu, MaxDur: 0.04s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_40_P1_LKCREEK2 | Apply 3-phase fault on CARTERJ2 to LKCREEK2 69kV line CKT 1, near LKCREEK2 69kV for 7 cycles. Open the faulted line and ELKCTY-2 to ELKCITY2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and ELKCTY-2 to ELKCITY2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open ELKCTY-2 to ELKCITY2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_40_P1_LKCREEK2 | Apply 3-phase fault on CARTERJ2 to LKCREEK2 69kV line CKT 1, near LKCREEK2 69kV for 7 cycles. Open the faulted line and ELKCTY-2 to ELKCITY2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and ELKCTY-2 to ELKCITY2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open ELKCTY-2 to ELKCITY2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.25pu, MaxDur: 0.04s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_41_P1_LKCREEK2 | Apply 3-phase fault on LKCREEK2 to LONEWLF2 69kV line CKT 1, near LKCREEK2 69kV for 7 cycles. Open the faulted line and GOTEBO 2 to LONEWLF2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and GOTEBO 2 to LONEWLF2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open GOTEBO 2 to LONEWLF2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_41_P1_LKCREEK2 | Apply 3-phase fault on LKCREEK2 to LONEWLF2 69kV line CKT 1, near LKCREEK2 69kV for 7 cycles. Open the faulted line and GOTEBO 2 to LONEWLF2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and GOTEBO 2 to LONEWLF2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open GOTEBO 2 to LONEWLF2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.24pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_41_P1_LKCREEK2 | Apply 3-phase fault on LKCREEK2 to LONEWLF2 69kV line CKT 1, near LKCREEK2 69kV for 7 cycles. Open the faulted line and GOTEBO 2 to LONEWLF2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and GOTEBO 2 to LONEWLF2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open GOTEBO 2 to LONEWLF2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_41_P1_LKCREEK2 | Apply 3-phase fault on LKCREEK2 to LONEWLF2 69kV line CKT 1, near LKCREEK2 69kV for 7 cycles. Open the faulted line and GOTEBO 2 to LONEWLF2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and GOTEBO 2 to LONEWLF2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open GOTEBO 2 to LONEWLF2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.23pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_42_P1_RUSSELL2 | Apply 3-phase fault on RUSSELL2 to VERNON 2 69kV line CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_42_P1_RUSSELL2 | Apply 3-phase fault on RUSSELL2 to VERNON 2 69kV line CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.25pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_42_P1_RUSSELL2 | Apply 3-phase fault on RUSSELL2 to VERNON 2 69kV line CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_42_P1_RUSSELL2 | Apply 3-phase fault on RUSSELL2 to VERNON 2 69kV line CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.24pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_43_P1_RUSSELL2 | Apply 3-phase fault on DUKE to RUSSELL2 69kV line CKT Z1, near RUSSELL2 69kV for 7 cycles. Open the faulted line and LAKEP2WT to ELDORDO2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and LAKEP2WT to ELDORDO2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open LAKEP2WT to ELDORDO2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_43_P1_RUSSELL2 | Apply 3-phase fault on DUKE to RUSSELL2 69kV line CKT Z1, near RUSSELL2 69kV for 7 cycles. Open the faulted line and LAKEP2WT to ELDORDO2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and LAKEP2WT to ELDORDO2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open LAKEP2WT to ELDORDO2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.25pu, MaxDur: 0.04s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_43_P1_RUSSELL2 | Apply 3-phase fault on DUKE to RUSSELL2 69kV line CKT Z1, near RUSSELL2 69kV for 7 cycles. Open the faulted line and LAKEP2WT to ELDORDO2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and LAKEP2WT to ELDORDO2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open LAKEP2WT to ELDORDO2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_43_P1_RUSSELL2 | Apply 3-phase fault on DUKE to RUSSELL2 69kV line CKT Z1, near RUSSELL2 69kV for 7 cycles. Open the faulted line and LAKEP2WT to ELDORDO2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and LAKEP2WT to ELDORDO2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open LAKEP2WT to ELDORDO2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.26pu, MaxDur: 0.04s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_44_P1_RUSSELL2 | Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_44_P1_RUSSELL2 | Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.26pu, MaxDur: 0.04s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_44_P1_RUSSELL2 | Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_44_P1_RUSSELL2 | Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.23pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_45_P1_RUSSELL2 | Apply 3-phase fault on ALTUS_ 2 to RUSSELL2 69kV line CKT 1, near RUSSELL2 69kV for 7 cycles. Open the faulted line and NAVJOTP2 to SNYDER 2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NAVJOTP2 to SNYDER 2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open NAVJOTP2 to SNYDER 2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_45_P1_RUSSELL2 | Apply 3-phase fault on ALTUS_ 2 to RUSSELL2 69kV line CKT 1, near RUSSELL2 69kV for 7 cycles. Open the faulted line and NAVJOTP2 to SNYDER 2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NAVJOTP2 to SNYDER 2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open NAVJOTP2 to SNYDER 2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.25pu, MaxDur: 0.04s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_45_P1_RUSSELL2 | Apply 3-phase fault on ALTUS_ 2 to RUSSELL2 69kV line CKT 1, near RUSSELL2 69kV for 7 cycles. Open the faulted line and NAVJOTP2 to SNYDER 2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NAVJOTP2 to SNYDER 2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open NAVJOTP2 to SNYDER 2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_45_P1_RUSSELL2 | Apply 3-phase fault on ALTUS_ 2 to RUSSELL2 69kV line CKT 1, near RUSSELL2 69kV for 7 cycles. Open the faulted line and NAVJOTP2 to SNYDER 2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NAVJOTP2 to SNYDER 2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open NAVJOTP2 to SNYDER 2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.26pu, MaxDur: 0.04s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_46_P1_RUSSELL4 | Apply 3-phase fault on LAKEP4WT to RUSSELL4 138kV line CKT 1, near RUSSELL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_46_P1_RUSSELL4 | Apply 3-phase fault on LAKEP4WT to RUSSELL4 138kV line CKT 1, near RUSSELL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_46_P1_RUSSELL4 | Apply 3-phase fault on LAKEP4WT to RUSSELL4 138kV line CKT 1, near RUSSELL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_46_P1_RUSSELL4 | Apply 3-phase fault on LAKEP4WT to RUSSELL4 138kV line CKT 1, near RUSSELL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_47_P1_RUSSELL4 | Apply 3-phase fault on ALTUSJT4 to RUSSELL4 138kV line CKT 1, near RUSSELL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_47_P1_RUSSELL4 | Apply 3-phase fault on ALTUSJT4 to RUSSELL4 138kV line CKT 1, near RUSSELL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_47_P1_RUSSELL4 | Apply 3-phase fault on ALTUSJT4 to RUSSELL4 138kV line CKT 1, near RUSSELL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_47_P1_RUSSELL4 | Apply 3-phase fault on ALTUSJT4 to RUSSELL4 138kV line CKT 1, near RUSSELL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_48_P1_SNYDER2 | Apply 3-phase fault on SNYDER 2 to TIPTONJ2 69kV line CKT 1, near SNYDER 2 69kV for 7 cycles. Open the faulted line and FREDRIK2 to HOLLSTR2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and FREDRIK2 to HOLLSTR2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open FREDRIK2 to HOLLSTR2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_48_P1_SNYDER2 | Apply 3-phase fault on SNYDER 2 to TIPTONJ2 69kV line CKT 1, near SNYDER 2 69kV for 7 cycles. Open the faulted line and FREDRIK2 to HOLLSTR2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and FREDRIK2 to HOLLSTR2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open FREDRIK2 to HOLLSTR2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_48_P1_SNYDER2 | Apply 3-phase fault on SNYDER 2 to TIPTONJ2 69kV line CKT 1, near SNYDER 2 69kV for 7 cycles. Open the faulted line and FREDRIK2 to HOLLSTR2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and FREDRIK2 to HOLLSTR2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open FREDRIK2 to HOLLSTR2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_48_P1_SNYDER2 | Apply 3-phase fault on SNYDER 2 to TIPTONJ2 69kV line CKT 1, near SNYDER 2 69kV for 7 cycles. Open the faulted line and FREDRIK2 to HOLLSTR2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and FREDRIK2 to HOLLSTR2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open FREDRIK2 to HOLLSTR2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_49_P1_SNYDER2 | Apply 3-phase fault on SNYDER 2 69kV/138kV/13.8kV transformer CKT 1, near SNYDER 2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_49_P1_SNYDER2 | Apply 3-phase fault on SNYDER 2 69kV/138kV/13.8kV transformer CKT 1, near SNYDER 2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_49_P1_SNYDER2 | Apply 3-phase fault on SNYDER 2 69kV/138kV/13.8kV transformer CKT 1, near SNYDER 2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_49_P1_SNYDER2 | Apply 3-phase fault on SNYDER 2 69kV/138kV/13.8kV transformer CKT 1, near SNYDER 2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_50_P1_SNYDER4 | Apply 3-phase fault on SNYDER 4 to CACHEJ4 138kV line CKT 1, near SNYDER 4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.30pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_50_P1_SNYDER4 | Apply 3-phase fault on SNYDER 4 to CACHEJ4 138kV line CKT 1, near SNYDER 4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.30pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_50_P1_SNYDER4 | Apply 3-phase fault on SNYDER 4 to CACHEJ4 138kV line CKT 1, near SNYDER 4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.28pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_50_P1_SNYDER4 | Apply 3-phase fault on SNYDER 4 to CACHEJ4 138kV line CKT 1, near SNYDER 4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.29pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_51_P1_VERNON2 | Apply 3-phase fault on LOCKETT2 to VERNON 2 69kV line CKT 1, near VERNON 2 69kV for 7 cycles. Open the faulted line and GUYER to HOLLSTR2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and GUYER to HOLLSTR2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open GUYER to HOLLSTR2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_51_P1_VERNON2 | Apply 3-phase fault on LOCKETT2 to VERNON 2 69kV line CKT 1, near VERNON 2 69kV for 7 cycles. Open the faulted line and GUYER to HOLLSTR2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and GUYER to HOLLSTR2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open GUYER to HOLLSTR2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_51_P1_VERNON2 | Apply 3-phase fault on LOCKETT2 to VERNON 2 69kV line CKT 1, near VERNON 2 69kV for 7 cycles. Open the faulted line and GUYER to HOLLSTR2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and GUYER to HOLLSTR2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open GUYER to HOLLSTR2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_51_P1_VERNON2 | Apply 3-phase fault on LOCKETT2 to VERNON 2 69kV line CKT 1, near VERNON 2 69kV for 7 cycles. Open the faulted line and GUYER to HOLLSTR2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and GUYER to HOLLSTR2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open GUYER to HOLLSTR2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_52_P1_VERNON2 | Apply 3-phase fault on VRNMTAP2 to VERNON 2 69kV line CKT 1, near VERNON 2 69kV for 7 cycles. Open the faulted line and TIPTE T2 to SNYDER-2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and TIPTE T2 to SNYDER-2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open TIPTE T2 to SNYDER-2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_52_P1_VERNON2 | Apply 3-phase fault on VRNMTAP2 to VERNON 2 69kV line CKT 1, near VERNON 2 69kV for 7 cycles. Open the faulted line and TIPTE T2 to SNYDER-2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and TIPTE T2 to SNYDER-2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open TIPTE T2 to SNYDER-2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_52_P1_VERNON2 | Apply 3-phase fault on VRNMTAP2 to VERNON 2 69kV line CKT 1, near VERNON 2 69kV for 7 cycles. Open the faulted line and TIPTE T2 to SNYDER-2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and TIPTE T2 to SNYDER-2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open TIPTE T2 to SNYDER-2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_52_P1_VERNON2 | Apply 3-phase fault on VRNMTAP2 to VERNON 2 69kV line CKT 1, near VERNON 2 69kV for 7 cycles. Open the faulted line and TIPTE T2 to SNYDER-2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and TIPTE T2 to SNYDER-2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open TIPTE T2 to SNYDER-2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_53_P1_CACHEJ4 | Apply 3-phase fault on CACHE4 to CACHEJ4 138kV line CKT 1, near CACHEJ4 138kV for 7 cycles. Open the faulted line and INDHOMA4 to GRNDFLD4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and INDHOMA4 to GRNDFLD4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open INDHOMA4 to GRNDFLD4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_53_P1_CACHEJ4 | Apply 3-phase fault on CACHE4 to CACHEJ4 138kV line CKT 1, near CACHEJ4 138kV for 7 cycles. Open the faulted line and INDHOMA4 to GRNDFLD4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and INDHOMA4 to GRNDFLD4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open INDHOMA4 to GRNDFLD4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_53_P1_CACHEJ4 | Apply 3-phase fault on CACHE4 to CACHEJ4 138kV line CKT 1, near CACHEJ4 138kV for 7 cycles. Open the faulted line and INDHOMA4 to GRNDFLD4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and INDHOMA4 to GRNDFLD4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open INDHOMA4 to GRNDFLD4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_53_P1_CACHEJ4 | Apply 3-phase fault on CACHE4 to CACHEJ4 138kV line CKT 1, near CACHEJ4 138kV for 7 cycles. Open the faulted line and INDHOMA4 to GRNDFLD4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and INDHOMA4 to GRNDFLD4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open INDHOMA4 to GRNDFLD4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_54_P1_CACHEJ4 | Apply 3-phase fault on MDCPRK4 to CACHEJ4 138kV line CKT 1, near CACHEJ4 138kV for 7 cycles. Open the faulted line and PARADSE4 to CHERRYRD 4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and PARADSE4 to CHERRYRD 4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open PARADSE4 to CHERRYRD 4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_54_P1_CACHEJ4 | Apply 3-phase fault on MDCPRK4 to CACHEJ4 138kV line CKT 1, near CACHEJ4 138kV for 7 cycles. Open the faulted line and PARADSE4 to CHERRYRD 4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and PARADSE4 to CHERRYRD 4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open PARADSE4 to CHERRYRD 4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_54_P1_CACHEJ4 | Apply 3-phase fault on MDCPRK4 to CACHEJ4 138kV line CKT 1, near CACHEJ4 138kV for 7 cycles. Open the faulted line and PARADSE4 to CHERRYRD 4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and PARADSE4 to CHERRYRD 4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open PARADSE4 to CHERRYRD 4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_54_P1_CACHEJ4 | Apply 3-phase fault on MDCPRK4 to CACHEJ4 138kV line CKT 1, near CACHEJ4 138kV for 7 cycles. Open the faulted line and PARADSE4 to CHERRYRD 4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and PARADSE4 to CHERRYRD 4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open PARADSE4 to CHERRYRD 4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_55_P1_OMMANGM2 | Apply 3-phase fault on GRANITE2 to OMMANGM2 69kV line CKT 1, near OMMANGM2 69kV for 7 cycles. Open the faulted line and GRANITE2 to LKCREEK2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and GRANITE2 to LKCREEK2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open GRANITE2 to LKCREEK2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_55_P1_OMMANGM2 | Apply 3-phase fault on GRANITE2 to OMMANGM2 69kV line CKT 1, near OMMANGM2 69kV for 7 cycles. Open the faulted line and GRANITE2 to LKCREEK2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and GRANITE2 to LKCREEK2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open GRANITE2 to LKCREEK2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.29pu, MaxDur: 0.05s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_55_P1_OMMANGM2 | Apply 3-phase fault on GRANITE2 to OMMANGM2 69kV line CKT 1, near OMMANGM2 69kV for 7 cycles. Open the faulted line and GRANITE2 to LKCREEK2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and GRANITE2 to LKCREEK2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open GRANITE2 to LKCREEK2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_55_P1_OMMANGM2 | Apply 3-phase fault on GRANITE2 to OMMANGM2 69kV line CKT 1, near OMMANGM2 69kV for 7 cycles. Open the faulted line and GRANITE2 to LKCREEK2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and GRANITE2 to LKCREEK2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open GRANITE2 to LKCREEK2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.30pu, MaxDur: 0.05s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_56_P1_G16-037-TAP | Apply 3-phase fault on GRACMNT7 to G16-037-TAP 345kV line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.54pu, MaxDur: 0.05s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_56_P1_G16-037-TAP | Apply 3-phase fault on GRACMNT7 to G16-037-TAP 345kV line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.55pu, MaxDur: 0.05s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_56_P1_G16-037-TAP | Apply 3-phase fault on GRACMNT7 to G16-037-TAP 345kV line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.54pu, MaxDur: 0.05s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_56_P1_G16-037-TAP | Apply 3-phase fault on GRACMNT7 to G16-037-TAP 345kV line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.53pu, MaxDur: 0.05s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_57_P1_G16-091-TAP | Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_57_P1_G16-091-TAP | Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_57_P1_G16-091-TAP | Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.29pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_57_P1_G16-091-TAP | Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.28pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_58_P1_G16-097-TAP | Apply 3-phase fault on S.W.S.-4 to G16-097-TAP 138kV line CKT 1, near G16-097-TAP 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_58_P1_G16-097-TAP | Apply 3-phase fault on S.W.S.-4 to G16-097-TAP 138kV line CKT 1, near G16-097-TAP 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_58_P1_G16-097-TAP | Apply 3-phase fault on S.W.S.-4 to G16-097-TAP 138kV line CKT 1, near G16-097-TAP 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_58_P1_G16-097-TAP | Apply 3-phase fault on S.W.S.-4 to G16-097-TAP 138kV line CKT 1, near G16-097-TAP 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_59_P1_TAP_G17-036 | Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV line CKT 1, near TAP_G17-036 138kV for 7 cycles. Open the faulted line and 112GORE4 to LAIRGST4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and 112GORE4 to LAIRGST4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open 112GORE4 to LAIRGST4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.40pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_59_P1_TAP_G17-036 | Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV line CKT 1, near TAP_G17-036 138kV for 7 cycles. Open the faulted line and 112GORE4 to LAIRGST4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and 112GORE4 to LAIRGST4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open 112GORE4 to LAIRGST4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.40pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_59_P1_TAP_G17-036 | Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV line CKT 1, near TAP_G17-036 138kV for 7 cycles. Open the faulted line and 112GORE4 to LAIRGST4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and 112GORE4 to LAIRGST4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open 112GORE4 to LAIRGST4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.35pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_59_P1_TAP_G17-036 | Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV line CKT 1, near TAP_G17-036 138kV for 7 cycles. Open the faulted line and 112GORE4 to LAIRGST4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and 112GORE4 to LAIRGST4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open 112GORE4 to LAIRGST4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.38pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_60_P1_TAP_G17-036 | Apply 3-phase fault on SNYDER-4 to TAP_G17-036 138kV line CKT 1, near TAP_G17-036 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.36pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_60_P1_TAP_G17-036 | Apply 3-phase fault on SNYDER-4 to TAP_G17-036 138kV line CKT 1, near TAP_G17-036 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.34pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_60_P1_TAP_G17-036 | Apply 3-phase fault on SNYDER-4 to TAP_G17-036 138kV line CKT 1, near TAP_G17-036 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.32pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_60_P1_TAP_G17-036 | Apply 3-phase fault on SNYDER-4 to TAP_G17-036 138kV line CKT 1, near TAP_G17-036 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.33pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_61_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_61_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_61_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_61_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_62_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_62_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_62_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_62_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_63_P1_WHEELER | Apply 3-phase fault on BORDER to TUCO_INT 345kV line CKT 1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line. Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection (due to size and location of the unit. No further simulation was peroformed)
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_63_P1_WHEELER | Apply 3-phase fault on BORDER to TUCO_INT 345kV line CKT 1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line. Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.21pu, MaxDur: 0.07s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_63_P1_WHEELER | Apply 3-phase fault on BORDER to TUCO_INT 345kV line CKT 1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line. Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection (due to size and location of the unit. No further simulation was peroformed)
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_63_P1_WHEELER | Apply 3-phase fault on BORDER to TUCO_INT 345kV line CKT 1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line. Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection (due to size and location of the unit. No further simulation was peroformed)
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_64_P1_SWEETWT6 | Apply 3-phase fault on BORDER to TUCO_INT 345kV line CKT 1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line. Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection (due to size and location of the unit. No further simulation was peroformed) Voltage spike observed : MaxV: 1.21pu, MaxDur: 0.01s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_64_P1_SWEETWT6 | Apply 3-phase fault on BORDER to TUCO_INT 345kV line CKT 1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line. Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.21pu, MaxDur: 0.07s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_64_P1_SWEETWT6 | Apply 3-phase fault on BORDER to TUCO_INT 345kV line CKT 1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line. Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection (due to size and location of the unit. No further simulation was peroformed)
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_64_P1_SWEETWT6 | Apply 3-phase fault on BORDER to TUCO_INT 345kV line CKT 1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line. Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection (due to size and location of the unit. No further simulation was peroformed)
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_65_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection (due to size and location of the unit. No further simulation was peroformed)
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_65_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_65_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection (due to size and location of the unit. No further simulation was peroformed) Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_65_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection (due to size and location of the unit. No further simulation was peroformed) Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_66_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_66_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_66_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_66_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_67_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection (due to size and location of the unit. No further simulation was peroformed)
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_67_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_67_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection (due to size and location of the unit. No further simulation was peroformed) Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_67_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection (due to size and location of the unit. No further simulation was peroformed) Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_68_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection (due to size and location of the unit. No further simulation was peroformed)
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_68_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_68_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection (due to size and location of the unit. No further simulation was peroformed) Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.00s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_68_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection (due to size and location of the unit. No further simulation was peroformed). Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.00s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_69_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.23pu, MaxDur: 0.02s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_69_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_69_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.26pu, MaxDur: 0.02s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_69_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.25pu, MaxDur: 0.02s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_70_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.31pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_70_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_70_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.33pu, MaxDur: 0.04s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_70_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.29pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_71_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_71_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_71_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_71_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_72_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.00s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_72_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.21pu, MaxDur: 0.02s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_72_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_72_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_73_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.21pu, MaxDur: 0.07s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_73_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_73_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_73_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_74_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.23pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_74_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.24pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_74_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.22pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_74_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_75_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.21pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_75_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_75_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.02s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_75_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.02s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_76_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.06s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_76_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_76_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.07s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_76_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_77_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.28pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_77_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_77_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.33pu, MaxDur: 0.04s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_77_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.32pu, MaxDur: 0.04s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_78_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_78_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_78_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_78_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_79_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_79_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_79_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.02s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_79_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_80_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.02s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_80_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_80_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.02s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_80_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.02s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_81_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_81_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_81_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed ; MaxV: 1.20pu, MaxDur: 0.06s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_81_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.06s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_82_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_82_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_82_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_82_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_83_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_83_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_83_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_83_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_84_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_84_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_84_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_84_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_85_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_85_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_85_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_85_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_86_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_86_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_86_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_86_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_87_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_87_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_87_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_87_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | 511939[OECGT1-1] & 511940[OECGT1-2] caused abnorml oscillations in both BC and TC for this contingency.
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_88_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_88_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_88_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.02s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_88_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.02s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_89_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_89_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_89_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_89_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_90_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_90_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_90_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_90_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_91_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_91_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_91_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | 511939[OECGT1-1,511940[OECGT1-2,511942[OECGT2-1 & 511943[OECGT2-2 caused abnormal oscillationss. The oscillationss were observed in BC and TC for this contingency.
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_91_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | 511939[OECGT1-1 &511940[OECGT1-2 caused abnormal oscillationss. The oscillationss were observed in BC and TC for this contingency.
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_92_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_92_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_92_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_92_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_93_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.02s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_93_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_93_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_93_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_94_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_94_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_94_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_94_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | 511939[OECGT1-1 &511940[OECGT1-2 caused abnormal oscillationss. The oscillationss were observed in BC and TC for this contingency.
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_95_P4_SNYDER-4 | Apply single-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted Three Winding and SNYDER-4 to ALTUSJT4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_95_P4_SNYDER-4 | Apply single-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted Three Winding and SNYDER-4 to ALTUSJT4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_95_P4_SNYDER-4 | Apply single-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted Three Winding and SNYDER-4 to ALTUSJT4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_95_P4_SNYDER-4 | Apply single-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted Three Winding and SNYDER-4 to ALTUSJT4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_96_P4_SNYDER-4 | Apply single-phase fault on SNYDER-4 to SNYDER 4 138kV line CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted line and SNYDRTER 13.8kV/138kV/69kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_96_P4_SNYDER-4 | Apply single-phase fault on SNYDER-4 to SNYDER 4 138kV line CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted line and SNYDRTER 13.8kV/138kV/69kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_96_P4_SNYDER-4 | Apply single-phase fault on SNYDER-4 to SNYDER 4 138kV line CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted line and SNYDRTER 13.8kV/138kV/69kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_96_P4_SNYDER-4 | Apply single-phase fault on SNYDER-4 to SNYDER 4 138kV line CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted line and SNYDRTER 13.8kV/138kV/69kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_97_P4_SNYDER-4 | Apply single-phase fault on SNYDER-4 to ALTUSJT4 138kV line CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted line and SNYDER-4 to SNYDER 4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_97_P4_SNYDER-4 | Apply single-phase fault on SNYDER-4 to ALTUSJT4 138kV line CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted line and SNYDER-4 to SNYDER 4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_97_P4_SNYDER-4 | Apply single-phase fault on SNYDER-4 to ALTUSJT4 138kV line CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted line and SNYDER-4 to SNYDER 4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_97_P4_SNYDER-4 | Apply single-phase fault on SNYDER-4 to ALTUSJT4 138kV line CKT 1, near SNYDER-4 138kV for 16 cycles with stuck breaker at SNYDER-4. Open the faulted line and SNYDER-4 to SNYDER 4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_98_P4_COMANC-4 | Apply single-phase fault on COMANC-4 to L.E.S.-4 138kV line CKT 1, near COMANC-4 138kV for 16 cycles with stuck breaker at COMANC-4. Open the faulted line and L.E.S.-4 to COMMTAP4 138kV line CKT 1 and DUNCAN-4 to OMDUNCN4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_98_P4_COMANC-4 | Apply single-phase fault on COMANC-4 to L.E.S.-4 138kV line CKT 1, near COMANC-4 138kV for 16 cycles with stuck breaker at COMANC-4. Open the faulted line and L.E.S.-4 to COMMTAP4 138kV line CKT 1 and DUNCAN-4 to OMDUNCN4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.21pu, MaxDur: 0.07s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_98_P4_COMANC-4 | Apply single-phase fault on COMANC-4 to L.E.S.-4 138kV line CKT 1, near COMANC-4 138kV for 16 cycles with stuck breaker at COMANC-4. Open the faulted line and L.E.S.-4 to COMMTAP4 138kV line CKT 1 and DUNCAN-4 to OMDUNCN4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_98_P4_COMANC-4 | Apply single-phase fault on COMANC-4 to L.E.S.-4 138kV line CKT 1, near COMANC-4 138kV for 16 cycles with stuck breaker at COMANC-4. Open the faulted line and L.E.S.-4 to COMMTAP4 138kV line CKT 1 and DUNCAN-4 to OMDUNCN4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_99_P4_ALTUSJT4 | Apply single-phase fault on ALTUSJT4 to RUSSELL4 138kV line CKT 1, near ALTUSJT4 138kV for 16 cycles with stuck breaker at ALTUSJT4. Open the faulted line and ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1 and HEADRIK2 to SNYDER-2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_99_P4_ALTUSJT4 | Apply single-phase fault on ALTUSJT4 to RUSSELL4 138kV line CKT 1, near ALTUSJT4 138kV for 16 cycles with stuck breaker at ALTUSJT4. Open the faulted line and ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1 and HEADRIK2 to SNYDER-2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_99_P4_ALTUSJT4 | Apply single-phase fault on ALTUSJT4 to RUSSELL4 138kV line CKT 1, near ALTUSJT4 138kV for 16 cycles with stuck breaker at ALTUSJT4. Open the faulted line and ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1 and HEADRIK2 to SNYDER-2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_99_P4_ALTUSJT4 | Apply single-phase fault on ALTUSJT4 to RUSSELL4 138kV line CKT 1, near ALTUSJT4 138kV for 16 cycles with stuck breaker at ALTUSJT4. Open the faulted line and ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1 and HEADRIK2 to SNYDER-2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_100_P4_ALTUSJT4 | Apply single-phase fault on ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1, near ALTUSJT4 138kV for 16 cycles with stuck breaker at ALTUSJT4. Open the faulted Three Winding and HEADRIK2 to SNYDER-2 69kV line CKT 1 and ALTUSJT4 to OMPARK-4 138kV line CKT 1 and HOB-JCT4 to MARTHA 4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_100_P4_ALTUSJT4 | Apply single-phase fault on ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1, near ALTUSJT4 138kV for 16 cycles with stuck breaker at ALTUSJT4. Open the faulted Three Winding and HEADRIK2 to SNYDER-2 69kV line CKT 1 and ALTUSJT4 to OMPARK-4 138kV line CKT 1 and HOB-JCT4 to MARTHA 4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_100_P4_ALTUSJT4 | Apply single-phase fault on ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1, near ALTUSJT4 138kV for 16 cycles with stuck breaker at ALTUSJT4. Open the faulted Three Winding and HEADRIK2 to SNYDER-2 69kV line CKT 1 and ALTUSJT4 to OMPARK-4 138kV line CKT 1 and HOB-JCT4 to MARTHA 4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_100_P4_ALTUSJT4 | Apply single-phase fault on ALTUS2-1 13.8kV/138kV/69kV transformer CKT 1, near ALTUSJT4 138kV for 16 cycles with stuck breaker at ALTUSJT4. Open the faulted Three Winding and HEADRIK2 to SNYDER-2 69kV line CKT 1 and ALTUSJT4 to OMPARK-4 138kV line CKT 1 and HOB-JCT4 to MARTHA 4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_101_P4_LES-4 | Apply single-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-4 138kV for 16 cycles with stuck breaker at L.E.S.-4. Open the faulted Three Winding and LES#4-1 13.8kV/138kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_101_P4_LES-4 | Apply single-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-4 138kV for 16 cycles with stuck breaker at L.E.S.-4. Open the faulted Three Winding and LES#4-1 13.8kV/138kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed :MaxV: 1.20pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_101_P4_LES-4 | Apply single-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-4 138kV for 16 cycles with stuck breaker at L.E.S.-4. Open the faulted Three Winding and LES#4-1 13.8kV/138kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_101_P4_LES-4 | Apply single-phase fault on LES#5-1 13.8kV/138kV/345kV transformer CKT 2, near L.E.S.-4 138kV for 16 cycles with stuck breaker at L.E.S.-4. Open the faulted Three Winding and LES#4-1 13.8kV/138kV/345kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_102_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted line and LES#5-1 13.8kV/138kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_102_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted line and LES#5-1 13.8kV/138kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_102_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted line and LES#5-1 13.8kV/138kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_102_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted line and LES#5-1 13.8kV/138kV/345kV transformer CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_103_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted line and O.K.U.-7 to L.E.S.-7 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_103_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted line and O.K.U.-7 to L.E.S.-7 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_103_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted line and O.K.U.-7 to L.E.S.-7 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_103_P4_LES-7 | Apply single-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted line and O.K.U.-7 to L.E.S.-7 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_104_P4_112GORE4 | Apply single-phase fault on 112GORE4 to RPPAPER4 138kV line CKT 1, near 112GORE4 138kV for 16 cycles with stuck breaker at 112GORE4. Open the faulted line and LWS-NTP4 to 112GORE4 138kV line CKT 1 and L.E.S.-4 to SHERID4 138kV line CKT 1 and LWSTAP 4 to L.E.S.-4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_104_P4_112GORE4 | Apply single-phase fault on 112GORE4 to RPPAPER4 138kV line CKT 1, near 112GORE4 138kV for 16 cycles with stuck breaker at 112GORE4. Open the faulted line and LWS-NTP4 to 112GORE4 138kV line CKT 1 and L.E.S.-4 to SHERID4 138kV line CKT 1 and LWSTAP 4 to L.E.S.-4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_104_P4_112GORE4 | Apply single-phase fault on 112GORE4 to RPPAPER4 138kV line CKT 1, near 112GORE4 138kV for 16 cycles with stuck breaker at 112GORE4. Open the faulted line and LWS-NTP4 to 112GORE4 138kV line CKT 1 and L.E.S.-4 to SHERID4 138kV line CKT 1 and LWSTAP 4 to L.E.S.-4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_104_P4_112GORE4 | Apply single-phase fault on 112GORE4 to RPPAPER4 138kV line CKT 1, near 112GORE4 138kV for 16 cycles with stuck breaker at 112GORE4. Open the faulted line and LWS-NTP4 to 112GORE4 138kV line CKT 1 and L.E.S.-4 to SHERID4 138kV line CKT 1 and LWSTAP 4 to L.E.S.-4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_105_P4_CHISHOLM6 | Apply single-phase fault on SWEETWT6 to CHISHOLM6 230kV line CKT 1, near CHISHOLM6 230kV for 16 cycles with stuck breaker at CHISHOLM6. Open the faulted line and ELKCITY6 to CHISHOLM6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_105_P4_CHISHOLM6 | Apply single-phase fault on SWEETWT6 to CHISHOLM6 230kV line CKT 1, near CHISHOLM6 230kV for 16 cycles with stuck breaker at CHISHOLM6. Open the faulted line and ELKCITY6 to CHISHOLM6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_105_P4_CHISHOLM6 | Apply single-phase fault on SWEETWT6 to CHISHOLM6 230kV line CKT 1, near CHISHOLM6 230kV for 16 cycles with stuck breaker at CHISHOLM6. Open the faulted line and ELKCITY6 to CHISHOLM6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_105_P4_CHISHOLM6 | Apply single-phase fault on SWEETWT6 to CHISHOLM6 230kV line CKT 1, near CHISHOLM6 230kV for 16 cycles with stuck breaker at CHISHOLM6. Open the faulted line and ELKCITY6 to CHISHOLM6 230kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_106_P4_CIMARON7 | Apply single-phase fault on CIMARON7 to DRAPER 7 345kV line CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted line and NORTWST7 to CIMARON7 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_106_P4_CIMARON7 | Apply single-phase fault on CIMARON7 to DRAPER 7 345kV line CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted line and NORTWST7 to CIMARON7 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_106_P4_CIMARON7 | Apply single-phase fault on CIMARON7 to DRAPER 7 345kV line CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted line and NORTWST7 to CIMARON7 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_106_P4_CIMARON7 | Apply single-phase fault on CIMARON7 to DRAPER 7 345kV line CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted line and NORTWST7 to CIMARON7 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_107_P4_CIMARON7 | Apply single-phase fault on CIMARON4 138kV/345kV/13.8kV transformer CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted Three Winding and CIMARON4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_107_P4_CIMARON7 | Apply single-phase fault on CIMARON4 138kV/345kV/13.8kV transformer CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted Three Winding and CIMARON4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_107_P4_CIMARON7 | Apply single-phase fault on CIMARON4 138kV/345kV/13.8kV transformer CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted Three Winding and CIMARON4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_107_P4_CIMARON7 | Apply single-phase fault on CIMARON4 138kV/345kV/13.8kV transformer CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted Three Winding and CIMARON4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_108_P4_CIMARON7 | Apply single-phase fault on CIMARON7 to MATHWSN7 345kV line CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted line and CIMARON7 to MATHWSN7 345kV line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_108_P4_CIMARON7 | Apply single-phase fault on CIMARON7 to MATHWSN7 345kV line CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted line and CIMARON7 to MATHWSN7 345kV line CKT 2 and clear the fault. | P4 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_108_P4_CIMARON7 | Apply single-phase fault on CIMARON7 to MATHWSN7 345kV line CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted line and CIMARON7 to MATHWSN7 345kV line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_108_P4_CIMARON7 | Apply single-phase fault on CIMARON7 to MATHWSN7 345kV line CKT 1, near CIMARON7 345kV for 16 cycles with stuck breaker at CIMARON7. Open the faulted line and CIMARON7 to MATHWSN7 345kV line CKT 2 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_109_P4_GRACMNT7 | Apply single-phase fault on MINCO to GRACMNT7 345kV line CKT 1, near GRACMNT7 345kV for 16 cycles with stuck breaker at GRACMNT7. Open the faulted line and GRACMNT7 345kV/13.8kV/138kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.02s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_109_P4_GRACMNT7 | Apply single-phase fault on MINCO to GRACMNT7 345kV line CKT 1, near GRACMNT7 345kV for 16 cycles with stuck breaker at GRACMNT7. Open the faulted line and GRACMNT7 345kV/13.8kV/138kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_109_P4_GRACMNT7 | Apply single-phase fault on MINCO to GRACMNT7 345kV line CKT 1, near GRACMNT7 345kV for 16 cycles with stuck breaker at GRACMNT7. Open the faulted line and GRACMNT7 345kV/13.8kV/138kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_109_P4_GRACMNT7 | Apply single-phase fault on MINCO to GRACMNT7 345kV line CKT 1, near GRACMNT7 345kV for 16 cycles with stuck breaker at GRACMNT7. Open the faulted line and GRACMNT7 345kV/13.8kV/138kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_110_P4_GRACMNT4 | Apply single-phase fault on GRACMNT4 to ANADARK4 138kV line CKT 1, near GRACMNT4 138kV for 16 cycles with stuck breaker at GRACMNT4. Open the faulted line and GRACMNT4 to WASHITA4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_110_P4_GRACMNT4 | Apply single-phase fault on GRACMNT4 to ANADARK4 138kV line CKT 1, near GRACMNT4 138kV for 16 cycles with stuck breaker at GRACMNT4. Open the faulted line and GRACMNT4 to WASHITA4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_110_P4_GRACMNT4 | Apply single-phase fault on GRACMNT4 to ANADARK4 138kV line CKT 1, near GRACMNT4 138kV for 16 cycles with stuck breaker at GRACMNT4. Open the faulted line and GRACMNT4 to WASHITA4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_110_P4_GRACMNT4 | Apply single-phase fault on GRACMNT4 to ANADARK4 138kV line CKT 1, near GRACMNT4 138kV for 16 cycles with stuck breaker at GRACMNT4. Open the faulted line and GRACMNT4 to WASHITA4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.05s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_111_P4_LKCREEK2 | Apply single-phase fault on LKCREEK2 to LONEWLF2 69kV line CKT 1, near LKCREEK2 69kV for 16 cycles with stuck breaker at LKCREEK2. Open the faulted line and GOTEBO 2 to LONEWLF2 69kV line CKT 1 and CARTERJ2 to LKCREEK2 69kV line CKT 1 and ELKCTY-2 to ELKCITY2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_111_P4_LKCREEK2 | Apply single-phase fault on LKCREEK2 to LONEWLF2 69kV line CKT 1, near LKCREEK2 69kV for 16 cycles with stuck breaker at LKCREEK2. Open the faulted line and GOTEBO 2 to LONEWLF2 69kV line CKT 1 and CARTERJ2 to LKCREEK2 69kV line CKT 1 and ELKCTY-2 to ELKCITY2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_111_P4_LKCREEK2 | Apply single-phase fault on LKCREEK2 to LONEWLF2 69kV line CKT 1, near LKCREEK2 69kV for 16 cycles with stuck breaker at LKCREEK2. Open the faulted line and GOTEBO 2 to LONEWLF2 69kV line CKT 1 and CARTERJ2 to LKCREEK2 69kV line CKT 1 and ELKCTY-2 to ELKCITY2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_111_P4_LKCREEK2 | Apply single-phase fault on LKCREEK2 to LONEWLF2 69kV line CKT 1, near LKCREEK2 69kV for 16 cycles with stuck breaker at LKCREEK2. Open the faulted line and GOTEBO 2 to LONEWLF2 69kV line CKT 1 and CARTERJ2 to LKCREEK2 69kV line CKT 1 and ELKCTY-2 to ELKCITY2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_112_P4_RUSSELL2 | Apply single-phase fault on ALTUS_ 2 to RUSSELL2 69kV line CKT 1, near RUSSELL2 69kV for 16 cycles with stuck breaker at RUSSELL2. Open the faulted line and RUSSELL2 to VERNON 2 69kV line CKT 1 and NAVJOTP2 to SNYDER 2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_112_P4_RUSSELL2 | Apply single-phase fault on ALTUS_ 2 to RUSSELL2 69kV line CKT 1, near RUSSELL2 69kV for 16 cycles with stuck breaker at RUSSELL2. Open the faulted line and RUSSELL2 to VERNON 2 69kV line CKT 1 and NAVJOTP2 to SNYDER 2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_112_P4_RUSSELL2 | Apply single-phase fault on ALTUS_ 2 to RUSSELL2 69kV line CKT 1, near RUSSELL2 69kV for 16 cycles with stuck breaker at RUSSELL2. Open the faulted line and RUSSELL2 to VERNON 2 69kV line CKT 1 and NAVJOTP2 to SNYDER 2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_112_P4_RUSSELL2 | Apply single-phase fault on ALTUS_ 2 to RUSSELL2 69kV line CKT 1, near RUSSELL2 69kV for 16 cycles with stuck breaker at RUSSELL2. Open the faulted line and RUSSELL2 to VERNON 2 69kV line CKT 1 and NAVJOTP2 to SNYDER 2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_113_P4_RUSSELL2 | Apply single-phase fault on ALTUS_ 2 to RUSSELL2 69kV line CKT 1, near RUSSELL2 69kV for 16 cycles with stuck breaker at RUSSELL2. Open the faulted line and NAVJOTP2 to SNYDER 2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_113_P4_RUSSELL2 | Apply single-phase fault on ALTUS_ 2 to RUSSELL2 69kV line CKT 1, near RUSSELL2 69kV for 16 cycles with stuck breaker at RUSSELL2. Open the faulted line and NAVJOTP2 to SNYDER 2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_113_P4_RUSSELL2 | Apply single-phase fault on ALTUS_ 2 to RUSSELL2 69kV line CKT 1, near RUSSELL2 69kV for 16 cycles with stuck breaker at RUSSELL2. Open the faulted line and NAVJOTP2 to SNYDER 2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_113_P4_RUSSELL2 | Apply single-phase fault on ALTUS_ 2 to RUSSELL2 69kV line CKT 1, near RUSSELL2 69kV for 16 cycles with stuck breaker at RUSSELL2. Open the faulted line and NAVJOTP2 to SNYDER 2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_114_P4_RUSSELL2 | Apply single-phase fault on DUKE to RUSSELL2 69kV line CKT Z1, near RUSSELL2 69kV for 16 cycles with stuck breaker at RUSSELL2. Open the faulted line and LAKEP2WT to ELDORDO2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_114_P4_RUSSELL2 | Apply single-phase fault on DUKE to RUSSELL2 69kV line CKT Z1, near RUSSELL2 69kV for 16 cycles with stuck breaker at RUSSELL2. Open the faulted line and LAKEP2WT to ELDORDO2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_114_P4_RUSSELL2 | Apply single-phase fault on DUKE to RUSSELL2 69kV line CKT Z1, near RUSSELL2 69kV for 16 cycles with stuck breaker at RUSSELL2. Open the faulted line and LAKEP2WT to ELDORDO2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_114_P4_RUSSELL2 | Apply single-phase fault on DUKE to RUSSELL2 69kV line CKT Z1, near RUSSELL2 69kV for 16 cycles with stuck breaker at RUSSELL2. Open the faulted line and LAKEP2WT to ELDORDO2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_115_P4_SNYDER2 | Apply single-phase fault on SNYDER 2 to TIPTONJ2 69kV line CKT 1, near SNYDER 2 69kV for 16 cycles with stuck breaker at SNYDER 2. Open the faulted line and FREDRIK2 to HOLLSTR2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_115_P4_SNYDER2 | Apply single-phase fault on SNYDER 2 to TIPTONJ2 69kV line CKT 1, near SNYDER 2 69kV for 16 cycles with stuck breaker at SNYDER 2. Open the faulted line and FREDRIK2 to HOLLSTR2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_115_P4_SNYDER2 | Apply single-phase fault on SNYDER 2 to TIPTONJ2 69kV line CKT 1, near SNYDER 2 69kV for 16 cycles with stuck breaker at SNYDER 2. Open the faulted line and FREDRIK2 to HOLLSTR2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_115_P4_SNYDER2 | Apply single-phase fault on SNYDER 2 to TIPTONJ2 69kV line CKT 1, near SNYDER 2 69kV for 16 cycles with stuck breaker at SNYDER 2. Open the faulted line and FREDRIK2 to HOLLSTR2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_116_P4_VERNON2 | Apply single-phase fault on LOCKETT2 to VERNON 2 69kV line CKT 1, near VERNON 2 69kV for 16 cycles with stuck breaker at VERNON 2. Open the faulted line and VRNMTAP2 to VERNON 2 69kV line CKT 1 and GUYER to HOLLSTR2 69kV line CKT 1 and TIPTE T2 to SNYDER-2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_116_P4_VERNON2 | Apply single-phase fault on LOCKETT2 to VERNON 2 69kV line CKT 1, near VERNON 2 69kV for 16 cycles with stuck breaker at VERNON 2. Open the faulted line and VRNMTAP2 to VERNON 2 69kV line CKT 1 and GUYER to HOLLSTR2 69kV line CKT 1 and TIPTE T2 to SNYDER-2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_116_P4_VERNON2 | Apply single-phase fault on LOCKETT2 to VERNON 2 69kV line CKT 1, near VERNON 2 69kV for 16 cycles with stuck breaker at VERNON 2. Open the faulted line and VRNMTAP2 to VERNON 2 69kV line CKT 1 and GUYER to HOLLSTR2 69kV line CKT 1 and TIPTE T2 to SNYDER-2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_116_P4_VERNON2 | Apply single-phase fault on LOCKETT2 to VERNON 2 69kV line CKT 1, near VERNON 2 69kV for 16 cycles with stuck breaker at VERNON 2. Open the faulted line and VRNMTAP2 to VERNON 2 69kV line CKT 1 and GUYER to HOLLSTR2 69kV line CKT 1 and TIPTE T2 to SNYDER-2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_117_P4_SNYDTERT | Apply single-phase fault on SNYDER 4 to CACHEJ4 138kV line CKT 1, near SNYDTERT 13.8kV for 16 cycles with stuck breaker at SNYDTERT. Open the faulted line and SNYDER 2 69kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_117_P4_SNYDTERT | Apply single-phase fault on SNYDER 4 to CACHEJ4 138kV line CKT 1, near SNYDTERT 13.8kV for 16 cycles with stuck breaker at SNYDTERT. Open the faulted line and SNYDER 2 69kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_117_P4_SNYDTERT | Apply single-phase fault on SNYDER 4 to CACHEJ4 138kV line CKT 1, near SNYDTERT 13.8kV for 16 cycles with stuck breaker at SNYDTERT. Open the faulted line and SNYDER 2 69kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_117_P4_SNYDTERT | Apply single-phase fault on SNYDER 4 to CACHEJ4 138kV line CKT 1, near SNYDTERT 13.8kV for 16 cycles with stuck breaker at SNYDTERT. Open the faulted line and SNYDER 2 69kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_118_P6_SNYDER-4 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV line CKT 1Apply 3-phase fault on SNYDER-4 to SNYDER 4 138kV line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.30pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_118_P6_SNYDER-4 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV line CKT 1Apply 3-phase fault on SNYDER-4 to SNYDER 4 138kV line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.31pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_118_P6_SNYDER-4 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV line CKT 1Apply 3-phase fault on SNYDER-4 to SNYDER 4 138kV line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.30pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_118_P6_SNYDER-4 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV line CKT 1Apply 3-phase fault on SNYDER-4 to SNYDER 4 138kV line CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.30pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_119_P6_SNYDER-4 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV line CKT 1Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.33pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_119_P6_SNYDER-4 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV line CKT 1Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.34pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_119_P6_SNYDER-4 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV line CKT 1Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.30pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_119_P6_SNYDER-4 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV line CKT 1Apply 3-phase fault on SNYDRTER 13.8kV/138kV/69kV transformer CKT 1, near SNYDER-4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.28pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_120_P6_COMANC-4 | Prior Outage of COMANC-4 to L.E.S.-4 138kV line CKT 1Apply 3-phase fault on L.E.S.-4 to COMMTAP4 138kV line CKT 1, near COMANC-4 138kV for 7 cycles. Open the faulted line and COMANC-4 to COMMTAP4 138kV line CKT 1 and DUNCAN-4 to OMDUNCN4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and COMANC-4 to COMMTAP4 138kV line CKT 1 and DUNCAN-4 to OMDUNCN4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open COMANC-4 to COMMTAP4 138kV line CKT 1. Simultaneously re-open DUNCAN-4 to OMDUNCN4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_120_P6_COMANC-4 | Prior Outage of COMANC-4 to L.E.S.-4 138kV line CKT 1Apply 3-phase fault on L.E.S.-4 to COMMTAP4 138kV line CKT 1, near COMANC-4 138kV for 7 cycles. Open the faulted line and COMANC-4 to COMMTAP4 138kV line CKT 1 and DUNCAN-4 to OMDUNCN4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and COMANC-4 to COMMTAP4 138kV line CKT 1 and DUNCAN-4 to OMDUNCN4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open COMANC-4 to COMMTAP4 138kV line CKT 1. Simultaneously re-open DUNCAN-4 to OMDUNCN4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_120_P6_COMANC-4 | Prior Outage of COMANC-4 to L.E.S.-4 138kV line CKT 1Apply 3-phase fault on L.E.S.-4 to COMMTAP4 138kV line CKT 1, near COMANC-4 138kV for 7 cycles. Open the faulted line and COMANC-4 to COMMTAP4 138kV line CKT 1 and DUNCAN-4 to OMDUNCN4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and COMANC-4 to COMMTAP4 138kV line CKT 1 and DUNCAN-4 to OMDUNCN4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open COMANC-4 to COMMTAP4 138kV line CKT 1. Simultaneously re-open DUNCAN-4 to OMDUNCN4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_120_P6_COMANC-4 | Prior Outage of COMANC-4 to L.E.S.-4 138kV line CKT 1Apply 3-phase fault on L.E.S.-4 to COMMTAP4 138kV line CKT 1, near COMANC-4 138kV for 7 cycles. Open the faulted line and COMANC-4 to COMMTAP4 138kV line CKT 1 and DUNCAN-4 to OMDUNCN4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and COMANC-4 to COMMTAP4 138kV line CKT 1 and DUNCAN-4 to OMDUNCN4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open COMANC-4 to COMMTAP4 138kV line CKT 1. Simultaneously re-open DUNCAN-4 to OMDUNCN4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_121_P6_112GORE4 | Prior Outage of SNYDER-4 to TAP_G17-036 138kV line CKT 1Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV line CKT 1, near 112GORE4 138kV for 7 cycles. Open the faulted line and LWSTAP 4 to L.E.S.-4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and LWSTAP 4 to L.E.S.-4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.40pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_121_P6_112GORE4 | Prior Outage of SNYDER-4 to TAP_G17-036 138kV line CKT 1Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV line CKT 1, near 112GORE4 138kV for 7 cycles. Open the faulted line and LWSTAP 4 to L.E.S.-4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and LWSTAP 4 to L.E.S.-4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.43pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_121_P6_112GORE4 | Prior Outage of SNYDER-4 to TAP_G17-036 138kV line CKT 1Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV line CKT 1, near 112GORE4 138kV for 7 cycles. Open the faulted line and LWSTAP 4 to L.E.S.-4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and LWSTAP 4 to L.E.S.-4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.36pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_121_P6_112GORE4 | Prior Outage of SNYDER-4 to TAP_G17-036 138kV line CKT 1Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV line CKT 1, near 112GORE4 138kV for 7 cycles. Open the faulted line and LWSTAP 4 to L.E.S.-4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and LWSTAP 4 to L.E.S.-4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.42pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_122_P6_112GORE4 | Prior Outage of COMANC-4 to 112GORE4 138kV line CKT 1Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV line CKT 1, near 112GORE4 138kV for 7 cycles. Open the faulted line and LWSTAP 4 to L.E.S.-4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and LWSTAP 4 to L.E.S.-4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.21pu, MaxDur: 0.02s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_122_P6_112GORE4 | Prior Outage of COMANC-4 to 112GORE4 138kV line CKT 1Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV line CKT 1, near 112GORE4 138kV for 7 cycles. Open the faulted line and LWSTAP 4 to L.E.S.-4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and LWSTAP 4 to L.E.S.-4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.21pu, MaxDur: 0.02s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_122_P6_112GORE4 | Prior Outage of COMANC-4 to 112GORE4 138kV line CKT 1Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV line CKT 1, near 112GORE4 138kV for 7 cycles. Open the faulted line and LWSTAP 4 to L.E.S.-4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and LWSTAP 4 to L.E.S.-4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_122_P6_112GORE4 | Prior Outage of COMANC-4 to 112GORE4 138kV line CKT 1Apply 3-phase fault on 112GORE4 to RPPAPER4 138kV line CKT 1, near 112GORE4 138kV for 7 cycles. Open the faulted line and LWSTAP 4 to L.E.S.-4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and LWSTAP 4 to L.E.S.-4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open LWSTAP 4 to L.E.S.-4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_123_P6_112GORE4 | Prior Outage of LWS-NTP4 to 112GORE4 138kV line CKT 1Prior Outage of L.E.S.-4 to SHERID4 138kV line CKT 1Apply 3-phase fault on COMANC-4 to 112GORE4 138kV line CKT 1, near 112GORE4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed :MaxV: 1.21pu, MaxDur: 0.02s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_123_P6_112GORE4 | Prior Outage of LWS-NTP4 to 112GORE4 138kV line CKT 1Prior Outage of L.E.S.-4 to SHERID4 138kV line CKT 1Apply 3-phase fault on COMANC-4 to 112GORE4 138kV line CKT 1, near 112GORE4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Vltage spike observed : MaxV: 1.21pu, MaxDur: 0.02s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_123_P6_112GORE4 | Prior Outage of LWS-NTP4 to 112GORE4 138kV line CKT 1Prior Outage of L.E.S.-4 to SHERID4 138kV line CKT 1Apply 3-phase fault on COMANC-4 to 112GORE4 138kV line CKT 1, near 112GORE4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.02s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_123_P6_112GORE4 | Prior Outage of LWS-NTP4 to 112GORE4 138kV line CKT 1Prior Outage of L.E.S.-4 to SHERID4 138kV line CKT 1Apply 3-phase fault on COMANC-4 to 112GORE4 138kV line CKT 1, near 112GORE4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_124_P6_112GORE4 | Prior Outage of 112GORE4 to RPPAPER4 138kV line CKT 1Prior Outage of LWSTAP 4 to L.E.S.-4 138kV line CKT 1Apply 3-phase fault on LWS-NTP4 to 112GORE4 138kV line CKT 1, near 112GORE4 138kV for 7 cycles. Open the faulted line and L.E.S.-4 to SHERID4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and L.E.S.-4 to SHERID4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open L.E.S.-4 to SHERID4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed :MaxV: 1.21pu, MaxDur: 0.02s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_124_P6_112GORE4 | Prior Outage of 112GORE4 to RPPAPER4 138kV line CKT 1Prior Outage of LWSTAP 4 to L.E.S.-4 138kV line CKT 1Apply 3-phase fault on LWS-NTP4 to 112GORE4 138kV line CKT 1, near 112GORE4 138kV for 7 cycles. Open the faulted line and L.E.S.-4 to SHERID4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and L.E.S.-4 to SHERID4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open L.E.S.-4 to SHERID4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.21pu, MaxDur: 0.02s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_124_P6_112GORE4 | Prior Outage of 112GORE4 to RPPAPER4 138kV line CKT 1Prior Outage of LWSTAP 4 to L.E.S.-4 138kV line CKT 1Apply 3-phase fault on LWS-NTP4 to 112GORE4 138kV line CKT 1, near 112GORE4 138kV for 7 cycles. Open the faulted line and L.E.S.-4 to SHERID4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and L.E.S.-4 to SHERID4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open L.E.S.-4 to SHERID4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.02s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_124_P6_112GORE4 | Prior Outage of 112GORE4 to RPPAPER4 138kV line CKT 1Prior Outage of LWSTAP 4 to L.E.S.-4 138kV line CKT 1Apply 3-phase fault on LWS-NTP4 to 112GORE4 138kV line CKT 1, near 112GORE4 138kV for 7 cycles. Open the faulted line and L.E.S.-4 to SHERID4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and L.E.S.-4 to SHERID4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open L.E.S.-4 to SHERID4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_125_P6_CHISHOLM7 | Prior Outage of MINCO to CIMARON7 345kV line CKT 1Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.43pu, MaxDur: 0.04s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_125_P6_CHISHOLM7 | Prior Outage of MINCO to CIMARON7 345kV line CKT 1Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.44pu, MaxDur: 0.04s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_125_P6_CHISHOLM7 | Prior Outage of MINCO to CIMARON7 345kV line CKT 1Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.43pu, MaxDur: 0.05s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_125_P6_CHISHOLM7 | Prior Outage of MINCO to CIMARON7 345kV line CKT 1Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.42pu, MaxDur: 0.04s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_126_P6_CHISHOLM7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV line CKT 1Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.40pu, MaxDur: 0.04s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_126_P6_CHISHOLM7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV line CKT 1Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.40pu, MaxDur: 0.04s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_126_P6_CHISHOLM7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV line CKT 1Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.39pu, MaxDur: 0.04s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_126_P6_CHISHOLM7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV line CKT 1Apply 3-phase fault on CHISHOLM7 345kV/230kV/13.19kV transformer CKT 1, near CHISHOLM7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.38pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_127_P6_CIMARON7 | Prior Outage of NORTWST7 to CIMARON7 345kV line CKT 1Apply 3-phase fault on CIMARON7 to DRAPER 7 345kV line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed :MaxV: 1.21pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_127_P6_CIMARON7 | Prior Outage of NORTWST7 to CIMARON7 345kV line CKT 1Apply 3-phase fault on CIMARON7 to DRAPER 7 345kV line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_127_P6_CIMARON7 | Prior Outage of NORTWST7 to CIMARON7 345kV line CKT 1Apply 3-phase fault on CIMARON7 to DRAPER 7 345kV line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.04s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_127_P6_CIMARON7 | Prior Outage of NORTWST7 to CIMARON7 345kV line CKT 1Apply 3-phase fault on CIMARON7 to DRAPER 7 345kV line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.04s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_128_P6_GRACMNT7 | Prior Outage of MINCO to CIMARON7 345kV line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.44pu, MaxDur: 0.05s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_128_P6_GRACMNT7 | Prior Outage of MINCO to CIMARON7 345kV line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_128_P6_GRACMNT7 | Prior Outage of MINCO to CIMARON7 345kV line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.42pu, MaxDur: 0.05s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_128_P6_GRACMNT7 | Prior Outage of MINCO to CIMARON7 345kV line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.42pu, MaxDur: 0.05s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_129_P6_GRACMNT7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_129_P6_GRACMNT7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_129_P6_GRACMNT7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.39pu, MaxDur: 0.04s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_129_P6_GRACMNT7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.38pu, MaxDur: 0.04s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_130_P6_GRACMNT7 | Prior Outage of MINCO to GRACMNT7 345kV line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | No | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_130_P6_GRACMNT7 | Prior Outage of MINCO to GRACMNT7 345kV line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.40pu, MaxDur: 0.30s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_130_P6_GRACMNT7 | Prior Outage of MINCO to GRACMNT7 345kV line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.41pu, MaxDur: 0.04s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_130_P6_GRACMNT7 | Prior Outage of MINCO to GRACMNT7 345kV line CKT 1Apply 3-phase fault on GRACMNT7 345kV/13.8kV/138kV transformer CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.40pu, MaxDur: 0.04s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_131_P6_GRACMNT7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV line CKT 1Apply 3-phase fault on MINCO to GRACMNT7 345kV line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | No | Yes | No | Yes | 520519[BCI WTG, 520520[BCII WTG & 520522[BCVI_WTG1 caused abnormal oscillationss in BC and TC. When these units are GNETed and the simulation is repeated, the oscillations subsided Voltage spike observed : MaxV: 1.40pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_131_P6_GRACMNT7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV line CKT 1Apply 3-phase fault on MINCO to GRACMNT7 345kV line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | No | Yes | No | Yes | 520519[BCI WTG, 520520[BCII WTG & 520522[BCVI_WTG1 caused abnormal oscillationss in BC and TC. When these units are GNETed and the simulation is repeated, the oscillationss subside. Voltage spike observd : MaxV: 1.39pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_131_P6_GRACMNT7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV line CKT 1Apply 3-phase fault on MINCO to GRACMNT7 345kV line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | 520519[BCI WTG, 520520[BCII WTG & 520522[BCVI_WTG1 caused abnormal oscillationss in TC. When these units are GNETed and the simulation is repeated, the oscillationss subside. Voltage spike observed :MaxV: 1.36pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_131_P6_GRACMNT7 | Prior Outage of L.E.S.-7 to G16-091-TAP 345kV line CKT 1Apply 3-phase fault on MINCO to GRACMNT7 345kV line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | No | Yes | No | Yes | 520519[BCI WTG, 520520[BCII WTG & 520522[BCVI_WTG1 caused abnormal oscillationss in TC. When these units are GNETed and the simulation is repeated, the oscillationss subside. Voltage spike observed :MaxV: 1.34pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_132_P6_RUSSELL2 | Prior Outage of DUKE to RUSSELL2 69kV line CKT Z1Prior Outage of LAKEP2WT to ELDORDO2 69kV line CKT 1Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed :MaxV: 1.26pu, MaxDur: 0.04s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_132_P6_RUSSELL2 | Prior Outage of DUKE to RUSSELL2 69kV line CKT Z1Prior Outage of LAKEP2WT to ELDORDO2 69kV line CKT 1Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.27pu, MaxDur: 0.05s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_132_P6_RUSSELL2 | Prior Outage of DUKE to RUSSELL2 69kV line CKT Z1Prior Outage of LAKEP2WT to ELDORDO2 69kV line CKT 1Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Vltage spike observed : MaxV: 1.26pu, MaxDur: 0.04s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_132_P6_RUSSELL2 | Prior Outage of DUKE to RUSSELL2 69kV line CKT Z1Prior Outage of LAKEP2WT to ELDORDO2 69kV line CKT 1Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Vltage spike observed : MaxV: 1.26pu, MaxDur: 0.04s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_133_P6_RUSSELL2 | Prior Outage of GRANITE2 to OMMANGM2 69kV line CKT 1Prior Outage of GRANITE2 to LKCREEK2 69kV line CKT 1Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.27pu, MaxDur: 0.05s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_133_P6_RUSSELL2 | Prior Outage of GRANITE2 to OMMANGM2 69kV line CKT 1Prior Outage of GRANITE2 to LKCREEK2 69kV line CKT 1Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.33pu, MaxDur: 0.05s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_133_P6_RUSSELL2 | Prior Outage of GRANITE2 to OMMANGM2 69kV line CKT 1Prior Outage of GRANITE2 to LKCREEK2 69kV line CKT 1Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.36pu, MaxDur: 0.05s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_133_P6_RUSSELL2 | Prior Outage of GRANITE2 to OMMANGM2 69kV line CKT 1Prior Outage of GRANITE2 to LKCREEK2 69kV line CKT 1Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.25pu, MaxDur: 0.04s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_134_P6_RUSSELL2 | Prior Outage of DUKE to RUSSELL2 69kV line CKT Z1Prior Outage of LAKEP2WT to ELDORDO2 69kV line CKT 1Apply 3-phase fault on RUSSELL2 to VERNON 2 69kV line CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.26pu, MaxDur: 0.04s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_134_P6_RUSSELL2 | Prior Outage of DUKE to RUSSELL2 69kV line CKT Z1Prior Outage of LAKEP2WT to ELDORDO2 69kV line CKT 1Apply 3-phase fault on RUSSELL2 to VERNON 2 69kV line CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.25pu, MaxDur: 0.04s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_134_P6_RUSSELL2 | Prior Outage of DUKE to RUSSELL2 69kV line CKT Z1Prior Outage of LAKEP2WT to ELDORDO2 69kV line CKT 1Apply 3-phase fault on RUSSELL2 to VERNON 2 69kV line CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.26pu, MaxDur: 0.04s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_134_P6_RUSSELL2 | Prior Outage of DUKE to RUSSELL2 69kV line CKT Z1Prior Outage of LAKEP2WT to ELDORDO2 69kV line CKT 1Apply 3-phase fault on RUSSELL2 to VERNON 2 69kV line CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.27pu, MaxDur: 0.04s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_135_P6_RUSSELL2 | Prior Outage of ALTUS_ 2 to RUSSELL2 69kV line CKT 1Prior Outage of NAVJOTP2 to SNYDER 2 69kV line CKT 1Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.26pu, MaxDur: 0.04s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_135_P6_RUSSELL2 | Prior Outage of ALTUS_ 2 to RUSSELL2 69kV line CKT 1Prior Outage of NAVJOTP2 to SNYDER 2 69kV line CKT 1Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.27pu, MaxDur: 0.04s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_135_P6_RUSSELL2 | Prior Outage of ALTUS_ 2 to RUSSELL2 69kV line CKT 1Prior Outage of NAVJOTP2 to SNYDER 2 69kV line CKT 1Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.25pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_135_P6_RUSSELL2 | Prior Outage of ALTUS_ 2 to RUSSELL2 69kV line CKT 1Prior Outage of NAVJOTP2 to SNYDER 2 69kV line CKT 1Apply 3-phase fault on RUSSELL2 69kV/138kV/13.8kV transformer CKT 1, near RUSSELL2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.25pu, MaxDur: 0.04s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_136_P6_G16-037-TAP | Prior Outage of SWEETWT6 to CHISHOLM6 230kV line CKT 1Apply 3-phase fault on GRACMNT7 to G16-037-TAP 345kV line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | No | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_136_P6_G16-037-TAP | Prior Outage of SWEETWT6 to CHISHOLM6 230kV line CKT 1Apply 3-phase fault on GRACMNT7 to G16-037-TAP 345kV line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | No | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_136_P6_G16-037-TAP | Prior Outage of SWEETWT6 to CHISHOLM6 230kV line CKT 1Apply 3-phase fault on GRACMNT7 to G16-037-TAP 345kV line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | No | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_136_P6_G16-037-TAP | Prior Outage of SWEETWT6 to CHISHOLM6 230kV line CKT 1Apply 3-phase fault on GRACMNT7 to G16-037-TAP 345kV line CKT 1, near G16-037-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | No | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_137_P6_G16-091-TAP | Prior Outage of MINCO to CIMARON7 345kV line CKT 1Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | No | Yes | No | Yes | 520519[BCI WTG, 520520[BCII WTG & 520522[BCVI_WTG1 caused abnormal oscillationss in TC. When these units are GNETed and the simulation is repeated, the oscillationss subside. Voltage spike observed : MaxV: 1.36pu, MaxDur: 0.04s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_137_P6_G16-091-TAP | Prior Outage of MINCO to CIMARON7 345kV line CKT 1Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | 520519[BCI WTG, 520520[BCII WTG & 520522[BCVI_WTG1 caused abnormal oscillationss in TC. When these units are GNETed and the simulation is repeated, the oscillationss subside. Voltage spike observed : MaxV: 1.37pu, MaxDur: 0.04s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_137_P6_G16-091-TAP | Prior Outage of MINCO to CIMARON7 345kV line CKT 1Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | 520519[BCI WTG, 520520[BCII WTG & 520522[BCVI_WTG1 caused abnormal oscillationss in TC. When these units are GNETed and the simulation is repeated, the oscillationss subside. Voltage spike observed : MaxV: 1.34pu, MaxDur: 0.04s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_137_P6_G16-091-TAP | Prior Outage of MINCO to CIMARON7 345kV line CKT 1Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV line CKT 1, near G16-091-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | No | Yes | No | Yes | 520519[BCI WTG, 520520[BCII WTG & 520522[BCVI_WTG1 caused abnormal oscillationss in TC. When these units are GNETed and the simulation is repeated, the oscillationss subside. Voltage spike observed : MaxV: 1.33pu, MaxDur: 0.04s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_138_P6_G17-051-TAP | Prior Outage of CARTERJ2 to LKCREEK2 69kV line CKT 1Prior Outage of ELKCTY-2 to ELKCITY2 69kV line CKT 1Apply 3-phase fault on RUSSELL2 to G17-051-TAP 69kV line CKT 1, near G17-051-TAP 69kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | 520519[BCI WTG, 520520[BCII WTG & 520522[BCVI_WTG1 caused abnormal oscillationss in TC. When these units are GNETed and the simulation is repeated, the oscillationss subside.
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_138_P6_G17-051-TAP | Prior Outage of CARTERJ2 to LKCREEK2 69kV line CKT 1Prior Outage of ELKCTY-2 to ELKCITY2 69kV line CKT 1Apply 3-phase fault on RUSSELL2 to G17-051-TAP 69kV line CKT 1, near G17-051-TAP 69kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | 520519[BCI WTG, 520520[BCII WTG & 520522[BCVI_WTG1 caused abnormal oscillationss in TC. When these units are GNETed and the simulation is repeated, the oscillationss subside. Voltage spike observed : MaxV: 1.57pu, MaxDur: 0.08s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_138_P6_G17-051-TAP | Prior Outage of CARTERJ2 to LKCREEK2 69kV line CKT 1Prior Outage of ELKCTY-2 to ELKCITY2 69kV line CKT 1Apply 3-phase fault on RUSSELL2 to G17-051-TAP 69kV line CKT 1, near G17-051-TAP 69kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | 520519[BCI WTG, 520520[BCII WTG & 520522[BCVI_WTG1 caused abnormal oscillationss in TC. When these units are GNETed and the simulation is repeated, the oscillationss subside.
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_138_P6_G17-051-TAP | Prior Outage of CARTERJ2 to LKCREEK2 69kV line CKT 1Prior Outage of ELKCTY-2 to ELKCITY2 69kV line CKT 1Apply 3-phase fault on RUSSELL2 to G17-051-TAP 69kV line CKT 1, near G17-051-TAP 69kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | 520519[BCI WTG, 520520[BCII WTG & 520522[BCVI_WTG1 caused abnormal oscillationss in TC. When these units are GNETed and the simulation is repeated, the oscillationss subside. Voltage spike observed : MaxV: 1.48pu, MaxDur: 0.07s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_139_P6_G17-051-TAP | Prior Outage of RUSSELL2 69kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on OMMANGM2 to G17-051-TAP 69kV line CKT 1, near G17-051-TAP 69kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_139_P6_G17-051-TAP | Prior Outage of RUSSELL2 69kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on OMMANGM2 to G17-051-TAP 69kV line CKT 1, near G17-051-TAP 69kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.36pu, MaxDur: 0.06s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_139_P6_G17-051-TAP | Prior Outage of RUSSELL2 69kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on OMMANGM2 to G17-051-TAP 69kV line CKT 1, near G17-051-TAP 69kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_139_P6_G17-051-TAP | Prior Outage of RUSSELL2 69kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on OMMANGM2 to G17-051-TAP 69kV line CKT 1, near G17-051-TAP 69kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_140_P6_TAP_G17-036 | Prior Outage of SNYDER 4 to CACHEJ4 138kV line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV line CKT 1, near TAP_G17-036 138kV for 7 cycles. Open the faulted line and 112GORE4 to LAIRGST4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and 112GORE4 to LAIRGST4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open 112GORE4 to LAIRGST4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.50pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_140_P6_TAP_G17-036 | Prior Outage of SNYDER 4 to CACHEJ4 138kV line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV line CKT 1, near TAP_G17-036 138kV for 7 cycles. Open the faulted line and 112GORE4 to LAIRGST4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and 112GORE4 to LAIRGST4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open 112GORE4 to LAIRGST4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.48pu, MaxDur: 0.07s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_140_P6_TAP_G17-036 | Prior Outage of SNYDER 4 to CACHEJ4 138kV line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV line CKT 1, near TAP_G17-036 138kV for 7 cycles. Open the faulted line and 112GORE4 to LAIRGST4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and 112GORE4 to LAIRGST4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open 112GORE4 to LAIRGST4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.43pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_140_P6_TAP_G17-036 | Prior Outage of SNYDER 4 to CACHEJ4 138kV line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV line CKT 1, near TAP_G17-036 138kV for 7 cycles. Open the faulted line and 112GORE4 to LAIRGST4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and 112GORE4 to LAIRGST4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open 112GORE4 to LAIRGST4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.44pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_141_P6_TAP_G17-036 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV line CKT 1, near TAP_G17-036 138kV for 7 cycles. Open the faulted line and 112GORE4 to LAIRGST4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and 112GORE4 to LAIRGST4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open 112GORE4 to LAIRGST4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.44pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_141_P6_TAP_G17-036 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV line CKT 1, near TAP_G17-036 138kV for 7 cycles. Open the faulted line and 112GORE4 to LAIRGST4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and 112GORE4 to LAIRGST4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open 112GORE4 to LAIRGST4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.45pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_141_P6_TAP_G17-036 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV line CKT 1, near TAP_G17-036 138kV for 7 cycles. Open the faulted line and 112GORE4 to LAIRGST4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and 112GORE4 to LAIRGST4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open 112GORE4 to LAIRGST4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.40pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_141_P6_TAP_G17-036 | Prior Outage of SNYDER-4 to ALTUSJT4 138kV line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV line CKT 1, near TAP_G17-036 138kV for 7 cycles. Open the faulted line and 112GORE4 to LAIRGST4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and 112GORE4 to LAIRGST4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open 112GORE4 to LAIRGST4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.41pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 19W | Transfer | FLT_142_P6_TAP_G17-036 | Prior Outage of ALTUSJT4 to OMPARK-4 138kV line CKT 1Prior Outage of HOB-JCT4 to MARTHA 4 138kV line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV line CKT 1, near TAP_G17-036 138kV for 7 cycles. Open the faulted line and 112GORE4 to LAIRGST4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and 112GORE4 to LAIRGST4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open 112GORE4 to LAIRGST4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.48pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21L | Transfer | FLT_142_P6_TAP_G17-036 | Prior Outage of ALTUSJT4 to OMPARK-4 138kV line CKT 1Prior Outage of HOB-JCT4 to MARTHA 4 138kV line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV line CKT 1, near TAP_G17-036 138kV for 7 cycles. Open the faulted line and 112GORE4 to LAIRGST4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and 112GORE4 to LAIRGST4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open 112GORE4 to LAIRGST4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.47pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 21S | Transfer | FLT_142_P6_TAP_G17-036 | Prior Outage of ALTUSJT4 to OMPARK-4 138kV line CKT 1Prior Outage of HOB-JCT4 to MARTHA 4 138kV line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV line CKT 1, near TAP_G17-036 138kV for 7 cycles. Open the faulted line and 112GORE4 to LAIRGST4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and 112GORE4 to LAIRGST4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open 112GORE4 to LAIRGST4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed ; MaxV: 1.42pu, MaxDur: 0.03s
South | 07 - Southwestern Oklahoma | 28S | Transfer | FLT_142_P6_TAP_G17-036 | Prior Outage of ALTUSJT4 to OMPARK-4 138kV line CKT 1Prior Outage of HOB-JCT4 to MARTHA 4 138kV line CKT 1Apply 3-phase fault on CACHE4 to TAP_G17-036 138kV line CKT 1, near TAP_G17-036 138kV for 7 cycles. Open the faulted line and 112GORE4 to LAIRGST4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and 112GORE4 to LAIRGST4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open 112GORE4 to LAIRGST4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.42pu, MaxDur: 0.03s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_1_P1_ARSHILL4 | Apply 3-phase fault on ARSHILL4 to STLGENS4 138kV line CKT 1, near ARSHILL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_1_P1_ARSHILL4 | Apply 3-phase fault on ARSHILL4 to STLGENS4 138kV line CKT 1, near ARSHILL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_1_P1_ARSHILL4 | Apply 3-phase fault on ARSHILL4 to STLGENS4 138kV line CKT 1, near ARSHILL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_1_P1_ARSHILL4 | Apply 3-phase fault on ARSHILL4 to STLGENS4 138kV line CKT 1, near ARSHILL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_2_P1_ARSHILL4 | Apply 3-phase fault on ARSHILL4 to FTHUMBG4 138kV line CKT 1, near ARSHILL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_2_P1_ARSHILL4 | Apply 3-phase fault on ARSHILL4 to FTHUMBG4 138kV line CKT 1, near ARSHILL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_2_P1_ARSHILL4 | Apply 3-phase fault on ARSHILL4 to FTHUMBG4 138kV line CKT 1, near ARSHILL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_2_P1_ARSHILL4 | Apply 3-phase fault on ARSHILL4 to FTHUMBG4 138kV line CKT 1, near ARSHILL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_3_P1_NMARKET2 | Apply 3-phase fault on ARSHILL2 to NMARKET2 69kV line CKT 1, near NMARKET2 69kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_3_P1_NMARKET2 | Apply 3-phase fault on ARSHILL2 to NMARKET2 69kV line CKT 1, near NMARKET2 69kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_3_P1_NMARKET2 | Apply 3-phase fault on ARSHILL2 to NMARKET2 69kV line CKT 1, near NMARKET2 69kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_3_P1_NMARKET2 | Apply 3-phase fault on ARSHILL2 to NMARKET2 69kV line CKT 1, near NMARKET2 69kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_4_P1_BLOOMBG2 | Apply 3-phase fault on BLOOMBG2 to IPC TAP2 69kV line CKT 1, near BLOOMBG2 69kV for 7 cycles. Open the faulted line and S_TEXARK to TEXARK 2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and S_TEXARK to TEXARK 2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open S_TEXARK to TEXARK 2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.21pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_4_P1_BLOOMBG2 | Apply 3-phase fault on BLOOMBG2 to IPC TAP2 69kV line CKT 1, near BLOOMBG2 69kV for 7 cycles. Open the faulted line and S_TEXARK to TEXARK 2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and S_TEXARK to TEXARK 2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open S_TEXARK to TEXARK 2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.22pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_4_P1_BLOOMBG2 | Apply 3-phase fault on BLOOMBG2 to IPC TAP2 69kV line CKT 1, near BLOOMBG2 69kV for 7 cycles. Open the faulted line and S_TEXARK to TEXARK 2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and S_TEXARK to TEXARK 2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open S_TEXARK to TEXARK 2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.21pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_4_P1_BLOOMBG2 | Apply 3-phase fault on BLOOMBG2 to IPC TAP2 69kV line CKT 1, near BLOOMBG2 69kV for 7 cycles. Open the faulted line and S_TEXARK to TEXARK 2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and S_TEXARK to TEXARK 2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open S_TEXARK to TEXARK 2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.21pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_5_P1_BLOOMBG2 | Apply 3-phase fault on ATLANTA2 to BLOOMBG2 69kV line CKT 1, near BLOOMBG2 69kV for 7 cycles. Open the faulted line and ATLANTA2 to WATLANT2 69kV line CKT 1 and ATLANTA2 to WATLANT2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and ATLANTA2 to WATLANT2 69kV line CKT 1 and ATLANTA2 to WATLANT2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open ATLANTA2 to WATLANT2 69kV line CKT 1. Simultaneously re-open ATLANTA2 to WATLANT2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed :MaxV: 1.21pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_5_P1_BLOOMBG2 | Apply 3-phase fault on ATLANTA2 to BLOOMBG2 69kV line CKT 1, near BLOOMBG2 69kV for 7 cycles. Open the faulted line and ATLANTA2 to WATLANT2 69kV line CKT 1 and ATLANTA2 to WATLANT2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and ATLANTA2 to WATLANT2 69kV line CKT 1 and ATLANTA2 to WATLANT2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open ATLANTA2 to WATLANT2 69kV line CKT 1. Simultaneously re-open ATLANTA2 to WATLANT2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.21pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_5_P1_BLOOMBG2 | Apply 3-phase fault on ATLANTA2 to BLOOMBG2 69kV line CKT 1, near BLOOMBG2 69kV for 7 cycles. Open the faulted line and ATLANTA2 to WATLANT2 69kV line CKT 1 and ATLANTA2 to WATLANT2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and ATLANTA2 to WATLANT2 69kV line CKT 1 and ATLANTA2 to WATLANT2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open ATLANTA2 to WATLANT2 69kV line CKT 1. Simultaneously re-open ATLANTA2 to WATLANT2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.21pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_5_P1_BLOOMBG2 | Apply 3-phase fault on ATLANTA2 to BLOOMBG2 69kV line CKT 1, near BLOOMBG2 69kV for 7 cycles. Open the faulted line and ATLANTA2 to WATLANT2 69kV line CKT 1 and ATLANTA2 to WATLANT2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and ATLANTA2 to WATLANT2 69kV line CKT 1 and ATLANTA2 to WATLANT2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open ATLANTA2 to WATLANT2 69kV line CKT 1. Simultaneously re-open ATLANTA2 to WATLANT2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.21pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_6_P1_TEXARK2 | Apply 3-phase fault on TEXARK 2 to WASHST 2 69kV line CKT 1, near TEXARK 2 69kV for 7 cycles. Open the faulted line and SUGHLET2 to TEX12ST2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and SUGHLET2 to TEX12ST2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open SUGHLET2 to TEX12ST2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_6_P1_TEXARK2 | Apply 3-phase fault on TEXARK 2 to WASHST 2 69kV line CKT 1, near TEXARK 2 69kV for 7 cycles. Open the faulted line and SUGHLET2 to TEX12ST2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and SUGHLET2 to TEX12ST2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open SUGHLET2 to TEX12ST2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_6_P1_TEXARK2 | Apply 3-phase fault on TEXARK 2 to WASHST 2 69kV line CKT 1, near TEXARK 2 69kV for 7 cycles. Open the faulted line and SUGHLET2 to TEX12ST2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and SUGHLET2 to TEX12ST2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open SUGHLET2 to TEX12ST2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_6_P1_TEXARK2 | Apply 3-phase fault on TEXARK 2 to WASHST 2 69kV line CKT 1, near TEXARK 2 69kV for 7 cycles. Open the faulted line and SUGHLET2 to TEX12ST2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and SUGHLET2 to TEX12ST2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open SUGHLET2 to TEX12ST2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_7_P1_TEXARK2 | Apply 3-phase fault on SETEXAR2 to TEXARK 2 69kV line CKT 1, near TEXARK 2 69kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_7_P1_TEXARK2 | Apply 3-phase fault on SETEXAR2 to TEXARK 2 69kV line CKT 1, near TEXARK 2 69kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_7_P1_TEXARK2 | Apply 3-phase fault on SETEXAR2 to TEXARK 2 69kV line CKT 1, near TEXARK 2 69kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_7_P1_TEXARK2 | Apply 3-phase fault on SETEXAR2 to TEXARK 2 69kV line CKT 1, near TEXARK 2 69kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_8_P1_WATLANT2 | Apply 3-phase fault on WATLANT2 69kV/138kV/13.19kV transformer CKT 1, near WATLANT2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_8_P1_WATLANT2 | Apply 3-phase fault on WATLANT2 69kV/138kV/13.19kV transformer CKT 1, near WATLANT2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_8_P1_WATLANT2 | Apply 3-phase fault on WATLANT2 69kV/138kV/13.19kV transformer CKT 1, near WATLANT2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_8_P1_WATLANT2 | Apply 3-phase fault on WATLANT2 69kV/138kV/13.19kV transformer CKT 1, near WATLANT2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_9_P1_WATLANT4 | Apply 3-phase fault on WATLANT4 to CASSTP4 138kV line CKT 1, near WATLANT4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_9_P1_WATLANT4 | Apply 3-phase fault on WATLANT4 to CASSTP4 138kV line CKT 1, near WATLANT4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_9_P1_WATLANT4 | Apply 3-phase fault on WATLANT4 to CASSTP4 138kV line CKT 1, near WATLANT4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_9_P1_WATLANT4 | Apply 3-phase fault on WATLANT4 to CASSTP4 138kV line CKT 1, near WATLANT4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_10_P1_WATLANT4 | Apply 3-phase fault on WATLANT4 to WILKES 4 138kV line CKT 1, near WATLANT4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_10_P1_WATLANT4 | Apply 3-phase fault on WATLANT4 to WILKES 4 138kV line CKT 1, near WATLANT4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_10_P1_WATLANT4 | Apply 3-phase fault on WATLANT4 to WILKES 4 138kV line CKT 1, near WATLANT4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_10_P1_WATLANT4 | Apply 3-phase fault on WATLANT4 to WILKES 4 138kV line CKT 1, near WATLANT4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_11_P1_HOSSTON2 | Apply 3-phase fault on GILLIAM2 to HOSSTON2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and GILLIAM2 to SUPEROR2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and GILLIAM2 to SUPEROR2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open GILLIAM2 to SUPEROR2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_11_P1_HOSSTON2 | Apply 3-phase fault on GILLIAM2 to HOSSTON2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and GILLIAM2 to SUPEROR2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and GILLIAM2 to SUPEROR2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open GILLIAM2 to SUPEROR2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_11_P1_HOSSTON2 | Apply 3-phase fault on GILLIAM2 to HOSSTON2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and GILLIAM2 to SUPEROR2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and GILLIAM2 to SUPEROR2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open GILLIAM2 to SUPEROR2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_11_P1_HOSSTON2 | Apply 3-phase fault on GILLIAM2 to HOSSTON2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and GILLIAM2 to SUPEROR2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and GILLIAM2 to SUPEROR2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open GILLIAM2 to SUPEROR2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_12_P1_HOSSTON2 | Apply 3-phase fault on HOSSTON2 to PLAINDL2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and NBENTON2 to MOTT TP2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NBENTON2 to MOTT TP2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open NBENTON2 to MOTT TP2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_12_P1_HOSSTON2 | Apply 3-phase fault on HOSSTON2 to PLAINDL2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and NBENTON2 to MOTT TP2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NBENTON2 to MOTT TP2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open NBENTON2 to MOTT TP2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_12_P1_HOSSTON2 | Apply 3-phase fault on HOSSTON2 to PLAINDL2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and NBENTON2 to MOTT TP2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NBENTON2 to MOTT TP2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open NBENTON2 to MOTT TP2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_12_P1_HOSSTON2 | Apply 3-phase fault on HOSSTON2 to PLAINDL2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and NBENTON2 to MOTT TP2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NBENTON2 to MOTT TP2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open NBENTON2 to MOTT TP2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_13_P1_HOSSTON2 | Apply 3-phase fault on HOSSTON2 to GODFREYRDTP2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and BLOOMBG2 to RODESSA2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BLOOMBG2 to RODESSA2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BLOOMBG2 to RODESSA2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_13_P1_HOSSTON2 | Apply 3-phase fault on HOSSTON2 to GODFREYRDTP2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and BLOOMBG2 to RODESSA2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BLOOMBG2 to RODESSA2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BLOOMBG2 to RODESSA2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.21pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_13_P1_HOSSTON2 | Apply 3-phase fault on HOSSTON2 to GODFREYRDTP2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and BLOOMBG2 to RODESSA2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BLOOMBG2 to RODESSA2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BLOOMBG2 to RODESSA2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_13_P1_HOSSTON2 | Apply 3-phase fault on HOSSTON2 to GODFREYRDTP2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and BLOOMBG2 to RODESSA2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BLOOMBG2 to RODESSA2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BLOOMBG2 to RODESSA2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_14_P1_LIEBERM2 | Apply 3-phase fault on LIEBERM2 69kV/138kV/13.19kV transformer CKT 3, near LIEBERM2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_14_P1_LIEBERM2 | Apply 3-phase fault on LIEBERM2 69kV/138kV/13.19kV transformer CKT 3, near LIEBERM2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_14_P1_LIEBERM2 | Apply 3-phase fault on LIEBERM2 69kV/138kV/13.19kV transformer CKT 3, near LIEBERM2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_14_P1_LIEBERM2 | Apply 3-phase fault on LIEBERM2 69kV/138kV/13.19kV transformer CKT 3, near LIEBERM2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_15_P1_LIEBERM2 | Apply 3-phase fault on BLANCH-2 to LIEBERM2 69kV line CKT 1, near LIEBERM2 69kV for 7 cycles. Open the faulted line and NMARKET2 to BLANCHR2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NMARKET2 to BLANCHR2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open NMARKET2 to BLANCHR2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_15_P1_LIEBERM2 | Apply 3-phase fault on BLANCH-2 to LIEBERM2 69kV line CKT 1, near LIEBERM2 69kV for 7 cycles. Open the faulted line and NMARKET2 to BLANCHR2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NMARKET2 to BLANCHR2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open NMARKET2 to BLANCHR2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_15_P1_LIEBERM2 | Apply 3-phase fault on BLANCH-2 to LIEBERM2 69kV line CKT 1, near LIEBERM2 69kV for 7 cycles. Open the faulted line and NMARKET2 to BLANCHR2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NMARKET2 to BLANCHR2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open NMARKET2 to BLANCHR2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_15_P1_LIEBERM2 | Apply 3-phase fault on BLANCH-2 to LIEBERM2 69kV line CKT 1, near LIEBERM2 69kV for 7 cycles. Open the faulted line and NMARKET2 to BLANCHR2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NMARKET2 to BLANCHR2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open NMARKET2 to BLANCHR2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_16_P1_LIEBERM4 | Apply 3-phase fault on LIEBERM4 to IPCJEFF4 138kV line CKT 1, near LIEBERM4 138kV for 7 cycles. Open the faulted line and IPCJEFF4 to JEFFRSN4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and IPCJEFF4 to JEFFRSN4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open IPCJEFF4 to JEFFRSN4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_16_P1_LIEBERM4 | Apply 3-phase fault on LIEBERM4 to IPCJEFF4 138kV line CKT 1, near LIEBERM4 138kV for 7 cycles. Open the faulted line and IPCJEFF4 to JEFFRSN4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and IPCJEFF4 to JEFFRSN4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open IPCJEFF4 to JEFFRSN4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_16_P1_LIEBERM4 | Apply 3-phase fault on LIEBERM4 to IPCJEFF4 138kV line CKT 1, near LIEBERM4 138kV for 7 cycles. Open the faulted line and IPCJEFF4 to JEFFRSN4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and IPCJEFF4 to JEFFRSN4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open IPCJEFF4 to JEFFRSN4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_16_P1_LIEBERM4 | Apply 3-phase fault on LIEBERM4 to IPCJEFF4 138kV line CKT 1, near LIEBERM4 138kV for 7 cycles. Open the faulted line and IPCJEFF4 to JEFFRSN4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and IPCJEFF4 to JEFFRSN4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open IPCJEFF4 to JEFFRSN4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_17_P1_LIEBERM4 | Apply 3-phase fault on LIEBERM4 to LONGWD 4 138kV line CKT 1, near LIEBERM4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_17_P1_LIEBERM4 | Apply 3-phase fault on LIEBERM4 to LONGWD 4 138kV line CKT 1, near LIEBERM4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_17_P1_LIEBERM4 | Apply 3-phase fault on LIEBERM4 to LONGWD 4 138kV line CKT 1, near LIEBERM4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_17_P1_LIEBERM4 | Apply 3-phase fault on LIEBERM4 to LONGWD 4 138kV line CKT 1, near LIEBERM4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_18_P1_LIEBERM4 | Apply 3-phase fault on LIEBERM4 to G16-167-TAP 138kV line CKT 1, near LIEBERM4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_18_P1_LIEBERM4 | Apply 3-phase fault on LIEBERM4 to G16-167-TAP 138kV line CKT 1, near LIEBERM4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_18_P1_LIEBERM4 | Apply 3-phase fault on LIEBERM4 to G16-167-TAP 138kV line CKT 1, near LIEBERM4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_18_P1_LIEBERM4 | Apply 3-phase fault on LIEBERM4 to G16-167-TAP 138kV line CKT 1, near LIEBERM4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_19_P1_LIEBERM4 | Apply 3-phase fault on ARSHILL4 to LIEBERM4 138kV line CKT 1, near LIEBERM4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_19_P1_LIEBERM4 | Apply 3-phase fault on ARSHILL4 to LIEBERM4 138kV line CKT 1, near LIEBERM4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_19_P1_LIEBERM4 | Apply 3-phase fault on ARSHILL4 to LIEBERM4 138kV line CKT 1, near LIEBERM4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_19_P1_LIEBERM4 | Apply 3-phase fault on ARSHILL4 to LIEBERM4 138kV line CKT 1, near LIEBERM4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_20_P1_LONGWD4 | Apply 3-phase fault on LONGWD 4 138kV/345kV/13.19kV transformer CKT 1, near LONGWD 4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_20_P1_LONGWD4 | Apply 3-phase fault on LONGWD 4 138kV/345kV/13.19kV transformer CKT 1, near LONGWD 4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_20_P1_LONGWD4 | Apply 3-phase fault on LONGWD 4 138kV/345kV/13.19kV transformer CKT 1, near LONGWD 4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_20_P1_LONGWD4 | Apply 3-phase fault on LONGWD 4 138kV/345kV/13.19kV transformer CKT 1, near LONGWD 4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_21_P1_LONGWD7 | Apply 3-phase fault on LONGWD 7 to WILKES 7 345kV line CKT 1, near LONGWD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_21_P1_LONGWD7 | Apply 3-phase fault on LONGWD 7 to WILKES 7 345kV line CKT 1, near LONGWD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_21_P1_LONGWD7 | Apply 3-phase fault on LONGWD 7 to WILKES 7 345kV line CKT 1, near LONGWD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_21_P1_LONGWD7 | Apply 3-phase fault on LONGWD 7 to WILKES 7 345kV line CKT 1, near LONGWD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_22_P1_LONGWD7 | Apply 3-phase fault on SW SHV 7 to LONGWD 7 345kV line CKT 1, near LONGWD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_22_P1_LONGWD7 | Apply 3-phase fault on SW SHV 7 to LONGWD 7 345kV line CKT 1, near LONGWD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_22_P1_LONGWD7 | Apply 3-phase fault on SW SHV 7 to LONGWD 7 345kV line CKT 1, near LONGWD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_22_P1_LONGWD7 | Apply 3-phase fault on SW SHV 7 to LONGWD 7 345kV line CKT 1, near LONGWD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_23_P1_NBENTON4 | Apply 3-phase fault on LINTNRD4 to NBENTON4 138kV line CKT 1, near NBENTON4 138kV for 7 cycles. Open the faulted line and RDPOINT4 to DEENPNT4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and RDPOINT4 to DEENPNT4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open RDPOINT4 to DEENPNT4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_23_P1_NBENTON4 | Apply 3-phase fault on LINTNRD4 to NBENTON4 138kV line CKT 1, near NBENTON4 138kV for 7 cycles. Open the faulted line and RDPOINT4 to DEENPNT4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and RDPOINT4 to DEENPNT4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open RDPOINT4 to DEENPNT4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_23_P1_NBENTON4 | Apply 3-phase fault on LINTNRD4 to NBENTON4 138kV line CKT 1, near NBENTON4 138kV for 7 cycles. Open the faulted line and RDPOINT4 to DEENPNT4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and RDPOINT4 to DEENPNT4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open RDPOINT4 to DEENPNT4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_23_P1_NBENTON4 | Apply 3-phase fault on LINTNRD4 to NBENTON4 138kV line CKT 1, near NBENTON4 138kV for 7 cycles. Open the faulted line and RDPOINT4 to DEENPNT4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and RDPOINT4 to DEENPNT4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open RDPOINT4 to DEENPNT4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_24_P1_SUPEROR2 | Apply 3-phase fault on OILCITY2 to SUPEROR2 69kV line CKT 1, near SUPEROR2 69kV for 7 cycles. Open the faulted line and LIEBERM2 to OILCITY2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and LIEBERM2 to OILCITY2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open LIEBERM2 to OILCITY2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_24_P1_SUPEROR2 | Apply 3-phase fault on OILCITY2 to SUPEROR2 69kV line CKT 1, near SUPEROR2 69kV for 7 cycles. Open the faulted line and LIEBERM2 to OILCITY2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and LIEBERM2 to OILCITY2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open LIEBERM2 to OILCITY2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_24_P1_SUPEROR2 | Apply 3-phase fault on OILCITY2 to SUPEROR2 69kV line CKT 1, near SUPEROR2 69kV for 7 cycles. Open the faulted line and LIEBERM2 to OILCITY2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and LIEBERM2 to OILCITY2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open LIEBERM2 to OILCITY2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_24_P1_SUPEROR2 | Apply 3-phase fault on OILCITY2 to SUPEROR2 69kV line CKT 1, near SUPEROR2 69kV for 7 cycles. Open the faulted line and LIEBERM2 to OILCITY2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and LIEBERM2 to OILCITY2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open LIEBERM2 to OILCITY2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_25_P1_SUPEROR2 | Apply 3-phase fault on SUPEROR2 to JEFFRSN2 69kV line CKT 1, near SUPEROR2 69kV for 7 cycles. Open the faulted line and JEFFRSN2 to WOODLWN2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and JEFFRSN2 to WOODLWN2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open JEFFRSN2 to WOODLWN2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_25_P1_SUPEROR2 | Apply 3-phase fault on SUPEROR2 to JEFFRSN2 69kV line CKT 1, near SUPEROR2 69kV for 7 cycles. Open the faulted line and JEFFRSN2 to WOODLWN2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and JEFFRSN2 to WOODLWN2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open JEFFRSN2 to WOODLWN2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_25_P1_SUPEROR2 | Apply 3-phase fault on SUPEROR2 to JEFFRSN2 69kV line CKT 1, near SUPEROR2 69kV for 7 cycles. Open the faulted line and JEFFRSN2 to WOODLWN2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and JEFFRSN2 to WOODLWN2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open JEFFRSN2 to WOODLWN2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_25_P1_SUPEROR2 | Apply 3-phase fault on SUPEROR2 to JEFFRSN2 69kV line CKT 1, near SUPEROR2 69kV for 7 cycles. Open the faulted line and JEFFRSN2 to WOODLWN2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and JEFFRSN2 to WOODLWN2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open JEFFRSN2 to WOODLWN2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_26_P1_WILKES4 | Apply 3-phase fault on WILKES 4 138kV/345kV/13.19kV transformer CKT 1, near WILKES 4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_26_P1_WILKES4 | Apply 3-phase fault on WILKES 4 138kV/345kV/13.19kV transformer CKT 1, near WILKES 4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_26_P1_WILKES4 | Apply 3-phase fault on WILKES 4 138kV/345kV/13.19kV transformer CKT 1, near WILKES 4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_26_P1_WILKES4 | Apply 3-phase fault on WILKES 4 138kV/345kV/13.19kV transformer CKT 1, near WILKES 4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_27_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_27_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_27_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-065-GEN2[1]. G17-065-GEN2[1] tripped on overfrequency. When the protection relay is disabled and the simulation is repeated, the unit becomes stable. The tripping is observed in BC and TC for this contingency.
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_27_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G17-065-GEN2[1]. G17-065-GEN2[1] tripped on overfrequency. When the protection relay is disabled and the simulation is repeated, the unit becomes stable. The tripping is observed in BC and TC for this contingency.
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_28_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_28_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_28_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_28_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_29_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_29_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_29_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_29_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_30_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV line CKT &1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line. Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. (Due to size and location of the unit, no further simulation was peroformed.)
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_30_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV line CKT &1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line. Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_30_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV line CKT &1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line. Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. (Due to size and location of the unit, no further simulation was peroformed.)
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_30_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV line CKT &1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line. Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. (Due to size and location of the unit, no further simulation was peroformed.)
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_31_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV line CKT &1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line. Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. (Due to size and location of the unit, no further simulation was peroformed.)
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_31_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV line CKT &1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line. Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_31_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV line CKT &1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line. Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. (Due to size and location of the unit, no further simulation was peroformed.)
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_31_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV line CKT &1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line. Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. (Due to size and location of the unit, no further simulation was peroformed.)
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_32_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. (Due to size and location of the unit, no further simulation was peroformed.) Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_32_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_32_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. (Due to size and location of the unit, no further simulation was peroformed.) Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_32_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. (Due to size and location of the unit, no further simulation was peroformed.) Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_33_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_33_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_33_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_33_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_34_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. (Due to size and location of the unit, no further simulation was peroformed.) Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_34_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_34_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. (Due to size and location of the unit, no further simulation was peroformed.) Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_34_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. (Due to size and location of the unit, no further simulation was peroformed.) Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.00s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_35_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. (Due to size and location of the unit, no further simulation was peroformed.) Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.00s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_35_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_35_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. (Due to size and location of the unit, no further simulation was peroformed.) Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.00s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_35_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. (Due to size and location of the unit, no further simulation was peroformed.) Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.00s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_36_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed :MaxV: 1.24pu, MaxDur: 0.02s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_36_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_36_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.25pu, MaxDur: 0.02s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_36_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.25pu, MaxDur: 0.02s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_37_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.31pu, MaxDur: 0.02s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_37_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_37_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.36pu, MaxDur: 0.02s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_37_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.36pu, MaxDur: 0.02s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_38_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_38_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_38_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_38_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_39_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_39_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_39_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_39_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_40_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.02s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_40_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_40_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_40_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_41_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.27pu, MaxDur: 0.03s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_41_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_41_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.27pu, MaxDur: 0.03s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_41_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.26pu, MaxDur: 0.03s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_42_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.23pu, MaxDur: 0.02s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_42_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_42_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.22pu, MaxDur: 0.02s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_42_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.21pu, MaxDur: 0.02s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_43_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_43_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_43_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.00s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_43_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.00s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_44_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed - MaxV: 1.20pu, MaxDur: 0.00s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_44_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_44_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.00s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_44_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.00s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_45_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed - MaxV: 1.33pu, MaxDur: 0.02s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_45_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_45_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.33pu, MaxDur: 0.02s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_45_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.33pu, MaxDur: 0.02s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_46_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_46_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_46_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_46_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_47_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.00s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_47_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_47_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.00s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_47_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.00s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_48_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_48_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_48_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed ; MaxV: 1.20pu, MaxDur: 0.00s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_48_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.00s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_49_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.00s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_49_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_49_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.06s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_49_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.07s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_50_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.00s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_50_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_50_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.00s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_50_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.00s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_51_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_51_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_51_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_51_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_52_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_52_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_52_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_52_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_53_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_53_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_53_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_53_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_54_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_54_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_54_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_54_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_55_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_55_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_55_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_55_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_56_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_56_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_56_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_56_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.00s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_57_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_57_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_57_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_57_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_58_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_58_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_58_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_58_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_59_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_59_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_59_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_59_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_60_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_60_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_60_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_60_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_61_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_61_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_61_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_61_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_62_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_62_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_62_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_62_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_63_P4_HOSSTON2 | Apply single-phase fault on HOSSTON2 to PLAINDL2 69kV line CKT 1, near HOSSTON2 69kV for 16 cycles with stuck breaker at HOSSTON2. Open the faulted line and NBENTON2 to MOTT TP2 69kV line CKT 1 and BLOOMBG2 to RODESSA2 69kV line CKT 1 and HOSSTON2 to GODFREYRDTP2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.24pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_63_P4_HOSSTON2 | Apply single-phase fault on HOSSTON2 to PLAINDL2 69kV line CKT 1, near HOSSTON2 69kV for 16 cycles with stuck breaker at HOSSTON2. Open the faulted line and NBENTON2 to MOTT TP2 69kV line CKT 1 and BLOOMBG2 to RODESSA2 69kV line CKT 1 and HOSSTON2 to GODFREYRDTP2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.25pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_63_P4_HOSSTON2 | Apply single-phase fault on HOSSTON2 to PLAINDL2 69kV line CKT 1, near HOSSTON2 69kV for 16 cycles with stuck breaker at HOSSTON2. Open the faulted line and NBENTON2 to MOTT TP2 69kV line CKT 1 and BLOOMBG2 to RODESSA2 69kV line CKT 1 and HOSSTON2 to GODFREYRDTP2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.24pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_63_P4_HOSSTON2 | Apply single-phase fault on HOSSTON2 to PLAINDL2 69kV line CKT 1, near HOSSTON2 69kV for 16 cycles with stuck breaker at HOSSTON2. Open the faulted line and NBENTON2 to MOTT TP2 69kV line CKT 1 and BLOOMBG2 to RODESSA2 69kV line CKT 1 and HOSSTON2 to GODFREYRDTP2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed :MaxV: 1.24pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_64_P4_HOSSTON2 | Apply single-phase fault on HOSSTON2 to VIVIAN 2 69kV line CKT 1, near HOSSTON2 69kV for 16 cycles with stuck breaker at HOSSTON2. Open the faulted line and SUPEROR2 to VIVIAN 2 69kV line CKT 1 and GILLIAM2 to HOSSTON2 69kV line CKT 1 and GILLIAM2 to SUPEROR2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.25pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_64_P4_HOSSTON2 | Apply single-phase fault on HOSSTON2 to VIVIAN 2 69kV line CKT 1, near HOSSTON2 69kV for 16 cycles with stuck breaker at HOSSTON2. Open the faulted line and SUPEROR2 to VIVIAN 2 69kV line CKT 1 and GILLIAM2 to HOSSTON2 69kV line CKT 1 and GILLIAM2 to SUPEROR2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.26pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_64_P4_HOSSTON2 | Apply single-phase fault on HOSSTON2 to VIVIAN 2 69kV line CKT 1, near HOSSTON2 69kV for 16 cycles with stuck breaker at HOSSTON2. Open the faulted line and SUPEROR2 to VIVIAN 2 69kV line CKT 1 and GILLIAM2 to HOSSTON2 69kV line CKT 1 and GILLIAM2 to SUPEROR2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed :MaxV: 1.25pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_64_P4_HOSSTON2 | Apply single-phase fault on HOSSTON2 to VIVIAN 2 69kV line CKT 1, near HOSSTON2 69kV for 16 cycles with stuck breaker at HOSSTON2. Open the faulted line and SUPEROR2 to VIVIAN 2 69kV line CKT 1 and GILLIAM2 to HOSSTON2 69kV line CKT 1 and GILLIAM2 to SUPEROR2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.25pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_65_P4_NBENTON4 | Apply single-phase fault on NBENTON2 69kV/138kV/13.19kV transformer CKT 1, near NBENTON4 138kV for 16 cycles with stuck breaker at NBENTON4. Open the faulted Three Winding and LINTNRD4 to NBENTON4 138kV line CKT 1 and RDPOINT4 to DEENPNT4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_65_P4_NBENTON4 | Apply single-phase fault on NBENTON2 69kV/138kV/13.19kV transformer CKT 1, near NBENTON4 138kV for 16 cycles with stuck breaker at NBENTON4. Open the faulted Three Winding and LINTNRD4 to NBENTON4 138kV line CKT 1 and RDPOINT4 to DEENPNT4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.22pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_65_P4_NBENTON4 | Apply single-phase fault on NBENTON2 69kV/138kV/13.19kV transformer CKT 1, near NBENTON4 138kV for 16 cycles with stuck breaker at NBENTON4. Open the faulted Three Winding and LINTNRD4 to NBENTON4 138kV line CKT 1 and RDPOINT4 to DEENPNT4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_65_P4_NBENTON4 | Apply single-phase fault on NBENTON2 69kV/138kV/13.19kV transformer CKT 1, near NBENTON4 138kV for 16 cycles with stuck breaker at NBENTON4. Open the faulted Three Winding and LINTNRD4 to NBENTON4 138kV line CKT 1 and RDPOINT4 to DEENPNT4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_66_P4_SUPEROR2 | Apply single-phase fault on SUPEROR2 to JEFFRSN2 69kV line CKT 1, near SUPEROR2 69kV for 16 cycles with stuck breaker at SUPEROR2. Open the faulted line and JEFFRSN2 to WOODLWN2 69kV line CKT 1 and OILCITY2 to SUPEROR2 69kV line CKT 1 and LIEBERM2 to OILCITY2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.28pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_66_P4_SUPEROR2 | Apply single-phase fault on SUPEROR2 to JEFFRSN2 69kV line CKT 1, near SUPEROR2 69kV for 16 cycles with stuck breaker at SUPEROR2. Open the faulted line and JEFFRSN2 to WOODLWN2 69kV line CKT 1 and OILCITY2 to SUPEROR2 69kV line CKT 1 and LIEBERM2 to OILCITY2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.29pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_66_P4_SUPEROR2 | Apply single-phase fault on SUPEROR2 to JEFFRSN2 69kV line CKT 1, near SUPEROR2 69kV for 16 cycles with stuck breaker at SUPEROR2. Open the faulted line and JEFFRSN2 to WOODLWN2 69kV line CKT 1 and OILCITY2 to SUPEROR2 69kV line CKT 1 and LIEBERM2 to OILCITY2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.28pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_66_P4_SUPEROR2 | Apply single-phase fault on SUPEROR2 to JEFFRSN2 69kV line CKT 1, near SUPEROR2 69kV for 16 cycles with stuck breaker at SUPEROR2. Open the faulted line and JEFFRSN2 to WOODLWN2 69kV line CKT 1 and OILCITY2 to SUPEROR2 69kV line CKT 1 and LIEBERM2 to OILCITY2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed :MaxV: 1.28pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_67_P6_ARSHILL4 | Prior Outage of ARSHILL4 to FTHUMBG4 138kV line CKT 1Apply 3-phase fault on ARSHILL4 to MCWILLI4 138kV line CKT 1, near ARSHILL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_67_P6_ARSHILL4 | Prior Outage of ARSHILL4 to FTHUMBG4 138kV line CKT 1Apply 3-phase fault on ARSHILL4 to MCWILLI4 138kV line CKT 1, near ARSHILL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_67_P6_ARSHILL4 | Prior Outage of ARSHILL4 to FTHUMBG4 138kV line CKT 1Apply 3-phase fault on ARSHILL4 to MCWILLI4 138kV line CKT 1, near ARSHILL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_67_P6_ARSHILL4 | Prior Outage of ARSHILL4 to FTHUMBG4 138kV line CKT 1Apply 3-phase fault on ARSHILL4 to MCWILLI4 138kV line CKT 1, near ARSHILL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_68_P6_HOSSTON2 | Prior Outage of HOSSTON2 to GODFREYRDTP2 69kV line CKT 1Prior Outage of BLOOMBG2 to RODESSA2 69kV line CKT 1Apply 3-phase fault on HOSSTON2 to PLAINDL2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and NBENTON2 to MOTT TP2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NBENTON2 to MOTT TP2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open NBENTON2 to MOTT TP2 69kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.22pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_68_P6_HOSSTON2 | Prior Outage of HOSSTON2 to GODFREYRDTP2 69kV line CKT 1Prior Outage of BLOOMBG2 to RODESSA2 69kV line CKT 1Apply 3-phase fault on HOSSTON2 to PLAINDL2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and NBENTON2 to MOTT TP2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NBENTON2 to MOTT TP2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open NBENTON2 to MOTT TP2 69kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.23pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_68_P6_HOSSTON2 | Prior Outage of HOSSTON2 to GODFREYRDTP2 69kV line CKT 1Prior Outage of BLOOMBG2 to RODESSA2 69kV line CKT 1Apply 3-phase fault on HOSSTON2 to PLAINDL2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and NBENTON2 to MOTT TP2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NBENTON2 to MOTT TP2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open NBENTON2 to MOTT TP2 69kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.22pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_68_P6_HOSSTON2 | Prior Outage of HOSSTON2 to GODFREYRDTP2 69kV line CKT 1Prior Outage of BLOOMBG2 to RODESSA2 69kV line CKT 1Apply 3-phase fault on HOSSTON2 to PLAINDL2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and NBENTON2 to MOTT TP2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NBENTON2 to MOTT TP2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open NBENTON2 to MOTT TP2 69kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed :- MaxV: 1.22pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_69_P6_HOSSTON2 | Prior Outage of HOSSTON2 to VIVIAN 2 69kV line CKT 1Prior Outage of SUPEROR2 to VIVIAN 2 69kV line CKT 1Apply 3-phase fault on GILLIAM2 to HOSSTON2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and GILLIAM2 to SUPEROR2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and GILLIAM2 to SUPEROR2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open GILLIAM2 to SUPEROR2 69kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.33pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_69_P6_HOSSTON2 | Prior Outage of HOSSTON2 to VIVIAN 2 69kV line CKT 1Prior Outage of SUPEROR2 to VIVIAN 2 69kV line CKT 1Apply 3-phase fault on GILLIAM2 to HOSSTON2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and GILLIAM2 to SUPEROR2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and GILLIAM2 to SUPEROR2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open GILLIAM2 to SUPEROR2 69kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Vltage spike observed : MaxV: 1.24pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_69_P6_HOSSTON2 | Prior Outage of HOSSTON2 to VIVIAN 2 69kV line CKT 1Prior Outage of SUPEROR2 to VIVIAN 2 69kV line CKT 1Apply 3-phase fault on GILLIAM2 to HOSSTON2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and GILLIAM2 to SUPEROR2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and GILLIAM2 to SUPEROR2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open GILLIAM2 to SUPEROR2 69kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed :MaxV: 1.33pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_69_P6_HOSSTON2 | Prior Outage of HOSSTON2 to VIVIAN 2 69kV line CKT 1Prior Outage of SUPEROR2 to VIVIAN 2 69kV line CKT 1Apply 3-phase fault on GILLIAM2 to HOSSTON2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and GILLIAM2 to SUPEROR2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and GILLIAM2 to SUPEROR2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open GILLIAM2 to SUPEROR2 69kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.33pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_70_P6_HOSSTON2 | Prior Outage of HOSSTON2 to PLAINDL2 69kV line CKT 1Prior Outage of NBENTON2 to MOTT TP2 69kV line CKT 1Apply 3-phase fault on HOSSTON2 to VIVIAN 2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and SUPEROR2 to VIVIAN 2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and SUPEROR2 to VIVIAN 2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open SUPEROR2 to VIVIAN 2 69kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_70_P6_HOSSTON2 | Prior Outage of HOSSTON2 to PLAINDL2 69kV line CKT 1Prior Outage of NBENTON2 to MOTT TP2 69kV line CKT 1Apply 3-phase fault on HOSSTON2 to VIVIAN 2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and SUPEROR2 to VIVIAN 2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and SUPEROR2 to VIVIAN 2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open SUPEROR2 to VIVIAN 2 69kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage spike observed : MaxV: 1.21pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_70_P6_HOSSTON2 | Prior Outage of HOSSTON2 to PLAINDL2 69kV line CKT 1Prior Outage of NBENTON2 to MOTT TP2 69kV line CKT 1Apply 3-phase fault on HOSSTON2 to VIVIAN 2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and SUPEROR2 to VIVIAN 2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and SUPEROR2 to VIVIAN 2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open SUPEROR2 to VIVIAN 2 69kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_70_P6_HOSSTON2 | Prior Outage of HOSSTON2 to PLAINDL2 69kV line CKT 1Prior Outage of NBENTON2 to MOTT TP2 69kV line CKT 1Apply 3-phase fault on HOSSTON2 to VIVIAN 2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and SUPEROR2 to VIVIAN 2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and SUPEROR2 to VIVIAN 2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open SUPEROR2 to VIVIAN 2 69kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_71_P6_LONGWD7 | Prior Outage of LONGWD 7 to WILKES 7 345kV line CKT 1Apply 3-phase fault on SW SHV 7 to LONGWD 7 345kV line CKT 1, near LONGWD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_71_P6_LONGWD7 | Prior Outage of LONGWD 7 to WILKES 7 345kV line CKT 1Apply 3-phase fault on SW SHV 7 to LONGWD 7 345kV line CKT 1, near LONGWD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_71_P6_LONGWD7 | Prior Outage of LONGWD 7 to WILKES 7 345kV line CKT 1Apply 3-phase fault on SW SHV 7 to LONGWD 7 345kV line CKT 1, near LONGWD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_71_P6_LONGWD7 | Prior Outage of LONGWD 7 to WILKES 7 345kV line CKT 1Apply 3-phase fault on SW SHV 7 to LONGWD 7 345kV line CKT 1, near LONGWD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_01_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_01_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.07s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_01_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_01_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_02_P1_HUGO | Apply 3-phase fault on HUGO 345kV/138kV/13.8kV transformer CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_02_P1_HUGO | Apply 3-phase fault on HUGO 345kV/138kV/13.8kV transformer CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.05s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_02_P1_HUGO | Apply 3-phase fault on HUGO 345kV/138kV/13.8kV transformer CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_02_P1_HUGO | Apply 3-phase fault on HUGO 345kV/138kV/13.8kV transformer CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_03_P1_VALIANT7 | Apply 3-phase fault on VALIANT4 138kV/345kV/13.8kV transformer CKT 2, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_03_P1_VALIANT7 | Apply 3-phase fault on VALIANT4 138kV/345kV/13.8kV transformer CKT 2, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.05s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_03_P1_VALIANT7 | Apply 3-phase fault on VALIANT4 138kV/345kV/13.8kV transformer CKT 2, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_03_P1_VALIANT7 | Apply 3-phase fault on VALIANT4 138kV/345kV/13.8kV transformer CKT 2, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_04_P1_HUGO | Apply 3-phase fault on VALIANT7 to HUGO 345kV line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_04_P1_HUGO | Apply 3-phase fault on VALIANT7 to HUGO 345kV line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.04s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_04_P1_HUGO | Apply 3-phase fault on VALIANT7 to HUGO 345kV line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_04_P1_HUGO | Apply 3-phase fault on VALIANT7 to HUGO 345kV line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_05_P1_JOHNCO7 | Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_05_P1_JOHNCO7 | Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.09s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_05_P1_JOHNCO7 | Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_05_P1_JOHNCO7 | Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_06_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_06_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.07s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_06_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_06_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_07_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to C-RIVER7 345kV line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_07_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to C-RIVER7 345kV line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.08s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_07_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to C-RIVER7 345kV line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_07_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to C-RIVER7 345kV line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_08_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to SEMINOL7 345kV line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_08_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to SEMINOL7 345kV line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.07s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_08_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to SEMINOL7 345kV line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_08_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to SEMINOL7 345kV line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_09_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL4 138kV/345kV/14.39kV transformer CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_09_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL4 138kV/345kV/14.39kV transformer CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_09_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL4 138kV/345kV/14.39kV transformer CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_09_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL4 138kV/345kV/14.39kV transformer CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_10_P1_SEMINOL7 | Apply 3-phase fault on DRAPER 7 to SEMINOL7 345kV line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_10_P1_SEMINOL7 | Apply 3-phase fault on DRAPER 7 to SEMINOL7 345kV line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_10_P1_SEMINOL7 | Apply 3-phase fault on DRAPER 7 to SEMINOL7 345kV line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_10_P1_SEMINOL7 | Apply 3-phase fault on DRAPER 7 to SEMINOL7 345kV line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_11_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_11_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_11_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_11_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_12_P1_SEMINOL7 | Apply 3-phase fault on ARCADIA7 to SEMINOL7 345kV line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_12_P1_SEMINOL7 | Apply 3-phase fault on ARCADIA7 to SEMINOL7 345kV line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_12_P1_SEMINOL7 | Apply 3-phase fault on ARCADIA7 to SEMINOL7 345kV line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_12_P1_SEMINOL7 | Apply 3-phase fault on ARCADIA7 to SEMINOL7 345kV line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_13_P1_VALIANT7 | Apply 3-phase fault on LYDIA to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_13_P1_VALIANT7 | Apply 3-phase fault on LYDIA to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.06s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_13_P1_VALIANT7 | Apply 3-phase fault on LYDIA to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_13_P1_VALIANT7 | Apply 3-phase fault on LYDIA to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_14_P1_VALIANT7 | Apply 3-phase fault on NWTXARK7 to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_14_P1_VALIANT7 | Apply 3-phase fault on NWTXARK7 to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.06s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_14_P1_VALIANT7 | Apply 3-phase fault on NWTXARK7 to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_14_P1_VALIANT7 | Apply 3-phase fault on NWTXARK7 to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_15_P1_LYDIA | Apply 3-phase fault on NWTXARK7 to LYDIA 345kV line CKT 1, near LYDIA 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_15_P1_LYDIA | Apply 3-phase fault on NWTXARK7 to LYDIA 345kV line CKT 1, near LYDIA 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_15_P1_LYDIA | Apply 3-phase fault on NWTXARK7 to LYDIA 345kV line CKT 1, near LYDIA 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_15_P1_LYDIA | Apply 3-phase fault on NWTXARK7 to LYDIA 345kV line CKT 1, near LYDIA 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_16_P1_NWTXARK7 | Apply 3-phase fault on NWTXARK7 to WELSH 345kV line CKT 1, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_16_P1_NWTXARK7 | Apply 3-phase fault on NWTXARK7 to WELSH 345kV line CKT 1, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_16_P1_NWTXARK7 | Apply 3-phase fault on NWTXARK7 to WELSH 345kV line CKT 1, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_16_P1_NWTXARK7 | Apply 3-phase fault on NWTXARK7 to WELSH 345kV line CKT 1, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_17_P1_NWTXARK7 | Apply 3-phase fault on TURK to NWTXARK7 345kV line CKT 1, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_17_P1_NWTXARK7 | Apply 3-phase fault on TURK to NWTXARK7 345kV line CKT 1, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_17_P1_NWTXARK7 | Apply 3-phase fault on TURK to NWTXARK7 345kV line CKT 1, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_17_P1_NWTXARK7 | Apply 3-phase fault on TURK to NWTXARK7 345kV line CKT 1, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_18_P1_NWTXARK7 | Apply 3-phase fault on NWTXARK4 138kV/345kV/13.8kV transformer CKT 2, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_18_P1_NWTXARK7 | Apply 3-phase fault on NWTXARK4 138kV/345kV/13.8kV transformer CKT 2, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_18_P1_NWTXARK7 | Apply 3-phase fault on NWTXARK4 138kV/345kV/13.8kV transformer CKT 2, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_18_P1_NWTXARK7 | Apply 3-phase fault on NWTXARK4 138kV/345kV/13.8kV transformer CKT 2, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_19_P1_LYDIA | Apply 3-phase fault on LYDIA to WELSH 345kV line CKT 1, near LYDIA 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_19_P1_LYDIA | Apply 3-phase fault on LYDIA to WELSH 345kV line CKT 1, near LYDIA 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_19_P1_LYDIA | Apply 3-phase fault on LYDIA to WELSH 345kV line CKT 1, near LYDIA 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_19_P1_LYDIA | Apply 3-phase fault on LYDIA to WELSH 345kV line CKT 1, near LYDIA 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_20_P1_G16-063-TAP | Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_20_P1_G16-063-TAP | Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.08s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_20_P1_G16-063-TAP | Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_20_P1_G16-063-TAP | Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_21_P1_SUNNYSD7 | Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_21_P1_SUNNYSD7 | Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_21_P1_SUNNYSD7 | Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_21_P1_SUNNYSD7 | Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_22_P1_JOHNCO7 | Apply 3-phase fault on JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_22_P1_JOHNCO7 | Apply 3-phase fault on JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_22_P1_JOHNCO7 | Apply 3-phase fault on JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_22_P1_JOHNCO7 | Apply 3-phase fault on JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_23_P1_SUNNYSD7 | Apply 3-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_23_P1_SUNNYSD7 | Apply 3-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_23_P1_SUNNYSD7 | Apply 3-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_23_P1_SUNNYSD7 | Apply 3-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_24_P1_SUNNYSD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_24_P1_SUNNYSD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_24_P1_SUNNYSD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_24_P1_SUNNYSD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_25_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.02s
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_25_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_25_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.01s
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_25_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.02s
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_26_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_26_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_26_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_26_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_27_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Open the faulted line and GRACMNT7 to G16-091-TAP 345kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and GRACMNT7 to G16-091-TAP 345kV line CKT 1. Re-open the faulted line after 6 cycles. Simultaneously re-open GRACMNT7 to G16-091-TAP 345kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_27_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Open the faulted line and GRACMNT7 to G16-091-TAP 345kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and GRACMNT7 to G16-091-TAP 345kV line CKT 1. Re-open the faulted line after 6 cycles. Simultaneously re-open GRACMNT7 to G16-091-TAP 345kV line CKT 1 and clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_27_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Open the faulted line and GRACMNT7 to G16-091-TAP 345kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and GRACMNT7 to G16-091-TAP 345kV line CKT 1. Re-open the faulted line after 6 cycles. Simultaneously re-open GRACMNT7 to G16-091-TAP 345kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_27_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Open the faulted line and GRACMNT7 to G16-091-TAP 345kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and GRACMNT7 to G16-091-TAP 345kV line CKT 1. Re-open the faulted line after 6 cycles. Simultaneously re-open GRACMNT7 to G16-091-TAP 345kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_28_P1_LES-7 | Apply 3-phase fault on L.E.S.-4 138kV/345kV/13.8kV transformer CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.26pu, MaxDur: 0.01s
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_28_P1_LES-7 | Apply 3-phase fault on L.E.S.-4 138kV/345kV/13.8kV transformer CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_28_P1_LES-7 | Apply 3-phase fault on L.E.S.-4 138kV/345kV/13.8kV transformer CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.25pu, MaxDur: 0.01s
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_28_P1_LES-7 | Apply 3-phase fault on L.E.S.-4 138kV/345kV/13.8kV transformer CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.23pu, MaxDur: 0.01s
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_29_P1_RUSHSPR7 | Apply 3-phase fault on RUSHSPR7 345kV/34.5kV/13.8kV transformer CKT 1, near RUSHSPR7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G15-045-GEN1[1]. G15-045-GEN1 tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_29_P1_RUSHSPR7 | Apply 3-phase fault on RUSHSPR7 345kV/34.5kV/13.8kV transformer CKT 1, near RUSHSPR7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | No | Yes | Yes | No | No | LVRT VIOL - - G15-045-GEN1[1]. G15-045-GEN1 tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_29_P1_RUSHSPR7 | Apply 3-phase fault on RUSHSPR7 345kV/34.5kV/13.8kV transformer CKT 1, near RUSHSPR7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G15-045-GEN1[1]. G15-045-GEN1 tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_29_P1_RUSHSPR7 | Apply 3-phase fault on RUSHSPR7 345kV/34.5kV/13.8kV transformer CKT 1, near RUSHSPR7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G15-045-GEN1[1]. G15-045-GEN1 tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_30_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.34pu, MaxDur: 0.03s
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_30_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_30_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.34pu, MaxDur: 0.03s
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_30_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.34pu, MaxDur: 0.03s
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_31_P1_HUGOPP4 | Apply 3-phase fault on VALIANT4 to HUGO PP4 138kV line CKT 1, near HUGO PP4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_31_P1_HUGOPP4 | Apply 3-phase fault on VALIANT4 to HUGO PP4 138kV line CKT 1, near HUGO PP4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_31_P1_HUGOPP4 | Apply 3-phase fault on VALIANT4 to HUGO PP4 138kV line CKT 1, near HUGO PP4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_31_P1_HUGOPP4 | Apply 3-phase fault on VALIANT4 to HUGO PP4 138kV line CKT 1, near HUGO PP4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_32_P1_HUGOPP4 | Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV line CKT 1, near HUGO PP4 138kV for 7 cycles. Open the faulted line and BROKNBW4 to HOLYCRK4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BROKNBW4 to HOLYCRK4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_32_P1_HUGOPP4 | Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV line CKT 1, near HUGO PP4 138kV for 7 cycles. Open the faulted line and BROKNBW4 to HOLYCRK4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BROKNBW4 to HOLYCRK4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_32_P1_HUGOPP4 | Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV line CKT 1, near HUGO PP4 138kV for 7 cycles. Open the faulted line and BROKNBW4 to HOLYCRK4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BROKNBW4 to HOLYCRK4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_32_P1_HUGOPP4 | Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV line CKT 1, near HUGO PP4 138kV for 7 cycles. Open the faulted line and BROKNBW4 to HOLYCRK4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BROKNBW4 to HOLYCRK4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_33_P1_FROGVIL4 | Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV line CKT 1, near FROGVIL4 138kV for 7 cycles. Open the faulted line and BENNGTN4 to UNGER 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BENNGTN4 to UNGER 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BENNGTN4 to UNGER 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_33_P1_FROGVIL4 | Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV line CKT 1, near FROGVIL4 138kV for 7 cycles. Open the faulted line and BENNGTN4 to UNGER 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BENNGTN4 to UNGER 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BENNGTN4 to UNGER 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_33_P1_FROGVIL4 | Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV line CKT 1, near FROGVIL4 138kV for 7 cycles. Open the faulted line and BENNGTN4 to UNGER 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BENNGTN4 to UNGER 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BENNGTN4 to UNGER 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_33_P1_FROGVIL4 | Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV line CKT 1, near FROGVIL4 138kV for 7 cycles. Open the faulted line and BENNGTN4 to UNGER 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BENNGTN4 to UNGER 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BENNGTN4 to UNGER 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_34_P1_BENNGTN4 | Apply 3-phase fault on BENNGTN4 to DURANTP4 138kV line CKT 1, near BENNGTN4 138kV for 7 cycles. Open the faulted line and S BROWN4 to KRSYJCTN4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and S BROWN4 to KRSYJCTN4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open S BROWN4 to KRSYJCTN4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_34_P1_BENNGTN4 | Apply 3-phase fault on BENNGTN4 to DURANTP4 138kV line CKT 1, near BENNGTN4 138kV for 7 cycles. Open the faulted line and S BROWN4 to KRSYJCTN4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and S BROWN4 to KRSYJCTN4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open S BROWN4 to KRSYJCTN4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_34_P1_BENNGTN4 | Apply 3-phase fault on BENNGTN4 to DURANTP4 138kV line CKT 1, near BENNGTN4 138kV for 7 cycles. Open the faulted line and S BROWN4 to KRSYJCTN4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and S BROWN4 to KRSYJCTN4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open S BROWN4 to KRSYJCTN4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_34_P1_BENNGTN4 | Apply 3-phase fault on BENNGTN4 to DURANTP4 138kV line CKT 1, near BENNGTN4 138kV for 7 cycles. Open the faulted line and S BROWN4 to KRSYJCTN4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and S BROWN4 to KRSYJCTN4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open S BROWN4 to KRSYJCTN4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_35_P1_HUGOPP4 | Apply 3-phase fault on SAWYER4 to HUGO PP4 138kV line CKT 1, near HUGO PP4 138kV for 7 cycles. Open the faulted line and ATOKA--4 to ATKEAST4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and ATOKA--4 to ATKEAST4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open ATOKA--4 to ATKEAST4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_35_P1_HUGOPP4 | Apply 3-phase fault on SAWYER4 to HUGO PP4 138kV line CKT 1, near HUGO PP4 138kV for 7 cycles. Open the faulted line and ATOKA--4 to ATKEAST4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and ATOKA--4 to ATKEAST4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open ATOKA--4 to ATKEAST4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_35_P1_HUGOPP4 | Apply 3-phase fault on SAWYER4 to HUGO PP4 138kV line CKT 1, near HUGO PP4 138kV for 7 cycles. Open the faulted line and ATOKA--4 to ATKEAST4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and ATOKA--4 to ATKEAST4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open ATOKA--4 to ATKEAST4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_35_P1_HUGOPP4 | Apply 3-phase fault on SAWYER4 to HUGO PP4 138kV line CKT 1, near HUGO PP4 138kV for 7 cycles. Open the faulted line and ATOKA--4 to ATKEAST4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and ATOKA--4 to ATKEAST4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open ATOKA--4 to ATKEAST4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_36_P1_ATOKA--4 | Apply 3-phase fault on ATOKA--4 to ATKWEST4 138kV line CKT 1, near ATOKA--4 138kV for 7 cycles. Open the faulted line and BOGYDPT4 to BOGGY4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BOGYDPT4 to BOGGY4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BOGYDPT4 to BOGGY4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_36_P1_ATOKA--4 | Apply 3-phase fault on ATOKA--4 to ATKWEST4 138kV line CKT 1, near ATOKA--4 138kV for 7 cycles. Open the faulted line and BOGYDPT4 to BOGGY4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BOGYDPT4 to BOGGY4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BOGYDPT4 to BOGGY4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_36_P1_ATOKA--4 | Apply 3-phase fault on ATOKA--4 to ATKWEST4 138kV line CKT 1, near ATOKA--4 138kV for 7 cycles. Open the faulted line and BOGYDPT4 to BOGGY4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BOGYDPT4 to BOGGY4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BOGYDPT4 to BOGGY4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_36_P1_ATOKA--4 | Apply 3-phase fault on ATOKA--4 to ATKWEST4 138kV line CKT 1, near ATOKA--4 138kV for 7 cycles. Open the faulted line and BOGYDPT4 to BOGGY4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BOGYDPT4 to BOGGY4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BOGYDPT4 to BOGGY4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_37_P1_ATOKA--4 | Apply 3-phase fault on ATOKA--4 to LEHIGH-4 138kV line CKT 1, near ATOKA--4 138kV for 7 cycles. Open the faulted line and TUPELO 4 to ALLENGT4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and TUPELO 4 to ALLENGT4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open TUPELO 4 to ALLENGT4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_37_P1_ATOKA--4 | Apply 3-phase fault on ATOKA--4 to LEHIGH-4 138kV line CKT 1, near ATOKA--4 138kV for 7 cycles. Open the faulted line and TUPELO 4 to ALLENGT4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and TUPELO 4 to ALLENGT4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open TUPELO 4 to ALLENGT4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_37_P1_ATOKA--4 | Apply 3-phase fault on ATOKA--4 to LEHIGH-4 138kV line CKT 1, near ATOKA--4 138kV for 7 cycles. Open the faulted line and TUPELO 4 to ALLENGT4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and TUPELO 4 to ALLENGT4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open TUPELO 4 to ALLENGT4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_37_P1_ATOKA--4 | Apply 3-phase fault on ATOKA--4 to LEHIGH-4 138kV line CKT 1, near ATOKA--4 138kV for 7 cycles. Open the faulted line and TUPELO 4 to ALLENGT4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and TUPELO 4 to ALLENGT4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open TUPELO 4 to ALLENGT4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_38_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to BOGGY4 138kV line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_38_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to BOGGY4 138kV line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_38_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to BOGGY4 138kV line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_38_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to BOGGY4 138kV line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_39_P1_BOGGY4 | Apply 3-phase fault on WAPANUCKA to BOGGY4 138kV line CKT 1, near BOGGY4 138kV for 7 cycles. Open the faulted line and WAPANUCKA to STNWLTP4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and WAPANUCKA to STNWLTP4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open WAPANUCKA to STNWLTP4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_39_P1_BOGGY4 | Apply 3-phase fault on WAPANUCKA to BOGGY4 138kV line CKT 1, near BOGGY4 138kV for 7 cycles. Open the faulted line and WAPANUCKA to STNWLTP4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and WAPANUCKA to STNWLTP4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open WAPANUCKA to STNWLTP4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_39_P1_BOGGY4 | Apply 3-phase fault on WAPANUCKA to BOGGY4 138kV line CKT 1, near BOGGY4 138kV for 7 cycles. Open the faulted line and WAPANUCKA to STNWLTP4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and WAPANUCKA to STNWLTP4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open WAPANUCKA to STNWLTP4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_39_P1_BOGGY4 | Apply 3-phase fault on WAPANUCKA to BOGGY4 138kV line CKT 1, near BOGGY4 138kV for 7 cycles. Open the faulted line and WAPANUCKA to STNWLTP4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and WAPANUCKA to STNWLTP4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open WAPANUCKA to STNWLTP4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_40_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to STNWLSW4 138kV line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_40_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to STNWLSW4 138kV line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_40_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to STNWLSW4 138kV line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_40_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to STNWLSW4 138kV line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_41_P1_TUPELO4 | Apply 3-phase fault on ALLEN to TUPELO 4 138kV line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_41_P1_TUPELO4 | Apply 3-phase fault on ALLEN to TUPELO 4 138kV line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_41_P1_TUPELO4 | Apply 3-phase fault on ALLEN to TUPELO 4 138kV line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_41_P1_TUPELO4 | Apply 3-phase fault on ALLEN to TUPELO 4 138kV line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_42_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to TUPELO 4 138kV line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_42_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to TUPELO 4 138kV line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_42_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to TUPELO 4 138kV line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_42_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to TUPELO 4 138kV line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_43_P1_VALIANT4 | Apply 3-phase fault on IDABEL-4 to VALIANT4 138kV line CKT 1, near VALIANT4 138kV for 7 cycles. Open the faulted line and B.BOWTP4 to CRAIGJT4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and B.BOWTP4 to CRAIGJT4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open B.BOWTP4 to CRAIGJT4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_43_P1_VALIANT4 | Apply 3-phase fault on IDABEL-4 to VALIANT4 138kV line CKT 1, near VALIANT4 138kV for 7 cycles. Open the faulted line and B.BOWTP4 to CRAIGJT4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and B.BOWTP4 to CRAIGJT4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open B.BOWTP4 to CRAIGJT4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_43_P1_VALIANT4 | Apply 3-phase fault on IDABEL-4 to VALIANT4 138kV line CKT 1, near VALIANT4 138kV for 7 cycles. Open the faulted line and B.BOWTP4 to CRAIGJT4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and B.BOWTP4 to CRAIGJT4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open B.BOWTP4 to CRAIGJT4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_43_P1_VALIANT4 | Apply 3-phase fault on IDABEL-4 to VALIANT4 138kV line CKT 1, near VALIANT4 138kV for 7 cycles. Open the faulted line and B.BOWTP4 to CRAIGJT4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and B.BOWTP4 to CRAIGJT4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open B.BOWTP4 to CRAIGJT4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_44_P1_CLAYTON4 | Apply 3-phase fault on CLAYTON4 to SARDIS 4 138kV line CKT 1, near CLAYTON4 138kV for 7 cycles. Open the faulted line and SARDIS 4 to ENOWILT4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and SARDIS 4 to ENOWILT4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open SARDIS 4 to ENOWILT4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.43pu, MaxDur: 0.01s
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_44_P1_CLAYTON4 | Apply 3-phase fault on CLAYTON4 to SARDIS 4 138kV line CKT 1, near CLAYTON4 138kV for 7 cycles. Open the faulted line and SARDIS 4 to ENOWILT4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and SARDIS 4 to ENOWILT4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open SARDIS 4 to ENOWILT4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.44pu, MaxDur: 0.01s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_44_P1_CLAYTON4 | Apply 3-phase fault on CLAYTON4 to SARDIS 4 138kV line CKT 1, near CLAYTON4 138kV for 7 cycles. Open the faulted line and SARDIS 4 to ENOWILT4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and SARDIS 4 to ENOWILT4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open SARDIS 4 to ENOWILT4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.43pu, MaxDur: 0.01s
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_44_P1_CLAYTON4 | Apply 3-phase fault on CLAYTON4 to SARDIS 4 138kV line CKT 1, near CLAYTON4 138kV for 7 cycles. Open the faulted line and SARDIS 4 to ENOWILT4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and SARDIS 4 to ENOWILT4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open SARDIS 4 to ENOWILT4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.43pu, MaxDur: 0.01s
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_45_P1_CRAIGJT4 | Apply 3-phase fault on CRAIGJT4 to MTRIVER4 138kV line CKT 1, near CRAIGJT4 138kV for 7 cycles. Open the faulted line and HOCHJCT4 to MTRIVER4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and HOCHJCT4 to MTRIVER4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open HOCHJCT4 to MTRIVER4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_45_P1_CRAIGJT4 | Apply 3-phase fault on CRAIGJT4 to MTRIVER4 138kV line CKT 1, near CRAIGJT4 138kV for 7 cycles. Open the faulted line and HOCHJCT4 to MTRIVER4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and HOCHJCT4 to MTRIVER4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open HOCHJCT4 to MTRIVER4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_45_P1_CRAIGJT4 | Apply 3-phase fault on CRAIGJT4 to MTRIVER4 138kV line CKT 1, near CRAIGJT4 138kV for 7 cycles. Open the faulted line and HOCHJCT4 to MTRIVER4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and HOCHJCT4 to MTRIVER4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open HOCHJCT4 to MTRIVER4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_45_P1_CRAIGJT4 | Apply 3-phase fault on CRAIGJT4 to MTRIVER4 138kV line CKT 1, near CRAIGJT4 138kV for 7 cycles. Open the faulted line and HOCHJCT4 to MTRIVER4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and HOCHJCT4 to MTRIVER4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open HOCHJCT4 to MTRIVER4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_46_P1_BRKNBW4 | Apply 3-phase fault on HOCHJCT4 to HOCHTWN4 138kV line CKT 1, near BRKN BW4 138kV for 7 cycles. Open the faulted line and BRKN BW4 to HOCHTWN4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BRKN BW4 to HOCHTWN4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BRKN BW4 to HOCHTWN4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_46_P1_BRKNBW4 | Apply 3-phase fault on HOCHJCT4 to HOCHTWN4 138kV line CKT 1, near BRKN BW4 138kV for 7 cycles. Open the faulted line and BRKN BW4 to HOCHTWN4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BRKN BW4 to HOCHTWN4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BRKN BW4 to HOCHTWN4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_46_P1_BRKNBW4 | Apply 3-phase fault on HOCHJCT4 to HOCHTWN4 138kV line CKT 1, near BRKN BW4 138kV for 7 cycles. Open the faulted line and BRKN BW4 to HOCHTWN4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BRKN BW4 to HOCHTWN4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BRKN BW4 to HOCHTWN4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_46_P1_BRKNBW4 | Apply 3-phase fault on HOCHJCT4 to HOCHTWN4 138kV line CKT 1, near BRKN BW4 138kV for 7 cycles. Open the faulted line and BRKN BW4 to HOCHTWN4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BRKN BW4 to HOCHTWN4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BRKN BW4 to HOCHTWN4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_47_P1_BROKNBW4 | Apply 3-phase fault on BROKNBW4 to GOLDENSW4 138kV line CKT 1, near BROKNBW4 138kV for 7 cycles. Open the faulted line and HOCHJCT4 to DOMINJCT4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and HOCHJCT4 to DOMINJCT4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open HOCHJCT4 to DOMINJCT4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_47_P1_BROKNBW4 | Apply 3-phase fault on BROKNBW4 to GOLDENSW4 138kV line CKT 1, near BROKNBW4 138kV for 7 cycles. Open the faulted line and HOCHJCT4 to DOMINJCT4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and HOCHJCT4 to DOMINJCT4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open HOCHJCT4 to DOMINJCT4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_47_P1_BROKNBW4 | Apply 3-phase fault on BROKNBW4 to GOLDENSW4 138kV line CKT 1, near BROKNBW4 138kV for 7 cycles. Open the faulted line and HOCHJCT4 to DOMINJCT4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and HOCHJCT4 to DOMINJCT4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open HOCHJCT4 to DOMINJCT4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_47_P1_BROKNBW4 | Apply 3-phase fault on BROKNBW4 to GOLDENSW4 138kV line CKT 1, near BROKNBW4 138kV for 7 cycles. Open the faulted line and HOCHJCT4 to DOMINJCT4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and HOCHJCT4 to DOMINJCT4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open HOCHJCT4 to DOMINJCT4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_48_P1_SBROWN4 | Apply 3-phase fault on S BROWN4 to BROWN 138kV line CKT 1, near S BROWN4 138kV for 7 cycles. Open the faulted line and BROWNTP4 to STRRDTP4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BROWNTP4 to STRRDTP4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BROWNTP4 to STRRDTP4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_48_P1_SBROWN4 | Apply 3-phase fault on S BROWN4 to BROWN 138kV line CKT 1, near S BROWN4 138kV for 7 cycles. Open the faulted line and BROWNTP4 to STRRDTP4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BROWNTP4 to STRRDTP4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BROWNTP4 to STRRDTP4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.06s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_48_P1_SBROWN4 | Apply 3-phase fault on S BROWN4 to BROWN 138kV line CKT 1, near S BROWN4 138kV for 7 cycles. Open the faulted line and BROWNTP4 to STRRDTP4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BROWNTP4 to STRRDTP4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BROWNTP4 to STRRDTP4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_48_P1_SBROWN4 | Apply 3-phase fault on S BROWN4 to BROWN 138kV line CKT 1, near S BROWN4 138kV for 7 cycles. Open the faulted line and BROWNTP4 to STRRDTP4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BROWNTP4 to STRRDTP4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BROWNTP4 to STRRDTP4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_49_P1_SBROWN4 | Apply 3-phase fault on S BROWN4 to RUSSETT4 138kV line CKT 1, near S BROWN4 138kV for 7 cycles. Open the faulted line and RUSSET-4 to RUSSETT4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and RUSSET-4 to RUSSETT4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open RUSSET-4 to RUSSETT4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_49_P1_SBROWN4 | Apply 3-phase fault on S BROWN4 to RUSSETT4 138kV line CKT 1, near S BROWN4 138kV for 7 cycles. Open the faulted line and RUSSET-4 to RUSSETT4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and RUSSET-4 to RUSSETT4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open RUSSET-4 to RUSSETT4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G16-030-GEN1[1]. Voltage Spike: 1.20pu, MaxDur: 0.06s G16-030-GEN1[1] tripped on overfrequency protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_49_P1_SBROWN4 | Apply 3-phase fault on S BROWN4 to RUSSETT4 138kV line CKT 1, near S BROWN4 138kV for 7 cycles. Open the faulted line and RUSSET-4 to RUSSETT4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and RUSSET-4 to RUSSETT4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open RUSSET-4 to RUSSETT4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_49_P1_SBROWN4 | Apply 3-phase fault on S BROWN4 to RUSSETT4 138kV line CKT 1, near S BROWN4 138kV for 7 cycles. Open the faulted line and RUSSET-4 to RUSSETT4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and RUSSET-4 to RUSSETT4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open RUSSET-4 to RUSSETT4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_50_P1_RUSSET-4 | Apply 3-phase fault on RUSSET-4 to GLASSES4 138kV line CKT 1, near RUSSET-4 138kV for 7 cycles. Open the faulted line and MADINDT4 to CANEYCK4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and MADINDT4 to CANEYCK4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open MADINDT4 to CANEYCK4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_50_P1_RUSSET-4 | Apply 3-phase fault on RUSSET-4 to GLASSES4 138kV line CKT 1, near RUSSET-4 138kV for 7 cycles. Open the faulted line and MADINDT4 to CANEYCK4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and MADINDT4 to CANEYCK4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open MADINDT4 to CANEYCK4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.09s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_50_P1_RUSSET-4 | Apply 3-phase fault on RUSSET-4 to GLASSES4 138kV line CKT 1, near RUSSET-4 138kV for 7 cycles. Open the faulted line and MADINDT4 to CANEYCK4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and MADINDT4 to CANEYCK4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open MADINDT4 to CANEYCK4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_50_P1_RUSSET-4 | Apply 3-phase fault on RUSSET-4 to GLASSES4 138kV line CKT 1, near RUSSET-4 138kV for 7 cycles. Open the faulted line and MADINDT4 to CANEYCK4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and MADINDT4 to CANEYCK4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open MADINDT4 to CANEYCK4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_51_P1_RUSSET-4 | Apply 3-phase fault on JOHNCO 4 to RUSSET-4 138kV line CKT 1, near RUSSET-4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_51_P1_RUSSET-4 | Apply 3-phase fault on JOHNCO 4 to RUSSET-4 138kV line CKT 1, near RUSSET-4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.09s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_51_P1_RUSSET-4 | Apply 3-phase fault on JOHNCO 4 to RUSSET-4 138kV line CKT 1, near RUSSET-4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_51_P1_RUSSET-4 | Apply 3-phase fault on JOHNCO 4 to RUSSET-4 138kV line CKT 1, near RUSSET-4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_52_P1_RUSSET-4 | Apply 3-phase fault on RUSSET-4 to STIRLNG4 138kV line CKT 1, near RUSSET-4 138kV for 7 cycles. Open the faulted line and SPRNDAL4 to DRPSPRG4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and SPRNDAL4 to DRPSPRG4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open SPRNDAL4 to DRPSPRG4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_52_P1_RUSSET-4 | Apply 3-phase fault on RUSSET-4 to STIRLNG4 138kV line CKT 1, near RUSSET-4 138kV for 7 cycles. Open the faulted line and SPRNDAL4 to DRPSPRG4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and SPRNDAL4 to DRPSPRG4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open SPRNDAL4 to DRPSPRG4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.09s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_52_P1_RUSSET-4 | Apply 3-phase fault on RUSSET-4 to STIRLNG4 138kV line CKT 1, near RUSSET-4 138kV for 7 cycles. Open the faulted line and SPRNDAL4 to DRPSPRG4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and SPRNDAL4 to DRPSPRG4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open SPRNDAL4 to DRPSPRG4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_52_P1_RUSSET-4 | Apply 3-phase fault on RUSSET-4 to STIRLNG4 138kV line CKT 1, near RUSSET-4 138kV for 7 cycles. Open the faulted line and SPRNDAL4 to DRPSPRG4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and SPRNDAL4 to DRPSPRG4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open SPRNDAL4 to DRPSPRG4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_53_P1_JOHNCO4 | Apply 3-phase fault on JOHNCO 4 to CANEYCK4 138kV line CKT 1, near JOHNCO 4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_53_P1_JOHNCO4 | Apply 3-phase fault on JOHNCO 4 to CANEYCK4 138kV line CKT 1, near JOHNCO 4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_53_P1_JOHNCO4 | Apply 3-phase fault on JOHNCO 4 to CANEYCK4 138kV line CKT 1, near JOHNCO 4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_53_P1_JOHNCO4 | Apply 3-phase fault on JOHNCO 4 to CANEYCK4 138kV line CKT 1, near JOHNCO 4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_54_P1_SPRNDAL4 | Apply 3-phase fault on FNDTION4 to SPRNDAL4 138kV line CKT 1, near SPRNDAL4 138kV for 7 cycles. Open the faulted line and FNDTION4 to CHIKSAW4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and FNDTION4 to CHIKSAW4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open FNDTION4 to CHIKSAW4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_54_P1_SPRNDAL4 | Apply 3-phase fault on FNDTION4 to SPRNDAL4 138kV line CKT 1, near SPRNDAL4 138kV for 7 cycles. Open the faulted line and FNDTION4 to CHIKSAW4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and FNDTION4 to CHIKSAW4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open FNDTION4 to CHIKSAW4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.09s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_54_P1_SPRNDAL4 | Apply 3-phase fault on FNDTION4 to SPRNDAL4 138kV line CKT 1, near SPRNDAL4 138kV for 7 cycles. Open the faulted line and FNDTION4 to CHIKSAW4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and FNDTION4 to CHIKSAW4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open FNDTION4 to CHIKSAW4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_54_P1_SPRNDAL4 | Apply 3-phase fault on FNDTION4 to SPRNDAL4 138kV line CKT 1, near SPRNDAL4 138kV for 7 cycles. Open the faulted line and FNDTION4 to CHIKSAW4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and FNDTION4 to CHIKSAW4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open FNDTION4 to CHIKSAW4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_55_P1_JOHNCO4 | Apply 3-phase fault on JOHNCO 4 to SXMLCKT4 138kV line CKT 1, near JOHNCO 4 138kV for 7 cycles. Open the faulted line and ARBUCKL4 to MILLCKT4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and ARBUCKL4 to MILLCKT4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open ARBUCKL4 to MILLCKT4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_55_P1_JOHNCO4 | Apply 3-phase fault on JOHNCO 4 to SXMLCKT4 138kV line CKT 1, near JOHNCO 4 138kV for 7 cycles. Open the faulted line and ARBUCKL4 to MILLCKT4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and ARBUCKL4 to MILLCKT4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open ARBUCKL4 to MILLCKT4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_55_P1_JOHNCO4 | Apply 3-phase fault on JOHNCO 4 to SXMLCKT4 138kV line CKT 1, near JOHNCO 4 138kV for 7 cycles. Open the faulted line and ARBUCKL4 to MILLCKT4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and ARBUCKL4 to MILLCKT4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open ARBUCKL4 to MILLCKT4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_55_P1_JOHNCO4 | Apply 3-phase fault on JOHNCO 4 to SXMLCKT4 138kV line CKT 1, near JOHNCO 4 138kV for 7 cycles. Open the faulted line and ARBUCKL4 to MILLCKT4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and ARBUCKL4 to MILLCKT4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open ARBUCKL4 to MILLCKT4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_56_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to ROCKYPT4 138kV line CKT 1, near SUNNYSD4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_56_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to ROCKYPT4 138kV line CKT 1, near SUNNYSD4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_56_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to ROCKYPT4 138kV line CKT 1, near SUNNYSD4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_56_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to ROCKYPT4 138kV line CKT 1, near SUNNYSD4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_57_P1_CARTER4 | Apply 3-phase fault on CARTER 4 to CHIKSAW4 138kV line CKT 1, near CARTER 4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_57_P1_CARTER4 | Apply 3-phase fault on CARTER 4 to CHIKSAW4 138kV line CKT 1, near CARTER 4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.09s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_57_P1_CARTER4 | Apply 3-phase fault on CARTER 4 to CHIKSAW4 138kV line CKT 1, near CARTER 4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_57_P1_CARTER4 | Apply 3-phase fault on CARTER 4 to CHIKSAW4 138kV line CKT 1, near CARTER 4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_58_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to UNIROY 4 138kV line CKT 1, near SUNNYSD4 138kV for 7 cycles. Open the faulted line and CARTER 4 to ARDWEST4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and CARTER 4 to ARDWEST4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open CARTER 4 to ARDWEST4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_58_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to UNIROY 4 138kV line CKT 1, near SUNNYSD4 138kV for 7 cycles. Open the faulted line and CARTER 4 to ARDWEST4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and CARTER 4 to ARDWEST4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open CARTER 4 to ARDWEST4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_58_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to UNIROY 4 138kV line CKT 1, near SUNNYSD4 138kV for 7 cycles. Open the faulted line and CARTER 4 to ARDWEST4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and CARTER 4 to ARDWEST4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open CARTER 4 to ARDWEST4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_58_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to UNIROY 4 138kV line CKT 1, near SUNNYSD4 138kV for 7 cycles. Open the faulted line and CARTER 4 to ARDWEST4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and CARTER 4 to ARDWEST4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open CARTER 4 to ARDWEST4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_59_P1_CARTER4 | Apply 3-phase fault on CARTER 4 to HONEYCK4 138kV line CKT 1, near CARTER 4 138kV for 7 cycles. Open the faulted line and ARBUCKL4 to SULPHR 4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and ARBUCKL4 to SULPHR 4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open ARBUCKL4 to SULPHR 4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_59_P1_CARTER4 | Apply 3-phase fault on CARTER 4 to HONEYCK4 138kV line CKT 1, near CARTER 4 138kV for 7 cycles. Open the faulted line and ARBUCKL4 to SULPHR 4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and ARBUCKL4 to SULPHR 4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open ARBUCKL4 to SULPHR 4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.09s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_59_P1_CARTER4 | Apply 3-phase fault on CARTER 4 to HONEYCK4 138kV line CKT 1, near CARTER 4 138kV for 7 cycles. Open the faulted line and ARBUCKL4 to SULPHR 4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and ARBUCKL4 to SULPHR 4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open ARBUCKL4 to SULPHR 4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_59_P1_CARTER4 | Apply 3-phase fault on CARTER 4 to HONEYCK4 138kV line CKT 1, near CARTER 4 138kV for 7 cycles. Open the faulted line and ARBUCKL4 to SULPHR 4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and ARBUCKL4 to SULPHR 4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open ARBUCKL4 to SULPHR 4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_60_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to VANOSTP4 138kV line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_60_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to VANOSTP4 138kV line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.04s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_60_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to VANOSTP4 138kV line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_60_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to VANOSTP4 138kV line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_61_P1_PARKLN4 | Apply 3-phase fault on VANOSS 4 to PARKLN 4 138kV line CKT 1, near PARKLN 4 138kV for 7 cycles. Open the faulted line and VANOSS 4 to VANOSTP4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and VANOSS 4 to VANOSTP4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open VANOSS 4 to VANOSTP4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_61_P1_PARKLN4 | Apply 3-phase fault on VANOSS 4 to PARKLN 4 138kV line CKT 1, near PARKLN 4 138kV for 7 cycles. Open the faulted line and VANOSS 4 to VANOSTP4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and VANOSS 4 to VANOSTP4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open VANOSS 4 to VANOSTP4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.06s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_61_P1_PARKLN4 | Apply 3-phase fault on VANOSS 4 to PARKLN 4 138kV line CKT 1, near PARKLN 4 138kV for 7 cycles. Open the faulted line and VANOSS 4 to VANOSTP4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and VANOSS 4 to VANOSTP4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open VANOSS 4 to VANOSTP4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_61_P1_PARKLN4 | Apply 3-phase fault on VANOSS 4 to PARKLN 4 138kV line CKT 1, near PARKLN 4 138kV for 7 cycles. Open the faulted line and VANOSS 4 to VANOSTP4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and VANOSS 4 to VANOSTP4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open VANOSS 4 to VANOSTP4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_62_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to PARKLN 4 138kV line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_62_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to PARKLN 4 138kV line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.04s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_62_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to PARKLN 4 138kV line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_62_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to PARKLN 4 138kV line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_63_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to MAUD 138kV line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_63_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to MAUD 138kV line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.04s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_63_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to MAUD 138kV line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_63_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to MAUD 138kV line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_64_P1_CARTRCO4 | Apply 3-phase fault on SUNNYSD4 to CARTRCO4 138kV line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_64_P1_CARTRCO4 | Apply 3-phase fault on SUNNYSD4 to CARTRCO4 138kV line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.04s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_64_P1_CARTRCO4 | Apply 3-phase fault on SUNNYSD4 to CARTRCO4 138kV line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_64_P1_CARTRCO4 | Apply 3-phase fault on SUNNYSD4 to CARTRCO4 138kV line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_65_P1_CARTRCO4 | Apply 3-phase fault on POOLVIL4 to CARTRCO4 138kV line CKT 1, near CARTRCO4 138kV for 7 cycles. Open the faulted line and DUNDEE 4 to HLTNTAP4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and DUNDEE 4 to HLTNTAP4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open DUNDEE 4 to HLTNTAP4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_65_P1_CARTRCO4 | Apply 3-phase fault on POOLVIL4 to CARTRCO4 138kV line CKT 1, near CARTRCO4 138kV for 7 cycles. Open the faulted line and DUNDEE 4 to HLTNTAP4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and DUNDEE 4 to HLTNTAP4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open DUNDEE 4 to HLTNTAP4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.04s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_65_P1_CARTRCO4 | Apply 3-phase fault on POOLVIL4 to CARTRCO4 138kV line CKT 1, near CARTRCO4 138kV for 7 cycles. Open the faulted line and DUNDEE 4 to HLTNTAP4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and DUNDEE 4 to HLTNTAP4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open DUNDEE 4 to HLTNTAP4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_65_P1_CARTRCO4 | Apply 3-phase fault on POOLVIL4 to CARTRCO4 138kV line CKT 1, near CARTRCO4 138kV for 7 cycles. Open the faulted line and DUNDEE 4 to HLTNTAP4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and DUNDEE 4 to HLTNTAP4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open DUNDEE 4 to HLTNTAP4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_66_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to LONEGRV4 138kV line CKT 1, near SUNNYSD4 138kV for 7 cycles. Open the faulted line and HLTNTAP4 to DILLARD4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and HLTNTAP4 to DILLARD4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open HLTNTAP4 to DILLARD4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_66_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to LONEGRV4 138kV line CKT 1, near SUNNYSD4 138kV for 7 cycles. Open the faulted line and HLTNTAP4 to DILLARD4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and HLTNTAP4 to DILLARD4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open HLTNTAP4 to DILLARD4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_66_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to LONEGRV4 138kV line CKT 1, near SUNNYSD4 138kV for 7 cycles. Open the faulted line and HLTNTAP4 to DILLARD4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and HLTNTAP4 to DILLARD4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open HLTNTAP4 to DILLARD4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_66_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to LONEGRV4 138kV line CKT 1, near SUNNYSD4 138kV for 7 cycles. Open the faulted line and HLTNTAP4 to DILLARD4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and HLTNTAP4 to DILLARD4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open HLTNTAP4 to DILLARD4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_67_P1_RATLIFF4 | Apply 3-phase fault on RATLIFF4 to PRARPNT4 138kV line CKT 1, near RATLIFF4 138kV for 7 cycles. Open the faulted line and SEMINOL4 to PAOLI- 4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and SEMINOL4 to PAOLI- 4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open SEMINOL4 to PAOLI- 4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_67_P1_RATLIFF4 | Apply 3-phase fault on RATLIFF4 to PRARPNT4 138kV line CKT 1, near RATLIFF4 138kV for 7 cycles. Open the faulted line and SEMINOL4 to PAOLI- 4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and SEMINOL4 to PAOLI- 4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open SEMINOL4 to PAOLI- 4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_67_P1_RATLIFF4 | Apply 3-phase fault on RATLIFF4 to PRARPNT4 138kV line CKT 1, near RATLIFF4 138kV for 7 cycles. Open the faulted line and SEMINOL4 to PAOLI- 4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and SEMINOL4 to PAOLI- 4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open SEMINOL4 to PAOLI- 4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_67_P1_RATLIFF4 | Apply 3-phase fault on RATLIFF4 to PRARPNT4 138kV line CKT 1, near RATLIFF4 138kV for 7 cycles. Open the faulted line and SEMINOL4 to PAOLI- 4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and SEMINOL4 to PAOLI- 4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open SEMINOL4 to PAOLI- 4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_68_P1_CARTRCO4 | Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_68_P1_CARTRCO4 | Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_68_P1_CARTRCO4 | Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_68_P1_CARTRCO4 | Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_69_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_69_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.06s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_69_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_69_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_70_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_70_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_70_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_70_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_71_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_71_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_71_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_71_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_72_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV line CKT 1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_72_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV line CKT 1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_72_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV line CKT 1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_72_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV line CKT 1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_73_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV line CKT 1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_73_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV line CKT 1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.07s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_73_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV line CKT 1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_73_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV line CKT 1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_74_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.01s LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_74_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.05s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_74_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.01s LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_74_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.01s LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_75_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_75_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_75_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_75_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_76_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.01s LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_76_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.05s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_76_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.01s LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_76_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.01s LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_77_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu,MaxDur: 0.00s LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_77_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_77_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.00s LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_77_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - LANoGSU10.60[W1]. Voltage Spike: 1.20pu, MaxDur: 0.00s LANOGSU10.60[W1] tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_78_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.24pu, MaxDur: 0.02s
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_78_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.22pu, MaxDur: 0.09s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_78_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.26pu, MaxDur: 0.02s
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_78_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.25pu, MaxDur: 0.02s
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_79_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.34pu, MaxDur: 0.04s
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_79_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.22pu, MaxDur: 0.09s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_79_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.30pu, MaxDur: 0.03s
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_79_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.35pu, MaxDur: 0.03s
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_80_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_80_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.07s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_80_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_80_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_81_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_81_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_81_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_81_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_82_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.27pu, MaxDur: 0.05s
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_82_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_82_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.27pu, MaxDur: 0.04s
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_82_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.25pu, MaxDur: 0.04s
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_83_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.23pu, MaxDur: 0.04s
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_83_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_83_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.22pu, MaxDur: 0.03s
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_83_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.03s
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_84_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.05s
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_84_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.05s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_84_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.05s
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_84_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.04s
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_85_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.23pu, MaxDur: 0.08s
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_85_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_85_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.09s
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_85_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.08s
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_86_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.33pu, MaxDur: 0.04s
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_86_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.22pu, MaxDur: 0.09s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_86_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.33pu, MaxDur: 0.04s
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_86_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.32pu, MaxDur: 0.04s
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_87_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_87_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.07s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_87_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_87_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_88_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.04s
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_88_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_88_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_88_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_89_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.04s
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_89_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.04s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_89_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.04s
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_89_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.04s
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_90_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.24pu, MaxDur: 0.08s
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_90_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_90_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.05s
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_90_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.08s
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_91_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.05s
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_91_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_91_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.04s
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_91_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.04s
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_92_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_92_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.05s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_92_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_92_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_93_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_93_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_93_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_93_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_94_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_94_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_94_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_94_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_95_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.05s
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_95_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | No | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_95_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_95_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.04s
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_96_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_96_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.05s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_96_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_96_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_97_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_97_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_97_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_97_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_98_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_98_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_98_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_98_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_99_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_99_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_99_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_99_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_100_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_100_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_100_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_100_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_101_P4_HUGO | Apply single-phase fault on VALIANT7 to HUGO 345kV line CKT 1, near HUGO 345kV for 16 cycles with stuck breaker at HUGO. Open the faulted line and HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_101_P4_HUGO | Apply single-phase fault on VALIANT7 to HUGO 345kV line CKT 1, near HUGO 345kV for 16 cycles with stuck breaker at HUGO. Open the faulted line and HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_101_P4_HUGO | Apply single-phase fault on VALIANT7 to HUGO 345kV line CKT 1, near HUGO 345kV for 16 cycles with stuck breaker at HUGO. Open the faulted line and HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_101_P4_HUGO | Apply single-phase fault on VALIANT7 to HUGO 345kV line CKT 1, near HUGO 345kV for 16 cycles with stuck breaker at HUGO. Open the faulted line and HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_102_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted line and NWTXARK7 to VALIANT7 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_102_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted line and NWTXARK7 to VALIANT7 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_102_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted line and NWTXARK7 to VALIANT7 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_102_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted line and NWTXARK7 to VALIANT7 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_103_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted line and PITTSB-7 to VALIANT7 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_103_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted line and PITTSB-7 to VALIANT7 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_103_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted line and PITTSB-7 to VALIANT7 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_103_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted line and PITTSB-7 to VALIANT7 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_104_P4_VALIANT7 | Apply single-phase fault on NWTXARK7 to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted line and PITTSB-7 to VALIANT7 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_104_P4_VALIANT7 | Apply single-phase fault on NWTXARK7 to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted line and PITTSB-7 to VALIANT7 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_104_P4_VALIANT7 | Apply single-phase fault on NWTXARK7 to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted line and PITTSB-7 to VALIANT7 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_104_P4_VALIANT7 | Apply single-phase fault on NWTXARK7 to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted line and PITTSB-7 to VALIANT7 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_105_P4_SUNNYSD7 | Apply single-phase fault on SUNNYSD7 345kV/138kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Three Winding and SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_105_P4_SUNNYSD7 | Apply single-phase fault on SUNNYSD7 345kV/138kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Three Winding and SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | No | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_105_P4_SUNNYSD7 | Apply single-phase fault on SUNNYSD7 345kV/138kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Three Winding and SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_105_P4_SUNNYSD7 | Apply single-phase fault on SUNNYSD7 345kV/138kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Three Winding and SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_106_P4_SUNNYSD7 | Apply single-phase fault on TERRYRD7 to SUNNYSD7 345kV line CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted line and JOHNCO 7 to SUNNYSD7 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_106_P4_SUNNYSD7 | Apply single-phase fault on TERRYRD7 to SUNNYSD7 345kV line CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted line and JOHNCO 7 to SUNNYSD7 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.09s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_106_P4_SUNNYSD7 | Apply single-phase fault on TERRYRD7 to SUNNYSD7 345kV line CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted line and JOHNCO 7 to SUNNYSD7 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_106_P4_SUNNYSD7 | Apply single-phase fault on TERRYRD7 to SUNNYSD7 345kV line CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted line and JOHNCO 7 to SUNNYSD7 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_107_P4_JOHNCO7 | Apply single-phase fault on PITTSB-7 to JOHNCO 7 345kV line CKT 1, near JOHNCO 7 345kV for 16 cycles with stuck breaker at JOHNCO 7. Open the faulted line and JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_107_P4_JOHNCO7 | Apply single-phase fault on PITTSB-7 to JOHNCO 7 345kV line CKT 1, near JOHNCO 7 345kV for 16 cycles with stuck breaker at JOHNCO 7. Open the faulted line and JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.06s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_107_P4_JOHNCO7 | Apply single-phase fault on PITTSB-7 to JOHNCO 7 345kV line CKT 1, near JOHNCO 7 345kV for 16 cycles with stuck breaker at JOHNCO 7. Open the faulted line and JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_107_P4_JOHNCO7 | Apply single-phase fault on PITTSB-7 to JOHNCO 7 345kV line CKT 1, near JOHNCO 7 345kV for 16 cycles with stuck breaker at JOHNCO 7. Open the faulted line and JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_108_P4_PITTSB-7 | Apply single-phase fault on PITTSB-7 to C-RIVER7 345kV line CKT 1, near PITTSB-7 345kV for 16 cycles with stuck breaker at PITTSB-7. Open the faulted line and PITTSB-7 to SEMINOL7 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_108_P4_PITTSB-7 | Apply single-phase fault on PITTSB-7 to C-RIVER7 345kV line CKT 1, near PITTSB-7 345kV for 16 cycles with stuck breaker at PITTSB-7. Open the faulted line and PITTSB-7 to SEMINOL7 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.06s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_108_P4_PITTSB-7 | Apply single-phase fault on PITTSB-7 to C-RIVER7 345kV line CKT 1, near PITTSB-7 345kV for 16 cycles with stuck breaker at PITTSB-7. Open the faulted line and PITTSB-7 to SEMINOL7 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_108_P4_PITTSB-7 | Apply single-phase fault on PITTSB-7 to C-RIVER7 345kV line CKT 1, near PITTSB-7 345kV for 16 cycles with stuck breaker at PITTSB-7. Open the faulted line and PITTSB-7 to SEMINOL7 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_109_P4_LES-7 | Apply single-phase fault on O.K.U.-7 to L.E.S.-7 345kV line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted line and L.E.S.-7 to G16-091-TAP 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_109_P4_LES-7 | Apply single-phase fault on O.K.U.-7 to L.E.S.-7 345kV line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted line and L.E.S.-7 to G16-091-TAP 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | No | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_109_P4_LES-7 | Apply single-phase fault on O.K.U.-7 to L.E.S.-7 345kV line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted line and L.E.S.-7 to G16-091-TAP 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_109_P4_LES-7 | Apply single-phase fault on O.K.U.-7 to L.E.S.-7 345kV line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted line and L.E.S.-7 to G16-091-TAP 345kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_110_P4_HUGOPP4 | Apply single-phase fault on VALIANT4 to HUGO PP4 138kV line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted line and HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_110_P4_HUGOPP4 | Apply single-phase fault on VALIANT4 to HUGO PP4 138kV line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted line and HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_110_P4_HUGOPP4 | Apply single-phase fault on VALIANT4 to HUGO PP4 138kV line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted line and HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_110_P4_HUGOPP4 | Apply single-phase fault on VALIANT4 to HUGO PP4 138kV line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted line and HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_111_P4_HUGOPP4 | Apply single-phase fault on HUGO PP4 to VALLANT4 138kV line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted line and BROKNBW4 to HOLYCRK4 138kV line CKT 1 and HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_111_P4_HUGOPP4 | Apply single-phase fault on HUGO PP4 to VALLANT4 138kV line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted line and BROKNBW4 to HOLYCRK4 138kV line CKT 1 and HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_111_P4_HUGOPP4 | Apply single-phase fault on HUGO PP4 to VALLANT4 138kV line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted line and BROKNBW4 to HOLYCRK4 138kV line CKT 1 and HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_111_P4_HUGOPP4 | Apply single-phase fault on HUGO PP4 to VALLANT4 138kV line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted line and BROKNBW4 to HOLYCRK4 138kV line CKT 1 and HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_112_P4_VALIANT4 | Apply single-phase fault on VALIANT4 138kV/345kV/13.8kV transformer CKT 2, near VALIANT4 138kV for 16 cycles with stuck breaker at VALIANT4. Open the faulted Three Winding and VALIANT4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_112_P4_VALIANT4 | Apply single-phase fault on VALIANT4 138kV/345kV/13.8kV transformer CKT 2, near VALIANT4 138kV for 16 cycles with stuck breaker at VALIANT4. Open the faulted Three Winding and VALIANT4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_112_P4_VALIANT4 | Apply single-phase fault on VALIANT4 138kV/345kV/13.8kV transformer CKT 2, near VALIANT4 138kV for 16 cycles with stuck breaker at VALIANT4. Open the faulted Three Winding and VALIANT4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_112_P4_VALIANT4 | Apply single-phase fault on VALIANT4 138kV/345kV/13.8kV transformer CKT 2, near VALIANT4 138kV for 16 cycles with stuck breaker at VALIANT4. Open the faulted Three Winding and VALIANT4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_113_P4_SBROWN4 | Apply single-phase fault on S BROWN4 to COLBRTP4 138kV line CKT 1, near S BROWN4 138kV for 16 cycles with stuck breaker at S BROWN4. Open the faulted line and S BROWN4 to RUSSETT4 138kV line CKT 1 and RUSSET-4 to RUSSETT4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_113_P4_SBROWN4 | Apply single-phase fault on S BROWN4 to COLBRTP4 138kV line CKT 1, near S BROWN4 138kV for 16 cycles with stuck breaker at S BROWN4. Open the faulted line and S BROWN4 to RUSSETT4 138kV line CKT 1 and RUSSET-4 to RUSSETT4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_113_P4_SBROWN4 | Apply single-phase fault on S BROWN4 to COLBRTP4 138kV line CKT 1, near S BROWN4 138kV for 16 cycles with stuck breaker at S BROWN4. Open the faulted line and S BROWN4 to RUSSETT4 138kV line CKT 1 and RUSSET-4 to RUSSETT4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_113_P4_SBROWN4 | Apply single-phase fault on S BROWN4 to COLBRTP4 138kV line CKT 1, near S BROWN4 138kV for 16 cycles with stuck breaker at S BROWN4. Open the faulted line and S BROWN4 to RUSSETT4 138kV line CKT 1 and RUSSET-4 to RUSSETT4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_114_P4_SBROWN4 | Apply single-phase fault on TUPELO 4 to S BROWN4 138kV line CKT 1, near S BROWN4 138kV for 16 cycles with stuck breaker at S BROWN4. Open the faulted line and S BROWN4 to RUSSETT4 138kV line CKT 1 and RUSSET-4 to RUSSETT4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_114_P4_SBROWN4 | Apply single-phase fault on TUPELO 4 to S BROWN4 138kV line CKT 1, near S BROWN4 138kV for 16 cycles with stuck breaker at S BROWN4. Open the faulted line and S BROWN4 to RUSSETT4 138kV line CKT 1 and RUSSET-4 to RUSSETT4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_114_P4_SBROWN4 | Apply single-phase fault on TUPELO 4 to S BROWN4 138kV line CKT 1, near S BROWN4 138kV for 16 cycles with stuck breaker at S BROWN4. Open the faulted line and S BROWN4 to RUSSETT4 138kV line CKT 1 and RUSSET-4 to RUSSETT4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_114_P4_SBROWN4 | Apply single-phase fault on TUPELO 4 to S BROWN4 138kV line CKT 1, near S BROWN4 138kV for 16 cycles with stuck breaker at S BROWN4. Open the faulted line and S BROWN4 to RUSSETT4 138kV line CKT 1 and RUSSET-4 to RUSSETT4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_115_P4_CARTRCO4 | Apply single-phase fault on SUNNYSD4 to CARTRCO4 138kV line CKT 1, near CARTRCO4 138kV for 16 cycles with stuck breaker at CARTRCO4. Open the faulted line and RATLIFF4 to CARTRCO4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | G1140G1204G10.6900 (#515917) and G1140G1204G20.6900 (#515919) have small oscillation responses. The primary mitigation was applied and the simulation was rerun. No further issues were observed. | Invalid contingencey
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_115_P4_CARTRCO4 | Apply single-phase fault on SUNNYSD4 to CARTRCO4 138kV line CKT 1, near CARTRCO4 138kV for 16 cycles with stuck breaker at CARTRCO4. Open the faulted line and RATLIFF4 to CARTRCO4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | G1140G1204G10.6900 (#515917) and G1140G1204G20.6900 (#515919) have small oscillation responses. The primary mitigation was applied and the simulation was rerun. No further issues were observed. | Invalid contingencey
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_115_P4_CARTRCO4 | Apply single-phase fault on SUNNYSD4 to CARTRCO4 138kV line CKT 1, near CARTRCO4 138kV for 16 cycles with stuck breaker at CARTRCO4. Open the faulted line and RATLIFF4 to CARTRCO4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | G1140G1204G10.6900 (#515917) and G1140G1204G20.6900 (#515919) have small oscillation responses. The primary mitigation was applied and the simulation was rerun. No further issues were observed. | Invalid contingencey
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_115_P4_CARTRCO4 | Apply single-phase fault on SUNNYSD4 to CARTRCO4 138kV line CKT 1, near CARTRCO4 138kV for 16 cycles with stuck breaker at CARTRCO4. Open the faulted line and RATLIFF4 to CARTRCO4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | G1140G1204G10.6900 (#515917) and G1140G1204G20.6900 (#515919) have small oscillation responses. The primary mitigation was applied and the simulation was rerun. No further issues were observed. | Invalid contingencey
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_116_P4_CARTRCO4 | Apply single-phase fault on SUNNYSD4 to CARTRCO4 138kV line CKT 1, near CARTRCO4 138kV for 16 cycles with stuck breaker at CARTRCO4. Open the faulted line and POOLVIL4 to CARTRCO4 138kV line CKT 1 and DUNDEE 4 to HLTNTAP4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_116_P4_CARTRCO4 | Apply single-phase fault on SUNNYSD4 to CARTRCO4 138kV line CKT 1, near CARTRCO4 138kV for 16 cycles with stuck breaker at CARTRCO4. Open the faulted line and POOLVIL4 to CARTRCO4 138kV line CKT 1 and DUNDEE 4 to HLTNTAP4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_116_P4_CARTRCO4 | Apply single-phase fault on SUNNYSD4 to CARTRCO4 138kV line CKT 1, near CARTRCO4 138kV for 16 cycles with stuck breaker at CARTRCO4. Open the faulted line and POOLVIL4 to CARTRCO4 138kV line CKT 1 and DUNDEE 4 to HLTNTAP4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_116_P4_CARTRCO4 | Apply single-phase fault on SUNNYSD4 to CARTRCO4 138kV line CKT 1, near CARTRCO4 138kV for 16 cycles with stuck breaker at CARTRCO4. Open the faulted line and POOLVIL4 to CARTRCO4 138kV line CKT 1 and DUNDEE 4 to HLTNTAP4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_117_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD7 345kV/138kV/13.8kV transformer CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Three Winding and SUNNYSD4 to ROCKYPT4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_117_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD7 345kV/138kV/13.8kV transformer CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Three Winding and SUNNYSD4 to ROCKYPT4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.08s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_117_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD7 345kV/138kV/13.8kV transformer CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Three Winding and SUNNYSD4 to ROCKYPT4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_117_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD7 345kV/138kV/13.8kV transformer CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Three Winding and SUNNYSD4 to ROCKYPT4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_118_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Three Winding and SUNNYSD4 to UNIROY 4 138kV line CKT 1 and CARTER 4 to ARDWEST4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_118_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Three Winding and SUNNYSD4 to UNIROY 4 138kV line CKT 1 and CARTER 4 to ARDWEST4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.09s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_118_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Three Winding and SUNNYSD4 to UNIROY 4 138kV line CKT 1 and CARTER 4 to ARDWEST4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_118_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Three Winding and SUNNYSD4 to UNIROY 4 138kV line CKT 1 and CARTER 4 to ARDWEST4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_119_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 to ROCKYPT4 138kV line CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted line and SUNNYSD4 to UNIROY 4 138kV line CKT 1 and CARTER 4 to ARDWEST4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_119_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 to ROCKYPT4 138kV line CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted line and SUNNYSD4 to UNIROY 4 138kV line CKT 1 and CARTER 4 to ARDWEST4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.08s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_119_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 to ROCKYPT4 138kV line CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted line and SUNNYSD4 to UNIROY 4 138kV line CKT 1 and CARTER 4 to ARDWEST4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_119_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 to ROCKYPT4 138kV line CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted line and SUNNYSD4 to UNIROY 4 138kV line CKT 1 and CARTER 4 to ARDWEST4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_120_P4_HUGOPP4 | Apply single-phase fault on VALIANT4 to HUGO PP4 138kV line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted line and HUGO PP4 to VALLANT4 138kV line CKT 1 and BROKNBW4 to HOLYCRK4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_120_P4_HUGOPP4 | Apply single-phase fault on VALIANT4 to HUGO PP4 138kV line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted line and HUGO PP4 to VALLANT4 138kV line CKT 1 and BROKNBW4 to HOLYCRK4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_120_P4_HUGOPP4 | Apply single-phase fault on VALIANT4 to HUGO PP4 138kV line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted line and HUGO PP4 to VALLANT4 138kV line CKT 1 and BROKNBW4 to HOLYCRK4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_120_P4_HUGOPP4 | Apply single-phase fault on VALIANT4 to HUGO PP4 138kV line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted line and HUGO PP4 to VALLANT4 138kV line CKT 1 and BROKNBW4 to HOLYCRK4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_121_P4_HUGOPP4 | Apply single-phase fault on HUGO 345kV/138kV/13.8kV transformer CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Three Winding and SAWYER4 to HUGO PP4 138kV line CKT 1 and ATOKA--4 to ATKEAST4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_121_P4_HUGOPP4 | Apply single-phase fault on HUGO 345kV/138kV/13.8kV transformer CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Three Winding and SAWYER4 to HUGO PP4 138kV line CKT 1 and ATOKA--4 to ATKEAST4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_121_P4_HUGOPP4 | Apply single-phase fault on HUGO 345kV/138kV/13.8kV transformer CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Three Winding and SAWYER4 to HUGO PP4 138kV line CKT 1 and ATOKA--4 to ATKEAST4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_121_P4_HUGOPP4 | Apply single-phase fault on HUGO 345kV/138kV/13.8kV transformer CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Three Winding and SAWYER4 to HUGO PP4 138kV line CKT 1 and ATOKA--4 to ATKEAST4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_122_P4_VALIANT4 | Apply single-phase fault on V-WEYCO4 to VALIANT4 138kV line CKT 1, near VALIANT4 138kV for 16 cycles with stuck breaker at VALIANT4. Open the faulted line and IDABEL-4 to VALIANT4 138kV line CKT 1 and B.BOWTP4 to CRAIGJT4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_122_P4_VALIANT4 | Apply single-phase fault on V-WEYCO4 to VALIANT4 138kV line CKT 1, near VALIANT4 138kV for 16 cycles with stuck breaker at VALIANT4. Open the faulted line and IDABEL-4 to VALIANT4 138kV line CKT 1 and B.BOWTP4 to CRAIGJT4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_122_P4_VALIANT4 | Apply single-phase fault on V-WEYCO4 to VALIANT4 138kV line CKT 1, near VALIANT4 138kV for 16 cycles with stuck breaker at VALIANT4. Open the faulted line and IDABEL-4 to VALIANT4 138kV line CKT 1 and B.BOWTP4 to CRAIGJT4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_122_P4_VALIANT4 | Apply single-phase fault on V-WEYCO4 to VALIANT4 138kV line CKT 1, near VALIANT4 138kV for 16 cycles with stuck breaker at VALIANT4. Open the faulted line and IDABEL-4 to VALIANT4 138kV line CKT 1 and B.BOWTP4 to CRAIGJT4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_123_P4_SEMINOL4 | Apply single-phase fault on SEMINOL4 138kV/345kV/14.39kV transformer CKT 1, near SEMINOL4 138kV for 16 cycles with stuck breaker at SEMINOL4. Open the faulted Three Winding and SEMINOL4 138kV/345kV/14.39kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_123_P4_SEMINOL4 | Apply single-phase fault on SEMINOL4 138kV/345kV/14.39kV transformer CKT 1, near SEMINOL4 138kV for 16 cycles with stuck breaker at SEMINOL4. Open the faulted Three Winding and SEMINOL4 138kV/345kV/14.39kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | No | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_123_P4_SEMINOL4 | Apply single-phase fault on SEMINOL4 138kV/345kV/14.39kV transformer CKT 1, near SEMINOL4 138kV for 16 cycles with stuck breaker at SEMINOL4. Open the faulted Three Winding and SEMINOL4 138kV/345kV/14.39kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_123_P4_SEMINOL4 | Apply single-phase fault on SEMINOL4 138kV/345kV/14.39kV transformer CKT 1, near SEMINOL4 138kV for 16 cycles with stuck breaker at SEMINOL4. Open the faulted Three Winding and SEMINOL4 138kV/345kV/14.39kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_124_P6_G16-063-TAP | Prior Outage of SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_124_P6_G16-063-TAP | Prior Outage of SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.08s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_124_P6_G16-063-TAP | Prior Outage of SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_124_P6_G16-063-TAP | Prior Outage of SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_125_P6_G16-063-TAP | Prior Outage of TERRYRD7 to SUNNYSD7 345kV line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_125_P6_G16-063-TAP | Prior Outage of TERRYRD7 to SUNNYSD7 345kV line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_125_P6_G16-063-TAP | Prior Outage of TERRYRD7 to SUNNYSD7 345kV line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_125_P6_G16-063-TAP | Prior Outage of TERRYRD7 to SUNNYSD7 345kV line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_126_P6_G16-063-TAP | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_126_P6_G16-063-TAP | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.07s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_126_P6_G16-063-TAP | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_126_P6_G16-063-TAP | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_127_P6_HUGO | Prior Outage of TERRYRD7 to SUNNYSD7 345kV line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_127_P6_HUGO | Prior Outage of TERRYRD7 to SUNNYSD7 345kV line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_127_P6_HUGO | Prior Outage of TERRYRD7 to SUNNYSD7 345kV line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_127_P6_HUGO | Prior Outage of TERRYRD7 to SUNNYSD7 345kV line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_128_P6_HUGO | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_128_P6_HUGO | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_128_P6_HUGO | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_128_P6_HUGO | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_129_P6_G16-063-TAP | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_129_P6_G16-063-TAP | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.08s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_129_P6_G16-063-TAP | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_129_P6_G16-063-TAP | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_130_P6_G16-063-TAP | Prior Outage of VALIANT7 to HUGO 345kV line CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_130_P6_G16-063-TAP | Prior Outage of VALIANT7 to HUGO 345kV line CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.09s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_130_P6_G16-063-TAP | Prior Outage of VALIANT7 to HUGO 345kV line CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_130_P6_G16-063-TAP | Prior Outage of VALIANT7 to HUGO 345kV line CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_131_P6_JOHNCO7 | Prior Outage of L.E.S.-7 to TERRYRD7 345kV line CKT 1Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.02s
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_131_P6_JOHNCO7 | Prior Outage of L.E.S.-7 to TERRYRD7 345kV line CKT 1Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.07s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_131_P6_JOHNCO7 | Prior Outage of L.E.S.-7 to TERRYRD7 345kV line CKT 1Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_131_P6_JOHNCO7 | Prior Outage of L.E.S.-7 to TERRYRD7 345kV line CKT 1Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.01s
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_132_P6_G16-063-TAP | Prior Outage of L.E.S.-7 to TERRYRD7 345kV line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_132_P6_G16-063-TAP | Prior Outage of L.E.S.-7 to TERRYRD7 345kV line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.05s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_132_P6_G16-063-TAP | Prior Outage of L.E.S.-7 to TERRYRD7 345kV line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_132_P6_G16-063-TAP | Prior Outage of L.E.S.-7 to TERRYRD7 345kV line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_133_P6_HUGO | Prior Outage of PITTSB-7 to VALIANT7 345kV line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_133_P6_HUGO | Prior Outage of PITTSB-7 to VALIANT7 345kV line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.03s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_133_P6_HUGO | Prior Outage of PITTSB-7 to VALIANT7 345kV line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_133_P6_HUGO | Prior Outage of PITTSB-7 to VALIANT7 345kV line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_134_P6_VALIANT7 | Prior Outage of NWTXARK7 to VALIANT7 345kV line CKT 1Apply 3-phase fault on LYDIA to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_134_P6_VALIANT7 | Prior Outage of NWTXARK7 to VALIANT7 345kV line CKT 1Apply 3-phase fault on LYDIA to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.05s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_134_P6_VALIANT7 | Prior Outage of NWTXARK7 to VALIANT7 345kV line CKT 1Apply 3-phase fault on LYDIA to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_134_P6_VALIANT7 | Prior Outage of NWTXARK7 to VALIANT7 345kV line CKT 1Apply 3-phase fault on LYDIA to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_135_P6_CARTRCO4 | Prior Outage of SUNNYSD4 to CARTRCO4 138kV line CKT 1Apply 3-phase fault on DUNDEE 4 to HLTNTAP4 138kV line CKT 1, near CARTRCO4 138kV for 7 cycles. Open the faulted line and POOLVIL4 to CARTRCO4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and POOLVIL4 to CARTRCO4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open POOLVIL4 to CARTRCO4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_135_P6_CARTRCO4 | Prior Outage of SUNNYSD4 to CARTRCO4 138kV line CKT 1Apply 3-phase fault on DUNDEE 4 to HLTNTAP4 138kV line CKT 1, near CARTRCO4 138kV for 7 cycles. Open the faulted line and POOLVIL4 to CARTRCO4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and POOLVIL4 to CARTRCO4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open POOLVIL4 to CARTRCO4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.28pu, MaxDur: 0.02s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_135_P6_CARTRCO4 | Prior Outage of SUNNYSD4 to CARTRCO4 138kV line CKT 1Apply 3-phase fault on DUNDEE 4 to HLTNTAP4 138kV line CKT 1, near CARTRCO4 138kV for 7 cycles. Open the faulted line and POOLVIL4 to CARTRCO4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and POOLVIL4 to CARTRCO4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open POOLVIL4 to CARTRCO4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.22pu, MaxDur: 0.01s
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_135_P6_CARTRCO4 | Prior Outage of SUNNYSD4 to CARTRCO4 138kV line CKT 1Apply 3-phase fault on DUNDEE 4 to HLTNTAP4 138kV line CKT 1, near CARTRCO4 138kV for 7 cycles. Open the faulted line and POOLVIL4 to CARTRCO4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and POOLVIL4 to CARTRCO4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open POOLVIL4 to CARTRCO4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.22pu, MaxDur: 0.01s
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_136_P6_CARTRCO4 | Prior Outage of SUNNYSD4 to CARTRCO4 138kV line CKT 1Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | G1140G1204G10.6900 (#515917) and G1140G1204G20.6900 (#515919) have small oscillation responses. The primary mitigation was applied and the simulation was rerun. No further issues were observed. | reduce outputs of G17-027-GEN20.6900 (#588714) to 21MW and G17-027-GEN30.6900 (#588715) to 18MW;
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_136_P6_CARTRCO4 | Prior Outage of SUNNYSD4 to CARTRCO4 138kV line CKT 1Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.21pu, MaxDur: 0.01s G1140G1204G10.6900 (#515917) and G1140G1204G20.6900 (#515919) have small oscillation responses. The primary mitigation was applied and the simulation was rerun. No further issues were observed. | reduce outputs of G17-027-GEN20.6900 (#588714) to 21MW and G17-027-GEN30.6900 (#588715) to 18MW;
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_136_P6_CARTRCO4 | Prior Outage of SUNNYSD4 to CARTRCO4 138kV line CKT 1Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | G1140G1204G10.6900 (#515917) and G1140G1204G20.6900 (#515919) have small oscillation responses. The primary mitigation was applied and the simulation was rerun. No further issues were observed. | reduce outputs of G17-027-GEN20.6900 (#588714) to 21MW and G17-027-GEN30.6900 (#588715) to 18MW;
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_136_P6_CARTRCO4 | Prior Outage of SUNNYSD4 to CARTRCO4 138kV line CKT 1Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | G1140G1204G10.6900 (#515917) and G1140G1204G20.6900 (#515919) have small oscillation responses. The primary mitigation was applied and the simulation was rerun. No further issues were observed. | reduce outputs of G17-027-GEN20.6900 (#588714) to 21MW and G17-027-GEN30.6900 (#588715) to 18MW;
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_137_P6_CARTRCO4 | Prior Outage of POOLVIL4 to CARTRCO4 138kV line CKT 1Prior Outage of DUNDEE 4 to HLTNTAP4 138kV line CKT 1Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.00s
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_137_P6_CARTRCO4 | Prior Outage of POOLVIL4 to CARTRCO4 138kV line CKT 1Prior Outage of DUNDEE 4 to HLTNTAP4 138kV line CKT 1Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Voltage Spike: 1.20pu, MaxDur: 0.05s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_137_P6_CARTRCO4 | Prior Outage of POOLVIL4 to CARTRCO4 138kV line CKT 1Prior Outage of DUNDEE 4 to HLTNTAP4 138kV line CKT 1Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_137_P6_CARTRCO4 | Prior Outage of POOLVIL4 to CARTRCO4 138kV line CKT 1Prior Outage of DUNDEE 4 to HLTNTAP4 138kV line CKT 1Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_138_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on VALIANT4 to HUGO PP4 138kV line CKT 1, near HUGO PP4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_138_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on VALIANT4 to HUGO PP4 138kV line CKT 1, near HUGO PP4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_138_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on VALIANT4 to HUGO PP4 138kV line CKT 1, near HUGO PP4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_139_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV line CKT 1, near HUGO PP4 138kV for 7 cycles. Open the faulted line and BROKNBW4 to HOLYCRK4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BROKNBW4 to HOLYCRK4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_139_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV line CKT 1, near HUGO PP4 138kV for 7 cycles. Open the faulted line and BROKNBW4 to HOLYCRK4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BROKNBW4 to HOLYCRK4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_139_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV line CKT 1, near HUGO PP4 138kV for 7 cycles. Open the faulted line and BROKNBW4 to HOLYCRK4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BROKNBW4 to HOLYCRK4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_139_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV line CKT 1, near HUGO PP4 138kV for 7 cycles. Open the faulted line and BROKNBW4 to HOLYCRK4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BROKNBW4 to HOLYCRK4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_140_P6_FROGVIL4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV line CKT 1, near FROGVIL4 138kV for 7 cycles. Open the faulted line and BENNGTN4 to UNGER 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BENNGTN4 to UNGER 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BENNGTN4 to UNGER 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_140_P6_FROGVIL4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV line CKT 1, near FROGVIL4 138kV for 7 cycles. Open the faulted line and BENNGTN4 to UNGER 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BENNGTN4 to UNGER 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BENNGTN4 to UNGER 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_140_P6_FROGVIL4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV line CKT 1, near FROGVIL4 138kV for 7 cycles. Open the faulted line and BENNGTN4 to UNGER 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BENNGTN4 to UNGER 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BENNGTN4 to UNGER 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_140_P6_FROGVIL4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV line CKT 1, near FROGVIL4 138kV for 7 cycles. Open the faulted line and BENNGTN4 to UNGER 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BENNGTN4 to UNGER 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BENNGTN4 to UNGER 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_141_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on SAWYER4 to HUGO PP4 138kV line CKT 1, near HUGO PP4 138kV for 7 cycles. Open the faulted line and ATOKA--4 to ATKEAST4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and ATOKA--4 to ATKEAST4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open ATOKA--4 to ATKEAST4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_141_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on SAWYER4 to HUGO PP4 138kV line CKT 1, near HUGO PP4 138kV for 7 cycles. Open the faulted line and ATOKA--4 to ATKEAST4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and ATOKA--4 to ATKEAST4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open ATOKA--4 to ATKEAST4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_141_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on SAWYER4 to HUGO PP4 138kV line CKT 1, near HUGO PP4 138kV for 7 cycles. Open the faulted line and ATOKA--4 to ATKEAST4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and ATOKA--4 to ATKEAST4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open ATOKA--4 to ATKEAST4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_141_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on SAWYER4 to HUGO PP4 138kV line CKT 1, near HUGO PP4 138kV for 7 cycles. Open the faulted line and ATOKA--4 to ATKEAST4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and ATOKA--4 to ATKEAST4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open ATOKA--4 to ATKEAST4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_142_P6_HUGOPP4 | Prior Outage of VALIANT4 to HUGO PP4 138kV line CKT 1Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV line CKT 1, near HUGO PP4 138kV for 7 cycles. Open the faulted line and BROKNBW4 to HOLYCRK4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BROKNBW4 to HOLYCRK4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_142_P6_HUGOPP4 | Prior Outage of VALIANT4 to HUGO PP4 138kV line CKT 1Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV line CKT 1, near HUGO PP4 138kV for 7 cycles. Open the faulted line and BROKNBW4 to HOLYCRK4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BROKNBW4 to HOLYCRK4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_142_P6_HUGOPP4 | Prior Outage of VALIANT4 to HUGO PP4 138kV line CKT 1Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV line CKT 1, near HUGO PP4 138kV for 7 cycles. Open the faulted line and BROKNBW4 to HOLYCRK4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BROKNBW4 to HOLYCRK4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_142_P6_HUGOPP4 | Prior Outage of VALIANT4 to HUGO PP4 138kV line CKT 1Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV line CKT 1, near HUGO PP4 138kV for 7 cycles. Open the faulted line and BROKNBW4 to HOLYCRK4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BROKNBW4 to HOLYCRK4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_143_P6_FROGVIL4 | Prior Outage of SAWYER4 to HUGO PP4 138kV line CKT 1Prior Outage of ATOKA--4 to ATKEAST4 138kV line CKT 1Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV line CKT 1, near FROGVIL4 138kV for 7 cycles. Open the faulted line and BENNGTN4 to UNGER 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BENNGTN4 to UNGER 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BENNGTN4 to UNGER 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_143_P6_FROGVIL4 | Prior Outage of SAWYER4 to HUGO PP4 138kV line CKT 1Prior Outage of ATOKA--4 to ATKEAST4 138kV line CKT 1Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV line CKT 1, near FROGVIL4 138kV for 7 cycles. Open the faulted line and BENNGTN4 to UNGER 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BENNGTN4 to UNGER 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BENNGTN4 to UNGER 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_143_P6_FROGVIL4 | Prior Outage of SAWYER4 to HUGO PP4 138kV line CKT 1Prior Outage of ATOKA--4 to ATKEAST4 138kV line CKT 1Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV line CKT 1, near FROGVIL4 138kV for 7 cycles. Open the faulted line and BENNGTN4 to UNGER 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BENNGTN4 to UNGER 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BENNGTN4 to UNGER 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_143_P6_FROGVIL4 | Prior Outage of SAWYER4 to HUGO PP4 138kV line CKT 1Prior Outage of ATOKA--4 to ATKEAST4 138kV line CKT 1Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV line CKT 1, near FROGVIL4 138kV for 7 cycles. Open the faulted line and BENNGTN4 to UNGER 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BENNGTN4 to UNGER 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BENNGTN4 to UNGER 138kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_144_P6_SBROWN4 | Prior Outage of S BROWN4 to RUSSETT4 138kV line CKT 1Prior Outage of RUSSET-4 to RUSSETT4 138kV line CKT 1Apply 3-phase fault on S BROWN4 to COLBRTP4 138kV line CKT 1, near S BROWN4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_144_P6_SBROWN4 | Prior Outage of S BROWN4 to RUSSETT4 138kV line CKT 1Prior Outage of RUSSET-4 to RUSSETT4 138kV line CKT 1Apply 3-phase fault on S BROWN4 to COLBRTP4 138kV line CKT 1, near S BROWN4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | No | LVRT VIOL - - G16-030-GEN1[1]. Voltage Spike: 1.20pu, MaxDur: 0.06s G16-030-GEN1[1] tripped on overfrequency protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_144_P6_SBROWN4 | Prior Outage of S BROWN4 to RUSSETT4 138kV line CKT 1Prior Outage of RUSSET-4 to RUSSETT4 138kV line CKT 1Apply 3-phase fault on S BROWN4 to COLBRTP4 138kV line CKT 1, near S BROWN4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_144_P6_SBROWN4 | Prior Outage of S BROWN4 to RUSSETT4 138kV line CKT 1Prior Outage of RUSSET-4 to RUSSETT4 138kV line CKT 1Apply 3-phase fault on S BROWN4 to COLBRTP4 138kV line CKT 1, near S BROWN4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT17-SB | Single Phase Fault with Stuck Breaker on BADGER 7 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to GEN-2011-014 (515686) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT11-SB | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT1-SB | Single Phase Fault with Stuck Breaker on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT2-SB | Single Phase Fault with Stuck Breaker on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to DRAPER 7 (514934) 345.0 kV Transmission Circuit b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT3-SB | Single Phase Fault with Stuck Breaker on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit b.2. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT4-SB | Single Phase Fault with Stuck Breaker on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to FSHRTAP7 (515610) 345.0 kV Transmission Circuit b.2. MINCO 7 (514801) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT8-SB | Single Phase Fault with Stuck Breaker on TATONGA7 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit b.2. TATONGA7 (515407) 345.0 kV to MAMTHPW7 (515585) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT9-SB | Single Phase Fault with Stuck Breaker on TATONGA7 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit b.2. TATONGA7 (515407) 345.0 kV to SLNGWND7 (515582) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT37-3PH | 3 Phase fault on CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYMAKR4 (514863) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit b.2. DVISION4 (514853) 138.0 kV to HAYMAKR4 (514863) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT42-3PH | 3 Phase fault on CANADN7 (515605) 345 kV Bus a. Apply fault at the CANADN7 (515605) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CANADN7 (515605) 345.0 kV to FSHRTAP7 (515610) 345.0 kV Transmission Circuit b.2. CIMARON7 (514901) 345.0 kV to FSHRTAP7 (515610) 345.0 kV Transmission Circuit b.3. KNGFSHR7 (515600) 345.0 kV to FSHRTAP7 (515610) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT15-3PH | 3 Phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT35-3PH | 3 Phase fault on CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV ThreeWinding | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT16-3PH | 3 Phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT3-PO | Prior Outage: BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit 3 Phase Fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT43-PO | Prior Outage: BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit 3 Phase Fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT13-SB | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT15-SB | Single Phase Fault with Stuck Breaker on BADGER 7 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to GEN-2011-014 (515686) 345.0 kV Transmission Circuit b.2. G16-003-TAP (560071) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT12-SB | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT35-PO | Prior Outage: CEMRD_TP4 (511576) 138.0 kV to CMTRYRD4 (515864) 138.0 kV Transmission Circuit TUTTLE4 (511501) 138.0 kV to LEONARD4 (511575) 138.0 kV Transmission Circuit TUTCONT4 (511425) 138.0 kV to CEMRD_TP4 (511576) 138.0 kV Transmission Circuit TUTCONT4 (511425) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit TUTCONT4 (511425) 138.0 kV to TUTTLE4 (511501) 138.0 kV Transmission Circuit T-CONCO4 (511424) 138.0 kV to CEMRD_TP4 (511576) 138.0 kV Transmission Circuit 3 Phase Fault on CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYMAKR4 (514863) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit b.2. DVISION4 (514853) 138.0 kV to HAYMAKR4 (514863) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT36-PO | Prior Outage: EL-RENO4 (514819) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit 3 Phase Fault on CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYMAKR4 (514863) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit b.2. DVISION4 (514853) 138.0 kV to HAYMAKR4 (514863) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT48-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit 3 Phase Fault on BADGER 7 (515677) 345 kV Bus a. Apply fault at the BADGER 7 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT46-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit 3 Phase Fault on BADGER 7 (515677) 345 kV Bus a. Apply fault at the BADGER 7 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT1-PO | Prior Outage: G16-003-TAP (560071) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit 3 Phase Fault on G16-003-TAP (560071) 345 kV Bus a. Apply fault at the G16-003-TAP (560071) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-003-TAP (560071) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT2-PO | Prior Outage: BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit 3 Phase Fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT45-PO | Prior Outage: BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit 3 Phase Fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT44-PO | Prior Outage: BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit 3 Phase Fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT26-PO | Prior Outage: CEMRD_TP4 (511576) 138.0 kV to CMTRYRD4 (515864) 138.0 kV Transmission Circuit TUTTLE4 (511501) 138.0 kV to LEONARD4 (511575) 138.0 kV Transmission Circuit TUTCONT4 (511425) 138.0 kV to CEMRD_TP4 (511576) 138.0 kV Transmission Circuit TUTCONT4 (511425) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit TUTCONT4 (511425) 138.0 kV to TUTTLE4 (511501) 138.0 kV Transmission Circuit T-CONCO4 (511424) 138.0 kV to CEMRD_TP4 (511576) 138.0 kV Transmission Circuit 3 Phase Fault on CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV ThreeWinding | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT27-PO | Prior Outage: EL-RENO4 (514819) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit 3 Phase Fault on CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV ThreeWinding | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT24-PO | Prior Outage: MCCLAIN4 (514902) 138.0 kV to STHLAKE4 (515481) 138.0 kV Transmission Circuit SARA 4 (514895) 138.0 kV to STHLAKE4 (515481) 138.0 kV Transmission Circuit SARA 4 (514895) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit 3 Phase Fault on CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV ThreeWinding | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT21-3PH | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV ThreeWinding | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT12-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV ThreeWinding | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT13-PO | Prior Outage: NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV ThreeWinding | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT22-3PH | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV ThreeWinding | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT14-PO | Prior Outage: NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV ThreeWinding | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT19-3PH | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT9-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT10-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT11-PO | Prior Outage: NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT6-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT7-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT5-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT8-PO | Prior Outage: NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT17-3PH | 3 Phase fault on NOVUS1 7 (523112) 345 kV Bus a. Apply fault at the NOVUS1 7 (523112) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV ThreeWinding | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT47-SB | Single Phase Fault with Stuck Breaker on MATHWSN7 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit b.2. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT48-SB | Single Phase Fault with Stuck Breaker on REDNGTN7 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit b.2. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT49-SB | Single Phase Fault with Stuck Breaker on TATONGA7 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit b.2. TATONGA7 (515407) 345.0 kV to SLNGWND7 (515582) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT32-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to G07621119-20 (515599) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT54-PO | Prior Outage: TRAVERSE1 (900001) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit 3 Phase Fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 19W | Transfer | G1_FLT45-3PH | 3 Phase fault on TRAVERSE1 (900001) 345 kV Bus a. Apply fault at the TRAVERSE1 (900001) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRAVERSE1 (900001) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21L | Transfer | G1_FLT11-SB | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21L | Transfer | G1_FLT1-SB | Single Phase Fault with Stuck Breaker on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21L | Transfer | G1_FLT2-SB | Single Phase Fault with Stuck Breaker on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to DRAPER 7 (514934) 345.0 kV Transmission Circuit b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21L | Transfer | G1_FLT3-SB | Single Phase Fault with Stuck Breaker on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit b.2. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21L | Transfer | G1_FLT4-SB | Single Phase Fault with Stuck Breaker on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to FSHRTAP7 (515610) 345.0 kV Transmission Circuit b.2. MINCO 7 (514801) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21L | Transfer | G1_FLT8-SB | Single Phase Fault with Stuck Breaker on TATONGA7 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit b.2. TATONGA7 (515407) 345.0 kV to MAMTHPW7 (515585) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21L | Transfer | G1_FLT9-SB | Single Phase Fault with Stuck Breaker on TATONGA7 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit b.2. TATONGA7 (515407) 345.0 kV to SLNGWND7 (515582) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21L | Transfer | G1_FLT39-3PH | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21L | Transfer | G1_FLT37-3PH | 3 Phase fault on CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYMAKR4 (514863) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit b.2. DVISION4 (514853) 138.0 kV to HAYMAKR4 (514863) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21L | Transfer | G1_FLT42-3PH | 3 Phase fault on CANADN7 (515605) 345 kV Bus a. Apply fault at the CANADN7 (515605) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CANADN7 (515605) 345.0 kV to FSHRTAP7 (515610) 345.0 kV Transmission Circuit b.2. CIMARON7 (514901) 345.0 kV to FSHRTAP7 (515610) 345.0 kV Transmission Circuit b.3. KNGFSHR7 (515600) 345.0 kV to FSHRTAP7 (515610) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21L | Transfer | G1_FLT44-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | No | Yes | Yes
Central | 01 - Woodward | 21L | Transfer | G1_FLT23-3PH | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21L | Transfer | G1_FLT35-3PH | 3 Phase fault on CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV ThreeWinding | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21L | Transfer | G1_FLT13-SB | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21L | Transfer | G1_FLT12-SB | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21L | Transfer | G1_FLT21-PO | Prior Outage: EL-RENO4 (514819) 138.0 kV to JENSENT4 (514820) 138.0 kV Transmission Circuit JENSENT4 (514820) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit JENSENT4 (514820) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit 3 Phase Fault on JENSEN 4 (514821) 138 kV Bus a. Apply fault at the JENSEN 4 (514821) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALBEAR4 (515460) 138.0 kV to TLBEART4 (515472) 138.0 kV Transmission Circuit b.2. CAN_GAS4 (511540) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit b.3. CAN_GAS4 (511540) 138.0 kV to TLBEART4 (515472) 138.0 kV Transmission Circuit b.4. CAN_GAS4 (511540) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21L | Transfer | G1_FLT35-PO | Prior Outage: CEMRD_TP4 (511576) 138.0 kV to CMTRYRD4 (515864) 138.0 kV Transmission Circuit TUTTLE4 (511501) 138.0 kV to LEONARD4 (511575) 138.0 kV Transmission Circuit TUTCONT4 (511425) 138.0 kV to CEMRD_TP4 (511576) 138.0 kV Transmission Circuit TUTCONT4 (511425) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit TUTCONT4 (511425) 138.0 kV to TUTTLE4 (511501) 138.0 kV Transmission Circuit T-CONCO4 (511424) 138.0 kV to CEMRD_TP4 (511576) 138.0 kV Transmission Circuit 3 Phase Fault on CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYMAKR4 (514863) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit b.2. DVISION4 (514853) 138.0 kV to HAYMAKR4 (514863) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21L | Transfer | G1_FLT36-PO | Prior Outage: EL-RENO4 (514819) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit 3 Phase Fault on CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYMAKR4 (514863) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit b.2. DVISION4 (514853) 138.0 kV to HAYMAKR4 (514863) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21L | Transfer | G1_FLT1-PO | Prior Outage: G16-003-TAP (560071) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit 3 Phase Fault on G16-003-TAP (560071) 345 kV Bus a. Apply fault at the G16-003-TAP (560071) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-003-TAP (560071) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21L | Transfer | G1_FLT51-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | No | Yes | Yes
Central | 01 - Woodward | 21L | Transfer | G1_FLT52-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | No | Yes | Yes
Central | 01 - Woodward | 21L | Transfer | G1_FLT50-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | No | Yes | Yes
Central | 01 - Woodward | 21L | Transfer | G1_FLT44-PO | Prior Outage: BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit 3 Phase Fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21L | Transfer | G1_FLT26-PO | Prior Outage: CEMRD_TP4 (511576) 138.0 kV to CMTRYRD4 (515864) 138.0 kV Transmission Circuit TUTTLE4 (511501) 138.0 kV to LEONARD4 (511575) 138.0 kV Transmission Circuit TUTCONT4 (511425) 138.0 kV to CEMRD_TP4 (511576) 138.0 kV Transmission Circuit TUTCONT4 (511425) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit TUTCONT4 (511425) 138.0 kV to TUTTLE4 (511501) 138.0 kV Transmission Circuit T-CONCO4 (511424) 138.0 kV to CEMRD_TP4 (511576) 138.0 kV Transmission Circuit 3 Phase Fault on CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV ThreeWinding | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21L | Transfer | G1_FLT27-PO | Prior Outage: EL-RENO4 (514819) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit 3 Phase Fault on CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV ThreeWinding | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21L | Transfer | G1_FLT25-PO | Prior Outage: HAYMAKR4 (514863) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit DVISION4 (514853) 138.0 kV to HAYMAKR4 (514863) 138.0 kV Transmission Circuit 3 Phase Fault on CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV ThreeWinding | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21L | Transfer | G1_FLT23-PO | Prior Outage: CZECHAL4 (514894) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit XEROX 4 (514893) 138.0 kV to CZECHAL4 (514894) 138.0 kV Transmission Circuit XEROX 4 (514893) 138.0 kV to MORGAN 4 (514896) 138.0 kV Transmission Circuit MUSTANG4 (514861) 138.0 kV to MORGAN 4 (514896) 138.0 kV Transmission Circuit 3 Phase Fault on CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV ThreeWinding | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21L | Transfer | G1_FLT24-PO | Prior Outage: MCCLAIN4 (514902) 138.0 kV to STHLAKE4 (515481) 138.0 kV Transmission Circuit SARA 4 (514895) 138.0 kV to STHLAKE4 (515481) 138.0 kV Transmission Circuit SARA 4 (514895) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit 3 Phase Fault on CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV ThreeWinding | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21L | Transfer | G1_FLT46-3PH | 3 Phase fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21L | Transfer | G1_FLT47-SB | Single Phase Fault with Stuck Breaker on MATHWSN7 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit b.2. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21L | Transfer | G1_FLT48-SB | Single Phase Fault with Stuck Breaker on REDNGTN7 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit b.2. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21L | Transfer | G1_FLT49-SB | Single Phase Fault with Stuck Breaker on TATONGA7 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit b.2. TATONGA7 (515407) 345.0 kV to SLNGWND7 (515582) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21L | Transfer | G1_FLT32-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to G07621119-20 (515599) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21L | Transfer | G1_FLT54-PO | Prior Outage: TRAVERSE1 (900001) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit 3 Phase Fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21L | Transfer | G1_FLT45-3PH | 3 Phase fault on TRAVERSE1 (900001) 345 kV Bus a. Apply fault at the TRAVERSE1 (900001) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRAVERSE1 (900001) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21S | Transfer | G1_FLT17-SB | Single Phase Fault with Stuck Breaker on BADGER 7 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to GEN-2011-014 (515686) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21S | Transfer | G1_FLT11-SB | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21S | Transfer | G1_FLT1-SB | Single Phase Fault with Stuck Breaker on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21S | Transfer | G1_FLT2-SB | Single Phase Fault with Stuck Breaker on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to DRAPER 7 (514934) 345.0 kV Transmission Circuit b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21S | Transfer | G1_FLT3-SB | Single Phase Fault with Stuck Breaker on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit b.2. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21S | Transfer | G1_FLT4-SB | Single Phase Fault with Stuck Breaker on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to FSHRTAP7 (515610) 345.0 kV Transmission Circuit b.2. MINCO 7 (514801) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21S | Transfer | G1_FLT8-SB | Single Phase Fault with Stuck Breaker on TATONGA7 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit b.2. TATONGA7 (515407) 345.0 kV to MAMTHPW7 (515585) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21S | Transfer | G1_FLT9-SB | Single Phase Fault with Stuck Breaker on TATONGA7 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit b.2. TATONGA7 (515407) 345.0 kV to SLNGWND7 (515582) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21S | Transfer | G1_FLT42-3PH | 3 Phase fault on CANADN7 (515605) 345 kV Bus a. Apply fault at the CANADN7 (515605) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CANADN7 (515605) 345.0 kV to FSHRTAP7 (515610) 345.0 kV Transmission Circuit b.2. CIMARON7 (514901) 345.0 kV to FSHRTAP7 (515610) 345.0 kV Transmission Circuit b.3. KNGFSHR7 (515600) 345.0 kV to FSHRTAP7 (515610) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21S | Transfer | G1_FLT15-3PH | 3 Phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21S | Transfer | G1_FLT16-3PH | 3 Phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21S | Transfer | G1_FLT3-PO | Prior Outage: BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit 3 Phase Fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21S | Transfer | G1_FLT43-PO | Prior Outage: BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit 3 Phase Fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21S | Transfer | G1_FLT13-SB | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21S | Transfer | G1_FLT15-SB | Single Phase Fault with Stuck Breaker on BADGER 7 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to GEN-2011-014 (515686) 345.0 kV Transmission Circuit b.2. G16-003-TAP (560071) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21S | Transfer | G1_FLT12-SB | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21S | Transfer | G1_FLT31-PO | Prior Outage: EL-RENO4 (514819) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit 3 Phase Fault on MUSTANG4 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CZECHAL4 (514894) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit b.2. XEROX 4 (514893) 138.0 kV to CZECHAL4 (514894) 138.0 kV Transmission Circuit b.3. XEROX 4 (514893) 138.0 kV to MORGAN 4 (514896) 138.0 kV Transmission Circuit b.4. MUSTANG4 (514861) 138.0 kV to MORGAN 4 (514896) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 511974: MACHINE TRIPPED ON OVERSPEED | DISABLE PROTECTION
Central | 01 - Woodward | 21S | Transfer | G1_FLT48-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit 3 Phase Fault on BADGER 7 (515677) 345 kV Bus a. Apply fault at the BADGER 7 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21S | Transfer | G1_FLT1-PO | Prior Outage: G16-003-TAP (560071) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit 3 Phase Fault on G16-003-TAP (560071) 345 kV Bus a. Apply fault at the G16-003-TAP (560071) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-003-TAP (560071) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 523160: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 01 - Woodward | 21S | Transfer | G1_FLT2-PO | Prior Outage: BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit 3 Phase Fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21S | Transfer | G1_FLT45-PO | Prior Outage: BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit 3 Phase Fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21S | Transfer | G1_FLT44-PO | Prior Outage: BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit 3 Phase Fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21S | Transfer | G1_FLT21-3PH | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV ThreeWinding | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21S | Transfer | G1_FLT12-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV ThreeWinding | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21S | Transfer | G1_FLT13-PO | Prior Outage: NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV ThreeWinding | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21S | Transfer | G1_FLT22-3PH | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV ThreeWinding | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21S | Transfer | G1_FLT14-PO | Prior Outage: NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV ThreeWinding | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21S | Transfer | G1_FLT19-3PH | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21S | Transfer | G1_FLT9-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21S | Transfer | G1_FLT10-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21S | Transfer | G1_FLT11-PO | Prior Outage: NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21S | Transfer | G1_FLT6-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21S | Transfer | G1_FLT7-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21S | Transfer | G1_FLT5-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21S | Transfer | G1_FLT8-PO | Prior Outage: NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21S | Transfer | G1_FLT17-3PH | 3 Phase fault on NOVUS1 7 (523112) 345 kV Bus a. Apply fault at the NOVUS1 7 (523112) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV ThreeWinding | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21S | Transfer | G1_FLT47-SB | Single Phase Fault with Stuck Breaker on MATHWSN7 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit b.2. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21S | Transfer | G1_FLT48-SB | Single Phase Fault with Stuck Breaker on REDNGTN7 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit b.2. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21S | Transfer | G1_FLT49-SB | Single Phase Fault with Stuck Breaker on TATONGA7 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit b.2. TATONGA7 (515407) 345.0 kV to SLNGWND7 (515582) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21S | Transfer | G1_FLT32-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to G07621119-20 (515599) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21S | Transfer | G1_FLT55-PO | Prior Outage: CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit 3 Phase Fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21S | Transfer | G1_FLT54-PO | Prior Outage: TRAVERSE1 (900001) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit 3 Phase Fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 21S | Transfer | G1_FLT45-3PH | 3 Phase fault on TRAVERSE1 (900001) 345 kV Bus a. Apply fault at the TRAVERSE1 (900001) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRAVERSE1 (900001) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 28S | Transfer | G1_FLT17-SB | Single Phase Fault with Stuck Breaker on BADGER 7 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to GEN-2011-014 (515686) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 28S | Transfer | G1_FLT11-SB | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 28S | Transfer | G1_FLT1-SB | Single Phase Fault with Stuck Breaker on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 28S | Transfer | G1_FLT2-SB | Single Phase Fault with Stuck Breaker on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to DRAPER 7 (514934) 345.0 kV Transmission Circuit b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 28S | Transfer | G1_FLT3-SB | Single Phase Fault with Stuck Breaker on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit b.2. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 28S | Transfer | G1_FLT4-SB | Single Phase Fault with Stuck Breaker on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to FSHRTAP7 (515610) 345.0 kV Transmission Circuit b.2. MINCO 7 (514801) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 28S | Transfer | G1_FLT8-SB | Single Phase Fault with Stuck Breaker on TATONGA7 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit b.2. TATONGA7 (515407) 345.0 kV to MAMTHPW7 (515585) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 28S | Transfer | G1_FLT9-SB | Single Phase Fault with Stuck Breaker on TATONGA7 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit b.2. TATONGA7 (515407) 345.0 kV to SLNGWND7 (515582) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 28S | Transfer | G1_FLT42-3PH | 3 Phase fault on CANADN7 (515605) 345 kV Bus a. Apply fault at the CANADN7 (515605) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CANADN7 (515605) 345.0 kV to FSHRTAP7 (515610) 345.0 kV Transmission Circuit b.2. CIMARON7 (514901) 345.0 kV to FSHRTAP7 (515610) 345.0 kV Transmission Circuit b.3. KNGFSHR7 (515600) 345.0 kV to FSHRTAP7 (515610) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 28S | Transfer | G1_FLT15-3PH | 3 Phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 28S | Transfer | G1_FLT12-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 588637: MACHINE TRIPPED DUE TO OVER FREQUENCY PROTECTION | DISABLE PROTECTION
Central | 01 - Woodward | 28S | Transfer | G1_FLT16-3PH | 3 Phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 28S | Transfer | G1_FLT3-PO | Prior Outage: BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit 3 Phase Fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 28S | Transfer | G1_FLT43-PO | Prior Outage: BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit 3 Phase Fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 28S | Transfer | G1_FLT13-SB | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 28S | Transfer | G1_FLT15-SB | Single Phase Fault with Stuck Breaker on BADGER 7 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to GEN-2011-014 (515686) 345.0 kV Transmission Circuit b.2. G16-003-TAP (560071) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 28S | Transfer | G1_FLT12-SB | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 28S | Transfer | G1_FLT1-PO | Prior Outage: G16-003-TAP (560071) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit 3 Phase Fault on G16-003-TAP (560071) 345 kV Bus a. Apply fault at the G16-003-TAP (560071) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-003-TAP (560071) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 523160: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 01 - Woodward | 28S | Transfer | G1_FLT2-PO | Prior Outage: BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit 3 Phase Fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 28S | Transfer | G1_FLT45-PO | Prior Outage: BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit 3 Phase Fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 28S | Transfer | G1_FLT44-PO | Prior Outage: BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit 3 Phase Fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 28S | Transfer | G1_FLT21-3PH | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV ThreeWinding | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 28S | Transfer | G1_FLT12-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV ThreeWinding | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 28S | Transfer | G1_FLT13-PO | Prior Outage: NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV ThreeWinding | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 28S | Transfer | G1_FLT22-3PH | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV ThreeWinding | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 28S | Transfer | G1_FLT14-PO | Prior Outage: NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV ThreeWinding | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 28S | Transfer | G1_FLT19-3PH | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 28S | Transfer | G1_FLT9-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 28S | Transfer | G1_FLT10-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 28S | Transfer | G1_FLT11-PO | Prior Outage: NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 28S | Transfer | G1_FLT6-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 28S | Transfer | G1_FLT7-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 28S | Transfer | G1_FLT5-PO | Prior Outage: HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 28S | Transfer | G1_FLT8-PO | Prior Outage: NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV ThreeWinding 3 Phase Fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 28S | Transfer | G1_FLT17-3PH | 3 Phase fault on NOVUS1 7 (523112) 345 kV Bus a. Apply fault at the NOVUS1 7 (523112) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV ThreeWinding | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 28S | Transfer | G1_FLT13-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 588637: MACHINE TRIPPED DUE TO OVER FREQUENCY PROTECTION | DISABLE PROTECTION
Central | 01 - Woodward | 28S | Transfer | G1_FLT14-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV ThreeWinding | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 588637: MACHINE TRIPPED DUE TO OVER FREQUENCY PROTECTION | DISABLE PROTECTION
Central | 01 - Woodward | 28S | Transfer | G1_FLT47-SB | Single Phase Fault with Stuck Breaker on MATHWSN7 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit b.2. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 28S | Transfer | G1_FLT48-SB | Single Phase Fault with Stuck Breaker on REDNGTN7 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit b.2. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 28S | Transfer | G1_FLT49-SB | Single Phase Fault with Stuck Breaker on TATONGA7 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit b.2. TATONGA7 (515407) 345.0 kV to SLNGWND7 (515582) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 28S | Transfer | G1_FLT32-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to G07621119-20 (515599) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 28S | Transfer | G1_FLT54-PO | Prior Outage: TRAVERSE1 (900001) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit 3 Phase Fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 01 - Woodward | 28S | Transfer | G1_FLT45-3PH | 3 Phase fault on TRAVERSE1 (900001) 345 kV Bus a. Apply fault at the TRAVERSE1 (900001) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRAVERSE1 (900001) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 19W | Transfer | G12_FLT44-3PH | 3 Phase fault on FARMNGTN 5 (504020) 161 kV Bus a. Apply fault at the FARMNGTN 5 (504020) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARMNGTN 5 (504020) 161.0 kV to FARM_1 2 (504021) 69.0 kV to FARM_T1 1 (504022) 13.8 kV ThreeWinding | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 19W | Transfer | G12_FLT36-3PH | 3 Phase fault on SILOAM 5 (506948) 161 kV Bus a. Apply fault at the SILOAM 5 (506948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SILOAM-1 (506917) 13.2 kV to SILOAM 5 (506948) 161.0 kV to SILOAM 2 (506973) 69.0 kV ThreeWinding | P1 | Stable | Yes | Yes | Yes | No | Yes | Yes
Central | 12 - Northwest Arkansas | 19W | Transfer | G12_FLT55-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 19W | Transfer | G12_FLT56-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to RSS T2 4 (509875) 138.0 kV to RSST2 T1 (509876) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 19W | Transfer | G12_FLT63-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit 3 Phase Fault on REDBUD 7 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 19W | Transfer | G12_FLT67-PO | Prior Outage: DARDANE5 (505508) 161.0 kV to CLARKSV5 (505514) 161.0 kV Transmission Circuit 3 Phase Fault on DARDANE5 (505508) 161 kV Bus a. Apply fault at the DARDANE5 (505508) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5RUSSELVL.S (337904) 161.0 kV to 5RUSSELVL.E! (337905) 161.0 kV Transmission Circuit b.2. 5RUSSELVL.S (337904) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit b.3. 5DARDANELLE (337903) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit b.4. 5DANVLE AR! (337902) 161.0 kV to 5DARDANELLE (337903) 161.0 kV Transmission Circuit b.5. 5HILLTOP% (338110) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 19W | Transfer | G12_FLT48-PO | Prior Outage: GREC TAP5 (512865) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit 3 Phase Fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 19W | Transfer | G12_FLT78-PO | Prior Outage: 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 19W | Transfer | G12_FLT76-PO | Prior Outage: 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 19W | Transfer | G12_FLT74-PO | Prior Outage: 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 19W | Transfer | G12_FLT29-PO | Prior Outage: CAR395 5 (547485) 161.0 kV to Trip Bus PUR421 5 (547491) 161.0 kV to Trip Bus 3 Phase Fault on ASB349 5 (547476) 161 kV Bus a. Apply fault at the ASB349 5 (547476) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 19W | Transfer | G12_FLT4-3PH | 3 Phase fault on LAR382 5 (547479) 161 kV Bus a. Apply fault at the LAR382 5 (547479) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAR382 5 (547479) 161.0 kV to GEN-2017-060 (588980) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 19W | Transfer | G12_FLT1-PO | Prior Outage: LAR382 5 (547479) 161.0 kV to GEN-2017-060 (588980) 161.0 kV Transmission Circuit 3 Phase Fault on CARTHAG5 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHAG5 (505488) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 19W | Transfer | G12_FLT2-PO | Prior Outage: LAR382 5 (547479) 161.0 kV to GEN-2017-060 (588980) 161.0 kV Transmission Circuit 3 Phase Fault on SPRGFLD5 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 19W | Transfer | G12_FLT65-SB | Single Phase Fault with Stuck Breaker on DARDANE5 (505508) 161 kV Bus a. Apply Fault at the DARDANE5 (505508) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DARDANE5 (505508) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 19W | Transfer | G12_FLT21-SB | Single Phase Fault with Stuck Breaker on FLINTCR5 (506934) 161 kV Bus a. Apply Fault at the FLINTCR5 (506934) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 19W | Transfer | G12_FLT62-SB | Single Phase Fault with Stuck Breaker on GREC TAP5 (512865) 345 kV Bus a. Apply Fault at the GREC TAP5 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREC TAP5 (512865) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 19W | Transfer | G12_FLT27-SB | Single Phase Fault with Stuck Breaker on ASB349 5 (547476) 161 kV Bus a. Apply Fault at the ASB349 5 (547476) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASB349 5 (547476) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 19W | Transfer | G12_FLT64-SB | Single Phase Fault with Stuck Breaker on FIREWHL-TAP (588839) 345 kV Bus a. Apply Fault at the FIREWHL-TAP (588839) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FIREWHL-TAP (588839) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21L | Transfer | G12_FLT44-3PH | 3 Phase fault on FARMNGTN 5 (504020) 161 kV Bus a. Apply fault at the FARMNGTN 5 (504020) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARMNGTN 5 (504020) 161.0 kV to FARM_1 2 (504021) 69.0 kV to FARM_T1 1 (504022) 13.8 kV ThreeWinding | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21L | Transfer | G12_FLT55-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21L | Transfer | G12_FLT56-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to RSS T2 4 (509875) 138.0 kV to RSST2 T1 (509876) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21L | Transfer | G12_FLT63-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit 3 Phase Fault on REDBUD 7 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21L | Transfer | G12_FLT48-PO | Prior Outage: GREC TAP5 (512865) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit 3 Phase Fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21L | Transfer | G12_FLT78-PO | Prior Outage: 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | No | Yes | Yes
Central | 12 - Northwest Arkansas | 21L | Transfer | G12_FLT76-PO | Prior Outage: 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | No | Yes | Yes
Central | 12 - Northwest Arkansas | 21L | Transfer | G12_FLT74-PO | Prior Outage: 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | No | Yes | Yes
Central | 12 - Northwest Arkansas | 21L | Transfer | G12_FLT29-PO | Prior Outage: CAR395 5 (547485) 161.0 kV to Trip Bus PUR421 5 (547491) 161.0 kV to Trip Bus 3 Phase Fault on ASB349 5 (547476) 161 kV Bus a. Apply fault at the ASB349 5 (547476) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21L | Transfer | G12_FLT30-PO | Prior Outage: LITCH 5 (532932) 161.0 kV to ASB349 5 (547476) 161.0 kV Transmission Circuit 3 Phase Fault on ASB349 5 (547476) 161 kV Bus a. Apply fault at the ASB349 5 (547476) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21L | Transfer | G12_FLT4-3PH | 3 Phase fault on LAR382 5 (547479) 161 kV Bus a. Apply fault at the LAR382 5 (547479) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAR382 5 (547479) 161.0 kV to GEN-2017-060 (588980) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21L | Transfer | G12_FLT1-PO | Prior Outage: LAR382 5 (547479) 161.0 kV to GEN-2017-060 (588980) 161.0 kV Transmission Circuit 3 Phase Fault on CARTHAG5 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHAG5 (505488) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21L | Transfer | G12_FLT2-PO | Prior Outage: LAR382 5 (547479) 161.0 kV to GEN-2017-060 (588980) 161.0 kV Transmission Circuit 3 Phase Fault on SPRGFLD5 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21L | Transfer | G12_FLT21-SB | Single Phase Fault with Stuck Breaker on FLINTCR5 (506934) 161 kV Bus a. Apply Fault at the FLINTCR5 (506934) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21L | Transfer | G12_FLT62-SB | Single Phase Fault with Stuck Breaker on GREC TAP5 (512865) 345 kV Bus a. Apply Fault at the GREC TAP5 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREC TAP5 (512865) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21L | Transfer | G12_FLT27-SB | Single Phase Fault with Stuck Breaker on ASB349 5 (547476) 161 kV Bus a. Apply Fault at the ASB349 5 (547476) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASB349 5 (547476) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT44-3PH | 3 Phase fault on FARMNGTN 5 (504020) 161 kV Bus a. Apply fault at the FARMNGTN 5 (504020) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARMNGTN 5 (504020) 161.0 kV to FARM_1 2 (504021) 69.0 kV to FARM_T1 1 (504022) 13.8 kV ThreeWinding | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT36-3PH | 3 Phase fault on SILOAM 5 (506948) 161 kV Bus a. Apply fault at the SILOAM 5 (506948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SILOAM-1 (506917) 13.2 kV to SILOAM 5 (506948) 161.0 kV to SILOAM 2 (506973) 69.0 kV ThreeWinding | P1 | Stable | Yes | Yes | Yes | No | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT15-SB | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit b.2. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV TwoWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT55-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT56-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to RSS T2 4 (509875) 138.0 kV to RSST2 T1 (509876) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT63-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit 3 Phase Fault on REDBUD 7 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT67-PO | Prior Outage: DARDANE5 (505508) 161.0 kV to CLARKSV5 (505514) 161.0 kV Transmission Circuit 3 Phase Fault on DARDANE5 (505508) 161 kV Bus a. Apply fault at the DARDANE5 (505508) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5RUSSELVL.S (337904) 161.0 kV to 5RUSSELVL.E! (337905) 161.0 kV Transmission Circuit b.2. 5RUSSELVL.S (337904) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit b.3. 5DARDANELLE (337903) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit b.4. 5DANVLE AR! (337902) 161.0 kV to 5DARDANELLE (337903) 161.0 kV Transmission Circuit b.5. 5HILLTOP% (338110) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT16-SB | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit b.2. MUSKOG4G (515223) 18.0 kV to MUSKOGE7 (515224) 345.0 kV TwoWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT78-PO | Prior Outage: 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT76-PO | Prior Outage: 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT74-PO | Prior Outage: 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT29-PO | Prior Outage: CAR395 5 (547485) 161.0 kV to Trip Bus PUR421 5 (547491) 161.0 kV to Trip Bus 3 Phase Fault on ASB349 5 (547476) 161 kV Bus a. Apply fault at the ASB349 5 (547476) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT4-3PH | 3 Phase fault on LAR382 5 (547479) 161 kV Bus a. Apply fault at the LAR382 5 (547479) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAR382 5 (547479) 161.0 kV to GEN-2017-060 (588980) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT1-PO | Prior Outage: LAR382 5 (547479) 161.0 kV to GEN-2017-060 (588980) 161.0 kV Transmission Circuit 3 Phase Fault on CARTHAG5 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHAG5 (505488) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT2-PO | Prior Outage: LAR382 5 (547479) 161.0 kV to GEN-2017-060 (588980) 161.0 kV Transmission Circuit 3 Phase Fault on SPRGFLD5 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT18-SB | Single Phase Fault with Stuck Breaker on CARTHAG5 (505488) 161 kV Bus a. Apply Fault at the CARTHAG5 (505488) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARTHAG5 (505488) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT65-SB | Single Phase Fault with Stuck Breaker on DARDANE5 (505508) 161 kV Bus a. Apply Fault at the DARDANE5 (505508) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DARDANE5 (505508) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT21-SB | Single Phase Fault with Stuck Breaker on FLINTCR5 (506934) 161 kV Bus a. Apply Fault at the FLINTCR5 (506934) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT62-SB | Single Phase Fault with Stuck Breaker on GREC TAP5 (512865) 345 kV Bus a. Apply Fault at the GREC TAP5 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREC TAP5 (512865) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT26-SB | Single Phase Fault with Stuck Breaker on RIV4525 (547469) 161 kV Bus a. Apply Fault at the RIV4525 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT27-SB | Single Phase Fault with Stuck Breaker on ASB349 5 (547476) 161 kV Bus a. Apply Fault at the ASB349 5 (547476) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASB349 5 (547476) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT64-SB | Single Phase Fault with Stuck Breaker on FIREWHL-TAP (588839) 345 kV Bus a. Apply Fault at the FIREWHL-TAP (588839) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FIREWHL-TAP (588839) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT48-PO | Prior Outage: GREC TAP5 (512865) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit 3 Phase Fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT44-3PH | 3 Phase fault on FARMNGTN 5 (504020) 161 kV Bus a. Apply fault at the FARMNGTN 5 (504020) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARMNGTN 5 (504020) 161.0 kV to FARM_1 2 (504021) 69.0 kV to FARM_T1 1 (504022) 13.8 kV ThreeWinding | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT36-3PH | 3 Phase fault on SILOAM 5 (506948) 161 kV Bus a. Apply fault at the SILOAM 5 (506948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SILOAM-1 (506917) 13.2 kV to SILOAM 5 (506948) 161.0 kV to SILOAM 2 (506973) 69.0 kV ThreeWinding | P1 | Stable | Yes | Yes | Yes | No | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT15-SB | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit b.2. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV TwoWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT55-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT56-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to RSS T2 4 (509875) 138.0 kV to RSST2 T1 (509876) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT63-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit 3 Phase Fault on REDBUD 7 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT67-PO | Prior Outage: DARDANE5 (505508) 161.0 kV to CLARKSV5 (505514) 161.0 kV Transmission Circuit 3 Phase Fault on DARDANE5 (505508) 161 kV Bus a. Apply fault at the DARDANE5 (505508) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5RUSSELVL.S (337904) 161.0 kV to 5RUSSELVL.E! (337905) 161.0 kV Transmission Circuit b.2. 5RUSSELVL.S (337904) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit b.3. 5DARDANELLE (337903) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit b.4. 5DANVLE AR! (337902) 161.0 kV to 5DARDANELLE (337903) 161.0 kV Transmission Circuit b.5. 5HILLTOP% (338110) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT16-SB | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit b.2. MUSKOG4G (515223) 18.0 kV to MUSKOGE7 (515224) 345.0 kV TwoWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT48-PO | Prior Outage: GREC TAP5 (512865) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit 3 Phase Fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT78-PO | Prior Outage: 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT76-PO | Prior Outage: 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT74-PO | Prior Outage: 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT29-PO | Prior Outage: CAR395 5 (547485) 161.0 kV to Trip Bus PUR421 5 (547491) 161.0 kV to Trip Bus 3 Phase Fault on ASB349 5 (547476) 161 kV Bus a. Apply fault at the ASB349 5 (547476) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT4-3PH | 3 Phase fault on LAR382 5 (547479) 161 kV Bus a. Apply fault at the LAR382 5 (547479) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAR382 5 (547479) 161.0 kV to GEN-2017-060 (588980) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT1-PO | Prior Outage: LAR382 5 (547479) 161.0 kV to GEN-2017-060 (588980) 161.0 kV Transmission Circuit 3 Phase Fault on CARTHAG5 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHAG5 (505488) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT2-PO | Prior Outage: LAR382 5 (547479) 161.0 kV to GEN-2017-060 (588980) 161.0 kV Transmission Circuit 3 Phase Fault on SPRGFLD5 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT18-SB | Single Phase Fault with Stuck Breaker on CARTHAG5 (505488) 161 kV Bus a. Apply Fault at the CARTHAG5 (505488) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARTHAG5 (505488) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT65-SB | Single Phase Fault with Stuck Breaker on DARDANE5 (505508) 161 kV Bus a. Apply Fault at the DARDANE5 (505508) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DARDANE5 (505508) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT21-SB | Single Phase Fault with Stuck Breaker on FLINTCR5 (506934) 161 kV Bus a. Apply Fault at the FLINTCR5 (506934) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT62-SB | Single Phase Fault with Stuck Breaker on GREC TAP5 (512865) 345 kV Bus a. Apply Fault at the GREC TAP5 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREC TAP5 (512865) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT26-SB | Single Phase Fault with Stuck Breaker on RIV4525 (547469) 161 kV Bus a. Apply Fault at the RIV4525 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT27-SB | Single Phase Fault with Stuck Breaker on ASB349 5 (547476) 161 kV Bus a. Apply Fault at the ASB349 5 (547476) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASB349 5 (547476) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT64-SB | Single Phase Fault with Stuck Breaker on FIREWHL-TAP (588839) 345 kV Bus a. Apply Fault at the FIREWHL-TAP (588839) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FIREWHL-TAP (588839) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT4-3PH | 3 Phase fault on 87TH 7 (532775) 345 kV Bus a. Apply fault at the 87TH 7 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT60-3PH | 3 Phase fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT5-3PH | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT54-3PH | 3 Phase fault on HOLT 7 (541510) 345 kV Bus a. Apply fault at the HOLT 7 (541510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT63-3PH | 3 Phase fault on CBLUFFS3 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT6-3PH | 3 Phase fault on ATCHSN 3 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT1-SB | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit b.2. ST JOE 3 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT2-SB | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT3-SB | Single Phase Fault with Stuck Breaker on HAWTHN5 (543665) 161 kV Bus a. Apply Fault at the HAWTHN5 (543665) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit b.2. HAW G5 1 (542951) 22.0 kV Trip Bus b.3. HAWTH 7 (542972) 345.0 kV to HAWT T20 (543644) 13.8 kV to HAWTHN5 (543665) 161.0 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT30-PO | Prior Outage: MC REAC1 (541411) 345.0 kV to Trip Bus MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit MC REAC2 (541412) 345.0 kV to Trip Bus 3 Phase Fault on HOLT_REACT7 (541517) 345 kV Bus a. Apply fault at the HOLT_REACT7 (541517) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit b.2. HOLT_REACT7 (541517) 345.0 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT48-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT49-PO | Prior Outage: STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT11-PO | Prior Outage: COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit 3 Phase Fault on 7FAIRPT (300039) 345 kV Bus a. Apply fault at the 7FAIRPT (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 3 (541199) 345.0 kV Transmission Circuit b.2. 7FAIRPT (300039) 345.0 kV to 5FAIRPT (300076) 161.0 kV TwoWinding b.3. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT33-PO | Prior Outage: 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit 3 Phase Fault on SIB REA1 (541414) 345 kV Bus a. Apply fault at the SIB REA1 (541414) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIB REA1 (541414) 345.0 kV to Trip Bus b.2. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT28-PO | Prior Outage: COOPER 3 (640139) 345.0 kV to ST JOE 3 (541199) 345.0 kV Transmission Circuit 3 Phase Fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT22-3PH | 3 Phase fault on ST JOE 3 (541199) 345 kV Bus a. Apply fault at the ST JOE 3 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STJOE 2T (541371) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT13-PO | Prior Outage: ST JOE 5 (541253) 161.0 kV to WOODBIN5 (541258) 161.0 kV Transmission Circuit 3 Phase Fault on ST JOE 3 (541199) 345 kV Bus a. Apply fault at the ST JOE 3 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STJOE 2T (541371) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT14-3PH | 3 Phase fault on ST JOE 3 (541199) 345 kV Bus a. Apply fault at the ST JOE 3 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 3 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT16-3PH | 3 Phase fault on ST JOE 3 (541199) 345 kV Bus a. Apply fault at the ST JOE 3 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 3 (541199) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT17-3PH | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 3 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT16-PO | Prior Outage: 5CLARK (300070) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit 3 Phase Fault on ARCHIE 5 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | No | 5892873: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION 589287: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT23-PO | Prior Outage: STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on W.GRDNR7 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT50-PO | Prior Outage: STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on W.GRDNR7 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT7-PO | Prior Outage: ST JOE 3 (541199) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit 3 Phase Fault on HAWTH 7 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT1-PO | Prior Outage: ST JOE 3 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit 3 Phase Fault on IATAN 7 (542982) 345 kV Bus a. Apply fault at the IATAN 7 (542982) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IATAN 7 (542982) 345.0 kV to G17-030-TAP (588736) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | No | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT10-3PH | 3 Phase fault on ATCHSN 3 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to WESTBORO 3 (635018) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT13-SB | Single Phase Fault with Stuck Breaker on 5CLINTN (300071) 161 kV Bus a. Apply Fault at the 5CLINTN (300071) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLINTN (300071) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT6-SB | Single Phase Fault with Stuck Breaker on STRANGR7 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT19-SB | Single Phase Fault with Stuck Breaker on NEVADA 5 (541208) 161 kV Bus a. Apply Fault at the NEVADA 5 (541208) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEVADA 5 (541208) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT22-SB | Single Phase Fault with Stuck Breaker on HOLT 7 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT26-SB | Single Phase Fault with Stuck Breaker on W.GRDNR7 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT29-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT34-SB | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT33-SB | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 3 (541199) 345.0 kV Transmission Circuit b.2. 7FAIRPT (300039) 345.0 kV to 5FAIRPT (300076) 161.0 kV TwoWinding b.3. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit b.4. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT37-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT38-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT39-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT61-3PH | 3 Phase fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 532957: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION 577193: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION 577200: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION 589063: UNKNOWN | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT45-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 532957: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION 577193: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION 577200: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION 589063: UNKNOWN | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT46-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 532957: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION 577193: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION 577200: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION 589063: UNKNOWN | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT47-PO | Prior Outage: STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 532957: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION 577193: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION 577200: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION 589063: UNKNOWN | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT59-PO | Prior Outage: WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | Yes | No | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT60-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | Yes | No | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT61-PO | Prior Outage: WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes |  | REDUCE WOLFCREEK TO 1100 MW
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT62-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes |  | REDUCE WOLFCREEK TO 1100 MW
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Transfer | G13_FLT74-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes |  | REDUCE WOLFCREEK TO 1100 MW
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT60-3PH | 3 Phase fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT61-3PH | 3 Phase fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT64-3PH | 3 Phase fault on S3451 3 (645451) 345 kV Bus a. Apply fault at the S3451 3 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT5-3PH | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT54-3PH | 3 Phase fault on HOLT 7 (541510) 345 kV Bus a. Apply fault at the HOLT 7 (541510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT8-3PH | 3 Phase fault on 7FAIRPT (300039) 345 kV Bus a. Apply fault at the 7FAIRPT (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 3 (541199) 345.0 kV Transmission Circuit b.2. 7FAIRPT (300039) 345.0 kV to 5FAIRPT (300076) 161.0 kV TwoWinding b.3. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT63-3PH | 3 Phase fault on CBLUFFS3 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT6-3PH | 3 Phase fault on ATCHSN 3 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT1-SB | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit b.2. ST JOE 3 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT2-SB | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT3-SB | Single Phase Fault with Stuck Breaker on HAWTHN5 (543665) 161 kV Bus a. Apply Fault at the HAWTHN5 (543665) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit b.2. HAW G5 1 (542951) 22.0 kV Trip Bus b.3. HAWTH 7 (542972) 345.0 kV to HAWT T20 (543644) 13.8 kV to HAWTHN5 (543665) 161.0 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT30-PO | Prior Outage: MC REAC1 (541411) 345.0 kV to Trip Bus MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit MC REAC2 (541412) 345.0 kV to Trip Bus 3 Phase Fault on HOLT_REACT7 (541517) 345 kV Bus a. Apply fault at the HOLT_REACT7 (541517) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit b.2. HOLT_REACT7 (541517) 345.0 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT48-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT5-PO | Prior Outage: STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit 3 Phase Fault on STRANGR7 (532772) 345 kV Bus a. Apply fault at the STRANGR7 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT45-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT47-PO | Prior Outage: STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT11-PO | Prior Outage: COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit 3 Phase Fault on 7FAIRPT (300039) 345 kV Bus a. Apply fault at the 7FAIRPT (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 3 (541199) 345.0 kV Transmission Circuit b.2. 7FAIRPT (300039) 345.0 kV to 5FAIRPT (300076) 161.0 kV TwoWinding b.3. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT28-PO | Prior Outage: COOPER 3 (640139) 345.0 kV to ST JOE 3 (541199) 345.0 kV Transmission Circuit 3 Phase Fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT44-3PH | 3 Phase fault on PECULR 7 (541198) 345 kV Bus a. Apply fault at the PECULR 7 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT52-3PH | 3 Phase fault on PECULR 7 (541198) 345 kV Bus a. Apply fault at the PECULR 7 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULRT (541372) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT20-PO | Prior Outage: STIL T22 (543648) 13.8 kV to Trip Bus 3 Phase Fault on PECULR 7 (541198) 345 kV Bus a. Apply fault at the PECULR 7 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULRT (541372) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT45-3PH | 3 Phase fault on PECULR 7 (541198) 345 kV Bus a. Apply fault at the PECULR 7 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT22-PO | Prior Outage: STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on PECULR 7 (541198) 345 kV Bus a. Apply fault at the PECULR 7 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT22-3PH | 3 Phase fault on ST JOE 3 (541199) 345 kV Bus a. Apply fault at the ST JOE 3 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STJOE 2T (541371) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT13-PO | Prior Outage: ST JOE 5 (541253) 161.0 kV to WOODBIN5 (541258) 161.0 kV Transmission Circuit 3 Phase Fault on ST JOE 3 (541199) 345 kV Bus a. Apply fault at the ST JOE 3 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STJOE 2T (541371) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT14-3PH | 3 Phase fault on ST JOE 3 (541199) 345 kV Bus a. Apply fault at the ST JOE 3 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 3 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT16-3PH | 3 Phase fault on ST JOE 3 (541199) 345 kV Bus a. Apply fault at the ST JOE 3 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 3 (541199) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT17-3PH | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 3 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT27-PO | Prior Outage: STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on PHILL 7 (541200) 345 kV Bus a. Apply fault at the PHILL 7 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT23-3PH | 3 Phase fault on LAKE RD5 (541255) 161 kV Bus a. Apply fault at the LAKE RD5 (541255) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKE RD5 (541255) 161.0 kV to IND PRK5 (541256) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT4-PO | Prior Outage: NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit 3 Phase Fault on EASTOWN7 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to G17-030-TAP (588736) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT42-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit 3 Phase Fault on W.GRDNR7 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT50-PO | Prior Outage: STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on W.GRDNR7 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT53-3PH | 3 Phase fault on STILWEL7 (542968) 345 kV Bus a. Apply fault at the STILWEL7 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STIL T22 (543648) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT24-PO | Prior Outage: STIL T11 (543647) 13.8 kV to Trip Bus 3 Phase Fault on STILWEL7 (542968) 345 kV Bus a. Apply fault at the STILWEL7 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STIL T22 (543648) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT47-3PH | 3 Phase fault on STILWEL7 (542968) 345 kV Bus a. Apply fault at the STILWEL7 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT1-PO | Prior Outage: ST JOE 3 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit 3 Phase Fault on IATAN 7 (542982) 345 kV Bus a. Apply fault at the IATAN 7 (542982) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IATAN 7 (542982) 345.0 kV to G17-030-TAP (588736) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | No | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT10-3PH | 3 Phase fault on ATCHSN 3 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to WESTBORO 3 (635018) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT6-SB | Single Phase Fault with Stuck Breaker on STRANGR7 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT22-SB | Single Phase Fault with Stuck Breaker on HOLT 7 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT26-SB | Single Phase Fault with Stuck Breaker on W.GRDNR7 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT58-3PH | 3 Phase fault on 5THMHLB3 (300133) 161 kV Bus a. Apply fault at the 5THMHLB3 (300133) 161 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5THMHLB3 (300133) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT34-SB | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Transfer | G13_FLT33-SB | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 3 (541199) 345.0 kV Transmission Circuit b.2. 7FAIRPT (300039) 345.0 kV to 5FAIRPT (300076) 161.0 kV TwoWinding b.3. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit b.4. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Transfer | G13_FLT2-3PH | 3 Phase fault on STRANGR7 (532772) 345 kV Bus a. Apply fault at the STRANGR7 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Transfer | G13_FLT60-3PH | 3 Phase fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Transfer | G13_FLT1-3PH | 3 Phase fault on STRANGR7 (532772) 345 kV Bus a. Apply fault at the STRANGR7 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Transfer | G13_FLT7-3PH | 3 Phase fault on STRANGR7 (532772) 345 kV Bus a. Apply fault at the STRANGR7 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRAN1 1 (532811) 14.4 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Transfer | G13_FLT5-3PH | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Transfer | G13_FLT54-3PH | 3 Phase fault on HOLT 7 (541510) 345 kV Bus a. Apply fault at the HOLT 7 (541510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Transfer | G13_FLT63-3PH | 3 Phase fault on CBLUFFS3 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Transfer | G13_FLT6-3PH | 3 Phase fault on ATCHSN 3 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Transfer | G13_FLT1-SB | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit b.2. ST JOE 3 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Transfer | G13_FLT2-SB | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Transfer | G13_FLT3-SB | Single Phase Fault with Stuck Breaker on HAWTHN5 (543665) 161 kV Bus a. Apply Fault at the HAWTHN5 (543665) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit b.2. HAW G5 1 (542951) 22.0 kV Trip Bus b.3. HAWTH 7 (542972) 345.0 kV to HAWT T20 (543644) 13.8 kV to HAWTHN5 (543665) 161.0 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Transfer | G13_FLT30-PO | Prior Outage: MC REAC1 (541411) 345.0 kV to Trip Bus MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit MC REAC2 (541412) 345.0 kV to Trip Bus 3 Phase Fault on HOLT_REACT7 (541517) 345 kV Bus a. Apply fault at the HOLT_REACT7 (541517) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit b.2. HOLT_REACT7 (541517) 345.0 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Transfer | G13_FLT25-3PH | 3 Phase fault on 5BUTLER (301342) 161 kV Bus a. Apply fault at the 5BUTLER (301342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BUTLER (301342) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit b.2. 5BUTLER (301342) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Transfer | G13_FLT15-PO | Prior Outage: ARCHIE 5 (541207) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit 3 Phase Fault on 5BUTLER (301342) 161 kV Bus a. Apply fault at the 5BUTLER (301342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BUTLER (301342) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit b.2. 5BUTLER (301342) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Transfer | G13_FLT14-PO | Prior Outage: ARCHIE 5 (541207) 161.0 kV to S.HARP 5 (541341) 161.0 kV Transmission Circuit 3 Phase Fault on 5BUTLER (301342) 161 kV Bus a. Apply fault at the 5BUTLER (301342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BUTLER (301342) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit b.2. 5BUTLER (301342) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Transfer | G13_FLT9-PO | Prior Outage: HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit 3 Phase Fault on STRANGR7 (532772) 345 kV Bus a. Apply fault at the STRANGR7 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Transfer | G13_FLT48-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Transfer | G13_FLT49-PO | Prior Outage: STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Transfer | G13_FLT35-PO | Prior Outage: STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit 3 Phase Fault on STRANGR7 (532772) 345 kV Bus a. Apply fault at the STRANGR7 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Transfer | G13_FLT36-PO | Prior Outage: HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit 3 Phase Fault on STRANGR7 (532772) 345 kV Bus a. Apply fault at the STRANGR7 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Transfer | G13_FLT11-PO | Prior Outage: COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit 3 Phase Fault on 7FAIRPT (300039) 345 kV Bus a. Apply fault at the 7FAIRPT (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 3 (541199) 345.0 kV Transmission Circuit b.2. 7FAIRPT (300039) 345.0 kV to 5FAIRPT (300076) 161.0 kV TwoWinding b.3. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Transfer | G13_FLT28-PO | Prior Outage: COOPER 3 (640139) 345.0 kV to ST JOE 3 (541199) 345.0 kV Transmission Circuit 3 Phase Fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Transfer | G13_FLT22-3PH | 3 Phase fault on ST JOE 3 (541199) 345 kV Bus a. Apply fault at the ST JOE 3 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STJOE 2T (541371) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Transfer | G13_FLT13-PO | Prior Outage: ST JOE 5 (541253) 161.0 kV to WOODBIN5 (541258) 161.0 kV Transmission Circuit 3 Phase Fault on ST JOE 3 (541199) 345 kV Bus a. Apply fault at the ST JOE 3 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STJOE 2T (541371) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Transfer | G13_FLT14-3PH | 3 Phase fault on ST JOE 3 (541199) 345 kV Bus a. Apply fault at the ST JOE 3 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 3 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Transfer | G13_FLT16-3PH | 3 Phase fault on ST JOE 3 (541199) 345 kV Bus a. Apply fault at the ST JOE 3 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 3 (541199) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Transfer | G13_FLT17-3PH | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 3 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Transfer | G13_FLT16-PO | Prior Outage: 5CLARK (300070) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit 3 Phase Fault on ARCHIE 5 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | No | 5892873: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION 589287: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Transfer | G13_FLT8-PO | Prior Outage: NASH T11 (543640) 13.8 kV to Trip Bus 3 Phase Fault on HAWTH 7 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Transfer | G13_FLT1-PO | Prior Outage: ST JOE 3 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit 3 Phase Fault on IATAN 7 (542982) 345 kV Bus a. Apply fault at the IATAN 7 (542982) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IATAN 7 (542982) 345.0 kV to G17-030-TAP (588736) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Transfer | G13_FLT10-3PH | 3 Phase fault on ATCHSN 3 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to WESTBORO 3 (635018) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Transfer | G13_FLT13-SB | Single Phase Fault with Stuck Breaker on 5CLINTN (300071) 161 kV Bus a. Apply Fault at the 5CLINTN (300071) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLINTN (300071) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Transfer | G13_FLT6-SB | Single Phase Fault with Stuck Breaker on STRANGR7 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Transfer | G13_FLT19-SB | Single Phase Fault with Stuck Breaker on NEVADA 5 (541208) 161 kV Bus a. Apply Fault at the NEVADA 5 (541208) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEVADA 5 (541208) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Transfer | G13_FLT22-SB | Single Phase Fault with Stuck Breaker on HOLT 7 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Transfer | G13_FLT26-SB | Single Phase Fault with Stuck Breaker on W.GRDNR7 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Transfer | G13_FLT29-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Transfer | G13_FLT34-SB | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Transfer | G13_FLT33-SB | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 3 (541199) 345.0 kV Transmission Circuit b.2. 7FAIRPT (300039) 345.0 kV to 5FAIRPT (300076) 161.0 kV TwoWinding b.3. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit b.4. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Transfer | G13_FLT59-PO | Prior Outage: WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | Yes | No | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Transfer | G13_FLT60-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | Yes | No | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT2-3PH | 3 Phase fault on STRANGR7 (532772) 345 kV Bus a. Apply fault at the STRANGR7 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT60-3PH | 3 Phase fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT1-3PH | 3 Phase fault on STRANGR7 (532772) 345 kV Bus a. Apply fault at the STRANGR7 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT7-3PH | 3 Phase fault on STRANGR7 (532772) 345 kV Bus a. Apply fault at the STRANGR7 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRAN1 1 (532811) 14.4 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT5-3PH | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT54-3PH | 3 Phase fault on HOLT 7 (541510) 345 kV Bus a. Apply fault at the HOLT 7 (541510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT63-3PH | 3 Phase fault on CBLUFFS3 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT6-3PH | 3 Phase fault on ATCHSN 3 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT1-SB | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit b.2. ST JOE 3 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT2-SB | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT3-SB | Single Phase Fault with Stuck Breaker on HAWTHN5 (543665) 161 kV Bus a. Apply Fault at the HAWTHN5 (543665) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit b.2. HAW G5 1 (542951) 22.0 kV Trip Bus b.3. HAWTH 7 (542972) 345.0 kV to HAWT T20 (543644) 13.8 kV to HAWTHN5 (543665) 161.0 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT30-PO | Prior Outage: MC REAC1 (541411) 345.0 kV to Trip Bus MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit MC REAC2 (541412) 345.0 kV to Trip Bus 3 Phase Fault on HOLT_REACT7 (541517) 345 kV Bus a. Apply fault at the HOLT_REACT7 (541517) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit b.2. HOLT_REACT7 (541517) 345.0 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT25-3PH | 3 Phase fault on 5BUTLER (301342) 161 kV Bus a. Apply fault at the 5BUTLER (301342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BUTLER (301342) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit b.2. 5BUTLER (301342) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT15-PO | Prior Outage: ARCHIE 5 (541207) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit 3 Phase Fault on 5BUTLER (301342) 161 kV Bus a. Apply fault at the 5BUTLER (301342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BUTLER (301342) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit b.2. 5BUTLER (301342) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT14-PO | Prior Outage: ARCHIE 5 (541207) 161.0 kV to S.HARP 5 (541341) 161.0 kV Transmission Circuit 3 Phase Fault on 5BUTLER (301342) 161 kV Bus a. Apply fault at the 5BUTLER (301342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BUTLER (301342) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit b.2. 5BUTLER (301342) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT9-PO | Prior Outage: HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit 3 Phase Fault on STRANGR7 (532772) 345 kV Bus a. Apply fault at the STRANGR7 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT48-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT49-PO | Prior Outage: STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT36-PO | Prior Outage: HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit 3 Phase Fault on STRANGR7 (532772) 345 kV Bus a. Apply fault at the STRANGR7 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT11-PO | Prior Outage: COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit 3 Phase Fault on 7FAIRPT (300039) 345 kV Bus a. Apply fault at the 7FAIRPT (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 3 (541199) 345.0 kV Transmission Circuit b.2. 7FAIRPT (300039) 345.0 kV to 5FAIRPT (300076) 161.0 kV TwoWinding b.3. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT28-PO | Prior Outage: COOPER 3 (640139) 345.0 kV to ST JOE 3 (541199) 345.0 kV Transmission Circuit 3 Phase Fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT22-3PH | 3 Phase fault on ST JOE 3 (541199) 345 kV Bus a. Apply fault at the ST JOE 3 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STJOE 2T (541371) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT13-PO | Prior Outage: ST JOE 5 (541253) 161.0 kV to WOODBIN5 (541258) 161.0 kV Transmission Circuit 3 Phase Fault on ST JOE 3 (541199) 345 kV Bus a. Apply fault at the ST JOE 3 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STJOE 2T (541371) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT14-3PH | 3 Phase fault on ST JOE 3 (541199) 345 kV Bus a. Apply fault at the ST JOE 3 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 3 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT16-3PH | 3 Phase fault on ST JOE 3 (541199) 345 kV Bus a. Apply fault at the ST JOE 3 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 3 (541199) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT17-3PH | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 3 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT16-PO | Prior Outage: 5CLARK (300070) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit 3 Phase Fault on ARCHIE 5 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | No | 5892873: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION 589287: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT13-3PH | 3 Phase fault on NASHUA 7 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT6-PO | Prior Outage: IATAN 11 (541150) 13.8 kV to Trip Bus 3 Phase Fault on NASHUA 7 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT21-3PH | 3 Phase fault on NASHUA 7 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASH T11 (543640) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT1-PO | Prior Outage: ST JOE 3 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit 3 Phase Fault on IATAN 7 (542982) 345 kV Bus a. Apply fault at the IATAN 7 (542982) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IATAN 7 (542982) 345.0 kV to G17-030-TAP (588736) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | No | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT10-3PH | 3 Phase fault on ATCHSN 3 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to WESTBORO 3 (635018) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT13-SB | Single Phase Fault with Stuck Breaker on 5CLINTN (300071) 161 kV Bus a. Apply Fault at the 5CLINTN (300071) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLINTN (300071) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT6-SB | Single Phase Fault with Stuck Breaker on STRANGR7 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT9-SB | Single Phase Fault with Stuck Breaker on STRANGR3 (533268) 115 kV Bus a. Apply Fault at the STRANGR3 (533268) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR3 (533268) 115.0 kV Trip Bus | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT19-SB | Single Phase Fault with Stuck Breaker on NEVADA 5 (541208) 161 kV Bus a. Apply Fault at the NEVADA 5 (541208) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEVADA 5 (541208) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT22-SB | Single Phase Fault with Stuck Breaker on HOLT 7 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT26-SB | Single Phase Fault with Stuck Breaker on W.GRDNR7 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT29-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT34-SB | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT33-SB | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 3 (541199) 345.0 kV Transmission Circuit b.2. 7FAIRPT (300039) 345.0 kV to 5FAIRPT (300076) 161.0 kV TwoWinding b.3. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit b.4. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | No | 635020: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT37-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT38-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT39-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT61-3PH | 3 Phase fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 532957: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION 577193: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION 577200: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION 589063: UNKNOWN | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT45-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 589063: UNKNOWN | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT46-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 532957: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION 577193: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION 577200: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION 589063: UNKNOWN | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT47-PO | Prior Outage: STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 532957: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION 577193: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION 577200: MACHINE TRIPPED DUE TO UNDER VOLTAGE PROTECTION 589063: UNKNOWN | DISABLE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT59-PO | Prior Outage: WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | Yes | No | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Transfer | G13_FLT60-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | Yes | No | Yes | Yes
Central | 03 - Spearville | 19W | Transfer | G3_FLT12-SB | Single Phase Fault with Stuck Breaker on POSTROCK7 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV ThreeWinding b.2. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit b.3. POSTROCK7 (530583) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | No | Yes | Yes
Central | 03 - Spearville | 19W | Transfer | G3_FLT59-PO | Prior Outage: MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit 3 Phase Fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit b.2. SETAB 7 (531465) 345.0 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 19W | Transfer | G3_FLT62-PO | Prior Outage: HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV ThreeWinding HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit 3 Phase Fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit b.2. GRTBEND6 (539679) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit b.3. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 19W | Transfer | G3_FLT60-PO | Prior Outage: GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV ThreeWinding BARBER 4 (539674) 138.0 kV to BARBER 3 (539760) 115.0 kV to BARBER-T (539917) 2.7 kV ThreeWinding 3 Phase Fault on HEIZER 3 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV ThreeWinding b.2. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit b.3. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 19W | Transfer | G3_FLT63-PO | Prior Outage: RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit 3 Phase Fault on RICE 6 (530686) 230 kV Bus a. Apply fault at the RICE 6 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 19W | Transfer | G3_FLT64-PO | Prior Outage: RICE 3 (530623) 115.0 kV to RICE 6 (530686) 230.0 kV to RICET1 (530687) 12.5 kV ThreeWinding 3 Phase Fault on RICE 6 (530686) 230 kV Bus a. Apply fault at the RICE 6 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 19W | Transfer | G3_FLT57-PO | Prior Outage: SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit 3 Phase Fault on MORRIS 6 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 (532863) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 19W | Transfer | G3_FLT55-PO | Prior Outage: ELMCREEK7 (539805) 345.0 kV to ELMCREK6 (539639) 230.0 kV to ELMCREEK1 (539806) 13.8 kV ThreeWinding 3 Phase Fault on NMANHT6 (532865) 230 kV Bus a. Apply fault at the NMANHT6 (532865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMANHT6 (532865) 230.0 kV to ELMCREK6 (539639) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 19W | Transfer | G3_FLT4-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 19W | Transfer | G3_FLT48-PO | Prior Outage: FINNEY 7 (523853) 345.0 kV to G17-032-TAP (588754) 345.0 kV Transmission Circuit 3 Phase Fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 19W | Transfer | G3_FLT39-3PH | 3 Phase fault on G17-032-TAP (588754) 345 kV Bus a. Apply fault at the G17-032-TAP (588754) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to G17-032-TAP (588754) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 19W | Transfer | G3_FLT49-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G17-021-TAP (588654) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 19W | Transfer | G3_FLT12-PO | Prior Outage: POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit 3 Phase Fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G17-021-TAP (588654) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 19W | Transfer | G3_FLT13-PO | Prior Outage: POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV ThreeWinding 3 Phase Fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G17-021-TAP (588654) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 19W | Transfer | G3_FLT51-3PH | 3 Phase fault on S-DODGE3 (539688) 115 kV Bus a. Apply fault at the S-DODGE3 (539688) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S-DODGE3 (539688) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 19W | Transfer | G3_FLT3-PO | Prior Outage: CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 03 - Spearville | 19W | Transfer | G3_FLT56-3PH | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to P1 MPT PRI (539852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 19W | Transfer | G3_FLT15-PO | Prior Outage: SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit 3 Phase Fault on G17-021-TAP (588654) 345 kV Bus a. Apply fault at the G17-021-TAP (588654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-021-TAP (588654) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 03 - Spearville | 19W | Transfer | G3_FLT16-PO | Prior Outage: SPERVIL7 (531469) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit 3 Phase Fault on G17-021-TAP (588654) 345 kV Bus a. Apply fault at the G17-021-TAP (588654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-021-TAP (588654) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 03 - Spearville | 19W | Transfer | G3_FLT33-SB | Single Phase Fault with Stuck Breaker on RICE 6 (530686) 230 kV Bus a. Apply Fault at the RICE 6 (530686) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 6 (530686) 230.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 19W | Transfer | G3_FLT18-SB | Single Phase Fault with Stuck Breaker on GRDNCTY3 (531445) 115 kV Bus a. Apply Fault at the GRDNCTY3 (531445) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDNCTY3 (531445) 115.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 19W | Transfer | G3_FLT19-SB | Single Phase Fault with Stuck Breaker on HOLCOMB3 (531448) 115 kV Bus a. Apply Fault at the HOLCOMB3 (531448) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB3 (531448) 115.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 19W | Transfer | G3_FLT21-SB | Single Phase Fault with Stuck Breaker on SPERVIL7 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 03 - Spearville | 19W | Transfer | G3_FLT22-SB | Single Phase Fault with Stuck Breaker on CNTRLPL3 (531485) 115 kV Bus a. Apply Fault at the CNTRLPL3 (531485) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CNTRLPL3 (531485) 115.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 19W | Transfer | G3_FLT23-SB | Single Phase Fault with Stuck Breaker on BUFFALO7 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 19W | Transfer | G3_FLT30-SB | Single Phase Fault with Stuck Breaker on UNIONRG6 (532874) 230 kV Bus a. Apply Fault at the UNIONRG6 (532874) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UNIONRG6 (532874) 230.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 19W | Transfer | G3_FLT24-SB | Single Phase Fault with Stuck Breaker on FLATRDG4 (539638) 138 kV Bus a. Apply Fault at the FLATRDG4 (539638) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLATRDG4 (539638) 138.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 19W | Transfer | G3_FLT29-SB | Single Phase Fault with Stuck Breaker on ELMCREK6 (539639) 230 kV Bus a. Apply Fault at the ELMCREK6 (539639) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELMCREK6 (539639) 230.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 19W | Transfer | G3_FLT25-SB | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 19W | Transfer | G3_FLT26-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 03 - Spearville | 19W | Transfer | G3_FLT88-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G17-021-TAP (588654) 345.0 kV Transmission Circuit b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 19W | Transfer | G3_FLT71-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 19W | Transfer | G3_FLT34-SB | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 19W | Transfer | G3_FLT38-SB | Single Phase Fault with Stuck Breaker on VIOLA 7 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 7 (532798) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 19W | Transfer | G3_FLT40-SB | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit b.2. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 03 - Spearville | 19W | Transfer | G3_FLT46-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit b.2. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 03 - Spearville | 19W | Sensitivity | G3_FLT13-3PH | 3 Phase fault on HOLCOMB3 (531448) 115 kV Bus a. Apply fault at the HOLCOMB3 (531448) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV ThreeWinding | P1 | Unstable | Yes | Yes | Yes | Yes | No | Yes |  | MITIGATION NOT REQUIRED - Informational only.
Central | 03 - Spearville | 21L | Transfer | G3_FLT68-3PH | 3 Phase fault on RICE 6 (530686) 230 kV Bus a. Apply fault at the RICE 6 (530686) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21L | Transfer | G3_FLT23-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 588637: MACHINE TRIPPED DUE TO OVER FREQUENCY PROTECTION | DISABLE PROTECTION
Central | 03 - Spearville | 21L | Transfer | G3_FLT12-SB | Single Phase Fault with Stuck Breaker on POSTROCK7 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV ThreeWinding b.2. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit b.3. POSTROCK7 (530583) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | No | Yes | Yes
Central | 03 - Spearville | 21L | Transfer | G3_FLT62-PO | Prior Outage: HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV ThreeWinding HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit 3 Phase Fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit b.2. GRTBEND6 (539679) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit b.3. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21L | Transfer | G3_FLT29-3PH | 3 Phase fault on SETAB 3 (531464) 115 kV Bus a. Apply fault at the SETAB 3 (531464) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SETAB 3 (531464) 115.0 kV to CNTRLPL3 (531485) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21L | Transfer | G3_FLT60-PO | Prior Outage: GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV ThreeWinding BARBER 4 (539674) 138.0 kV to BARBER 3 (539760) 115.0 kV to BARBER-T (539917) 2.7 kV ThreeWinding 3 Phase Fault on HEIZER 3 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV ThreeWinding b.2. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit b.3. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21L | Transfer | G3_FLT63-PO | Prior Outage: RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit 3 Phase Fault on RICE 6 (530686) 230 kV Bus a. Apply fault at the RICE 6 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21L | Transfer | G3_FLT64-PO | Prior Outage: RICE 3 (530623) 115.0 kV to RICE 6 (530686) 230.0 kV to RICET1 (530687) 12.5 kV ThreeWinding 3 Phase Fault on RICE 6 (530686) 230 kV Bus a. Apply fault at the RICE 6 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21L | Transfer | G3_FLT55-PO | Prior Outage: ELMCREEK7 (539805) 345.0 kV to ELMCREK6 (539639) 230.0 kV to ELMCREEK1 (539806) 13.8 kV ThreeWinding 3 Phase Fault on NMANHT6 (532865) 230 kV Bus a. Apply fault at the NMANHT6 (532865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMANHT6 (532865) 230.0 kV to ELMCREK6 (539639) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21L | Transfer | G3_FLT5-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 588637: MACHINE TRIPPED DUE TO OVER FREQUENCY PROTECTION | DISABLE PROTECTION
Central | 03 - Spearville | 21L | Transfer | G3_FLT2-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 588637: MACHINE TRIPPED DUE TO OVER FREQUENCY PROTECTION | DISABLE PROTECTION
Central | 03 - Spearville | 21L | Transfer | G3_FLT1-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 588637: MACHINE TRIPPED DUE TO OVER FREQUENCY PROTECTION | DISABLE PROTECTION
Central | 03 - Spearville | 21L | Transfer | G3_FLT48-PO | Prior Outage: FINNEY 7 (523853) 345.0 kV to G17-032-TAP (588754) 345.0 kV Transmission Circuit 3 Phase Fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21L | Transfer | G3_FLT39-3PH | 3 Phase fault on G17-032-TAP (588754) 345 kV Bus a. Apply fault at the G17-032-TAP (588754) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to G17-032-TAP (588754) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21L | Transfer | G3_FLT46-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21L | Transfer | G3_FLT21-PO | Prior Outage: SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit 3 Phase Fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21L | Transfer | G3_FLT48-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21L | Transfer | G3_FLT49-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G17-021-TAP (588654) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21L | Transfer | G3_FLT12-PO | Prior Outage: POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit 3 Phase Fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G17-021-TAP (588654) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21L | Transfer | G3_FLT13-PO | Prior Outage: POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV ThreeWinding 3 Phase Fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G17-021-TAP (588654) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21L | Transfer | G3_FLT14-PO | Prior Outage: POSTROCK7 (530583) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit 3 Phase Fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G17-021-TAP (588654) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21L | Transfer | G3_FLT51-3PH | 3 Phase fault on S-DODGE3 (539688) 115 kV Bus a. Apply fault at the S-DODGE3 (539688) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S-DODGE3 (539688) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21L | Transfer | G3_FLT54-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 588637: MACHINE TRIPPED DUE TO OVER FREQUENCY PROTECTION | DISABLE PROTECTION
Central | 03 - Spearville | 21L | Transfer | G3_FLT3-PO | Prior Outage: CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 03 - Spearville | 21L | Transfer | G3_FLT55-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 588637: MACHINE TRIPPED DUE TO OVER FREQUENCY PROTECTION | DISABLE PROTECTION
Central | 03 - Spearville | 21L | Transfer | G3_FLT56-3PH | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to P1 MPT PRI (539852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21L | Transfer | G3_FLT58-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV ThreeWinding | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 588637: MACHINE TRIPPED DUE TO OVER FREQUENCY PROTECTION | DISABLE PROTECTION
Central | 03 - Spearville | 21L | Transfer | G3_FLT8-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV ThreeWinding | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 588637: MACHINE TRIPPED DUE TO OVER FREQUENCY PROTECTION | DISABLE PROTECTION
Central | 03 - Spearville | 21L | Transfer | G3_FLT9-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV ThreeWinding | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 588637: MACHINE TRIPPED DUE TO OVER FREQUENCY PROTECTION | DISABLE PROTECTION
Central | 03 - Spearville | 21L | Transfer | G3_FLT59-3PH | 3 Phase fault on IRONWOOD7 (539803) 345 kV Bus a. Apply fault at the IRONWOOD7 (539803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IRONWOOD7 (539803) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21L | Transfer | G3_FLT15-PO | Prior Outage: SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit 3 Phase Fault on G17-021-TAP (588654) 345 kV Bus a. Apply fault at the G17-021-TAP (588654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-021-TAP (588654) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21L | Transfer | G3_FLT16-PO | Prior Outage: SPERVIL7 (531469) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit 3 Phase Fault on G17-021-TAP (588654) 345 kV Bus a. Apply fault at the G17-021-TAP (588654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-021-TAP (588654) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 03 - Spearville | 21L | Transfer | G3_FLT33-SB | Single Phase Fault with Stuck Breaker on RICE 6 (530686) 230 kV Bus a. Apply Fault at the RICE 6 (530686) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 6 (530686) 230.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21L | Transfer | G3_FLT19-SB | Single Phase Fault with Stuck Breaker on HOLCOMB3 (531448) 115 kV Bus a. Apply Fault at the HOLCOMB3 (531448) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB3 (531448) 115.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21L | Transfer | G3_FLT21-SB | Single Phase Fault with Stuck Breaker on SPERVIL7 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21L | Transfer | G3_FLT22-SB | Single Phase Fault with Stuck Breaker on CNTRLPL3 (531485) 115 kV Bus a. Apply Fault at the CNTRLPL3 (531485) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CNTRLPL3 (531485) 115.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21L | Transfer | G3_FLT23-SB | Single Phase Fault with Stuck Breaker on BUFFALO7 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21L | Transfer | G3_FLT24-SB | Single Phase Fault with Stuck Breaker on FLATRDG4 (539638) 138 kV Bus a. Apply Fault at the FLATRDG4 (539638) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLATRDG4 (539638) 138.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21L | Transfer | G3_FLT29-SB | Single Phase Fault with Stuck Breaker on ELMCREK6 (539639) 230 kV Bus a. Apply Fault at the ELMCREK6 (539639) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELMCREK6 (539639) 230.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21L | Transfer | G3_FLT25-SB | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21L | Transfer | G3_FLT26-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21L | Transfer | G3_FLT89-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21L | Transfer | G3_FLT88-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G17-021-TAP (588654) 345.0 kV Transmission Circuit b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21L | Transfer | G3_FLT73-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 588637: MACHINE TRIPPED DUE TO OVER FREQUENCY PROTECTION | DISABLE PROTECTION
Central | 03 - Spearville | 21L | Transfer | G3_FLT72-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 588637: MACHINE TRIPPED DUE TO OVER FREQUENCY PROTECTION | DISABLE PROTECTION
Central | 03 - Spearville | 21L | Transfer | G3_FLT38-SB | Single Phase Fault with Stuck Breaker on VIOLA 7 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 7 (532798) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21L | Transfer | G3_FLT40-SB | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit b.2. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 03 - Spearville | 21L | Transfer | G3_FLT46-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit b.2. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 03 - Spearville | 21L | Sensitivity | G3_FLT13-3PH | 3 Phase fault on HOLCOMB3 (531448) 115 kV Bus a. Apply fault at the HOLCOMB3 (531448) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV ThreeWinding | P1 | Unstable | Yes | Yes | Yes | Yes | No | Yes |  | MITIGATION NOT REQUIRED - Informational only.
Central | 03 - Spearville | 21S | Transfer | G3_FLT12-SB | Single Phase Fault with Stuck Breaker on POSTROCK7 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV ThreeWinding b.2. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit b.3. POSTROCK7 (530583) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | No | Yes | Yes
Central | 03 - Spearville | 21S | Transfer | G3_FLT62-PO | Prior Outage: HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV ThreeWinding HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit 3 Phase Fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit b.2. GRTBEND6 (539679) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit b.3. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21S | Transfer | G3_FLT60-PO | Prior Outage: GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV ThreeWinding BARBER 4 (539674) 138.0 kV to BARBER 3 (539760) 115.0 kV to BARBER-T (539917) 2.7 kV ThreeWinding 3 Phase Fault on HEIZER 3 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV ThreeWinding b.2. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit b.3. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21S | Transfer | G3_FLT63-PO | Prior Outage: RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit 3 Phase Fault on RICE 6 (530686) 230 kV Bus a. Apply fault at the RICE 6 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21S | Transfer | G3_FLT64-PO | Prior Outage: RICE 3 (530623) 115.0 kV to RICE 6 (530686) 230.0 kV to RICET1 (530687) 12.5 kV ThreeWinding 3 Phase Fault on RICE 6 (530686) 230 kV Bus a. Apply fault at the RICE 6 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21S | Transfer | G3_FLT57-PO | Prior Outage: SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit 3 Phase Fault on MORRIS 6 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 (532863) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21S | Transfer | G3_FLT55-PO | Prior Outage: ELMCREEK7 (539805) 345.0 kV to ELMCREK6 (539639) 230.0 kV to ELMCREEK1 (539806) 13.8 kV ThreeWinding 3 Phase Fault on NMANHT6 (532865) 230 kV Bus a. Apply fault at the NMANHT6 (532865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMANHT6 (532865) 230.0 kV to ELMCREK6 (539639) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21S | Transfer | G3_FLT4-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit b.2. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21S | Transfer | G3_FLT48-PO | Prior Outage: FINNEY 7 (523853) 345.0 kV to G17-032-TAP (588754) 345.0 kV Transmission Circuit 3 Phase Fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21S | Transfer | G3_FLT39-3PH | 3 Phase fault on G17-032-TAP (588754) 345 kV Bus a. Apply fault at the G17-032-TAP (588754) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to G17-032-TAP (588754) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21S | Transfer | G3_FLT49-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G17-021-TAP (588654) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21S | Transfer | G3_FLT12-PO | Prior Outage: POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit 3 Phase Fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G17-021-TAP (588654) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21S | Transfer | G3_FLT13-PO | Prior Outage: POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV ThreeWinding 3 Phase Fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G17-021-TAP (588654) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21S | Transfer | G3_FLT51-3PH | 3 Phase fault on S-DODGE3 (539688) 115 kV Bus a. Apply fault at the S-DODGE3 (539688) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S-DODGE3 (539688) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21S | Transfer | G3_FLT3-PO | Prior Outage: CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 03 - Spearville | 21S | Transfer | G3_FLT56-3PH | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to P1 MPT PRI (539852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21S | Transfer | G3_FLT10-PO | Prior Outage: CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV ThreeWinding | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 588637: MACHINE TRIPPED DUE TO OVER FREQUENCY PROTECTION | DISABLE PROTECTION
Central | 03 - Spearville | 21S | Transfer | G3_FLT33-SB | Single Phase Fault with Stuck Breaker on RICE 6 (530686) 230 kV Bus a. Apply Fault at the RICE 6 (530686) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 6 (530686) 230.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21S | Transfer | G3_FLT18-SB | Single Phase Fault with Stuck Breaker on GRDNCTY3 (531445) 115 kV Bus a. Apply Fault at the GRDNCTY3 (531445) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDNCTY3 (531445) 115.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21S | Transfer | G3_FLT19-SB | Single Phase Fault with Stuck Breaker on HOLCOMB3 (531448) 115 kV Bus a. Apply Fault at the HOLCOMB3 (531448) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB3 (531448) 115.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21S | Transfer | G3_FLT22-SB | Single Phase Fault with Stuck Breaker on CNTRLPL3 (531485) 115 kV Bus a. Apply Fault at the CNTRLPL3 (531485) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CNTRLPL3 (531485) 115.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21S | Transfer | G3_FLT23-SB | Single Phase Fault with Stuck Breaker on BUFFALO7 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21S | Transfer | G3_FLT30-SB | Single Phase Fault with Stuck Breaker on UNIONRG6 (532874) 230 kV Bus a. Apply Fault at the UNIONRG6 (532874) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UNIONRG6 (532874) 230.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21S | Transfer | G3_FLT24-SB | Single Phase Fault with Stuck Breaker on FLATRDG4 (539638) 138 kV Bus a. Apply Fault at the FLATRDG4 (539638) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLATRDG4 (539638) 138.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21S | Transfer | G3_FLT29-SB | Single Phase Fault with Stuck Breaker on ELMCREK6 (539639) 230 kV Bus a. Apply Fault at the ELMCREK6 (539639) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELMCREK6 (539639) 230.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21S | Transfer | G3_FLT25-SB | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21S | Transfer | G3_FLT26-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 03 - Spearville | 21S | Transfer | G3_FLT88-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G17-021-TAP (588654) 345.0 kV Transmission Circuit b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21S | Transfer | G3_FLT71-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21S | Transfer | G3_FLT34-SB | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21S | Transfer | G3_FLT38-SB | Single Phase Fault with Stuck Breaker on VIOLA 7 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 7 (532798) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 21S | Transfer | G3_FLT40-SB | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit b.2. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 03 - Spearville | 21S | Transfer | G3_FLT46-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit b.2. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 03 - Spearville | 21S | Sensitivity | G3_FLT13-3PH | 3 Phase fault on HOLCOMB3 (531448) 115 kV Bus a. Apply fault at the HOLCOMB3 (531448) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV ThreeWinding | P1 | Unstable | Yes | Yes | Yes | Yes | No | Yes |  | MITIGATION NOT REQUIRED - Informational only.
Central | 03 - Spearville | 28S | Transfer | G3_FLT12-SB | Single Phase Fault with Stuck Breaker on POSTROCK7 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV ThreeWinding b.2. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit b.3. POSTROCK7 (530583) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | No | Yes | Yes
Central | 03 - Spearville | 28S | Transfer | G3_FLT22-PO | Prior Outage: HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV ThreeWinding 3 Phase Fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 28S | Transfer | G3_FLT62-PO | Prior Outage: HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV ThreeWinding HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit 3 Phase Fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit b.2. GRTBEND6 (539679) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit b.3. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 28S | Transfer | G3_FLT60-PO | Prior Outage: GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV ThreeWinding BARBER 4 (539674) 138.0 kV to BARBER 3 (539760) 115.0 kV to BARBER-T (539917) 2.7 kV ThreeWinding 3 Phase Fault on HEIZER 3 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV ThreeWinding b.2. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit b.3. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 28S | Transfer | G3_FLT63-PO | Prior Outage: RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit 3 Phase Fault on RICE 6 (530686) 230 kV Bus a. Apply fault at the RICE 6 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 28S | Transfer | G3_FLT64-PO | Prior Outage: RICE 3 (530623) 115.0 kV to RICE 6 (530686) 230.0 kV to RICET1 (530687) 12.5 kV ThreeWinding 3 Phase Fault on RICE 6 (530686) 230 kV Bus a. Apply fault at the RICE 6 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 28S | Transfer | G3_FLT57-PO | Prior Outage: SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit 3 Phase Fault on MORRIS 6 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 (532863) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 28S | Transfer | G3_FLT55-PO | Prior Outage: ELMCREEK7 (539805) 345.0 kV to ELMCREK6 (539639) 230.0 kV to ELMCREEK1 (539806) 13.8 kV ThreeWinding 3 Phase Fault on NMANHT6 (532865) 230 kV Bus a. Apply fault at the NMANHT6 (532865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMANHT6 (532865) 230.0 kV to ELMCREK6 (539639) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 28S | Transfer | G3_FLT48-PO | Prior Outage: FINNEY 7 (523853) 345.0 kV to G17-032-TAP (588754) 345.0 kV Transmission Circuit 3 Phase Fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 28S | Transfer | G3_FLT39-3PH | 3 Phase fault on G17-032-TAP (588754) 345 kV Bus a. Apply fault at the G17-032-TAP (588754) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to G17-032-TAP (588754) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 28S | Transfer | G3_FLT49-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G17-021-TAP (588654) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 28S | Transfer | G3_FLT12-PO | Prior Outage: POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit 3 Phase Fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G17-021-TAP (588654) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 28S | Transfer | G3_FLT13-PO | Prior Outage: POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV ThreeWinding 3 Phase Fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G17-021-TAP (588654) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 28S | Transfer | G3_FLT51-3PH | 3 Phase fault on S-DODGE3 (539688) 115 kV Bus a. Apply fault at the S-DODGE3 (539688) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S-DODGE3 (539688) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 28S | Transfer | G3_FLT3-PO | Prior Outage: CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 03 - Spearville | 28S | Transfer | G3_FLT56-3PH | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to P1 MPT PRI (539852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 28S | Transfer | G3_FLT33-SB | Single Phase Fault with Stuck Breaker on RICE 6 (530686) 230 kV Bus a. Apply Fault at the RICE 6 (530686) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 6 (530686) 230.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 28S | Transfer | G3_FLT18-SB | Single Phase Fault with Stuck Breaker on GRDNCTY3 (531445) 115 kV Bus a. Apply Fault at the GRDNCTY3 (531445) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDNCTY3 (531445) 115.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 28S | Transfer | G3_FLT19-SB | Single Phase Fault with Stuck Breaker on HOLCOMB3 (531448) 115 kV Bus a. Apply Fault at the HOLCOMB3 (531448) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB3 (531448) 115.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 28S | Transfer | G3_FLT21-SB | Single Phase Fault with Stuck Breaker on SPERVIL7 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 03 - Spearville | 28S | Transfer | G3_FLT22-SB | Single Phase Fault with Stuck Breaker on CNTRLPL3 (531485) 115 kV Bus a. Apply Fault at the CNTRLPL3 (531485) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CNTRLPL3 (531485) 115.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 28S | Transfer | G3_FLT23-SB | Single Phase Fault with Stuck Breaker on BUFFALO7 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 28S | Transfer | G3_FLT30-SB | Single Phase Fault with Stuck Breaker on UNIONRG6 (532874) 230 kV Bus a. Apply Fault at the UNIONRG6 (532874) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UNIONRG6 (532874) 230.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 28S | Transfer | G3_FLT24-SB | Single Phase Fault with Stuck Breaker on FLATRDG4 (539638) 138 kV Bus a. Apply Fault at the FLATRDG4 (539638) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLATRDG4 (539638) 138.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 28S | Transfer | G3_FLT29-SB | Single Phase Fault with Stuck Breaker on ELMCREK6 (539639) 230 kV Bus a. Apply Fault at the ELMCREK6 (539639) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELMCREK6 (539639) 230.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 28S | Transfer | G3_FLT25-SB | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 28S | Transfer | G3_FLT26-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 03 - Spearville | 28S | Transfer | G3_FLT87-3PH | 3 Phase fault on G17-021-TAP (588654) 345 kV Bus a. Apply fault at the G17-021-TAP (588654) 345 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-021-TAP (588654) 345.0 kV to G16-049-TAP (589484) 345.0 kV Transmission Circuit b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 589373: MACHINE TRIPPED DUE TO OVER FREQUENCY PROTECTION | DISABLE PROTECTION
Central | 03 - Spearville | 28S | Transfer | G3_FLT88-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G17-021-TAP (588654) 345.0 kV Transmission Circuit b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 28S | Transfer | G3_FLT71-PO | Prior Outage: WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit 3 Phase Fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 28S | Transfer | G3_FLT72-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 588637: MACHINE TRIPPED DUE TO OVER FREQUENCY PROTECTION | DISABLE PROTECTION
Central | 03 - Spearville | 28S | Transfer | G3_FLT34-SB | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 28S | Transfer | G3_FLT38-SB | Single Phase Fault with Stuck Breaker on VIOLA 7 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 7 (532798) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 03 - Spearville | 28S | Transfer | G3_FLT40-SB | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit b.2. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 03 - Spearville | 28S | Transfer | G3_FLT46-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit b.2. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 03 - Spearville | 28S | Sensitivity | G3_FLT13-3PH | 3 Phase fault on HOLCOMB3 (531448) 115 kV Bus a. Apply fault at the HOLCOMB3 (531448) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV ThreeWinding | P1 | Unstable | Yes | Yes | Yes | Yes | No | Yes |  | MITIGATION NOT REQUIRED - Informational only.
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT21-3PH | 3 Phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT92-3PH | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT93-3PH | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT14-3PH | 3 Phase fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT16-3PH | 3 Phase fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT17-3PH | 3 Phase fault on DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT83-3PH | 3 Phase fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT20-3PH | 3 Phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT89-3PH | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 515882: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION 515883: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION 515900: MACHINE TRIPPED DUE TO OVER FREQUENCY PROTECTION 599089: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION 599090: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT84-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT5-3PH | 3 Phase fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT8-3PH | 3 Phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT40-3PH | 3 Phase fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT145-3PH | 3 Phase fault on VIOLA 4 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT97-3PH | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT146-3PH | 3 Phase fault on GILL 4 (533047) 138 kV Bus a. Apply fault at the GILL 4 (533047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL 4 (533047) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT148-3PH | 3 Phase fault on SUMNER 4 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT3-3PH | 3 Phase fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT156-3PH | 3 Phase fault on BENTON 4 (532986) 138 kV Bus a. Apply fault at the BENTON 4 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTN1 1 (532821) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT9-3PH | 3 Phase fault on NEOSHO 4 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 1 1 (532824) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT86-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICH11 1 (532829) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT85-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICH12 1 (532830) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT144-3PH | 3 Phase fault on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA1X1 (532832) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT77-3PH | 3 Phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT136-3PH | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 (509790) 138.0 kV to OWAS88_4 (509887) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT163-3PH | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT47-3PH | 3 Phase fault on REDBUD 7 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT162-3PH | 3 Phase fault on BROOKLINE 7 (549984) 345 kV Bus a. Apply fault at the BROOKLINE 7 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT19-3PH | 3 Phase fault on DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT58-3PH | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT57-3PH | 3 Phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 (515045) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT90-3PH | 3 Phase fault on SUMMIT 7 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to G16-112-TAP (587894) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT33-SB | Single Phase Fault with Stuck Breaker on HUNTERS7 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit b.2. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT34-SB | Single Phase Fault with Stuck Breaker on HUNTERS7 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit b.2. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT35-SB | Single Phase Fault with Stuck Breaker on HUNTERS7 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit b.2. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT40-SB | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT98-SB | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT96-SB | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT95-SB | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit b.2. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT97-SB | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT38-SB | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT39-SB | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT36-SB | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT37-SB | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT99-SB | Single Phase Fault with Stuck Breaker on WOODRNG7 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT17-SB | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1_21 (512821) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT18-SB | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV TwoWinding b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT43-SB | Single Phase Fault with Stuck Breaker on RENO 7 (532771) 345 kV Bus a. Apply Fault at the RENO 7 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to RENO 2X1 (532810) 14.4 kV to RENO 3 (533416) 115.0 kV ThreeWinding b.2. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT5-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to RSS T2 4 (509875) 138.0 kV to RSST2 T1 (509876) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT3-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT4-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to RSS T2 4 (509875) 138.0 kV to RSST2 T1 (509876) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT92-SB | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV ThreeWinding b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT11-SB | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA2-1 (509868) 34.5 kV ThreeWinding b.2. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA1-1 (509881) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT12-SB | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit b.2. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT13-SB | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA5-1 (509874) 34.5 kV ThreeWinding b.2. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT32-3PH | 3 Phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT80-3PH | 3 Phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT117-3PH | 3 Phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT120-3PH | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to 412SUB 5 (512637) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT119-3PH | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT67-3PH | 3 Phase fault on WMAIN ST5 (512742) 161 kV Bus a. Apply fault at the WMAIN ST5 (512742) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WMAIN ST5 (512742) 161.0 kV to NWMAID5 (512757) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT65-3PH | 3 Phase fault on GERALDGAY5 (512760) 161 kV Bus a. Apply fault at the GERALDGAY5 (512760) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWMAID5 (512757) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT31-3PH | 3 Phase fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT74-3PH | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT54-3PH | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT152-3PH | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT49-3PH | 3 Phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT55-3PH | 3 Phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT48-3PH | 3 Phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT25-3PH | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT154-3PH | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT150-3PH | 3 Phase fault on HUNTERS7 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT143-3PH | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 515882: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION 515883: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION 515900: MACHINE TRIPPED DUE TO OVER FREQUENCY PROTECTION 599089: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION 599090: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT149-3PH | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV ThreeWinding | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT91-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 588637: MACHINE TRIPPED DUE TO OVER FREQUENCY PROTECTION | DISABLE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT82-3PH | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT167-3PH | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT19-SB | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT123-3PH | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT41-SB | Single Phase Fault with Stuck Breaker on EMPEC 7 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT44-SB | Single Phase Fault with Stuck Breaker on BENTON 7 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT94-3PH | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT96-3PH | 3 Phase fault on COWSKIN4 (533038) 138 kV Bus a. Apply fault at the COWSKIN4 (533038) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit b.2. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT95-3PH | 3 Phase fault on LAKERDG4 (533053) 138 kV Bus a. Apply fault at the LAKERDG4 (533053) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKERDG4 (533053) 138.0 kV Trip Bus b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit b.3. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT98-3PH | 3 Phase fault on SG12COL4 (533065) 138 kV Bus a. Apply fault at the SG12COL4 (533065) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit b.2. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit b.3. SG12COL4 (533065) 138.0 kV Trip Bus b.4. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit b.5. WWUPLNT4 (533016) 138.0 kV Trip Bus b.6. BENTLEY4 (533015) 138.0 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT41-3PH | 3 Phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT87-SB | Single Phase Fault with Stuck Breaker on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to SOONER2G (514806) 20.0 kV TwoWinding b.2. SOONER 7 (514803) 345.0 kV to G16-100-TAP (587804) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT48-SB | Single Phase Fault with Stuck Breaker on RENO 7 (532771) 345 kV Bus a. Apply Fault at the RENO 7 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to RENO 1X1 (532807) 14.4 kV to RENO 3 (533416) 115.0 kV ThreeWinding b.2. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT113-3PH | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G16-100-TAP (587804) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT38-PO | Prior Outage: CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 (515045) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT37-PO | Prior Outage: SEMINOL7 (515045) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit 3 Phase Fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 (515422) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT41-PO | Prior Outage: MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT6-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT7-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT20-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT10-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT21-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT85-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT84-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT86-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit 3 Phase Fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT181-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT187-PO | Prior Outage: VIOLA 7 (532798) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 515882: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION 515883: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT82-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT80-PO | Prior Outage: RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT185-PO | Prior Outage: RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT118-PO | Prior Outage: HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT119-PO | Prior Outage: RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV ThreeWinding 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT186-PO | Prior Outage: VIOLA 7 (532798) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT3-PO | Prior Outage: LITCH 5 (532932) 161.0 kV to FRANKLIN5 (532938) 161.0 kV Transmission Circuit 3 Phase Fault on MARMTNE5 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT11-PO | Prior Outage: 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT12-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT13-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT1-PO | Prior Outage: N345 1 1 (532824) 13.8 kV to Trip Bus 3 Phase Fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT15-PO | Prior Outage: 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 4 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 1 1 (532824) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT16-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 4 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 1 1 (532824) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT17-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 4 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 1 1 (532824) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT79-PO | Prior Outage: WICH11 1 (532829) 13.8 kV to Trip Bus 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICH12 1 (532830) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 533141: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT117-PO | Prior Outage: SCJ1X1 (999532) 13.8 kV to Trip Bus 3 Phase Fault on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA1X1 (532832) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT74-PO | Prior Outage: CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit 3 Phase Fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT75-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT73-PO | Prior Outage: OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit 3 Phase Fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT111-PO | Prior Outage: EXCLART4 (510401) 138.0 kV to G17-077-TAP (589154) 138.0 kV Transmission Circuit 3 Phase Fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 (510402) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit b.2. BIRDHOL4 (510398) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.3. BIRDHOL4 (510398) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT32-PO | Prior Outage: PITTSB-7 (510907) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT130-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit 3 Phase Fault on REDBUD 7 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT131-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit 3 Phase Fault on REDBUD 7 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT132-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit 3 Phase Fault on REDBUD 7 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT178-PO | Prior Outage: WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit 3 Phase Fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT172-PO | Prior Outage: T.NO.--7 (509852) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit 3 Phase Fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT175-PO | Prior Outage: T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit 3 Phase Fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT176-PO | Prior Outage: T.NO.--7 (509852) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit 3 Phase Fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT100-SB | Single Phase Fault with Stuck Breaker on WOODRNG7 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit b.2. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT102-SB | Single Phase Fault with Stuck Breaker on WOODRNG7 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit b.2. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT173-PO | Prior Outage: T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit 3 Phase Fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT171-PO | Prior Outage: WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit 3 Phase Fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT174-PO | Prior Outage: T.NO.--7 (509852) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit 3 Phase Fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT164-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit 3 Phase Fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT71-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT165-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit 3 Phase Fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT63-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT62-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT61-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit 3 Phase Fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT36-PO | Prior Outage: CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit 3 Phase Fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 (515422) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT129-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit 3 Phase Fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT133-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit 3 Phase Fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT35-PO | Prior Outage: MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit 3 Phase Fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 (515422) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT34-PO | Prior Outage: MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit 3 Phase Fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 (515422) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT169-PO | Prior Outage: RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT140-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT167-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit 3 Phase Fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT168-PO | Prior Outage: RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit 3 Phase Fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT144-PO | Prior Outage: WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit 3 Phase Fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT146-PO | Prior Outage: WOODRNG7 (514715) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit 3 Phase Fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT121-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT123-PO | Prior Outage: RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT116-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT124-PO | Prior Outage: WICH12 1 (532830) 13.8 kV to Trip Bus 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 515900: MACHINE TRIPPED DUE TO OVER FREQUENCY PROTECTION | DISABLE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT122-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT120-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT147-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT150-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT137-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to THUNDER7 (515894) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT139-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to THUNDER7 (515894) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT33-PO | Prior Outage: C-RIVER4 (510946) 138.0 kV to C-RIVER1 (510947) 13.8 kV to C-RIVER7 (515422) 345.0 kV ThreeWinding 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT148-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 588637: MACHINE TRIPPED DUE TO OVER FREQUENCY PROTECTION | DISABLE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT87-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT78-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT88-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT29-3PH | 3 Phase fault on 7MORGAN (300045) 345 kV Bus a. Apply fault at the 7MORGAN (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT163-PO | Prior Outage: 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit 3 Phase Fault on 7MORGAN (300045) 345 kV Bus a. Apply fault at the 7MORGAN (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT162-PO | Prior Outage: BROOKLINE 7 (549984) 345.0 kV to FLINTCR7 (506935) 345.0 kV Transmission Circuit 3 Phase Fault on 7MORGAN (300045) 345 kV Bus a. Apply fault at the 7MORGAN (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT15-3PH | 3 Phase fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT105-PO | Prior Outage: 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit 3 Phase Fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT6-3PH | 3 Phase fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT30-3PH | 3 Phase fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV TwoWinding | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT45-PO | Prior Outage: 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV TwoWinding 3 Phase Fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV TwoWinding | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT136-PO | Prior Outage: 7MORGAN (300045) 345.0 kV to 7HUBEN (300042) 345.0 kV Transmission Circuit 3 Phase Fault on 7JASPER (300949) 345 kV Bus a. Apply fault at the 7JASPER (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7JASPER (300949) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT134-PO | Prior Outage: BROOKLINE 7 (549984) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit 3 Phase Fault on 7JASPER (300949) 345 kV Bus a. Apply fault at the 7JASPER (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7JASPER (300949) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT137-3PH | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 (509790) 138.0 kV to 141PINE4 (509892) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT81-3PH | 3 Phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT153-3PH | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT145-PO | Prior Outage: WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit 3 Phase Fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT112-3PH | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT142-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to THUNDER7 (515894) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT141-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to THUNDER7 (515894) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G16-100-TAP (587804) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT42-3PH | 3 Phase fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 (515422) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT87-3PH | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT12-3PH | 3 Phase fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT153-PO | Prior Outage: 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT8-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT9-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT88-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT159-3PH | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT147-3PH | 3 Phase fault on VIOLA 4 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to CONWAY (539009) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT152-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 588637: MACHINE TRIPPED DUE TO OVER FREQUENCY PROTECTION | DISABLE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT151-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 588637: MACHINE TRIPPED DUE TO OVER FREQUENCY PROTECTION | DISABLE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT149-PO | Prior Outage: THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 588637: MACHINE TRIPPED DUE TO OVER FREQUENCY PROTECTION | DISABLE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT18-3PH | 3 Phase fault on W.GRDNR7 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT7-3PH | 3 Phase fault on STILWEL7 (542968) 345 kV Bus a. Apply fault at the STILWEL7 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT161-PO | Prior Outage: BROOKLINE 7 (549984) 345.0 kV to FLINTCR7 (506935) 345.0 kV Transmission Circuit 3 Phase Fault on BROOKLINE 7 (549984) 345 kV Bus a. Apply fault at the BROOKLINE 7 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROOKLINE 7 (549984) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT55-SB | Single Phase Fault with Stuck Breaker on 7SPORTSMAN (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT57-SB | Single Phase Fault with Stuck Breaker on BUFFALO7 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT65-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT66-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT103-SB | Single Phase Fault with Stuck Breaker on BROOKLINE 7 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROOKLINE 7 (549984) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT164-3PH | 3 Phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT173-3PH | 3 Phase fault on BUTLER 4 (532987) 138 kV Bus a. Apply fault at the BUTLER 4 (532987) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV Trip Bus b.2. BUTLER 4 (532987) 138.0 kV to BUTLERN2 (533583) 69.0 kV TwoWinding | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT109-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT110-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT111-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT112-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT114-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. After 6.6 additional cycles, trip the WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV ThreeWinding and remove fault | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT188-PO | Prior Outage: WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | No | Yes | No | Yes |  | REDUCE WAVERLY TO 0.0 MW
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT189-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | No | Yes | No | Yes |  | REDUCE WAVERLY TO 0.0 MW
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT190-PO | Prior Outage: WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | No | Yes | No | Yes |  | REDUCE WAVERLY TO 0.0 MW
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT191-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | No | Yes | No | Yes |  | REDUCE WAVERLY TO 0.0 MW
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT194-PO | Prior Outage: WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | No | Yes | No | Yes |  | REDUCE WAVERLY TO 0.0 MW AND WOLFCREEK TO 1100 MW
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT195-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | No | Yes | No | Yes |  | REDUCE WAVERLY TO 0.0 MW AND WOLFCREEK TO 1100 MW
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT198-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT199-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT202-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT203-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT206-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | No | Yes | No | Yes |  | REDUCE WOLFCREEK TO 1100 MW
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT207-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | No | Yes | No | Yes |  | REDUCE WOLFCREEK TO 1100 MW
Central | 08 - North Oklahoma/South Central Kansas | 19W | Transfer | G8_FLT117-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip the WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. After 6.6 additional cycles, remove fault | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 19W | Sensitivity | G8_FLT115-3PH | 3 Phase fault on PENSA 2 (512628) 69 kV Bus a. Apply fault at the PENSA 2 (512628) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENSA 2 (512628) 69.0 kV to PENSA 5 (512654) 161.0 kV to PENSA 1 (512841) 13.8 kV ThreeWinding | P1 | Unstable | Yes | Yes | Yes | Yes | No | Yes |  | MITIGATION NOT REQUIRED - Informational only.
Central | 08 - North Oklahoma/South Central Kansas | 19W | Sensitivity | G8_FLT114-3PH | 3 Phase fault on PENSA 5 (512654) 161 kV Bus a. Apply fault at the PENSA 5 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENSA 5 (512654) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Unstable | Yes | Yes | Yes | Yes | No | Yes |  | MITIGATION NOT REQUIRED - Informational only.
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT22-3PH | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 578533: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT34-3PH | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 578533: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT21-3PH | 3 Phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT92-3PH | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT93-3PH | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT13-3PH | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT14-3PH | 3 Phase fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT16-3PH | 3 Phase fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT17-3PH | 3 Phase fault on DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT83-3PH | 3 Phase fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT20-3PH | 3 Phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT33-3PH | 3 Phase fault on SWISVAL7 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT89-3PH | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 515882: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT84-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT5-3PH | 3 Phase fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT8-3PH | 3 Phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT171-3PH | 3 Phase fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT172-3PH | 3 Phase fault on RICE 6 (530686) 230 kV Bus a. Apply fault at the RICE 6 (530686) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT170-3PH | 3 Phase fault on EMCPHER6 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 (532872) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT4-3PH | 3 Phase fault on LITCH 5 (532932) 161 kV Bus a. Apply fault at the LITCH 5 (532932) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITCH 5 (532932) 161.0 kV to FRANKLIN5 (532938) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT40-3PH | 3 Phase fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT39-3PH | 3 Phase fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT38-3PH | 3 Phase fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT145-3PH | 3 Phase fault on VIOLA 4 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT97-3PH | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT146-3PH | 3 Phase fault on GILL 4 (533047) 138 kV Bus a. Apply fault at the GILL 4 (533047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL 4 (533047) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT148-3PH | 3 Phase fault on SUMNER 4 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT3-3PH | 3 Phase fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT156-3PH | 3 Phase fault on BENTON 4 (532986) 138 kV Bus a. Apply fault at the BENTON 4 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTN1 1 (532821) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT9-3PH | 3 Phase fault on NEOSHO 4 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 1 1 (532824) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT86-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICH11 1 (532829) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT85-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICH12 1 (532830) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT144-3PH | 3 Phase fault on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA1X1 (532832) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT122-3PH | 3 Phase fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5ELMCRK (300993) 161.0 kV to CATSAGR5 (512638) 161.0 kV Transmission Circuit b.2. 5ELMCRK (300993) 161.0 kV to COLINS 5 (512627) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT77-3PH | 3 Phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT130-3PH | 3 Phase fault on KERR GR3 (512634) 115 kV Bus a. Apply fault at the KERR GR3 (512634) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L GROVE3 (510423) 115.0 kV to KERR GR3 (512634) 115.0 kV Transmission Circuit b.2. LSTAR--3 (510399) 115.0 kV to PRY-JCT3 (510407) 115.0 kV Transmission Circuit b.3. LSTAR--3 (510399) 115.0 kV to L GROVE3 (510423) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT134-3PH | 3 Phase fault on BA.N-ST4 (509786) 138 kV Bus a. Apply fault at the BA.N-ST4 (509786) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA.N-ST4 (509786) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit b.2. LLAN WT4 (509770) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit b.3. DAWSONT4 (509803) 138.0 kV to N21ST--4 (509866) 138.0 kV Transmission Circuit b.4. LLAN WT4 (509770) 138.0 kV to DAWSONT4 (509803) 138.0 kV Transmission Circuit b.5. DAWSON-4 (509792) 138.0 kV to DAWSONT4 (509803) 138.0 kV Transmission Circuit b.6. BA.N-ST4 (509786) 138.0 kV to ONETA--4 (509806) 138.0 kV Transmission Circuit b.7. CATOOSA4 (509790) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT136-3PH | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 (509790) 138.0 kV to OWAS88_4 (509887) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT135-3PH | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYO--N4 (509779) 138.0 kV to E41ST_W4 (509886) 138.0 kV Transmission Circuit b.2. MINGO-N4 (509760) 138.0 kV to 21STTAP4 (509828) 138.0 kV Transmission Circuit b.3. LLAN ET4 (509771) 138.0 kV to E41ST_W4 (509886) 138.0 kV Transmission Circuit b.4. LLAN ET4 (509771) 138.0 kV to CATOOSA4 (509790) 138.0 kV Transmission Circuit b.5. MINGO-N4 (509760) 138.0 kV to MAYO--N4 (509779) 138.0 kV Transmission Circuit b.6. T.S.E.-4 (509811) 138.0 kV to 21STTAP4 (509828) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT138-3PH | 3 Phase fault on PCATSAT4 (509841) 138 kV Bus a. Apply fault at the PCATSAT4 (509841) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCATSAT4 (509841) 138.0 kV to OWASO2_4 (509843) 138.0 kV Transmission Circuit b.2. CATOOSA4 (509790) 138.0 kV to PCATSAT4 (509841) 138.0 kV Transmission Circuit b.3. OWASO2_4 (509843) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT139-3PH | 3 Phase fault on TERNITP4 (509835) 138 kV Bus a. Apply fault at the TERNITP4 (509835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERNITP4 (509835) 138.0 kV to VERDIGS4 (509854) 138.0 kV Transmission Circuit b.2. CLARTOK4 (509864) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit b.3. VERDIGS4 (509854) 138.0 kV to CLARTOK4 (509864) 138.0 kV Transmission Circuit b.4. CATOOSA4 (509790) 138.0 kV to TERNITP4 (509835) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT43-3PH | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 (510907) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT45-3PH | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 (510907) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT163-3PH | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT47-3PH | 3 Phase fault on REDBUD 7 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT162-3PH | 3 Phase fault on BROOKLINE 7 (549984) 345 kV Bus a. Apply fault at the BROOKLINE 7 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT19-3PH | 3 Phase fault on DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT46-3PH | 3 Phase fault on VALIANT7 (510911) 345 kV Bus a. Apply fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 (510907) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT58-3PH | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT51-3PH | 3 Phase fault on CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAMSPR7 (506945) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT52-3PH | 3 Phase fault on CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT57-3PH | 3 Phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 (515045) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT90-3PH | 3 Phase fault on SUMMIT 7 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to G16-112-TAP (587894) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT1-3PH | 3 Phase fault on MARMTNE5 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT2-3PH | 3 Phase fault on FRANKLIN5 (532938) 161 kV Bus a. Apply fault at the FRANKLIN5 (532938) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT33-SB | Single Phase Fault with Stuck Breaker on HUNTERS7 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit b.2. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT34-SB | Single Phase Fault with Stuck Breaker on HUNTERS7 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit b.2. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT35-SB | Single Phase Fault with Stuck Breaker on HUNTERS7 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit b.2. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT52-SB | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit b.2. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV TwoWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT27-SB | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT40-SB | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT23-SB | Single Phase Fault with Stuck Breaker on PECANCK7 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC21 (515759) 13.8 kV ThreeWinding b.2. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT98-SB | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT96-SB | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT95-SB | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit b.2. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT97-SB | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT38-SB | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT39-SB | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT36-SB | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT37-SB | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT99-SB | Single Phase Fault with Stuck Breaker on WOODRNG7 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT101-SB | Single Phase Fault with Stuck Breaker on WOODRNG4 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV ThreeWinding b.2. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT14-SB | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT15-SB | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1_21 (512821) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT17-SB | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1_21 (512821) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT43-SB | Single Phase Fault with Stuck Breaker on RENO 7 (532771) 345 kV Bus a. Apply Fault at the RENO 7 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to RENO 2X1 (532810) 14.4 kV to RENO 3 (533416) 115.0 kV ThreeWinding b.2. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT3-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT4-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to RSS T2 4 (509875) 138.0 kV to RSST2 T1 (509876) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT76-SB | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit b.2. T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV to T.NO.2-4 (509895) 138.0 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT77-SB | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV to T.NO.2-4 (509895) 138.0 kV ThreeWinding b.2. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT78-SB | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit b.2. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT79-SB | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT91-SB | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT92-SB | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV ThreeWinding b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT93-SB | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT94-SB | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT10-SB | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT32-3PH | 3 Phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT80-3PH | 3 Phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT117-3PH | 3 Phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT70-3PH | 3 Phase fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit b.2. 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT72-3PH | 3 Phase fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT73-3PH | 3 Phase fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT120-3PH | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to 412SUB 5 (512637) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT119-3PH | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT66-3PH | 3 Phase fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT114-3PH | 3 Phase fault on PENSA 5 (512654) 161 kV Bus a. Apply fault at the PENSA 5 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENSA 5 (512654) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT67-3PH | 3 Phase fault on WMAIN ST5 (512742) 161 kV Bus a. Apply fault at the WMAIN ST5 (512742) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WMAIN ST5 (512742) 161.0 kV to NWMAID5 (512757) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT65-3PH | 3 Phase fault on GERALDGAY5 (512760) 161 kV Bus a. Apply fault at the GERALDGAY5 (512760) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWMAID5 (512757) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT31-3PH | 3 Phase fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT69-3PH | 3 Phase fault on 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT74-3PH | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT140-3PH | 3 Phase fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT124-3PH | 3 Phase fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT50-3PH | 3 Phase fault on CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT108-3PH | 3 Phase fault on S.S.---4 (509815) 138 kV Bus a. Apply fault at the S.S.---4 (509815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRATTV-4 (509758) 138.0 kV to BLUEBEL4 (515242) 138.0 kV Transmission Circuit b.2. PRATTV-4 (509758) 138.0 kV to S.S.---4 (509815) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT54-3PH | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT152-3PH | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT49-3PH | 3 Phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT105-3PH | 3 Phase fault on TRYON 4 (515675) 138 kV Bus a. Apply fault at the TRYON 4 (515675) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNIPE 4 (515514) 138.0 kV to SPGVLLY4 (515574) 138.0 kV Transmission Circuit b.2. KNIPE 4 (515514) 138.0 kV to TRYON 4 (515675) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT109-3PH | 3 Phase fault on BLUEBEL4 (515242) 138 kV Bus a. Apply fault at the BLUEBEL4 (515242) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIBBENS4 (515237) 138.0 kV to BEELINE4 (515247) 138.0 kV Transmission Circuit b.2. POLECTP4 (515218) 138.0 kV to TIBBENS4 (515237) 138.0 kV Transmission Circuit b.3. POLECTP4 (515218) 138.0 kV to HICKORY4 (515244) 138.0 kV Transmission Circuit b.4. BLUEBEL4 (515242) 138.0 kV to BOWDEN 4 (515243) 138.0 kV Transmission Circuit b.5. POLECTP4 (515218) 138.0 kV to POLECAT4 (515219) 138.0 kV Transmission Circuit b.6. BOWDEN 4 (515243) 138.0 kV to HICKORY4 (515244) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT55-3PH | 3 Phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT48-3PH | 3 Phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT25-3PH | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT154-3PH | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT150-3PH | 3 Phase fault on HUNTERS7 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT143-3PH | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 515882: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT151-3PH | 3 Phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV ThreeWinding | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT63-3PH | 3 Phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 (515044) 138.0 kV to SEMINOL7 (515045) 345.0 kV to SEMINO11 (515756) 14.4 kV ThreeWinding | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT53-3PH | 3 Phase fault on PECANCK5 (515234) 161 kV Bus a. Apply fault at the PECANCK5 (515234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC21 (515759) 13.8 kV ThreeWinding | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT149-3PH | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV ThreeWinding | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT10-3PH | 3 Phase fault on MARMTNW5 (532935) 161 kV Bus a. Apply fault at the MARMTNW5 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT91-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT82-3PH | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT167-3PH | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT11-3PH | 3 Phase fault on MARMTNE5 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | 584584: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT19-SB | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT79-3PH | 3 Phase fault on CLARMR 5 (512651) 161 kV Bus a. Apply fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT68-3PH | 3 Phase fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT75-3PH | 3 Phase fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT123-3PH | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT64-3PH | 3 Phase fault on GRDA1 5 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT76-3PH | 3 Phase fault on GRDA1 5 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA1 2 (512727) 69.0 kV to GRDA1_11 (512816) 13.8 kV ThreeWinding | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT116-3PH | 3 Phase fault on 5SPORTSMAN (300741) 161 kV Bus a. Apply fault at the 5SPORTSMAN (300741) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT41-SB | Single Phase Fault with Stuck Breaker on EMPEC 7 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT42-SB | Single Phase Fault with Stuck Breaker on RENO 7 (532771) 345 kV Bus a. Apply Fault at the RENO 7 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT44-SB | Single Phase Fault with Stuck Breaker on BENTON 7 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT94-3PH | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT35-3PH | 3 Phase fault on MONTGOM4 (533004) 138 kV Bus a. Apply fault at the MONTGOM4 (533004) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit b.2. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT96-3PH | 3 Phase fault on COWSKIN4 (533038) 138 kV Bus a. Apply fault at the COWSKIN4 (533038) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit b.2. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT95-3PH | 3 Phase fault on LAKERDG4 (533053) 138 kV Bus a. Apply fault at the LAKERDG4 (533053) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKERDG4 (533053) 138.0 kV Trip Bus b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit b.3. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT98-3PH | 3 Phase fault on SG12COL4 (533065) 138 kV Bus a. Apply fault at the SG12COL4 (533065) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit b.2. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit b.3. SG12COL4 (533065) 138.0 kV Trip Bus b.4. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit b.5. WWUPLNT4 (533016) 138.0 kV Trip Bus b.6. BENTLEY4 (533015) 138.0 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT25-SB | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEMINOL7 (515045) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT41-3PH | 3 Phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT87-SB | Single Phase Fault with Stuck Breaker on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to SOONER2G (514806) 20.0 kV TwoWinding b.2. SOONER 7 (514803) 345.0 kV to G16-100-TAP (587804) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT48-SB | Single Phase Fault with Stuck Breaker on RENO 7 (532771) 345 kV Bus a. Apply Fault at the RENO 7 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to RENO 1X1 (532807) 14.4 kV to RENO 3 (533416) 115.0 kV ThreeWinding b.2. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT113-3PH | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G16-100-TAP (587804) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT28-3PH | 3 Phase fault on G17-022-TAP (588664) 138 kV Bus a. Apply fault at the G17-022-TAP (588664) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit b.2. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT26-SB | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT45-SB | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT46-SB | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH12 1 (532830) 13.8 kV ThreeWinding b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT77-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on CLARMR 5 (512651) 161 kV Bus a. Apply fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT66-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT65-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT64-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit 3 Phase Fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT72-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on GRDA1 5 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA1 2 (512727) 69.0 kV to GRDA1_11 (512816) 13.8 kV ThreeWinding | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT27-3PH | 3 Phase fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT31-PO | Prior Outage: MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT23-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT24-PO | Prior Outage: 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT22-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT25-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT38-PO | Prior Outage: CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 (515045) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT39-PO | Prior Outage: MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 (515045) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT37-PO | Prior Outage: SEMINOL7 (515045) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit 3 Phase Fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 (515422) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT41-PO | Prior Outage: MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT125-PO | Prior Outage: CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit 3 Phase Fault on RICE 6 (530686) 230 kV Bus a. Apply fault at the RICE 6 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT184-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit 3 Phase Fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT89-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit 3 Phase Fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT180-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit 3 Phase Fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT19-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT6-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT7-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT20-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT10-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT21-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT85-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT84-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT86-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit 3 Phase Fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT179-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT181-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT182-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT187-PO | Prior Outage: VIOLA 7 (532798) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT82-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT80-PO | Prior Outage: RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT185-PO | Prior Outage: RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT118-PO | Prior Outage: HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 578533: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT119-PO | Prior Outage: RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV ThreeWinding 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT81-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT83-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT186-PO | Prior Outage: VIOLA 7 (532798) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT126-PO | Prior Outage: RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit 3 Phase Fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT128-PO | Prior Outage: SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit 3 Phase Fault on EMCPHER6 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT3-PO | Prior Outage: LITCH 5 (532932) 161.0 kV to FRANKLIN5 (532938) 161.0 kV Transmission Circuit 3 Phase Fault on MARMTNE5 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT2-PO | Prior Outage: FRANKLIN1 (533122) 12.5 kV to Trip Bus 3 Phase Fault on MARMTNE5 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT30-PO | Prior Outage: MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT28-PO | Prior Outage: MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT26-PO | Prior Outage: BUTLER 4 (532987) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT14-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT11-PO | Prior Outage: 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT12-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT13-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT1-PO | Prior Outage: N345 1 1 (532824) 13.8 kV to Trip Bus 3 Phase Fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT18-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 4 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 1 1 (532824) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT15-PO | Prior Outage: 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 4 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 1 1 (532824) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT16-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 4 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 1 1 (532824) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT17-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 4 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 1 1 (532824) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT79-PO | Prior Outage: WICH11 1 (532829) 13.8 kV to Trip Bus 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICH12 1 (532830) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT117-PO | Prior Outage: SCJ1X1 (999532) 13.8 kV to Trip Bus 3 Phase Fault on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA1X1 (532832) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT74-PO | Prior Outage: CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit 3 Phase Fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT75-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT73-PO | Prior Outage: OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit 3 Phase Fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT111-PO | Prior Outage: EXCLART4 (510401) 138.0 kV to G17-077-TAP (589154) 138.0 kV Transmission Circuit 3 Phase Fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 (510402) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit b.2. BIRDHOL4 (510398) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.3. BIRDHOL4 (510398) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT32-PO | Prior Outage: PITTSB-7 (510907) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT130-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit 3 Phase Fault on REDBUD 7 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT131-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit 3 Phase Fault on REDBUD 7 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT132-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit 3 Phase Fault on REDBUD 7 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT178-PO | Prior Outage: WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit 3 Phase Fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT172-PO | Prior Outage: T.NO.--7 (509852) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit 3 Phase Fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT175-PO | Prior Outage: T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit 3 Phase Fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT176-PO | Prior Outage: T.NO.--7 (509852) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit 3 Phase Fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT49-SB | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit b.2. MUSKOG4G (515223) 18.0 kV to MUSKOGE7 (515224) 345.0 kV TwoWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT100-SB | Single Phase Fault with Stuck Breaker on WOODRNG7 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit b.2. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT102-SB | Single Phase Fault with Stuck Breaker on WOODRNG7 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit b.2. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT173-PO | Prior Outage: T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit 3 Phase Fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT171-PO | Prior Outage: WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit 3 Phase Fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT174-PO | Prior Outage: T.NO.--7 (509852) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit 3 Phase Fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT164-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit 3 Phase Fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT54-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit b.2. 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT53-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit b.2. 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT51-PO | Prior Outage: DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit b.2. 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT52-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit b.2. 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT60-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT104-PO | Prior Outage: PENSA 2 (512628) 69.0 kV to PENSA 5 (512654) 161.0 kV to PENSA 1 (512841) 13.8 kV ThreeWinding 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT59-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT103-PO | Prior Outage: KERR GR5 (512635) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT58-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT102-PO | Prior Outage: PENSA 5 (512654) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT97-PO | Prior Outage: KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT99-PO | Prior Outage: MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER2 1 (512837) 13.2 kV ThreeWinding 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT100-PO | Prior Outage: 5ELMCRK (300993) 161.0 kV to CATSAGR5 (512638) 161.0 kV Transmission Circuit 5ELMCRK (300993) 161.0 kV to COLINS 5 (512627) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT101-PO | Prior Outage: 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT96-PO | Prior Outage: 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT98-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT70-PO | Prior Outage: CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT71-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT67-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to GRDA1 2 (512727) 69.0 kV to GRDA1_11 (512816) 13.8 kV ThreeWinding 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT68-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT69-PO | Prior Outage: OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT165-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit 3 Phase Fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT166-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit 3 Phase Fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT50-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT49-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT46-PO | Prior Outage: 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit 3 Phase Fault on 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT47-PO | Prior Outage: DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit 3 Phase Fault on 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT48-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit 3 Phase Fault on 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT63-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT62-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT61-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit 3 Phase Fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT36-PO | Prior Outage: CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit 3 Phase Fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 (515422) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT129-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit 3 Phase Fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT133-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit 3 Phase Fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT40-PO | Prior Outage: CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT160-PO | Prior Outage: PECANCK7 (515235) 345.0 kV to R.S.S.-7 (509782) 345.0 kV Transmission Circuit 3 Phase Fault on PECANCK7 (515235) 345 kV Bus a. Apply fault at the PECANCK7 (515235) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECANCK7 (515235) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT35-PO | Prior Outage: MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit 3 Phase Fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 (515422) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT34-PO | Prior Outage: MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit 3 Phase Fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 (515422) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT169-PO | Prior Outage: RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT140-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT167-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit 3 Phase Fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT168-PO | Prior Outage: RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit 3 Phase Fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT144-PO | Prior Outage: WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit 3 Phase Fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT146-PO | Prior Outage: WOODRNG7 (514715) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit 3 Phase Fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT121-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT123-PO | Prior Outage: RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT116-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT124-PO | Prior Outage: WICH12 1 (532830) 13.8 kV to Trip Bus 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT122-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT120-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 515882: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION 515883: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION 515927: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION 599090: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT147-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT150-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT137-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to THUNDER7 (515894) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT139-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to THUNDER7 (515894) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT33-PO | Prior Outage: C-RIVER4 (510946) 138.0 kV to C-RIVER1 (510947) 13.8 kV to C-RIVER7 (515422) 345.0 kV ThreeWinding 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT148-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT87-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT78-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT88-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT135-PO | Prior Outage: BROOKLINE 7 (549984) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit 3 Phase Fault on 7MORGAN (300045) 345 kV Bus a. Apply fault at the 7MORGAN (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to 7HUBEN (300042) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT29-3PH | 3 Phase fault on 7MORGAN (300045) 345 kV Bus a. Apply fault at the 7MORGAN (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT163-PO | Prior Outage: 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit 3 Phase Fault on 7MORGAN (300045) 345 kV Bus a. Apply fault at the 7MORGAN (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT162-PO | Prior Outage: BROOKLINE 7 (549984) 345.0 kV to FLINTCR7 (506935) 345.0 kV Transmission Circuit 3 Phase Fault on 7MORGAN (300045) 345 kV Bus a. Apply fault at the 7MORGAN (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT15-3PH | 3 Phase fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT105-PO | Prior Outage: 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit 3 Phase Fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT6-3PH | 3 Phase fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT30-3PH | 3 Phase fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV TwoWinding | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT45-PO | Prior Outage: 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV TwoWinding 3 Phase Fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV TwoWinding | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT136-PO | Prior Outage: 7MORGAN (300045) 345.0 kV to 7HUBEN (300042) 345.0 kV Transmission Circuit 3 Phase Fault on 7JASPER (300949) 345 kV Bus a. Apply fault at the 7JASPER (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7JASPER (300949) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT134-PO | Prior Outage: BROOKLINE 7 (549984) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit 3 Phase Fault on 7JASPER (300949) 345 kV Bus a. Apply fault at the 7JASPER (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7JASPER (300949) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT137-3PH | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 (509790) 138.0 kV to 141PINE4 (509892) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT81-3PH | 3 Phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT153-3PH | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT145-PO | Prior Outage: WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit 3 Phase Fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT138-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT112-3PH | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT142-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to THUNDER7 (515894) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT143-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to G16-100-TAP (587804) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT141-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to THUNDER7 (515894) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G16-100-TAP (587804) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT42-3PH | 3 Phase fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 (515422) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT87-3PH | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT12-3PH | 3 Phase fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT153-PO | Prior Outage: 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT8-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT9-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT26-3PH | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT88-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT159-3PH | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT147-3PH | 3 Phase fault on VIOLA 4 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to CONWAY (539009) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT152-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT151-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT149-PO | Prior Outage: THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT18-3PH | 3 Phase fault on W.GRDNR7 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT7-3PH | 3 Phase fault on STILWEL7 (542968) 345 kV Bus a. Apply fault at the STILWEL7 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT161-PO | Prior Outage: BROOKLINE 7 (549984) 345.0 kV to FLINTCR7 (506935) 345.0 kV Transmission Circuit 3 Phase Fault on BROOKLINE 7 (549984) 345 kV Bus a. Apply fault at the BROOKLINE 7 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROOKLINE 7 (549984) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT55-SB | Single Phase Fault with Stuck Breaker on 7SPORTSMAN (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT56-SB | Single Phase Fault with Stuck Breaker on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT57-SB | Single Phase Fault with Stuck Breaker on BUFFALO7 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT58-SB | Single Phase Fault with Stuck Breaker on NEOSHO 7 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT59-SB | Single Phase Fault with Stuck Breaker on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT105-SB | Single Phase Fault with Stuck Breaker on CIRCLE 6 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT104-SB | Single Phase Fault with Stuck Breaker on SUMMIT 6 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT64-SB | Single Phase Fault with Stuck Breaker on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 4 (533021) 138.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT65-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT66-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT103-SB | Single Phase Fault with Stuck Breaker on BROOKLINE 7 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROOKLINE 7 (549984) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT168-3PH | 3 Phase fault on 7MORGAN (300045) 345 kV Bus a. Apply fault at the 7MORGAN (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT164-3PH | 3 Phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT174-3PH | 3 Phase fault on MILANTP4 (539675) 138 kV Bus a. Apply fault at the MILANTP4 (539675) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILANTP4 (539675) 138.0 kV Trip Bus b.2. VIOLA 4 (533075) 138.0 kV to CONWAY (539009) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT173-3PH | 3 Phase fault on BUTLER 4 (532987) 138 kV Bus a. Apply fault at the BUTLER 4 (532987) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV Trip Bus b.2. BUTLER 4 (532987) 138.0 kV to BUTLERN2 (533583) 69.0 kV TwoWinding | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT109-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT110-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT111-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT112-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT113-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21L | Transfer | G8_FLT114-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. After 6.6 additional cycles, trip the WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV ThreeWinding and remove fault | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT21-3PH | 3 Phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT93-3PH | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT14-3PH | 3 Phase fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT16-3PH | 3 Phase fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT83-3PH | 3 Phase fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT20-3PH | 3 Phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT89-3PH | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT84-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT5-3PH | 3 Phase fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT8-3PH | 3 Phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT145-3PH | 3 Phase fault on VIOLA 4 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT97-3PH | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT146-3PH | 3 Phase fault on GILL 4 (533047) 138 kV Bus a. Apply fault at the GILL 4 (533047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL 4 (533047) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT148-3PH | 3 Phase fault on SUMNER 4 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT156-3PH | 3 Phase fault on BENTON 4 (532986) 138 kV Bus a. Apply fault at the BENTON 4 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTN1 1 (532821) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT86-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICH11 1 (532829) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT85-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICH12 1 (532830) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT144-3PH | 3 Phase fault on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA1X1 (532832) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT163-3PH | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT47-3PH | 3 Phase fault on REDBUD 7 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT58-3PH | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT33-SB | Single Phase Fault with Stuck Breaker on HUNTERS7 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit b.2. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT34-SB | Single Phase Fault with Stuck Breaker on HUNTERS7 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit b.2. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT35-SB | Single Phase Fault with Stuck Breaker on HUNTERS7 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit b.2. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT52-SB | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit b.2. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV TwoWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT40-SB | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT21-SB | Single Phase Fault with Stuck Breaker on PECANCK7 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT23-SB | Single Phase Fault with Stuck Breaker on PECANCK7 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC21 (515759) 13.8 kV ThreeWinding b.2. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT98-SB | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT95-SB | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit b.2. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT97-SB | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT38-SB | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT39-SB | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT36-SB | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT37-SB | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT18-SB | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV TwoWinding b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT5-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to RSS T2 4 (509875) 138.0 kV to RSST2 T1 (509876) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT3-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT4-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to RSS T2 4 (509875) 138.0 kV to RSST2 T1 (509876) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT10-SB | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT32-3PH | 3 Phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT54-3PH | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT152-3PH | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT49-3PH | 3 Phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT25-3PH | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT165-3PH | 3 Phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT154-3PH | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT150-3PH | 3 Phase fault on HUNTERS7 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT143-3PH | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT149-3PH | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV ThreeWinding | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT91-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT82-3PH | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT167-3PH | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT41-SB | Single Phase Fault with Stuck Breaker on EMPEC 7 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT44-SB | Single Phase Fault with Stuck Breaker on BENTON 7 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT96-3PH | 3 Phase fault on COWSKIN4 (533038) 138 kV Bus a. Apply fault at the COWSKIN4 (533038) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit b.2. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT95-3PH | 3 Phase fault on LAKERDG4 (533053) 138 kV Bus a. Apply fault at the LAKERDG4 (533053) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKERDG4 (533053) 138.0 kV Trip Bus b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit b.3. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT98-3PH | 3 Phase fault on SG12COL4 (533065) 138 kV Bus a. Apply fault at the SG12COL4 (533065) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit b.2. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit b.3. SG12COL4 (533065) 138.0 kV Trip Bus b.4. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit b.5. WWUPLNT4 (533016) 138.0 kV Trip Bus b.6. BENTLEY4 (533015) 138.0 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT87-SB | Single Phase Fault with Stuck Breaker on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to SOONER2G (514806) 20.0 kV TwoWinding b.2. SOONER 7 (514803) 345.0 kV to G16-100-TAP (587804) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT113-3PH | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G16-100-TAP (587804) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT41-PO | Prior Outage: MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT6-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT7-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT20-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT10-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT84-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT86-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit 3 Phase Fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT179-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT181-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT187-PO | Prior Outage: VIOLA 7 (532798) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT82-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT80-PO | Prior Outage: RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT185-PO | Prior Outage: RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT118-PO | Prior Outage: HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT119-PO | Prior Outage: RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV ThreeWinding 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT81-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT83-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT186-PO | Prior Outage: VIOLA 7 (532798) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT3-PO | Prior Outage: LITCH 5 (532932) 161.0 kV to FRANKLIN5 (532938) 161.0 kV Transmission Circuit 3 Phase Fault on MARMTNE5 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT13-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT79-PO | Prior Outage: WICH11 1 (532829) 13.8 kV to Trip Bus 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICH12 1 (532830) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT117-PO | Prior Outage: SCJ1X1 (999532) 13.8 kV to Trip Bus 3 Phase Fault on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA1X1 (532832) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT111-PO | Prior Outage: EXCLART4 (510401) 138.0 kV to G17-077-TAP (589154) 138.0 kV Transmission Circuit 3 Phase Fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 (510402) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit b.2. BIRDHOL4 (510398) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.3. BIRDHOL4 (510398) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT32-PO | Prior Outage: PITTSB-7 (510907) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT130-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit 3 Phase Fault on REDBUD 7 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT131-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit 3 Phase Fault on REDBUD 7 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT132-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit 3 Phase Fault on REDBUD 7 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT178-PO | Prior Outage: WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit 3 Phase Fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT172-PO | Prior Outage: T.NO.--7 (509852) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit 3 Phase Fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT175-PO | Prior Outage: T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit 3 Phase Fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT176-PO | Prior Outage: T.NO.--7 (509852) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit 3 Phase Fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT49-SB | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit b.2. MUSKOG4G (515223) 18.0 kV to MUSKOGE7 (515224) 345.0 kV TwoWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT173-PO | Prior Outage: T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit 3 Phase Fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT171-PO | Prior Outage: WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit 3 Phase Fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT174-PO | Prior Outage: T.NO.--7 (509852) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit 3 Phase Fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT71-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT129-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit 3 Phase Fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT133-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit 3 Phase Fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT160-PO | Prior Outage: PECANCK7 (515235) 345.0 kV to R.S.S.-7 (509782) 345.0 kV Transmission Circuit 3 Phase Fault on PECANCK7 (515235) 345 kV Bus a. Apply fault at the PECANCK7 (515235) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECANCK7 (515235) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT43-PO | Prior Outage: CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit 3 Phase Fault on FTSMITH7 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT169-PO | Prior Outage: RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT140-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT167-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit 3 Phase Fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT170-PO | Prior Outage: RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit 3 Phase Fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT168-PO | Prior Outage: RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit 3 Phase Fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT144-PO | Prior Outage: WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit 3 Phase Fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT146-PO | Prior Outage: WOODRNG7 (514715) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit 3 Phase Fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT121-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT123-PO | Prior Outage: RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 515926: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION 599089: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT116-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT124-PO | Prior Outage: WICH12 1 (532830) 13.8 kV to Trip Bus 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT122-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT120-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT150-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT137-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to THUNDER7 (515894) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT139-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to THUNDER7 (515894) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT148-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 588637: MACHINE TRIPPED DUE TO OVER FREQUENCY PROTECTION | DISABLE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT87-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT78-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT88-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT6-3PH | 3 Phase fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT81-3PH | 3 Phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT153-3PH | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT145-PO | Prior Outage: WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit 3 Phase Fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT138-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT112-3PH | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT142-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to THUNDER7 (515894) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT143-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to G16-100-TAP (587804) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT141-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to THUNDER7 (515894) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G16-100-TAP (587804) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT87-3PH | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT12-3PH | 3 Phase fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT153-PO | Prior Outage: 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT8-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT9-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT88-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT159-3PH | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT147-3PH | 3 Phase fault on VIOLA 4 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to CONWAY (539009) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT152-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT151-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | No | 588637: MACHINE TRIPPED DUE TO OVER FREQUENCY PROTECTION | DISABLE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT149-PO | Prior Outage: THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT57-SB | Single Phase Fault with Stuck Breaker on BUFFALO7 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT65-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT66-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT164-3PH | 3 Phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT173-3PH | 3 Phase fault on BUTLER 4 (532987) 138 kV Bus a. Apply fault at the BUTLER 4 (532987) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV Trip Bus b.2. BUTLER 4 (532987) 138.0 kV to BUTLERN2 (533583) 69.0 kV TwoWinding | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT114-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. After 6.6 additional cycles, trip the WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV ThreeWinding and remove fault | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT194-PO | Prior Outage: WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes |  | REDUCE WAVERLY TO 0.0 MW
Central | 08 - North Oklahoma/South Central Kansas | 21S | Transfer | G8_FLT195-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes |  | REDUCE WAVERLY TO 0.0 MW
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT22-3PH | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT34-3PH | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT21-3PH | 3 Phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT92-3PH | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT93-3PH | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT13-3PH | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT14-3PH | 3 Phase fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT16-3PH | 3 Phase fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT17-3PH | 3 Phase fault on DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT83-3PH | 3 Phase fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT33-3PH | 3 Phase fault on SWISVAL7 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT89-3PH | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT84-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT5-3PH | 3 Phase fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT8-3PH | 3 Phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT171-3PH | 3 Phase fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT172-3PH | 3 Phase fault on RICE 6 (530686) 230 kV Bus a. Apply fault at the RICE 6 (530686) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT170-3PH | 3 Phase fault on EMCPHER6 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 (532872) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT4-3PH | 3 Phase fault on LITCH 5 (532932) 161 kV Bus a. Apply fault at the LITCH 5 (532932) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITCH 5 (532932) 161.0 kV to FRANKLIN5 (532938) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT40-3PH | 3 Phase fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT39-3PH | 3 Phase fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT38-3PH | 3 Phase fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT145-3PH | 3 Phase fault on VIOLA 4 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT97-3PH | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT146-3PH | 3 Phase fault on GILL 4 (533047) 138 kV Bus a. Apply fault at the GILL 4 (533047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL 4 (533047) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT148-3PH | 3 Phase fault on SUMNER 4 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT3-3PH | 3 Phase fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT156-3PH | 3 Phase fault on BENTON 4 (532986) 138 kV Bus a. Apply fault at the BENTON 4 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTN1 1 (532821) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT9-3PH | 3 Phase fault on NEOSHO 4 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 1 1 (532824) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT86-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICH11 1 (532829) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT85-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICH12 1 (532830) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT144-3PH | 3 Phase fault on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA1X1 (532832) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT122-3PH | 3 Phase fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5ELMCRK (300993) 161.0 kV to CATSAGR5 (512638) 161.0 kV Transmission Circuit b.2. 5ELMCRK (300993) 161.0 kV to COLINS 5 (512627) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT77-3PH | 3 Phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT130-3PH | 3 Phase fault on KERR GR3 (512634) 115 kV Bus a. Apply fault at the KERR GR3 (512634) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L GROVE3 (510423) 115.0 kV to KERR GR3 (512634) 115.0 kV Transmission Circuit b.2. LSTAR--3 (510399) 115.0 kV to PRY-JCT3 (510407) 115.0 kV Transmission Circuit b.3. LSTAR--3 (510399) 115.0 kV to L GROVE3 (510423) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT134-3PH | 3 Phase fault on BA.N-ST4 (509786) 138 kV Bus a. Apply fault at the BA.N-ST4 (509786) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA.N-ST4 (509786) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit b.2. LLAN WT4 (509770) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit b.3. DAWSONT4 (509803) 138.0 kV to N21ST--4 (509866) 138.0 kV Transmission Circuit b.4. LLAN WT4 (509770) 138.0 kV to DAWSONT4 (509803) 138.0 kV Transmission Circuit b.5. DAWSON-4 (509792) 138.0 kV to DAWSONT4 (509803) 138.0 kV Transmission Circuit b.6. BA.N-ST4 (509786) 138.0 kV to ONETA--4 (509806) 138.0 kV Transmission Circuit b.7. CATOOSA4 (509790) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT136-3PH | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 (509790) 138.0 kV to OWAS88_4 (509887) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT135-3PH | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYO--N4 (509779) 138.0 kV to E41ST_W4 (509886) 138.0 kV Transmission Circuit b.2. MINGO-N4 (509760) 138.0 kV to 21STTAP4 (509828) 138.0 kV Transmission Circuit b.3. LLAN ET4 (509771) 138.0 kV to E41ST_W4 (509886) 138.0 kV Transmission Circuit b.4. LLAN ET4 (509771) 138.0 kV to CATOOSA4 (509790) 138.0 kV Transmission Circuit b.5. MINGO-N4 (509760) 138.0 kV to MAYO--N4 (509779) 138.0 kV Transmission Circuit b.6. T.S.E.-4 (509811) 138.0 kV to 21STTAP4 (509828) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT125-3PH | 3 Phase fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 (510402) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit b.2. BIRDHOL4 (510398) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.3. BIRDHOL4 (510398) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT138-3PH | 3 Phase fault on PCATSAT4 (509841) 138 kV Bus a. Apply fault at the PCATSAT4 (509841) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCATSAT4 (509841) 138.0 kV to OWASO2_4 (509843) 138.0 kV Transmission Circuit b.2. CATOOSA4 (509790) 138.0 kV to PCATSAT4 (509841) 138.0 kV Transmission Circuit b.3. OWASO2_4 (509843) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT139-3PH | 3 Phase fault on TERNITP4 (509835) 138 kV Bus a. Apply fault at the TERNITP4 (509835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERNITP4 (509835) 138.0 kV to VERDIGS4 (509854) 138.0 kV Transmission Circuit b.2. CLARTOK4 (509864) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit b.3. VERDIGS4 (509854) 138.0 kV to CLARTOK4 (509864) 138.0 kV Transmission Circuit b.4. CATOOSA4 (509790) 138.0 kV to TERNITP4 (509835) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT126-3PH | 3 Phase fault on PRY-JCT4 (510419) 138 kV Bus a. Apply fault at the PRY-JCT4 (510419) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCARBDE4 (510366) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.2. MCARBDE4 (510366) 138.0 kV to PRY_CRK4 (510431) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT43-3PH | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 (510907) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT45-3PH | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 (510907) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT163-3PH | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT47-3PH | 3 Phase fault on REDBUD 7 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT162-3PH | 3 Phase fault on BROOKLINE 7 (549984) 345 kV Bus a. Apply fault at the BROOKLINE 7 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT19-3PH | 3 Phase fault on DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT46-3PH | 3 Phase fault on VALIANT7 (510911) 345 kV Bus a. Apply fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 (510907) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT58-3PH | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT131-3PH | 3 Phase fault on PRY-JCT2 (510400) 69 kV Bus a. Apply fault at the PRY-JCT2 (510400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ADAIR--2 (510387) 69.0 kV to VINITA-2 (510404) 69.0 kV Transmission Circuit b.2. ADAIR--2 (510387) 69.0 kV to PRY-JCT2 (510400) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT128-3PH | 3 Phase fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE1-1 (510368) 13.8 kV to GROVE 4 (510402) 138.0 kV to GROVE 5 (510411) 161.0 kV ThreeWinding | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT127-3PH | 3 Phase fault on PRY-JCT2 (510400) 69 kV Bus a. Apply fault at the PRY-JCT2 (510400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRYJT2-1 (510369) 13.8 kV to PRY-JCT2 (510400) 69.0 kV to PRY-JCT4 (510419) 138.0 kV ThreeWinding | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT61-3PH | 3 Phase fault on 8ANO% (337909) 500 kV Bus a. Apply fault at the 8ANO% (337909) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% (337909) 500.0 kV to 5ANO% (337912) 161.0 kV to 1ANO AUX (337913) 22.0 kV ThreeWinding | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT62-3PH | 3 Phase fault on FTSMITH8 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT51-3PH | 3 Phase fault on CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAMSPR7 (506945) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT52-3PH | 3 Phase fault on CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT57-3PH | 3 Phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 (515045) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT60-3PH | 3 Phase fault on FTSMITH7 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV ThreeWinding | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT90-3PH | 3 Phase fault on SUMMIT 7 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to G16-112-TAP (587894) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT1-3PH | 3 Phase fault on MARMTNE5 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT2-3PH | 3 Phase fault on FRANKLIN5 (532938) 161 kV Bus a. Apply fault at the FRANKLIN5 (532938) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT53-SB | Single Phase Fault with Stuck Breaker on C-RIVER7 (515422) 345 kV Bus a. Apply Fault at the C-RIVER7 (515422) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C-RIVER4 (510946) 138.0 kV to C-RIVER1 (510947) 13.8 kV to C-RIVER7 (515422) 345.0 kV ThreeWinding b.2. PITTSB-7 (510907) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT50-SB | Single Phase Fault with Stuck Breaker on FTSMITH7 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT51-SB | Single Phase Fault with Stuck Breaker on FTSMITH7 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT30-SB | Single Phase Fault with Stuck Breaker on FTSMITH8 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH31 (515727) 13.8 kV ThreeWinding b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT31-SB | Single Phase Fault with Stuck Breaker on FTSMITH8 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH31 (515727) 13.8 kV ThreeWinding b.2. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT29-SB | Single Phase Fault with Stuck Breaker on FTSMITH8 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV ThreeWinding b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT33-SB | Single Phase Fault with Stuck Breaker on HUNTERS7 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit b.2. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT34-SB | Single Phase Fault with Stuck Breaker on HUNTERS7 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit b.2. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT35-SB | Single Phase Fault with Stuck Breaker on HUNTERS7 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit b.2. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT52-SB | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit b.2. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV TwoWinding | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT27-SB | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT40-SB | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT22-SB | Single Phase Fault with Stuck Breaker on PECANCK7 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit b.2. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC11 (515749) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT21-SB | Single Phase Fault with Stuck Breaker on PECANCK7 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT20-SB | Single Phase Fault with Stuck Breaker on PECANCK7 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC11 (515749) 13.8 kV ThreeWinding b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT24-SB | Single Phase Fault with Stuck Breaker on PECANCK7 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit b.2. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC21 (515759) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT23-SB | Single Phase Fault with Stuck Breaker on PECANCK7 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC21 (515759) 13.8 kV ThreeWinding b.2. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT98-SB | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT96-SB | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT95-SB | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit b.2. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT97-SB | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT38-SB | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT39-SB | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT36-SB | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT37-SB | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT99-SB | Single Phase Fault with Stuck Breaker on WOODRNG7 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT101-SB | Single Phase Fault with Stuck Breaker on WOODRNG4 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV ThreeWinding b.2. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT14-SB | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT15-SB | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1_21 (512821) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT17-SB | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1_21 (512821) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT1-SB | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1_21 (512821) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT18-SB | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV TwoWinding b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT43-SB | Single Phase Fault with Stuck Breaker on RENO 7 (532771) 345 kV Bus a. Apply Fault at the RENO 7 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to RENO 2X1 (532810) 14.4 kV to RENO 3 (533416) 115.0 kV ThreeWinding b.2. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT47-SB | Single Phase Fault with Stuck Breaker on CHAMSPR7 (506945) 345 kV Bus a. Apply Fault at the CHAMSPR7 (506945) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHAMSPR7 (506945) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit b.2. CHAMSPR1 (506919) 13.8 kV to CHAMSPR5 (506944) 161.0 kV to CHAMSPR7 (506945) 345.0 kV ThreeWinding | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT2-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit b.2. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT9-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT7-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to RSS T2 4 (509875) 138.0 kV to RSST2 T1 (509876) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT8-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV ThreeWinding b.2. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT5-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to RSS T2 4 (509875) 138.0 kV to RSST2 T1 (509876) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT6-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV ThreeWinding b.2. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT3-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT4-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to RSS T2 4 (509875) 138.0 kV to RSST2 T1 (509876) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT76-SB | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit b.2. T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV to T.NO.2-4 (509895) 138.0 kV ThreeWinding | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT77-SB | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV to T.NO.2-4 (509895) 138.0 kV ThreeWinding b.2. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT78-SB | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit b.2. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT79-SB | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT91-SB | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT92-SB | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV ThreeWinding b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT93-SB | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT94-SB | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV ThreeWinding | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT10-SB | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT11-SB | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA2-1 (509868) 34.5 kV ThreeWinding b.2. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA1-1 (509881) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT12-SB | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit b.2. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT13-SB | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA5-1 (509874) 34.5 kV ThreeWinding b.2. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT32-3PH | 3 Phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT80-3PH | 3 Phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT117-3PH | 3 Phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT70-3PH | 3 Phase fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit b.2. 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT72-3PH | 3 Phase fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT73-3PH | 3 Phase fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT120-3PH | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to 412SUB 5 (512637) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT119-3PH | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT78-3PH | 3 Phase fault on OKAYGR 5 (512640) 161 kV Bus a. Apply fault at the OKAYGR 5 (512640) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT66-3PH | 3 Phase fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT114-3PH | 3 Phase fault on PENSA 5 (512654) 161 kV Bus a. Apply fault at the PENSA 5 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENSA 5 (512654) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT67-3PH | 3 Phase fault on WMAIN ST5 (512742) 161 kV Bus a. Apply fault at the WMAIN ST5 (512742) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WMAIN ST5 (512742) 161.0 kV to NWMAID5 (512757) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT65-3PH | 3 Phase fault on GERALDGAY5 (512760) 161 kV Bus a. Apply fault at the GERALDGAY5 (512760) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWMAID5 (512757) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT129-3PH | 3 Phase fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 (510402) 138.0 kV to COWSKIN 4 (512719) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT31-3PH | 3 Phase fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT69-3PH | 3 Phase fault on 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT74-3PH | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT140-3PH | 3 Phase fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT124-3PH | 3 Phase fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT50-3PH | 3 Phase fault on CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT108-3PH | 3 Phase fault on S.S.---4 (509815) 138 kV Bus a. Apply fault at the S.S.---4 (509815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRATTV-4 (509758) 138.0 kV to BLUEBEL4 (515242) 138.0 kV Transmission Circuit b.2. PRATTV-4 (509758) 138.0 kV to S.S.---4 (509815) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT54-3PH | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT152-3PH | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT49-3PH | 3 Phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT105-3PH | 3 Phase fault on TRYON 4 (515675) 138 kV Bus a. Apply fault at the TRYON 4 (515675) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNIPE 4 (515514) 138.0 kV to SPGVLLY4 (515574) 138.0 kV Transmission Circuit b.2. KNIPE 4 (515514) 138.0 kV to TRYON 4 (515675) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT106-3PH | 3 Phase fault on CUSHING4 (515033) 138 kV Bus a. Apply fault at the CUSHING4 (515033) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSHING4 (515033) 138.0 kV to PAYNESB4 (515039) 138.0 kV Transmission Circuit b.2. PAYNESB4 (515039) 138.0 kV to SPGVLLY4 (515574) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT104-3PH | 3 Phase fault on GRNWOOD2 (515416) 69 kV Bus a. Apply fault at the GRNWOOD2 (515416) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKGROV2 (515021) 69.0 kV to GRNWOOD2 (515416) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT111-3PH | 3 Phase fault on BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 (515035) 138.0 kV to KEYWEST4 (515048) 138.0 kV Transmission Circuit b.2. KEYWEST4 (515048) 138.0 kV to BELLCOW4 (515369) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT110-3PH | 3 Phase fault on BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK4 (515233) 138.0 kV to BEGGS 4 (515249) 138.0 kV Transmission Circuit b.2. BRISTOW4 (515035) 138.0 kV to BEGGS 4 (515249) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT107-3PH | 3 Phase fault on WARWICK4 (515047) 138 kV Bus a. Apply fault at the WARWICK4 (515047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARWICK4 (515047) 138.0 kV to TRYON 4 (515675) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT109-3PH | 3 Phase fault on BLUEBEL4 (515242) 138 kV Bus a. Apply fault at the BLUEBEL4 (515242) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIBBENS4 (515237) 138.0 kV to BEELINE4 (515247) 138.0 kV Transmission Circuit b.2. POLECTP4 (515218) 138.0 kV to TIBBENS4 (515237) 138.0 kV Transmission Circuit b.3. POLECTP4 (515218) 138.0 kV to HICKORY4 (515244) 138.0 kV Transmission Circuit b.4. BLUEBEL4 (515242) 138.0 kV to BOWDEN 4 (515243) 138.0 kV Transmission Circuit b.5. POLECTP4 (515218) 138.0 kV to POLECAT4 (515219) 138.0 kV Transmission Circuit b.6. BOWDEN 4 (515243) 138.0 kV to HICKORY4 (515244) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT56-3PH | 3 Phase fault on FTSMITH7 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT55-3PH | 3 Phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT48-3PH | 3 Phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT25-3PH | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT165-3PH | 3 Phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT154-3PH | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT102-3PH | 3 Phase fault on BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 (515035) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT101-3PH | 3 Phase fault on CUSHING4 (515033) 138 kV Bus a. Apply fault at the CUSHING4 (515033) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSHING4 (515033) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT100-3PH | 3 Phase fault on LNWOODT4 (515453) 138 kV Bus a. Apply fault at the LNWOODT4 (515453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNWOODT4 (515453) 138.0 kV to TRYON 4 (515675) 138.0 kV Transmission Circuit b.2. LINWOOD4 (515401) 138.0 kV to LNWOODT4 (515453) 138.0 kV Transmission Circuit b.3. GRTPLNS4 (515043) 138.0 kV to LNWOODT4 (515453) 138.0 kV Transmission Circuit b.4. GRTPLNS4 (515043) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT150-3PH | 3 Phase fault on HUNTERS7 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT143-3PH | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT151-3PH | 3 Phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV ThreeWinding | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT103-3PH | 3 Phase fault on CUSHING2 (515032) 69 kV Bus a. Apply fault at the CUSHING2 (515032) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSHING2 (515032) 69.0 kV to CUSHING4 (515033) 138.0 kV to CUSHING1 (515718) 13.2 kV ThreeWinding | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT63-3PH | 3 Phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 (515044) 138.0 kV to SEMINOL7 (515045) 345.0 kV to SEMINO11 (515756) 14.4 kV ThreeWinding | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT53-3PH | 3 Phase fault on PECANCK5 (515234) 161 kV Bus a. Apply fault at the PECANCK5 (515234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC21 (515759) 13.8 kV ThreeWinding | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT59-3PH | 3 Phase fault on FTSMTHW5 (515301) 161 kV Bus a. Apply fault at the FTSMTHW5 (515301) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV ThreeWinding | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT99-3PH | 3 Phase fault on GRNWOOD2 (515416) 69 kV Bus a. Apply fault at the GRNWOOD2 (515416) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWOOD2 (515416) 69.0 kV to GRNWOOD4 (515417) 138.0 kV to GRNWOD11 (515418) 13.8 kV ThreeWinding | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT44-3PH | 3 Phase fault on C-RIVER4 (510946) 138 kV Bus a. Apply fault at the C-RIVER4 (510946) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C-RIVER4 (510946) 138.0 kV to C-RIVER1 (510947) 13.8 kV to C-RIVER7 (515422) 345.0 kV ThreeWinding | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT149-3PH | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV ThreeWinding | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT10-3PH | 3 Phase fault on MARMTNW5 (532935) 161 kV Bus a. Apply fault at the MARMTNW5 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT91-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | No | 588637: MACHINE TRIPPED DUE TO OVER FREQUENCY PROTECTION | DISABLE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT82-3PH | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT167-3PH | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT11-3PH | 3 Phase fault on MARMTNE5 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | No | 584584: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT24-3PH | 3 Phase fault on FRANKLIN2 (533876) 69 kV Bus a. Apply fault at the FRANKLIN2 (533876) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN1 (533122) 12.5 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT23-3PH | 3 Phase fault on MARMATN2 (533639) 69 kV Bus a. Apply fault at the MARMATN2 (533639) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMATN1 (532955) 13.2 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT36-3PH | 3 Phase fault on ALTOO W2 (533674) 69 kV Bus a. Apply fault at the ALTOO W2 (533674) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO1 1 (533086) 13.2 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT37-3PH | 3 Phase fault on ALTOO E2 (533673) 69 kV Bus a. Apply fault at the ALTOO E2 (533673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO3 1 (533087) 13.2 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT19-SB | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT16-SB | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT28-SB | Single Phase Fault with Stuck Breaker on FTSMITH8 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV ThreeWinding b.2. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT79-3PH | 3 Phase fault on CLARMR 5 (512651) 161 kV Bus a. Apply fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT68-3PH | 3 Phase fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT75-3PH | 3 Phase fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT123-3PH | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT64-3PH | 3 Phase fault on GRDA1 5 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT132-3PH | 3 Phase fault on PRY-JCT2 (510400) 69 kV Bus a. Apply fault at the PRY-JCT2 (510400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY-JCT2 (510400) 69.0 kV to PRYORC12 (512810) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT76-3PH | 3 Phase fault on GRDA1 5 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA1 2 (512727) 69.0 kV to GRDA1_11 (512816) 13.8 kV ThreeWinding | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT71-3PH | 3 Phase fault on MAID 2 (512626) 69 kV Bus a. Apply fault at the MAID 2 (512626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER1 1 (512836) 13.2 kV ThreeWinding | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT118-3PH | 3 Phase fault on MAID 2 (512626) 69 kV Bus a. Apply fault at the MAID 2 (512626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER2 1 (512837) 13.2 kV ThreeWinding | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT115-3PH | 3 Phase fault on PENSA 2 (512628) 69 kV Bus a. Apply fault at the PENSA 2 (512628) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENSA 2 (512628) 69.0 kV to PENSA 5 (512654) 161.0 kV to PENSA 1 (512841) 13.8 kV ThreeWinding | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT116-3PH | 3 Phase fault on 5SPORTSMAN (300741) 161 kV Bus a. Apply fault at the 5SPORTSMAN (300741) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT41-SB | Single Phase Fault with Stuck Breaker on EMPEC 7 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT42-SB | Single Phase Fault with Stuck Breaker on RENO 7 (532771) 345 kV Bus a. Apply Fault at the RENO 7 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT44-SB | Single Phase Fault with Stuck Breaker on BENTON 7 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT94-3PH | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT35-3PH | 3 Phase fault on MONTGOM4 (533004) 138 kV Bus a. Apply fault at the MONTGOM4 (533004) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit b.2. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT96-3PH | 3 Phase fault on COWSKIN4 (533038) 138 kV Bus a. Apply fault at the COWSKIN4 (533038) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit b.2. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT95-3PH | 3 Phase fault on LAKERDG4 (533053) 138 kV Bus a. Apply fault at the LAKERDG4 (533053) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKERDG4 (533053) 138.0 kV Trip Bus b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit b.3. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT98-3PH | 3 Phase fault on SG12COL4 (533065) 138 kV Bus a. Apply fault at the SG12COL4 (533065) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit b.2. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit b.3. SG12COL4 (533065) 138.0 kV Trip Bus b.4. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit b.5. WWUPLNT4 (533016) 138.0 kV Trip Bus b.6. BENTLEY4 (533015) 138.0 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT25-SB | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEMINOL7 (515045) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT41-3PH | 3 Phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT87-SB | Single Phase Fault with Stuck Breaker on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to SOONER2G (514806) 20.0 kV TwoWinding b.2. SOONER 7 (514803) 345.0 kV to G16-100-TAP (587804) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT48-SB | Single Phase Fault with Stuck Breaker on RENO 7 (532771) 345 kV Bus a. Apply Fault at the RENO 7 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to RENO 1X1 (532807) 14.4 kV to RENO 3 (533416) 115.0 kV ThreeWinding b.2. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT113-3PH | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G16-100-TAP (587804) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT28-3PH | 3 Phase fault on G17-022-TAP (588664) 138 kV Bus a. Apply fault at the G17-022-TAP (588664) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit b.2. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT26-SB | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT45-SB | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT46-SB | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH12 1 (532830) 13.8 kV ThreeWinding b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT77-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on CLARMR 5 (512651) 161 kV Bus a. Apply fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT66-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT65-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT64-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit 3 Phase Fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT72-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on GRDA1 5 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA1 2 (512727) 69.0 kV to GRDA1_11 (512816) 13.8 kV ThreeWinding | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT57-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 2 (512626) 69 kV Bus a. Apply fault at the MAID 2 (512626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER1 1 (512836) 13.2 kV ThreeWinding | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT56-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on MAID 2 (512626) 69 kV Bus a. Apply fault at the MAID 2 (512626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER1 1 (512836) 13.2 kV ThreeWinding | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT55-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 2 (512626) 69 kV Bus a. Apply fault at the MAID 2 (512626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER1 1 (512836) 13.2 kV ThreeWinding | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT27-3PH | 3 Phase fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT31-PO | Prior Outage: MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT23-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT24-PO | Prior Outage: 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT22-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT25-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT38-PO | Prior Outage: CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 (515045) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT39-PO | Prior Outage: MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 (515045) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT37-PO | Prior Outage: SEMINOL7 (515045) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit 3 Phase Fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 (515422) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT41-PO | Prior Outage: MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT125-PO | Prior Outage: CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit 3 Phase Fault on RICE 6 (530686) 230 kV Bus a. Apply fault at the RICE 6 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT184-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit 3 Phase Fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT89-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit 3 Phase Fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT183-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT180-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit 3 Phase Fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT19-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT6-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT7-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT20-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT10-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT21-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT85-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT84-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT86-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit 3 Phase Fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT179-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT181-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT182-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT187-PO | Prior Outage: VIOLA 7 (532798) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | No | 587463: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION 587466: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT82-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT80-PO | Prior Outage: RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT185-PO | Prior Outage: RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | No | 533141: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT118-PO | Prior Outage: HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT119-PO | Prior Outage: RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV ThreeWinding 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT81-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT83-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT186-PO | Prior Outage: VIOLA 7 (532798) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT126-PO | Prior Outage: RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit 3 Phase Fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT128-PO | Prior Outage: SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit 3 Phase Fault on EMCPHER6 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT127-PO | Prior Outage: SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit 3 Phase Fault on SMOKYHL6 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT3-PO | Prior Outage: LITCH 5 (532932) 161.0 kV to FRANKLIN5 (532938) 161.0 kV Transmission Circuit 3 Phase Fault on MARMTNE5 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT2-PO | Prior Outage: FRANKLIN1 (533122) 12.5 kV to Trip Bus 3 Phase Fault on MARMTNE5 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT4-PO | Prior Outage: MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit 3 Phase Fault on FRANKLIN5 (532938) 161 kV Bus a. Apply fault at the FRANKLIN5 (532938) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT5-PO | Prior Outage: MARMTNE5 (532934) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit 3 Phase Fault on FRANKLIN5 (532938) 161 kV Bus a. Apply fault at the FRANKLIN5 (532938) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT30-PO | Prior Outage: MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT29-PO | Prior Outage: ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT28-PO | Prior Outage: MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT27-PO | Prior Outage: ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT26-PO | Prior Outage: BUTLER 4 (532987) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit 3 Phase Fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT14-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT11-PO | Prior Outage: 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT12-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT13-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT1-PO | Prior Outage: N345 1 1 (532824) 13.8 kV to Trip Bus 3 Phase Fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 2 1 (532825) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT18-PO | Prior Outage: ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 4 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 1 1 (532824) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT15-PO | Prior Outage: 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 4 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 1 1 (532824) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT16-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 4 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 1 1 (532824) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT17-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 4 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N345 1 1 (532824) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT79-PO | Prior Outage: WICH11 1 (532829) 13.8 kV to Trip Bus 3 Phase Fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICH12 1 (532830) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | No | 533141: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT117-PO | Prior Outage: SCJ1X1 (999532) 13.8 kV to Trip Bus 3 Phase Fault on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA1X1 (532832) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT74-PO | Prior Outage: CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit 3 Phase Fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT75-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT73-PO | Prior Outage: OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit 3 Phase Fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT109-PO | Prior Outage: L GROVE3 (510423) 115.0 kV to KERR GR3 (512634) 115.0 kV Transmission Circuit LSTAR--3 (510399) 115.0 kV to PRY-JCT3 (510407) 115.0 kV Transmission Circuit LSTAR--3 (510399) 115.0 kV to L GROVE3 (510423) 115.0 kV Transmission Circuit 3 Phase Fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 (510402) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit b.2. BIRDHOL4 (510398) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.3. BIRDHOL4 (510398) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT107-PO | Prior Outage: MCARBDE4 (510366) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit MCARBDE4 (510366) 138.0 kV to PRY_CRK4 (510431) 138.0 kV Transmission Circuit 3 Phase Fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 (510402) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit b.2. BIRDHOL4 (510398) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.3. BIRDHOL4 (510398) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT106-PO | Prior Outage: PRYJT2-1 (510369) 13.8 kV to PRY-JCT2 (510400) 69.0 kV to PRY-JCT4 (510419) 138.0 kV ThreeWinding 3 Phase Fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 (510402) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit b.2. BIRDHOL4 (510398) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.3. BIRDHOL4 (510398) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT110-PO | Prior Outage: INOLATP4 (509752) 138.0 kV to CATOOSA4 (509790) 138.0 kV Transmission Circuit 3 Phase Fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 (510402) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit b.2. BIRDHOL4 (510398) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.3. BIRDHOL4 (510398) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT111-PO | Prior Outage: EXCLART4 (510401) 138.0 kV to G17-077-TAP (589154) 138.0 kV Transmission Circuit 3 Phase Fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 (510402) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit b.2. BIRDHOL4 (510398) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.3. BIRDHOL4 (510398) 138.0 kV to JAY 4 (510421) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT112-PO | Prior Outage: BA.N-ST4 (509786) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit LLAN WT4 (509770) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit DAWSONT4 (509803) 138.0 kV to N21ST--4 (509866) 138.0 kV Transmission Circuit LLAN WT4 (509770) 138.0 kV to DAWSONT4 (509803) 138.0 kV Transmission Circuit DAWSON-4 (509792) 138.0 kV to DAWSONT4 (509803) 138.0 kV Transmission Circuit BA.N-ST4 (509786) 138.0 kV to ONETA--4 (509806) 138.0 kV Transmission Circuit CATOOSA4 (509790) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit 3 Phase Fault on PRY-JCT4 (510419) 138 kV Bus a. Apply fault at the PRY-JCT4 (510419) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCARBDE4 (510366) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.2. MCARBDE4 (510366) 138.0 kV to PRY_CRK4 (510431) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT108-PO | Prior Outage: PRYJT2-1 (510369) 13.8 kV to PRY-JCT2 (510400) 69.0 kV to PRY-JCT4 (510419) 138.0 kV ThreeWinding 3 Phase Fault on PRY-JCT4 (510419) 138 kV Bus a. Apply fault at the PRY-JCT4 (510419) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCARBDE4 (510366) 138.0 kV to PRY-JCT4 (510419) 138.0 kV Transmission Circuit b.2. MCARBDE4 (510366) 138.0 kV to PRY_CRK4 (510431) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT32-PO | Prior Outage: PITTSB-7 (510907) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT130-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit 3 Phase Fault on REDBUD 7 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT131-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit 3 Phase Fault on REDBUD 7 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT132-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit 3 Phase Fault on REDBUD 7 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT178-PO | Prior Outage: WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit 3 Phase Fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT172-PO | Prior Outage: T.NO.--7 (509852) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit 3 Phase Fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT175-PO | Prior Outage: T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit 3 Phase Fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT176-PO | Prior Outage: T.NO.--7 (509852) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit 3 Phase Fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT54-SB | Single Phase Fault with Stuck Breaker on C-RIVER7 (515422) 345 kV Bus a. Apply Fault at the C-RIVER7 (515422) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C-RIVER4 (510946) 138.0 kV to C-RIVER1 (510947) 13.8 kV to C-RIVER7 (515422) 345.0 kV ThreeWinding b.2. FIREWHL-TAP (588839) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT32-SB | Single Phase Fault with Stuck Breaker on C-RIVER7 (515422) 345 kV Bus a. Apply Fault at the C-RIVER7 (515422) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PITTSB-7 (510907) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit b.2. FIREWHL-TAP (588839) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT49-SB | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit b.2. MUSKOG4G (515223) 18.0 kV to MUSKOGE7 (515224) 345.0 kV TwoWinding | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT86-SB | Single Phase Fault with Stuck Breaker on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-061-TAP (560084) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit b.2. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT85-SB | Single Phase Fault with Stuck Breaker on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 4 (514802) 138.0 kV to SOONER 7 (514803) 345.0 kV to SOONER 1 (515760) 13.8 kV ThreeWinding b.2. CLEVLND7 (512694) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT100-SB | Single Phase Fault with Stuck Breaker on WOODRNG7 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit b.2. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT102-SB | Single Phase Fault with Stuck Breaker on WOODRNG7 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit b.2. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT173-PO | Prior Outage: T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit 3 Phase Fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT171-PO | Prior Outage: WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit 3 Phase Fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT174-PO | Prior Outage: T.NO.--7 (509852) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit 3 Phase Fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT164-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit 3 Phase Fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT54-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit b.2. 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT53-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit b.2. 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT51-PO | Prior Outage: DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit b.2. 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT52-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit b.2. 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT60-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT104-PO | Prior Outage: PENSA 2 (512628) 69.0 kV to PENSA 5 (512654) 161.0 kV to PENSA 1 (512841) 13.8 kV ThreeWinding 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT59-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT103-PO | Prior Outage: KERR GR5 (512635) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT58-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT102-PO | Prior Outage: PENSA 5 (512654) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT97-PO | Prior Outage: KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT99-PO | Prior Outage: MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER2 1 (512837) 13.2 kV ThreeWinding 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT100-PO | Prior Outage: 5ELMCRK (300993) 161.0 kV to CATSAGR5 (512638) 161.0 kV Transmission Circuit 5ELMCRK (300993) 161.0 kV to COLINS 5 (512627) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT101-PO | Prior Outage: 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT96-PO | Prior Outage: 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT98-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit 3 Phase Fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT76-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on OKAYGR 5 (512640) 161 kV Bus a. Apply fault at the OKAYGR 5 (512640) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT70-PO | Prior Outage: CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT71-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT67-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to GRDA1 2 (512727) 69.0 kV to GRDA1_11 (512816) 13.8 kV ThreeWinding 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT68-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT69-PO | Prior Outage: OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit 3 Phase Fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT165-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit 3 Phase Fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT166-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit 3 Phase Fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT50-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT49-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT46-PO | Prior Outage: 5LOCSTGV (300274) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit 5LOCSTGV (300274) 161.0 kV to 5CDRCRST (301344) 161.0 kV Transmission Circuit 3 Phase Fault on 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT47-PO | Prior Outage: DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit 3 Phase Fault on 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT48-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit 3 Phase Fault on 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT63-PO | Prior Outage: GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit 3 Phase Fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT62-PO | Prior Outage: GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV ThreeWinding 3 Phase Fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT61-PO | Prior Outage: MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit 3 Phase Fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT36-PO | Prior Outage: CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit 3 Phase Fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 (515422) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT129-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit 3 Phase Fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT133-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit 3 Phase Fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT40-PO | Prior Outage: CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT160-PO | Prior Outage: PECANCK7 (515235) 345.0 kV to R.S.S.-7 (509782) 345.0 kV Transmission Circuit 3 Phase Fault on PECANCK7 (515235) 345 kV Bus a. Apply fault at the PECANCK7 (515235) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECANCK7 (515235) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT35-PO | Prior Outage: MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit 3 Phase Fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 (515422) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT44-PO | Prior Outage: SEMINOL7 (515045) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit 3 Phase Fault on FTSMITH7 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT43-PO | Prior Outage: CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit 3 Phase Fault on FTSMITH7 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT42-PO | Prior Outage: MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit 3 Phase Fault on FTSMITH7 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT34-PO | Prior Outage: MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit 3 Phase Fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 (515422) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT169-PO | Prior Outage: RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT140-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT167-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit 3 Phase Fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT170-PO | Prior Outage: RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit 3 Phase Fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT168-PO | Prior Outage: RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit 3 Phase Fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT144-PO | Prior Outage: WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit 3 Phase Fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT146-PO | Prior Outage: WOODRNG7 (514715) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit 3 Phase Fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT93-PO | Prior Outage: BRISTOW4 (515035) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit 3 Phase Fault on GRNWOOD2 (515416) 69 kV Bus a. Apply fault at the GRNWOOD2 (515416) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWOOD2 (515416) 69.0 kV to GRNWOOD4 (515417) 138.0 kV to GRNWOD11 (515418) 13.8 kV ThreeWinding | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT95-PO | Prior Outage: CUSHING4 (515033) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit 3 Phase Fault on BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 (515035) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT94-PO | Prior Outage: CUSHING4 (515033) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit 3 Phase Fault on GRNWOOD2 (515416) 69 kV Bus a. Apply fault at the GRNWOOD2 (515416) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWOOD2 (515416) 69.0 kV to GRNWOOD4 (515417) 138.0 kV to GRNWOD11 (515418) 13.8 kV ThreeWinding | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT91-PO | Prior Outage: BRISTOW4 (515035) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit 3 Phase Fault on LNWOODT4 (515453) 138 kV Bus a. Apply fault at the LNWOODT4 (515453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNWOODT4 (515453) 138.0 kV to TRYON 4 (515675) 138.0 kV Transmission Circuit b.2. LINWOOD4 (515401) 138.0 kV to LNWOODT4 (515453) 138.0 kV Transmission Circuit b.3. GRTPLNS4 (515043) 138.0 kV to LNWOODT4 (515453) 138.0 kV Transmission Circuit b.4. GRTPLNS4 (515043) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT92-PO | Prior Outage: CUSHING4 (515033) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit 3 Phase Fault on LNWOODT4 (515453) 138 kV Bus a. Apply fault at the LNWOODT4 (515453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNWOODT4 (515453) 138.0 kV to TRYON 4 (515675) 138.0 kV Transmission Circuit b.2. LINWOOD4 (515401) 138.0 kV to LNWOODT4 (515453) 138.0 kV Transmission Circuit b.3. GRTPLNS4 (515043) 138.0 kV to LNWOODT4 (515453) 138.0 kV Transmission Circuit b.4. GRTPLNS4 (515043) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT90-PO | Prior Outage: GRNWOOD2 (515416) 69.0 kV to GRNWOOD4 (515417) 138.0 kV to GRNWOD11 (515418) 13.8 kV ThreeWinding 3 Phase Fault on LNWOODT4 (515453) 138 kV Bus a. Apply fault at the LNWOODT4 (515453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNWOODT4 (515453) 138.0 kV to TRYON 4 (515675) 138.0 kV Transmission Circuit b.2. LINWOOD4 (515401) 138.0 kV to LNWOODT4 (515453) 138.0 kV Transmission Circuit b.3. GRTPLNS4 (515043) 138.0 kV to LNWOODT4 (515453) 138.0 kV Transmission Circuit b.4. GRTPLNS4 (515043) 138.0 kV to GRNWOOD4 (515417) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT121-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT123-PO | Prior Outage: RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | No | 515882: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION 515833: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION 515900: MACHINE TRIPPED DUE TO OVER FREQUENCY PROTECTION 599089: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT116-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT124-PO | Prior Outage: WICH12 1 (532830) 13.8 kV to Trip Bus 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | No | 515900: MACHINE TRIPPED DUE TO OVER FREQUENCY PROTECTION | DISABLE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT122-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | No | 515882: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION 515883: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION 515900: MACHINE TRIPPED DUE TO OVER FREQUENCY PROTECTION 587463: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION 587466: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION 588193: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION 599089: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION 599090: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT120-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit 3 Phase Fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | No | 515900: MACHINE TRIPPED DUE TO OVER FREQUENCY PROTECTION 587483: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION 587486: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION 599089: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION 599090: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT147-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT150-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT137-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to THUNDER7 (515894) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT139-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to THUNDER7 (515894) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT33-PO | Prior Outage: C-RIVER4 (510946) 138.0 kV to C-RIVER1 (510947) 13.8 kV to C-RIVER7 (515422) 345.0 kV ThreeWinding 3 Phase Fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT148-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT87-PO | Prior Outage: BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT78-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT88-PO | Prior Outage: WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | No | 533141: MACHINE TRIPPED DUE TO OVER VOLTAGE PROTECTION | DISABLE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT135-PO | Prior Outage: BROOKLINE 7 (549984) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit 3 Phase Fault on 7MORGAN (300045) 345 kV Bus a. Apply fault at the 7MORGAN (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to 7HUBEN (300042) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT29-3PH | 3 Phase fault on 7MORGAN (300045) 345 kV Bus a. Apply fault at the 7MORGAN (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT163-PO | Prior Outage: 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit 3 Phase Fault on 7MORGAN (300045) 345 kV Bus a. Apply fault at the 7MORGAN (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT162-PO | Prior Outage: BROOKLINE 7 (549984) 345.0 kV to FLINTCR7 (506935) 345.0 kV Transmission Circuit 3 Phase Fault on 7MORGAN (300045) 345 kV Bus a. Apply fault at the 7MORGAN (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT15-3PH | 3 Phase fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT105-PO | Prior Outage: 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit 3 Phase Fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT6-3PH | 3 Phase fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT30-3PH | 3 Phase fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV TwoWinding | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT45-PO | Prior Outage: 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV TwoWinding 3 Phase Fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV TwoWinding | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT136-PO | Prior Outage: 7MORGAN (300045) 345.0 kV to 7HUBEN (300042) 345.0 kV Transmission Circuit 3 Phase Fault on 7JASPER (300949) 345 kV Bus a. Apply fault at the 7JASPER (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7JASPER (300949) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT134-PO | Prior Outage: BROOKLINE 7 (549984) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit 3 Phase Fault on 7JASPER (300949) 345 kV Bus a. Apply fault at the 7JASPER (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7JASPER (300949) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT133-3PH | 3 Phase fault on INOLATP4 (509752) 138 kV Bus a. Apply fault at the INOLATP4 (509752) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INOLATP4 (509752) 138.0 kV to CATOOSA4 (509790) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT137-3PH | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 (509790) 138.0 kV to 141PINE4 (509892) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT81-3PH | 3 Phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT141-3PH | 3 Phase fault on EXCLART4 (510401) 138 kV Bus a. Apply fault at the EXCLART4 (510401) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXCLART4 (510401) 138.0 kV to G17-077-TAP (589154) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT142-3PH | 3 Phase fault on G17-077-TAP (589154) 138 kV Bus a. Apply fault at the G17-077-TAP (589154) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY_CRK4 (510431) 138.0 kV to G17-077-TAP (589154) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT113-PO | Prior Outage: BA.N-ST4 (509786) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit LLAN WT4 (509770) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit DAWSONT4 (509803) 138.0 kV to N21ST--4 (509866) 138.0 kV Transmission Circuit LLAN WT4 (509770) 138.0 kV to DAWSONT4 (509803) 138.0 kV Transmission Circuit DAWSON-4 (509792) 138.0 kV to DAWSONT4 (509803) 138.0 kV Transmission Circuit BA.N-ST4 (509786) 138.0 kV to ONETA--4 (509806) 138.0 kV Transmission Circuit CATOOSA4 (509790) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit 3 Phase Fault on G17-077-TAP (589154) 138 kV Bus a. Apply fault at the G17-077-TAP (589154) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY_CRK4 (510431) 138.0 kV to G17-077-TAP (589154) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT114-PO | Prior Outage: CATOOSA4 (509790) 138.0 kV to OWAS88_4 (509887) 138.0 kV Transmission Circuit 3 Phase Fault on G17-077-TAP (589154) 138 kV Bus a. Apply fault at the G17-077-TAP (589154) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY_CRK4 (510431) 138.0 kV to G17-077-TAP (589154) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT115-PO | Prior Outage: PCATSAT4 (509841) 138.0 kV to OWASO2_4 (509843) 138.0 kV Transmission Circuit CATOOSA4 (509790) 138.0 kV to PCATSAT4 (509841) 138.0 kV Transmission Circuit OWASO2_4 (509843) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit 3 Phase Fault on G17-077-TAP (589154) 138 kV Bus a. Apply fault at the G17-077-TAP (589154) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY_CRK4 (510431) 138.0 kV to G17-077-TAP (589154) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT153-3PH | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT145-PO | Prior Outage: WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit 3 Phase Fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT138-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT112-3PH | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT142-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to THUNDER7 (515894) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT143-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to G16-100-TAP (587804) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G16-061-TAP (560084) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT141-PO | Prior Outage: SOONER 7 (514803) 345.0 kV to THUNDER7 (515894) 345.0 kV Transmission Circuit 3 Phase Fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G16-100-TAP (587804) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT42-3PH | 3 Phase fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 (515422) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT87-3PH | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT12-3PH | 3 Phase fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT153-PO | Prior Outage: 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT8-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT9-PO | Prior Outage: DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT26-3PH | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT88-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT159-3PH | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT147-3PH | 3 Phase fault on VIOLA 4 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to CONWAY (539009) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT152-PO | Prior Outage: DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | No | 588637: MACHINE TRIPPED DUE TO OVER FREQUENCY PROTECTION | DISABLE PROTECTION
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT151-PO | Prior Outage: BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT149-PO | Prior Outage: THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit 3 Phase Fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT18-3PH | 3 Phase fault on W.GRDNR7 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT7-3PH | 3 Phase fault on STILWEL7 (542968) 345 kV Bus a. Apply fault at the STILWEL7 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT161-PO | Prior Outage: BROOKLINE 7 (549984) 345.0 kV to FLINTCR7 (506935) 345.0 kV Transmission Circuit 3 Phase Fault on BROOKLINE 7 (549984) 345 kV Bus a. Apply fault at the BROOKLINE 7 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROOKLINE 7 (549984) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT55-SB | Single Phase Fault with Stuck Breaker on 7SPORTSMAN (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT56-SB | Single Phase Fault with Stuck Breaker on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT57-SB | Single Phase Fault with Stuck Breaker on BUFFALO7 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT58-SB | Single Phase Fault with Stuck Breaker on NEOSHO 7 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT59-SB | Single Phase Fault with Stuck Breaker on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT105-SB | Single Phase Fault with Stuck Breaker on CIRCLE 6 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV Trip Bus | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT104-SB | Single Phase Fault with Stuck Breaker on SUMMIT 6 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV Trip Bus | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT60-SB | Single Phase Fault with Stuck Breaker on MARMTNE5 (532934) 161 kV Bus a. Apply Fault at the MARMTNE5 (532934) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNE5 (532934) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT61-SB | Single Phase Fault with Stuck Breaker on MARMTNW5 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 (532935) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNW5 (532935) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT62-SB | Single Phase Fault with Stuck Breaker on FRANKLIN5 (532938) 161 kV Bus a. Apply Fault at the FRANKLIN5 (532938) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRANKLIN5 (532938) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT63-SB | Single Phase Fault with Stuck Breaker on ALTOONA4 (533001) 138 kV Bus a. Apply Fault at the ALTOONA4 (533001) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTOONA4 (533001) 138.0 kV Trip Bus | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT64-SB | Single Phase Fault with Stuck Breaker on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 4 (533021) 138.0 kV Trip Bus | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT65-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT66-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT103-SB | Single Phase Fault with Stuck Breaker on BROOKLINE 7 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROOKLINE 7 (549984) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT168-3PH | 3 Phase fault on 7MORGAN (300045) 345 kV Bus a. Apply fault at the 7MORGAN (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT164-3PH | 3 Phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT174-3PH | 3 Phase fault on MILANTP4 (539675) 138 kV Bus a. Apply fault at the MILANTP4 (539675) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILANTP4 (539675) 138.0 kV Trip Bus b.2. VIOLA 4 (533075) 138.0 kV to CONWAY (539009) 138.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT173-3PH | 3 Phase fault on BUTLER 4 (532987) 138 kV Bus a. Apply fault at the BUTLER 4 (532987) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV Trip Bus b.2. BUTLER 4 (532987) 138.0 kV to BUTLERN2 (533583) 69.0 kV TwoWinding | P1 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT109-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT110-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT111-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT112-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT113-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT114-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. After 6.6 additional cycles, trip the WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV ThreeWinding and remove fault | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT188-PO | Prior Outage: WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | No | Yes | No | Yes |  | REDUCE WAVERLY TO 0.0 MW
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT189-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | No | Yes | No | Yes |  | REDUCE WAVERLY TO 0.0 MW
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT190-PO | Prior Outage: WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | No | Yes | No | Yes |  | REDUCE WAVERLY TO 0.0 MW
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT191-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | No | Yes | No | Yes |  | REDUCE WAVERLY TO 0.0 MW
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT194-PO | Prior Outage: WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | No | Yes | No | Yes |  | REDUCE WAVERLY TO 0.0 MW
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT195-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | No | Yes | No | Yes |  | REDUCE WAVERLY TO 0.0 MW
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT196-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT197-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT198-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT199-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT200-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT201-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT202-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT203-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT204-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT205-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT206-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT207-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit | P6 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT115-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip the WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit b.2. After 6.6 additional cycles, remove fault | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT116-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip the WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit b.2. After 6.6 additional cycles, remove fault | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT117-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip the WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. After 6.6 additional cycles, remove fault | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Transfer | G8_FLT118-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip the WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV ThreeWinding b.2. After 6.6 additional cycles, remove fault | P4 | Stable | Yes | Yes | No | Yes | Yes | Yes
Central | 08 - North Oklahoma/South Central Kansas | 28S | Sensitivity | G8_FLT115-3PH | 3 Phase fault on PENSA 2 (512628) 69 kV Bus a. Apply fault at the PENSA 2 (512628) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENSA 2 (512628) 69.0 kV to PENSA 5 (512654) 161.0 kV to PENSA 1 (512841) 13.8 kV ThreeWinding | P1 | Unstable | Yes | Yes | Yes | Yes | No | Yes |  | MITIGATION NOT REQUIRED - Informational only.
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-01 | 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-02 | 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-03 | 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-04 | 3-ph fault on Hoskins 345kV to 230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-05 | 3-ph fault on Hoskins 345kV to 115/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-06 | 3-ph fault on RAUN to J748POI 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-07 | 3-ph fault on RAUN to SIOUXCY 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-08 | 3-ph fault on RAUN to S3451 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-09 | 3-ph fault on RAUN to IDA CO W 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-10 | 3-ph fault on RAUN 345kV to 161/13.8kV TF AC, near RAUN 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-11 | 3-ph fault on RAUN 345kV to 161kV TF BC, near RAUN 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-12 | 3-ph fault on Antelope to Holt 345kV crt 1, near Antelope. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-13 | 3-ph fault on Antelope 345kV to 115/13.8kV TF crt 1, near Antelope 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-14 | 3-ph fault on SHELCRK to COLMB.E3 345kV crt 1, near SHELCRK. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-15 | 3-ph fault on SHELCRK 345kV to 230/13.8kV TF crt 1, near SHELCRK 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-16 | 3-ph fault on Holt to GRPRAR1-LNX3 345kV crt 1, near Holt. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-17 | 3-ph fault on Holt to GR ISLD-LNX3 345kV crt 1, near Holt. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-18 | 3-ph fault on Holt to GR THEDFRD3 345kV crt 1, near Holt. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-19 | 3-ph fault on COLMB.E3 to GR NW68HOLDRG3 345kV crt 1, near COLMB.E3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-20 | 3-ph fault on J748POI to CHEROKEE 345kV crt 1, near J748POI. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-21 | 3-ph fault on SIOUXCY-LNX3 to SPLT RK3 345kV crt 1, near SIOUXCY-LNX3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-22 | 3-ph fault on S3451 to S3459 345kV crt 1, near S3451. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-23 | 3-ph fault on S3451 to S3454 345kV crt 1, near S3451. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-SLG-24 | SLG fault on Hoskins 345kV to SHELCRK 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins 345/230/13.8kV TF T2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-SLG-25 | SLG fault on Hoskins to RAUN 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins 345/115/13.8kV TF T4. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-SLG-26 | SLG fault on Hoskins to RAUN 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins 345/230/13.8kV TF T2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-SLG-27 | SLG fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins to Antelope 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-SLG-28 | SLG fault on Hoskins to RAUN 345kV crt 1, near Hoskins 345kV for 16 cycles. Clear fault by tripping the Faulted crt and RAUN to S3451 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-SLG-29 | SLG fault on Hoskins to SHELCRK , near Hoskins 345kV for 16 cycles. Clear fault by tripping the Faulted crt, SHELCRK to COLMB.E3 345kV crt 1 and SHELCRK 345/230/13.8kV TF T1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-SLG-30 | SLG fault on Hoskins to Antelope 345kV crt 1, near Hoskins 345kV for 16 cycles. Clear fault by tripping Antelope 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-SLG-31 | SLG fault on RAUN 345/161/13.8kV TF AC, near RAUN 345kV for 16 cycles. Clear fault by tripping the Faulted crt, RAUN 345/24kV TF crt 1 and #4 NEAL generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-SLG-32 | SLG fault on RAUN 345/161kV TF BC, near RAUN 345kV for 16 cycles. Clear fault by tripping the Faulted crt, RAUN 345/22kV TF crt 1 and #3 NEAL generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-SLG-33 | SLG fault on RAUN to J748POI 345kV crt 1, near RAUN 345kV for 16 cycles. Clear fault by tripping J748POI 345kV bus and J748GEN generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-SLG-34 | SLG fault on RAUN to S3451 345kV crt 1, near RAUN for 16 cycles. Clear fault by tripping the Faulted crt and S3451 345/161/13.8kV TF T4. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-SLG-35 | SLG fault on SHELCRK to COLMB.E3 345kV crt 1, near SHELCRK 345kV for 16 cycles. Clear fault by tripping COLMB.E3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-36 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | No | No | No | No | No | No | The power swing caused oscillation between G16-159, G15-007, G16-021 and G16-043. Voltage collapse observed from power flow analysis. | Curtail G16-159, G15-007, G16-021 and G16-043 to 75% of their maximum capacity when prior outage exists.
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-37 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-38 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-39 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins 345/115/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-40 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | No | No | No | No | No | No | The power swing caused oscillation between G16-159, G15-007, G16-021 and G16-043. Voltage collapse observed from power flow analysis. | Curtail G16-159, G15-007, G16-021 and G16-043 to 75% of their maximum capacity when prior outage exists.
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-41 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-42 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-43 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-44 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-45 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-46 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-47 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins 345/115/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-48 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-49 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-50 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-51 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins 345kV to 115/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-52 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-53 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-54 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 19W | Sensitivity | G16-159-3ph-55 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-01 | 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-02 | 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-03 | 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-04 | 3-ph fault on Hoskins 345kV to 230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-05 | 3-ph fault on Hoskins 345kV to 115/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-06 | 3-ph fault on RAUN to J748POI 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-07 | 3-ph fault on RAUN to SIOUXCY 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-08 | 3-ph fault on RAUN to S3451 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-09 | 3-ph fault on RAUN to IDA CO W 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-10 | 3-ph fault on RAUN 345kV to 161/13.8kV TF AC, near RAUN 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-11 | 3-ph fault on RAUN 345kV to 161kV TF BC, near RAUN 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-12 | 3-ph fault on Antelope to Holt 345kV crt 1, near Antelope. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-13 | 3-ph fault on Antelope 345kV to 115/13.8kV TF crt 1, near Antelope 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-14 | 3-ph fault on SHELCRK to COLMB.E3 345kV crt 1, near SHELCRK. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-15 | 3-ph fault on SHELCRK 345kV to 230/13.8kV TF crt 1, near SHELCRK 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-16 | 3-ph fault on Holt to GRPRAR1-LNX3 345kV crt 1, near Holt. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-17 | 3-ph fault on Holt to GR ISLD-LNX3 345kV crt 1, near Holt. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-18 | 3-ph fault on Holt to GR THEDFRD3 345kV crt 1, near Holt. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-19 | 3-ph fault on COLMB.E3 to GR NW68HOLDRG3 345kV crt 1, near COLMB.E3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-20 | 3-ph fault on J748POI to CHEROKEE 345kV crt 1, near J748POI. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-21 | 3-ph fault on SIOUXCY-LNX3 to SPLT RK3 345kV crt 1, near SIOUXCY-LNX3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-22 | 3-ph fault on S3451 to S3459 345kV crt 1, near S3451. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-23 | 3-ph fault on S3451 to S3454 345kV crt 1, near S3451. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-SLG-24 | SLG fault on Hoskins 345kV to SHELCRK 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins 345/230/13.8kV TF T2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-SLG-25 | SLG fault on Hoskins to RAUN 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins 345/115/13.8kV TF T4. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-SLG-26 | SLG fault on Hoskins to RAUN 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins 345/230/13.8kV TF T2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-SLG-27 | SLG fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins to Antelope 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-SLG-28 | SLG fault on Hoskins to RAUN 345kV crt 1, near Hoskins 345kV for 16 cycles. Clear fault by tripping the Faulted crt and RAUN to S3451 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-SLG-29 | SLG fault on Hoskins to SHELCRK , near Hoskins 345kV for 16 cycles. Clear fault by tripping the Faulted crt, SHELCRK to COLMB.E3 345kV crt 1 and SHELCRK 345/230/13.8kV TF T1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-SLG-30 | SLG fault on Hoskins to Antelope 345kV crt 1, near Hoskins 345kV for 16 cycles. Clear fault by tripping Antelope 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-SLG-31 | SLG fault on RAUN 345/161/13.8kV TF AC, near RAUN 345kV for 16 cycles. Clear fault by tripping the Faulted crt, RAUN 345/24kV TF crt 1 and #4 NEAL generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-SLG-32 | SLG fault on RAUN 345/161kV TF BC, near RAUN 345kV for 16 cycles. Clear fault by tripping the Faulted crt, RAUN 345/22kV TF crt 1 and #3 NEAL generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-SLG-33 | SLG fault on RAUN to J748POI 345kV crt 1, near RAUN 345kV for 16 cycles. Clear fault by tripping J748POI 345kV bus and J748GEN generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-SLG-34 | SLG fault on RAUN to S3451 345kV crt 1, near RAUN for 16 cycles. Clear fault by tripping the Faulted crt and S3451 345/161/13.8kV TF T4. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-SLG-35 | SLG fault on SHELCRK to COLMB.E3 345kV crt 1, near SHELCRK 345kV for 16 cycles. Clear fault by tripping COLMB.E3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-36 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | No | No | No | No | No | No | The power swing caused oscillation between G16-159, G15-007, G16-021 and G16-043. Voltage collapse observed from power flow analysis. | Curtail G16-159, G15-007, G16-021 and G16-043 to 75% of their maximum capacity when prior outage exists.
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-37 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-38 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-39 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins 345/115/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-40 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | No | No | No | No | No | No | The power swing caused oscillation between G16-159, G15-007, G16-021 and G16-043. Voltage collapse observed from power flow analysis. | Curtail G16-159, G15-007, G16-021 and G16-043 to 75% of their maximum capacity when prior outage exists.
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-41 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-42 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-43 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-44 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-45 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-46 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-47 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins 345/115/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-48 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-49 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-50 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-51 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins 345kV to 115/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-52 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-53 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-54 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-55 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-01 | 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-02 | 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-03 | 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-04 | 3-ph fault on Hoskins 345kV to 230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-05 | 3-ph fault on Hoskins 345kV to 115/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-06 | 3-ph fault on RAUN to J748POI 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-07 | 3-ph fault on RAUN to SIOUXCY 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-08 | 3-ph fault on RAUN to S3451 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-09 | 3-ph fault on RAUN to IDA CO W 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-10 | 3-ph fault on RAUN 345kV to 161/13.8kV TF AC, near RAUN 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-11 | 3-ph fault on RAUN 345kV to 161kV TF BC, near RAUN 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-12 | 3-ph fault on Antelope to Holt 345kV crt 1, near Antelope. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-13 | 3-ph fault on Antelope 345kV to 115/13.8kV TF crt 1, near Antelope 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-14 | 3-ph fault on SHELCRK to COLMB.E3 345kV crt 1, near SHELCRK. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-15 | 3-ph fault on SHELCRK 345kV to 230/13.8kV TF crt 1, near SHELCRK 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-16 | 3-ph fault on Holt to GRPRAR1-LNX3 345kV crt 1, near Holt. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-17 | 3-ph fault on Holt to GR ISLD-LNX3 345kV crt 1, near Holt. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-18 | 3-ph fault on Holt to GR THEDFRD3 345kV crt 1, near Holt. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-19 | 3-ph fault on COLMB.E3 to GR NW68HOLDRG3 345kV crt 1, near COLMB.E3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-20 | 3-ph fault on J748POI to CHEROKEE 345kV crt 1, near J748POI. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-21 | 3-ph fault on SIOUXCY-LNX3 to SPLT RK3 345kV crt 1, near SIOUXCY-LNX3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-22 | 3-ph fault on S3451 to S3459 345kV crt 1, near S3451. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-23 | 3-ph fault on S3451 to S3454 345kV crt 1, near S3451. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-SLG-24 | SLG fault on Hoskins 345kV to SHELCRK 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins 345/230/13.8kV TF T2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-SLG-25 | SLG fault on Hoskins to RAUN 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins 345/115/13.8kV TF T4. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-SLG-26 | SLG fault on Hoskins to RAUN 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins 345/230/13.8kV TF T2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-SLG-27 | SLG fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins to Antelope 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-SLG-28 | SLG fault on Hoskins to RAUN 345kV crt 1, near Hoskins 345kV for 16 cycles. Clear fault by tripping the Faulted crt and RAUN to S3451 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-SLG-29 | SLG fault on Hoskins to SHELCRK , near Hoskins 345kV for 16 cycles. Clear fault by tripping the Faulted crt, SHELCRK to COLMB.E3 345kV crt 1 and SHELCRK 345/230/13.8kV TF T1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-SLG-30 | SLG fault on Hoskins to Antelope 345kV crt 1, near Hoskins 345kV for 16 cycles. Clear fault by tripping Antelope 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-SLG-31 | SLG fault on RAUN 345/161/13.8kV TF AC, near RAUN 345kV for 16 cycles. Clear fault by tripping the Faulted crt, RAUN 345/24kV TF crt 1 and #4 NEAL generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-SLG-32 | SLG fault on RAUN 345/161kV TF BC, near RAUN 345kV for 16 cycles. Clear fault by tripping the Faulted crt, RAUN 345/22kV TF crt 1 and #3 NEAL generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-SLG-33 | SLG fault on RAUN to J748POI 345kV crt 1, near RAUN 345kV for 16 cycles. Clear fault by tripping J748POI 345kV bus and J748GEN generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-SLG-34 | SLG fault on RAUN to S3451 345kV crt 1, near RAUN for 16 cycles. Clear fault by tripping the Faulted crt and S3451 345/161/13.8kV TF T4. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-SLG-35 | SLG fault on SHELCRK to COLMB.E3 345kV crt 1, near SHELCRK 345kV for 16 cycles. Clear fault by tripping COLMB.E3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-36 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | No | No | No | No | No | No | The power swing caused oscillation between G16-159, G15-007, G16-021 and G16-043. Voltage collapse observed from power flow analysis. | Curtail G16-159, G15-007, G16-021 and G16-043 to 75% of their maximum capacity when prior outage exists.
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-37 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-38 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-39 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins 345/115/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21S | Sensitivity | G16-159-3ph-40 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | No | No | No | No | No | No | The power swing caused oscillation between G16-159, G15-007, G16-021 and G16-043. Voltage collapse observed from power flow analysis. | Curtail G16-159, G15-007, G16-021 and G16-043 to 75% of their maximum capacity when prior outage exists.
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-41 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-42 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-43 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-44 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-45 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-46 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-47 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins 345/115/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-48 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-49 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-50 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-51 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins 345kV to 115/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-52 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-53 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-54 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 21L-AD0 | Sensitivity | G16-159-3ph-55 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-01 | 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-02 | 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-03 | 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-04 | 3-ph fault on Hoskins 345kV to 230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-05 | 3-ph fault on Hoskins 345kV to 115/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-06 | 3-ph fault on RAUN to J748POI 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-07 | 3-ph fault on RAUN to SIOUXCY 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-08 | 3-ph fault on RAUN to S3451 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-09 | 3-ph fault on RAUN to IDA CO W 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-10 | 3-ph fault on RAUN 345kV to 161/13.8kV TF AC, near RAUN 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-11 | 3-ph fault on RAUN 345kV to 161kV TF BC, near RAUN 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-12 | 3-ph fault on Antelope to Holt 345kV crt 1, near Antelope. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-13 | 3-ph fault on Antelope 345kV to 115/13.8kV TF crt 1, near Antelope 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-14 | 3-ph fault on SHELCRK to COLMB.E3 345kV crt 1, near SHELCRK. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-15 | 3-ph fault on SHELCRK 345kV to 230/13.8kV TF crt 1, near SHELCRK 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-16 | 3-ph fault on Holt to GRPRAR1-LNX3 345kV crt 1, near Holt. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-17 | 3-ph fault on Holt to GR ISLD-LNX3 345kV crt 1, near Holt. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-18 | 3-ph fault on Holt to GR THEDFRD3 345kV crt 1, near Holt. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-19 | 3-ph fault on COLMB.E3 to GR NW68HOLDRG3 345kV crt 1, near COLMB.E3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-20 | 3-ph fault on J748POI to CHEROKEE 345kV crt 1, near J748POI. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-21 | 3-ph fault on SIOUXCY-LNX3 to SPLT RK3 345kV crt 1, near SIOUXCY-LNX3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-22 | 3-ph fault on S3451 to S3459 345kV crt 1, near S3451. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-23 | 3-ph fault on S3451 to S3454 345kV crt 1, near S3451. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-SLG-24 | SLG fault on Hoskins 345kV to SHELCRK 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins 345/230/13.8kV TF T2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-SLG-25 | SLG fault on Hoskins to RAUN 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins 345/115/13.8kV TF T4. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-SLG-26 | SLG fault on Hoskins to RAUN 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins 345/230/13.8kV TF T2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-SLG-27 | SLG fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins to Antelope 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-SLG-28 | SLG fault on Hoskins to RAUN 345kV crt 1, near Hoskins 345kV for 16 cycles. Clear fault by tripping the Faulted crt and RAUN to S3451 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-SLG-29 | SLG fault on Hoskins to SHELCRK , near Hoskins 345kV for 16 cycles. Clear fault by tripping the Faulted crt, SHELCRK to COLMB.E3 345kV crt 1 and SHELCRK 345/230/13.8kV TF T1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-SLG-30 | SLG fault on Hoskins to Antelope 345kV crt 1, near Hoskins 345kV for 16 cycles. Clear fault by tripping Antelope 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-SLG-31 | SLG fault on RAUN 345/161/13.8kV TF AC, near RAUN 345kV for 16 cycles. Clear fault by tripping the Faulted crt, RAUN 345/24kV TF crt 1 and #4 NEAL generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-SLG-32 | SLG fault on RAUN 345/161kV TF BC, near RAUN 345kV for 16 cycles. Clear fault by tripping the Faulted crt, RAUN 345/22kV TF crt 1 and #3 NEAL generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-SLG-33 | SLG fault on RAUN to J748POI 345kV crt 1, near RAUN 345kV for 16 cycles. Clear fault by tripping J748POI 345kV bus and J748GEN generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-SLG-34 | SLG fault on RAUN to S3451 345kV crt 1, near RAUN for 16 cycles. Clear fault by tripping the Faulted crt and S3451 345/161/13.8kV TF T4. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-SLG-35 | SLG fault on SHELCRK to COLMB.E3 345kV crt 1, near SHELCRK 345kV for 16 cycles. Clear fault by tripping COLMB.E3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-36 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | No | No | No | No | No | No | The power swing caused oscillation between G16-159, G15-007, G16-021 and G16-043. Voltage collapse observed from power flow analysis. | Curtail G16-159, G15-007, G16-021 and G16-043 to 75% of their maximum capacity when prior outage exists.
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-37 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-38 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-39 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins 345/115/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-40 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | No | No | No | No | No | No | The power swing caused oscillation between G16-159, G15-007, G16-021 and G16-043. Voltage collapse observed from power flow analysis. | Curtail G16-159, G15-007, G16-021 and G16-043 to 75% of their maximum capacity when prior outage exists.
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-41 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-42 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-43 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-44 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-45 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-46 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-47 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins 345/115/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-48 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-49 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-50 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-51 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins 345kV to 115/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-52 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-53 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-54 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Sensitivity | G16-159-3ph-55 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes

## Sensitivity Dispatch
Gen Number | Bus | Close Proximity | Group | Season | MW Amount
GEN-2017-011 | 560071 | None | 01 WDWRD | None | None
GEN-2017-028 | 514821 | Bus: 515000 ID: 1 Name: Mclain | 01 WDWRD | 19W | 148.9
GEN-2017-028 | 514821 | Bus: 515000 ID: 1 Name: Mclain | 01 WDWRD | 21L | 148.9
GEN-2017-028 | 514821 | Bus: 515000 ID: 1 Name: Mclain | 01 WDWRD | 21S | 148.9
GEN-2017-028 | 514821 | Bus: 515000 ID: 1 Name: Mclain | 01 WDWRD | 28S | 148.9
GEN-2017-028 | 514821 | Bus: 514998 ID: 1 Name: Mclain | 01 WDWRD | 19W | 170.3
GEN-2017-028 | 514821 | Bus: 514998 ID: 1 Name: Mclain | 01 WDWRD | 21L | 170.3
GEN-2017-028 | 514821 | Bus: 514998 ID: 1 Name: Mclain | 01 WDWRD | 21S | 170.3
GEN-2017-028 | 514821 | Bus: 514998 ID: 1 Name: Mclain | 01 WDWRD | 28S | 170.3
GEN-2017-028 | 514821 | Bus: 514999 ID: 1 Name: Mclain | 01 WDWRD | 19W | 149.2
GEN-2017-028 | 514821 | Bus: 514999 ID: 1 Name: Mclain | 01 WDWRD | 21L | 149.2
GEN-2017-028 | 514821 | Bus: 514999 ID: 1 Name: Mclain | 01 WDWRD | 21S | 149.2
GEN-2017-028 | 514821 | Bus: 514999 ID: 1 Name: Mclain | 01 WDWRD | 28S | 149.2
GEN-2017-052 | 588914 | Bus: 531381 ID: 1 Name: Johnson 2 | 03 SPRVLLE | 19W | 0.52
GEN-2017-052 | 588914 | Bus: 531381 ID: 1 Name: Johnson 2 | 03 SPRVLLE | 21L | 0.52
GEN-2017-052 | 588914 | Bus: 531381 ID: 1 Name: Johnson 2 | 03 SPRVLLE | 21S | 0.52
GEN-2017-052 | 588914 | Bus: 531381 ID: 1 Name: Johnson 2 | 03 SPRVLLE | 28S | 0.52
GEN-2017-052 | 588914 | Bus: 531381 ID: 2 Name: Johnson 2 | 03 SPRVLLE | 19W | 0.84
GEN-2017-052 | 588914 | Bus: 531381 ID: 2 Name: Johnson 2 | 03 SPRVLLE | 21L | 0.84
GEN-2017-052 | 588914 | Bus: 531381 ID: 2 Name: Johnson 2 | 03 SPRVLLE | 21S | 0.84
GEN-2017-052 | 588914 | Bus: 531381 ID: 2 Name: Johnson 2 | 03 SPRVLLE | 28S | 0.84
GEN-2017-052 | 588914 | Bus: 531381 ID: 3 Name: Johnson 2 | 03 SPRVLLE | 19W | 1.01
GEN-2017-052 | 588914 | Bus: 531381 ID: 3 Name: Johnson 2 | 03 SPRVLLE | 21L | 1.01
GEN-2017-052 | 588914 | Bus: 531381 ID: 3 Name: Johnson 2 | 03 SPRVLLE | 21S | 1.01
GEN-2017-052 | 588914 | Bus: 531381 ID: 3 Name: Johnson 2 | 03 SPRVLLE | 28S | 1.01
GEN-2017-052 | 588914 | Bus: 531381 ID: 4 Name: Johnson 2 | 03 SPRVLLE | 19W | 0.22
GEN-2017-052 | 588914 | Bus: 531381 ID: 4 Name: Johnson 2 | 03 SPRVLLE | 21L | 0.22
GEN-2017-052 | 588914 | Bus: 531381 ID: 4 Name: Johnson 2 | 03 SPRVLLE | 21S | 0.22
GEN-2017-052 | 588914 | Bus: 531381 ID: 4 Name: Johnson 2 | 03 SPRVLLE | 28S | 0.22
GEN-2017-052 | 588914 | Bus: 531381 ID: 5 Name: Johnson 2 | 03 SPRVLLE | 19W | 0.24
GEN-2017-052 | 588914 | Bus: 531381 ID: 5 Name: Johnson 2 | 03 SPRVLLE | 21L | 0.24
GEN-2017-052 | 588914 | Bus: 531381 ID: 5 Name: Johnson 2 | 03 SPRVLLE | 21S | 0.24
GEN-2017-052 | 588914 | Bus: 531381 ID: 5 Name: Johnson 2 | 03 SPRVLLE | 28S | 0.24
GEN-2017-052 | 588914 | Bus: 531201 ID: 1 Name: GEN-2012-007 | 03 SPRVLLE | 19W | 60
GEN-2017-052 | 588914 | Bus: 531201 ID: 1 Name: GEN-2012-007 | 03 SPRVLLE | 21L | 60
GEN-2017-052 | 588914 | Bus: 531201 ID: 1 Name: GEN-2012-007 | 03 SPRVLLE | 21S | 60
GEN-2017-052 | 588914 | Bus: 531201 ID: 1 Name: GEN-2012-007 | 03 SPRVLLE | 28S | 60
GEN-2017-052 | 588914 | Bus: 531202 ID: 7 Name: GEN-2012-007 | 03 SPRVLLE | 19W | 60
GEN-2017-052 | 588914 | Bus: 531202 ID: 7 Name: GEN-2012-007 | 03 SPRVLLE | 21L | 60
GEN-2017-052 | 588914 | Bus: 531202 ID: 7 Name: GEN-2012-007 | 03 SPRVLLE | 21S | 60
GEN-2017-052 | 588914 | Bus: 531202 ID: 7 Name: GEN-2012-007 | 03 SPRVLLE | 28S | 60
GEN-2017-052 | 588914 | Bus: 531447 ID: 1 Name: Holcomb | 03 SPRVLLE | 19W | 384
GEN-2017-052 | 588914 | Bus: 531447 ID: 1 Name: Holcomb | 03 SPRVLLE | 21L | 384
GEN-2017-052 | 588914 | Bus: 531447 ID: 1 Name: Holcomb | 03 SPRVLLE | 21S | 384
GEN-2017-052 | 588914 | Bus: 531447 ID: 1 Name: Holcomb | 03 SPRVLLE | 28S | 384
GEN-2017-052 | 588914 | Bus: 579403 ID: 1 Name: Buffalo Dunes | 03 SPRVLLE | 19W | 249.75
GEN-2017-052 | 588914 | Bus: 579403 ID: 1 Name: Buffalo Dunes | 03 SPRVLLE | 21L | 249.75
GEN-2017-052 | 588914 | Bus: 579403 ID: 1 Name: Buffalo Dunes | 03 SPRVLLE | 21S | 249.75
GEN-2017-052 | 588914 | Bus: 579403 ID: 1 Name: Buffalo Dunes | 03 SPRVLLE | 28S | 249.75
GEN-2017-052 | 588914 | Bus: 531461 ID: 4 Name: S4 | 03 SPRVLLE | 19W | 57
GEN-2017-052 | 588914 | Bus: 531461 ID: 4 Name: S4 | 03 SPRVLLE | 21L | 57
GEN-2017-052 | 588914 | Bus: 531461 ID: 4 Name: S4 | 03 SPRVLLE | 21S | 57
GEN-2017-052 | 588914 | Bus: 531461 ID: 4 Name: S4 | 03 SPRVLLE | 28S | 57
GEN-2017-052 | 588914 | Bus: 531462 ID: 5 Name: S5 | 03 SPRVLLE | 19W | 55
GEN-2017-052 | 588914 | Bus: 531462 ID: 5 Name: S5 | 03 SPRVLLE | 21L | 55
GEN-2017-052 | 588914 | Bus: 531462 ID: 5 Name: S5 | 03 SPRVLLE | 21S | 55
GEN-2017-052 | 588914 | Bus: 531462 ID: 5 Name: S5 | 03 SPRVLLE | 28S | 55
GEN-2017-052 | 588914 | Bus: 531459 ID: 2 Name: S2 | 03 SPRVLLE | 19W | 97
GEN-2017-052 | 588914 | Bus: 531459 ID: 2 Name: S2 | 03 SPRVLLE | 21L | 97
GEN-2017-052 | 588914 | Bus: 531459 ID: 2 Name: S2 | 03 SPRVLLE | 21S | 97
GEN-2017-052 | 588914 | Bus: 531459 ID: 2 Name: S2 | 03 SPRVLLE | 28S | 97
GEN-2017-052 | 588914 | Bus: 531381 ID: 6 Name: Johnson 2 | 03 SPRVLLE | 19W | 1.08
GEN-2017-052 | 588914 | Bus: 531381 ID: 6 Name: Johnson 2 | 03 SPRVLLE | 21L | 1.08
GEN-2017-052 | 588914 | Bus: 531381 ID: 6 Name: Johnson 2 | 03 SPRVLLE | 21S | 1.08
GEN-2017-052 | 588914 | Bus: 531381 ID: 6 Name: Johnson 2 | 03 SPRVLLE | 28S | 1.08
GEN-2017-052 | 588914 | Bus: 531381 ID: 7 Name: Johnson 2 | 03 SPRVLLE | 19W | 1.29
GEN-2017-052 | 588914 | Bus: 531381 ID: 7 Name: Johnson 2 | 03 SPRVLLE | 21L | 1.29
GEN-2017-052 | 588914 | Bus: 531381 ID: 7 Name: Johnson 2 | 03 SPRVLLE | 21S | 1.29
GEN-2017-052 | 588914 | Bus: 531381 ID: 7 Name: Johnson 2 | 03 SPRVLLE | 28S | 1.29
GEN-2017-052 | 588914 | Bus: 531399 ID: 1 Name: Lakin 3 | 03 SPRVLLE | 19W | 1.01
GEN-2017-052 | 588914 | Bus: 531399 ID: 1 Name: Lakin 3 | 03 SPRVLLE | 21L | 1.01
GEN-2017-052 | 588914 | Bus: 531399 ID: 1 Name: Lakin 3 | 03 SPRVLLE | 21S | 1.01
GEN-2017-052 | 588914 | Bus: 531399 ID: 1 Name: Lakin 3 | 03 SPRVLLE | 28S | 1.01
GEN-2017-052 | 588914 | Bus: 531399 ID: 2 Name: Lakin 3 | 03 SPRVLLE | 19W | 0.98
GEN-2017-052 | 588914 | Bus: 531399 ID: 2 Name: Lakin 3 | 03 SPRVLLE | 21L | 0.98
GEN-2017-052 | 588914 | Bus: 531399 ID: 2 Name: Lakin 3 | 03 SPRVLLE | 21S | 0.98
GEN-2017-052 | 588914 | Bus: 531399 ID: 2 Name: Lakin 3 | 03 SPRVLLE | 28S | 0.98
GEN-2017-052 | 588914 | Bus: 531399 ID: 3 Name: Lakin 3 | 03 SPRVLLE | 19W | 1.08
GEN-2017-052 | 588914 | Bus: 531399 ID: 3 Name: Lakin 3 | 03 SPRVLLE | 21L | 1.08
GEN-2017-052 | 588914 | Bus: 531399 ID: 3 Name: Lakin 3 | 03 SPRVLLE | 21S | 1.08
GEN-2017-052 | 588914 | Bus: 531399 ID: 3 Name: Lakin 3 | 03 SPRVLLE | 28S | 1.08
GEN-2017-052 | 588914 | Bus: 531399 ID: 4 Name: Lakin 3 | 03 SPRVLLE | 19W | 1.18
GEN-2017-052 | 588914 | Bus: 531399 ID: 4 Name: Lakin 3 | 03 SPRVLLE | 21L | 1.18
GEN-2017-052 | 588914 | Bus: 531399 ID: 4 Name: Lakin 3 | 03 SPRVLLE | 21S | 1.18
GEN-2017-052 | 588914 | Bus: 531399 ID: 4 Name: Lakin 3 | 03 SPRVLLE | 28S | 1.18
GEN-2017-032 | 588754 | Bus: 599951 ID: 1 Name: Lamar | 03 SPRVLLE | 19W | 1000
GEN-2017-032 | 588754 | Bus: 599951 ID: 1 Name: Lamar | 03 SPRVLLE | 21L | 1000
GEN-2017-032 | 588754 | Bus: 599951 ID: 1 Name: Lamar | 03 SPRVLLE | 21S | 1000
GEN-2017-032 | 588754 | Bus: 599951 ID: 1 Name: Lamar | 03 SPRVLLE | 28S | 1000
GEN-2017-032 | 588754 | Bus: 531447 ID: 1 Name: Holcomb | 03 SPRVLLE | 19W | 384
GEN-2017-032 | 588754 | Bus: 531447 ID: 1 Name: Holcomb | 03 SPRVLLE | 21L | 384
GEN-2017-032 | 588754 | Bus: 531447 ID: 1 Name: Holcomb | 03 SPRVLLE | 21S | 384
GEN-2017-032 | 588754 | Bus: 531447 ID: 1 Name: Holcomb | 03 SPRVLLE | 28S | 384
GEN-2017-021 | 588654 | Bus: 531447 ID: 1 Name: Holcomb | 03 SPRVLLE | 19W | 384
GEN-2017-021 | 588654 | Bus: 531447 ID: 1 Name: Holcomb | 03 SPRVLLE | 21L | 384
GEN-2017-021 | 588654 | Bus: 531447 ID: 1 Name: Holcomb | 03 SPRVLLE | 21S | 384
GEN-2017-021 | 588654 | Bus: 531447 ID: 1 Name: Holcomb | 03 SPRVLLE | 28S | 384
GEN-2017-099 | 588654 | Bus: 531447 ID: 1 Name: Holcomb | 03 SPRVLLE | 19W | 384
GEN-2017-099 | 588654 | Bus: 531447 ID: 1 Name: Holcomb | 03 SPRVLLE | 21L | 384
GEN-2017-099 | 588654 | Bus: 531447 ID: 1 Name: Holcomb | 03 SPRVLLE | 21S | 384
GEN-2017-099 | 588654 | Bus: 531447 ID: 1 Name: Holcomb | 03 SPRVLLE | 28S | 384
GEN-2017-018 | 539801 | None | 03 SPRVLLE | None | None
GEN-2017-005 | 588504 | Bus: 589203 ID: 1 Name: GEN-2017-082 | 08 N-OK & S-KS | 19W (Sensitivity C) | 24
GEN-2017-005 | 588504 | Bus: 589203 ID: 1 Name: GEN-2017-082 | 08 N-OK & S-KS | 21L (Sensitivity C) | 24
GEN-2017-005 | 588504 | Bus: 589203 ID: 1 Name: GEN-2017-082 | 08 N-OK & S-KS | 21S (Sensitivity C) | 24
GEN-2017-005 | 588504 | Bus: 589203 ID: 1 Name: GEN-2017-082 | 08 N-OK & S-KS | 28S | 24
GEN-2017-005 | 588504 | Bus: 589204 ID: 1 Name: GEN-2017-082 | 08 N-OK & S-KS | 19W (Sensitivity C) | 125.4
GEN-2017-005 | 588504 | Bus: 589204 ID: 1 Name: GEN-2017-082 | 08 N-OK & S-KS | 21L (Sensitivity C) | 125.4
GEN-2017-005 | 588504 | Bus: 589204 ID: 1 Name: GEN-2017-082 | 08 N-OK & S-KS | 21S (Sensitivity C) | 125.4
GEN-2017-005 | 588504 | Bus: 589204 ID: 1 Name: GEN-2017-082 | 08 N-OK & S-KS | 28S | 125.4
GEN-2017-005 | 588504 | Bus: 542955 ID: 1 Name: Lacygne | 08 N-OK & S-KS | 19W (Sensitivity C) | 810.8
GEN-2017-005 | 588504 | Bus: 542955 ID: 1 Name: Lacygne | 08 N-OK & S-KS | 21L (Sensitivity C) | 810.8
GEN-2017-005 | 588504 | Bus: 542955 ID: 1 Name: Lacygne | 08 N-OK & S-KS | 21S (Sensitivity C) | 810.8
GEN-2017-005 | 588504 | Bus: 542955 ID: 1 Name: Lacygne | 08 N-OK & S-KS | 28S | 810.8
GEN-2017-005 | 588504 | Bus: 542956 ID: 2 Name: Lacygne | 08 N-OK & S-KS | 19W (Sensitivity C) | 717.8
GEN-2017-005 | 588504 | Bus: 542956 ID: 2 Name: Lacygne | 08 N-OK & S-KS | 21L (Sensitivity C) | 717.8
GEN-2017-005 | 588504 | Bus: 542956 ID: 2 Name: Lacygne | 08 N-OK & S-KS | 21S (Sensitivity C) | 717.8
GEN-2017-005 | 588504 | Bus: 542956 ID: 2 Name: Lacygne | 08 N-OK & S-KS | 28S | 717.8
GEN-2017-005 | 588504 | Bus: 533774 ID: 1 Name: ASGI-2012-008 | 08 N-OK & S-KS | 19W (Sensitivity C) | 1.6
GEN-2017-005 | 588504 | Bus: 533774 ID: 1 Name: ASGI-2012-008 | 08 N-OK & S-KS | 21L (Sensitivity C) | 1.6
GEN-2017-005 | 588504 | Bus: 533774 ID: 1 Name: ASGI-2012-008 | 08 N-OK & S-KS | 21S (Sensitivity C) | 1.6
GEN-2017-005 | 588504 | Bus: 533774 ID: 1 Name: ASGI-2012-008 | 08 N-OK & S-KS | 28S | 1.6
GEN-2017-005 | 588504 | Bus: 533774 ID: 2 Name: ASGI-2012-008 | 08 N-OK & S-KS | 19W (Sensitivity C) | 1.95
GEN-2017-005 | 588504 | Bus: 533774 ID: 2 Name: ASGI-2012-008 | 08 N-OK & S-KS | 21L (Sensitivity C) | 1.95
GEN-2017-005 | 588504 | Bus: 533774 ID: 2 Name: ASGI-2012-008 | 08 N-OK & S-KS | 21S (Sensitivity C) | 1.95
GEN-2017-005 | 588504 | Bus: 533774 ID: 2 Name: ASGI-2012-008 | 08 N-OK & S-KS | 28S | 1.95
GEN-2017-005 | 588504 | Bus: 547647 ID: 1 Name: GEN-2004-017 | 08 N-OK & S-KS | 19W (Sensitivity C) | 16
GEN-2017-005 | 588504 | Bus: 547647 ID: 1 Name: GEN-2004-017 | 08 N-OK & S-KS | 21L (Sensitivity C) | 16
GEN-2017-005 | 588504 | Bus: 547647 ID: 1 Name: GEN-2004-017 | 08 N-OK & S-KS | 21S (Sensitivity C) | 16
GEN-2017-005 | 588504 | Bus: 547647 ID: 1 Name: GEN-2004-017 | 08 N-OK & S-KS | 28S | 16
GEN-2017-005 | 588504 | Bus: 547647 ID: 2 Name: GEN-2004-017 | 08 N-OK & S-KS | 19W (Sensitivity C) | 17
GEN-2017-005 | 588504 | Bus: 547647 ID: 2 Name: GEN-2004-017 | 08 N-OK & S-KS | 21L (Sensitivity C) | 17
GEN-2017-005 | 588504 | Bus: 547647 ID: 2 Name: GEN-2004-017 | 08 N-OK & S-KS | 21S (Sensitivity C) | 17
GEN-2017-005 | 588504 | Bus: 547647 ID: 2 Name: GEN-2004-017 | 08 N-OK & S-KS | 28S | 17
GEN-2017-005 | 588504 | Bus: 547642 ID: 1 Name: GEN-2014-028 | 08 N-OK & S-KS | 19W (Sensitivity C) | 173.67
GEN-2017-005 | 588504 | Bus: 547642 ID: 1 Name: GEN-2014-028 | 08 N-OK & S-KS | 21L (Sensitivity C) | 173.67
GEN-2017-005 | 588504 | Bus: 547642 ID: 1 Name: GEN-2014-028 | 08 N-OK & S-KS | 21S (Sensitivity C) | 142
GEN-2017-005 | 588504 | Bus: 547642 ID: 1 Name: GEN-2014-028 | 08 N-OK & S-KS | 28S | 142
GEN-2017-005 | 588504 | Bus: 547643 ID: 1 Name: GEN-2014-028 | 08 N-OK & S-KS | 19W (Sensitivity C) | 136.33
GEN-2017-005 | 588504 | Bus: 547643 ID: 1 Name: GEN-2014-028 | 08 N-OK & S-KS | 21L (Sensitivity C) | 136.33
GEN-2017-005 | 588504 | Bus: 547643 ID: 1 Name: GEN-2014-028 | 08 N-OK & S-KS | 21S (Sensitivity C) | 114
GEN-2017-005 | 588504 | Bus: 547643 ID: 1 Name: GEN-2014-028 | 08 N-OK & S-KS | 28S | 114
GEN-2017-005 | 588504 | Bus: 543069 ID: 5 Name: ASGI-2016-003 | 08 N-OK & S-KS | 19W (Sensitivity C) | 3.1
GEN-2017-005 | 588504 | Bus: 543069 ID: 5 Name: ASGI-2016-003 | 08 N-OK & S-KS | 21L (Sensitivity C) | 3.1
GEN-2017-005 | 588504 | Bus: 543069 ID: 5 Name: ASGI-2016-003 | 08 N-OK & S-KS | 21S (Sensitivity C) | 3.1
GEN-2017-005 | 588504 | Bus: 543069 ID: 5 Name: ASGI-2016-003 | 08 N-OK & S-KS | 28S | 3.1
GEN-2017-005 | 588504 | Bus: 529201 ID: 1 Name: GEN-2012-041 | 08 N-OK & S-KS | 19W (Sensitivity C) | 121.488
GEN-2017-005 | 588504 | Bus: 529201 ID: 1 Name: GEN-2012-041 | 08 N-OK & S-KS | 21L (Sensitivity C) | 121.488
GEN-2017-005 | 588504 | Bus: 529201 ID: 1 Name: GEN-2012-041 | 08 N-OK & S-KS | 21S (Sensitivity C) | 85.3
GEN-2017-005 | 588504 | Bus: 529201 ID: 1 Name: GEN-2012-041 | 08 N-OK & S-KS | 28S | 85.3
GEN-2017-009 | 588544 | Bus: 542955 ID: 1 Name: Lacygne | 08 N-OK & S-KS | 19W (Sensitivity C) | 810.8
GEN-2017-009 | 588544 | Bus: 542955 ID: 1 Name: Lacygne | 08 N-OK & S-KS | 21L (Sensitivity C) | 810.8
GEN-2017-009 | 588544 | Bus: 542955 ID: 1 Name: Lacygne | 08 N-OK & S-KS | 21S (Sensitivity C) | 810.8
GEN-2017-009 | 588544 | Bus: 542955 ID: 1 Name: Lacygne | 08 N-OK & S-KS | 28S | 810.8
GEN-2017-009 | 588544 | Bus: 542956 ID: 2 Name: Lacygne | 08 N-OK & S-KS | 19W (Sensitivity C) | 717.8
GEN-2017-009 | 588544 | Bus: 542956 ID: 2 Name: Lacygne | 08 N-OK & S-KS | 21L (Sensitivity C) | 717.8
GEN-2017-009 | 588544 | Bus: 542956 ID: 2 Name: Lacygne | 08 N-OK & S-KS | 21S (Sensitivity C) | 717.8
GEN-2017-009 | 588544 | Bus: 542956 ID: 2 Name: Lacygne | 08 N-OK & S-KS | 28S | 717.8
GEN-2017-009 | 588544 | Bus: 532751 ID: 1 Name: Wolfcreek | 08 N-OK & S-KS | 19W (Sensitivity C) | 1286
GEN-2017-009 | 588544 | Bus: 532751 ID: 1 Name: Wolfcreek | 08 N-OK & S-KS | 21L (Sensitivity C) | 1261
GEN-2017-009 | 588544 | Bus: 532751 ID: 1 Name: Wolfcreek | 08 N-OK & S-KS | 21S (Sensitivity C) | 1261
GEN-2017-009 | 588544 | Bus: 532751 ID: 1 Name: Wolfcreek | 08 N-OK & S-KS | 28S | 1261
GEN-2017-009 | 588544 | Bus: 529201 ID: 1 Name: GEN-2012-041 | 08 N-OK & S-KS | 19W (Sensitivity C) | 121.488
GEN-2017-009 | 588544 | Bus: 529201 ID: 1 Name: GEN-2012-041 | 08 N-OK & S-KS | 21L (Sensitivity C) | 121.488
GEN-2017-009 | 588544 | Bus: 529201 ID: 1 Name: GEN-2012-041 | 08 N-OK & S-KS | 21S (Sensitivity C) | 85.3
GEN-2017-009 | 588544 | Bus: 529201 ID: 1 Name: GEN-2012-041 | 08 N-OK & S-KS | 28S | 85.3
GEN-2017-009 | 588544 | Bus: 511840 ID: 1 Name: Northeastern | 08 N-OK & S-KS | 19W (Sensitivity C) | 499.7
GEN-2017-009 | 588544 | Bus: 511840 ID: 1 Name: Northeastern | 08 N-OK & S-KS | 21L (Sensitivity C) | 499.7
GEN-2017-009 | 588544 | Bus: 511840 ID: 1 Name: Northeastern | 08 N-OK & S-KS | 21S (Sensitivity C) | 499.7
GEN-2017-009 | 588544 | Bus: 511840 ID: 1 Name: Northeastern | 08 N-OK & S-KS | 28S | 491.2
GEN-2017-009 | 588544 | Bus: 547647 ID: 1 Name: GEN-2004-017 | 08 N-OK & S-KS | 19W (Sensitivity C) | 16
GEN-2017-009 | 588544 | Bus: 547647 ID: 1 Name: GEN-2004-017 | 08 N-OK & S-KS | 21L (Sensitivity C) | 16
GEN-2017-009 | 588544 | Bus: 547647 ID: 1 Name: GEN-2004-017 | 08 N-OK & S-KS | 21S (Sensitivity C) | 16
GEN-2017-009 | 588544 | Bus: 547647 ID: 1 Name: GEN-2004-017 | 08 N-OK & S-KS | 28S | 16
GEN-2017-009 | 588544 | Bus: 547647 ID: 2 Name: GEN-2004-017 | 08 N-OK & S-KS | 19W (Sensitivity C) | 17
GEN-2017-009 | 588544 | Bus: 547647 ID: 2 Name: GEN-2004-017 | 08 N-OK & S-KS | 21L (Sensitivity C) | 17
GEN-2017-009 | 588544 | Bus: 547647 ID: 2 Name: GEN-2004-017 | 08 N-OK & S-KS | 21S (Sensitivity C) | 17
GEN-2017-009 | 588544 | Bus: 547647 ID: 2 Name: GEN-2004-017 | 08 N-OK & S-KS | 28S | 17
GEN-2017-009 | 588544 | Bus: 547642 ID: 1 Name: GEN-2014-028 | 08 N-OK & S-KS | 19W (Sensitivity C) | 173.67
GEN-2017-009 | 588544 | Bus: 547642 ID: 1 Name: GEN-2014-028 | 08 N-OK & S-KS | 21L (Sensitivity C) | 173.67
GEN-2017-009 | 588544 | Bus: 547642 ID: 1 Name: GEN-2014-028 | 08 N-OK & S-KS | 21S (Sensitivity C) | 142
GEN-2017-009 | 588544 | Bus: 547642 ID: 1 Name: GEN-2014-028 | 08 N-OK & S-KS | 28S | 142
GEN-2017-009 | 588544 | Bus: 547643 ID: 1 Name: GEN-2014-028 | 08 N-OK & S-KS | 19W (Sensitivity C) | 136.33
GEN-2017-009 | 588544 | Bus: 547643 ID: 1 Name: GEN-2014-028 | 08 N-OK & S-KS | 21L (Sensitivity C) | 136.33
GEN-2017-009 | 588544 | Bus: 547643 ID: 1 Name: GEN-2014-028 | 08 N-OK & S-KS | 21S (Sensitivity C) | 114
GEN-2017-009 | 588544 | Bus: 547643 ID: 1 Name: GEN-2014-028 | 08 N-OK & S-KS | 28S | 114
GEN-2017-022 | 588664 | Bus: 542955 ID: 1 Name: Lacygne | 08 N-OK & S-KS | 19W (Sensitivity C) | 810.8
GEN-2017-022 | 588664 | Bus: 542955 ID: 1 Name: Lacygne | 08 N-OK & S-KS | 21L (Sensitivity C) | 810.8
GEN-2017-022 | 588664 | Bus: 542955 ID: 1 Name: Lacygne | 08 N-OK & S-KS | 21S (Sensitivity C) | 810.8
GEN-2017-022 | 588664 | Bus: 542955 ID: 1 Name: Lacygne | 08 N-OK & S-KS | 28S | 810.8
GEN-2017-022 | 588664 | Bus: 542956 ID: 2 Name: Lacygne | 08 N-OK & S-KS | 19W (Sensitivity C) | 717.8
GEN-2017-022 | 588664 | Bus: 542956 ID: 2 Name: Lacygne | 08 N-OK & S-KS | 21L (Sensitivity C) | 717.8
GEN-2017-022 | 588664 | Bus: 542956 ID: 2 Name: Lacygne | 08 N-OK & S-KS | 21S (Sensitivity C) | 717.8
GEN-2017-022 | 588664 | Bus: 542956 ID: 2 Name: Lacygne | 08 N-OK & S-KS | 28S | 717.8
GEN-2017-022 | 588664 | Bus: 533592 ID: 1 Name: Getty | 08 N-OK & S-KS | 19W (Sensitivity C) | 35
GEN-2017-022 | 588664 | Bus: 533592 ID: 1 Name: Getty | 08 N-OK & S-KS | 21L (Sensitivity C) | 35
GEN-2017-022 | 588664 | Bus: 533592 ID: 1 Name: Getty | 08 N-OK & S-KS | 21S (Sensitivity C) | 35
GEN-2017-022 | 588664 | Bus: 533592 ID: 1 Name: Getty | 08 N-OK & S-KS | 28S | 35
GEN-2017-061 | 512742 | Bus: 512689 ID: 1 Name: GRDA | 08 N-OK & S-KS | 19W (Sensitivity B) | 0
GEN-2017-061 | 512742 | Bus: 512689 ID: 1 Name: GRDA | 08 N-OK & S-KS | 21L (Sensitivity B) | 0
GEN-2017-061 | 512742 | Bus: 512689 ID: 1 Name: GRDA | 08 N-OK & S-KS | 21S | 0
GEN-2017-061 | 512742 | Bus: 512689 ID: 1 Name: GRDA | 08 N-OK & S-KS | 28S | 0
GEN-2017-061 | 512742 | Bus: 512688 ID: 2 Name: GRDA | 08 N-OK & S-KS | 19W (Sensitivity B) | 520
GEN-2017-061 | 512742 | Bus: 512688 ID: 2 Name: GRDA | 08 N-OK & S-KS | 21L (Sensitivity B) | 520
GEN-2017-061 | 512742 | Bus: 512688 ID: 2 Name: GRDA | 08 N-OK & S-KS | 21S | 520
GEN-2017-061 | 512742 | Bus: 512688 ID: 2 Name: GRDA | 08 N-OK & S-KS | 28S | 520
GEN-2017-061 | 512742 | Bus: 300031 ID: 1 Name: Choteau | 08 N-OK & S-KS | 19W (Sensitivity B) | 163.1
GEN-2017-061 | 512742 | Bus: 300031 ID: 1 Name: Choteau | 08 N-OK & S-KS | 21L (Sensitivity B) | 154.9
GEN-2017-061 | 512742 | Bus: 300031 ID: 1 Name: Choteau | 08 N-OK & S-KS | 21S | 154.9
GEN-2017-061 | 512742 | Bus: 300031 ID: 1 Name: Choteau | 08 N-OK & S-KS | 28S | 154.9
GEN-2017-061 | 512742 | Bus: 300032 ID: 1 Name: Choteau | 08 N-OK & S-KS | 19W (Sensitivity B) | 157
GEN-2017-061 | 512742 | Bus: 300032 ID: 1 Name: Choteau | 08 N-OK & S-KS | 21L (Sensitivity B) | 149.1
GEN-2017-061 | 512742 | Bus: 300032 ID: 1 Name: Choteau | 08 N-OK & S-KS | 21S | 149.1
GEN-2017-061 | 512742 | Bus: 300032 ID: 1 Name: Choteau | 08 N-OK & S-KS | 28S | 149.1
GEN-2017-061 | 512742 | Bus: 300033 ID: 1 Name: Choteau | 08 N-OK & S-KS | 19W (Sensitivity B) | 157
GEN-2017-061 | 512742 | Bus: 300033 ID: 1 Name: Choteau | 08 N-OK & S-KS | 21L (Sensitivity B) | 149.1
GEN-2017-061 | 512742 | Bus: 300033 ID: 1 Name: Choteau | 08 N-OK & S-KS | 21S | 149.1
GEN-2017-061 | 512742 | Bus: 300033 ID: 1 Name: Choteau | 08 N-OK & S-KS | 28S | 149.1
GEN-2017-061 | 512742 | Bus: 300020 ID: 1 Name: Choteau | 08 N-OK & S-KS | 19W (Sensitivity B) | 157
GEN-2017-061 | 512742 | Bus: 300020 ID: 1 Name: Choteau | 08 N-OK & S-KS | 21L (Sensitivity B) | 0
GEN-2017-061 | 512742 | Bus: 300020 ID: 1 Name: Choteau | 08 N-OK & S-KS | 21S | 149.1
GEN-2017-061 | 512742 | Bus: 300020 ID: 1 Name: Choteau | 08 N-OK & S-KS | 28S | 149.1
GEN-2017-061 | 512742 | Bus: 300021 ID: 1 Name: Choteau | 08 N-OK & S-KS | 19W (Sensitivity B) | 157
GEN-2017-061 | 512742 | Bus: 300021 ID: 1 Name: Choteau | 08 N-OK & S-KS | 21L (Sensitivity B) | 149.1
GEN-2017-061 | 512742 | Bus: 300021 ID: 1 Name: Choteau | 08 N-OK & S-KS | 21S | 149.1
GEN-2017-061 | 512742 | Bus: 300021 ID: 1 Name: Choteau | 08 N-OK & S-KS | 28S | 149.1
GEN-2017-061 | 512742 | Bus: 300024 ID: 1 Name: Choteau | 08 N-OK & S-KS | 19W (Sensitivity B) | 163.1
GEN-2017-061 | 512742 | Bus: 300024 ID: 1 Name: Choteau | 08 N-OK & S-KS | 21L (Sensitivity B) | 154.9
GEN-2017-061 | 512742 | Bus: 300024 ID: 1 Name: Choteau | 08 N-OK & S-KS | 21S | 154.9
GEN-2017-061 | 512742 | Bus: 300024 ID: 1 Name: Choteau | 08 N-OK & S-KS | 28S | 154.9
GEN-2017-061 | 512742 | Bus: 512615 ID: 1 Name: GEN-2013-028 | 08 N-OK & S-KS | 19W (Sensitivity B) | 199.5
GEN-2017-061 | 512742 | Bus: 512615 ID: 1 Name: GEN-2013-028 | 08 N-OK & S-KS | 21L (Sensitivity B) | 199.5
GEN-2017-061 | 512742 | Bus: 512615 ID: 1 Name: GEN-2013-028 | 08 N-OK & S-KS | 21S | 191.8
GEN-2017-061 | 512742 | Bus: 512615 ID: 1 Name: GEN-2013-028 | 08 N-OK & S-KS | 28S | 191.8
GEN-2017-061 | 512742 | Bus: 512614 ID: 1 Name: GEN-2013-028 | 08 N-OK & S-KS | 19W (Sensitivity B) | 360
GEN-2017-061 | 512742 | Bus: 512614 ID: 1 Name: GEN-2013-028 | 08 N-OK & S-KS | 21L (Sensitivity B) | 360
GEN-2017-061 | 512742 | Bus: 512614 ID: 1 Name: GEN-2013-028 | 08 N-OK & S-KS | 21S | 324.6
GEN-2017-061 | 512742 | Bus: 512614 ID: 1 Name: GEN-2013-028 | 08 N-OK & S-KS | 28S | 324.6
GEN-2017-061 | 512742 | Bus: 512608 ID: 1 Name: Salina | 08 N-OK & S-KS | 19W (Sensitivity B) | 43
GEN-2017-061 | 512742 | Bus: 512608 ID: 1 Name: Salina | 08 N-OK & S-KS | 21L (Sensitivity B) | 43
GEN-2017-061 | 512742 | Bus: 512608 ID: 1 Name: Salina | 08 N-OK & S-KS | 21S | 43
GEN-2017-061 | 512742 | Bus: 512608 ID: 1 Name: Salina | 08 N-OK & S-KS | 28S | 43
GEN-2017-061 | 512742 | Bus: 512612 ID: 5 Name: Salina | 08 N-OK & S-KS | 19W (Sensitivity B) | 43
GEN-2017-061 | 512742 | Bus: 512612 ID: 5 Name: Salina | 08 N-OK & S-KS | 21L (Sensitivity B) | 43
GEN-2017-061 | 512742 | Bus: 512612 ID: 5 Name: Salina | 08 N-OK & S-KS | 21S | 43
GEN-2017-061 | 512742 | Bus: 512612 ID: 5 Name: Salina | 08 N-OK & S-KS | 28S | 43
GEN-2017-061 | 512742 | Bus: 512611 ID: 4 Name: Salina | 08 N-OK & S-KS | 19W (Sensitivity B) | 43
GEN-2017-061 | 512742 | Bus: 512611 ID: 4 Name: Salina | 08 N-OK & S-KS | 21L (Sensitivity B) | 43
GEN-2017-061 | 512742 | Bus: 512611 ID: 4 Name: Salina | 08 N-OK & S-KS | 21S | 43
GEN-2017-061 | 512742 | Bus: 512611 ID: 4 Name: Salina | 08 N-OK & S-KS | 28S | 43
GEN-2017-061 | 512742 | Bus: 512609 ID: 2 Name: Salina | 08 N-OK & S-KS | 19W (Sensitivity B) | 43
GEN-2017-061 | 512742 | Bus: 512609 ID: 2 Name: Salina | 08 N-OK & S-KS | 21L (Sensitivity B) | 43
GEN-2017-061 | 512742 | Bus: 512609 ID: 2 Name: Salina | 08 N-OK & S-KS | 21S | 43
GEN-2017-061 | 512742 | Bus: 512609 ID: 2 Name: Salina | 08 N-OK & S-KS | 28S | 43
GEN-2017-061 | 512742 | Bus: 512613 ID: 6 Name: Salina | 08 N-OK & S-KS | 19W (Sensitivity B) | 43
GEN-2017-061 | 512742 | Bus: 512613 ID: 6 Name: Salina | 08 N-OK & S-KS | 21L (Sensitivity B) | 43
GEN-2017-061 | 512742 | Bus: 512613 ID: 6 Name: Salina | 08 N-OK & S-KS | 21S | 43
GEN-2017-061 | 512742 | Bus: 512613 ID: 6 Name: Salina | 08 N-OK & S-KS | 28S | 43
GEN-2017-061 | 512742 | Bus: 512610 ID: 3 Name: Salina | 08 N-OK & S-KS | 19W (Sensitivity B) | 43
GEN-2017-061 | 512742 | Bus: 512610 ID: 3 Name: Salina | 08 N-OK & S-KS | 21L (Sensitivity B) | 43
GEN-2017-061 | 512742 | Bus: 512610 ID: 3 Name: Salina | 08 N-OK & S-KS | 21S | 43
GEN-2017-061 | 512742 | Bus: 512610 ID: 3 Name: Salina | 08 N-OK & S-KS | 28S | 43
GEN-2017-061 | 512742 | Bus: 512847 ID: 4 Name: Kerr | 08 N-OK & S-KS | 19W (Sensitivity B) | 32
GEN-2017-061 | 512742 | Bus: 512847 ID: 4 Name: Kerr | 08 N-OK & S-KS | 21L (Sensitivity B) | 32
GEN-2017-061 | 512742 | Bus: 512847 ID: 4 Name: Kerr | 08 N-OK & S-KS | 21S | 32
GEN-2017-061 | 512742 | Bus: 512847 ID: 4 Name: Kerr | 08 N-OK & S-KS | 28S | 32
GEN-2017-061 | 512742 | Bus: 512846 ID: 1 Name: Kerr | 08 N-OK & S-KS | 19W (Sensitivity B) | 32
GEN-2017-061 | 512742 | Bus: 512846 ID: 1 Name: Kerr | 08 N-OK & S-KS | 21L (Sensitivity B) | 32
GEN-2017-061 | 512742 | Bus: 512846 ID: 1 Name: Kerr | 08 N-OK & S-KS | 21S | 32
GEN-2017-061 | 512742 | Bus: 512846 ID: 1 Name: Kerr | 08 N-OK & S-KS | 28S | 32
GEN-2017-061 | 512742 | Bus: 512600 ID: 2 Name: Kerr | 08 N-OK & S-KS | 19W (Sensitivity B) | 32
GEN-2017-061 | 512742 | Bus: 512600 ID: 2 Name: Kerr | 08 N-OK & S-KS | 21L (Sensitivity B) | 32
GEN-2017-061 | 512742 | Bus: 512600 ID: 2 Name: Kerr | 08 N-OK & S-KS | 21S | 32
GEN-2017-061 | 512742 | Bus: 512600 ID: 2 Name: Kerr | 08 N-OK & S-KS | 28S | 32
GEN-2017-061 | 512742 | Bus: 512601 ID: 3 Name: Kerr | 08 N-OK & S-KS | 19W (Sensitivity B) | 32
GEN-2017-061 | 512742 | Bus: 512601 ID: 3 Name: Kerr | 08 N-OK & S-KS | 21L (Sensitivity B) | 32
GEN-2017-061 | 512742 | Bus: 512601 ID: 3 Name: Kerr | 08 N-OK & S-KS | 21S | 32
GEN-2017-061 | 512742 | Bus: 512601 ID: 3 Name: Kerr | 08 N-OK & S-KS | 28S | 32
GEN-2017-068 | 532796 | Bus: 532724 ID: 1 Name: EEC | 08 N-OK & S-KS | 19W (Sensitivity A) | 90
GEN-2017-068 | 532796 | Bus: 532724 ID: 1 Name: EEC | 08 N-OK & S-KS | 21L (Sensitivity A) | 76
GEN-2017-068 | 532796 | Bus: 532724 ID: 1 Name: EEC | 08 N-OK & S-KS | 21S | 72
GEN-2017-068 | 532796 | Bus: 532724 ID: 1 Name: EEC | 08 N-OK & S-KS | 28S | 72
GEN-2017-068 | 532796 | Bus: 532725 ID: 1 Name: EEC | 08 N-OK & S-KS | 19W (Sensitivity A) | 165
GEN-2017-068 | 532796 | Bus: 532725 ID: 1 Name: EEC | 08 N-OK & S-KS | 21L (Sensitivity A) | 155
GEN-2017-068 | 532796 | Bus: 532725 ID: 1 Name: EEC | 08 N-OK & S-KS | 21S | 147
GEN-2017-068 | 532796 | Bus: 532725 ID: 1 Name: EEC | 08 N-OK & S-KS | 28S | 147
GEN-2017-068 | 532796 | Bus: 532723 ID: 1 Name: EEC | 08 N-OK & S-KS | 19W (Sensitivity A) | 90
GEN-2017-068 | 532796 | Bus: 532723 ID: 1 Name: EEC | 08 N-OK & S-KS | 21L (Sensitivity A) | 76
GEN-2017-068 | 532796 | Bus: 532723 ID: 1 Name: EEC | 08 N-OK & S-KS | 21S | 72
GEN-2017-068 | 532796 | Bus: 532723 ID: 1 Name: EEC | 08 N-OK & S-KS | 28S | 72
GEN-2017-068 | 532796 | Bus: 532722 ID: 1 Name: EEC | 08 N-OK & S-KS | 19W (Sensitivity A) | 0
GEN-2017-068 | 532796 | Bus: 532722 ID: 1 Name: EEC | 08 N-OK & S-KS | 21L (Sensitivity A) | 0
GEN-2017-068 | 532796 | Bus: 532722 ID: 1 Name: EEC | 08 N-OK & S-KS | 21S | 0
GEN-2017-068 | 532796 | Bus: 532722 ID: 1 Name: EEC | 08 N-OK & S-KS | 28S | 0
GEN-2017-068 | 532796 | Bus: 532721 ID: 1 Name: EEC | 08 N-OK & S-KS | 19W (Sensitivity A) | 0
GEN-2017-068 | 532796 | Bus: 532721 ID: 1 Name: EEC | 08 N-OK & S-KS | 21L (Sensitivity A) | 0
GEN-2017-068 | 532796 | Bus: 532721 ID: 1 Name: EEC | 08 N-OK & S-KS | 21S | 0
GEN-2017-068 | 532796 | Bus: 532721 ID: 1 Name: EEC | 08 N-OK & S-KS | 28S | 0
GEN-2017-068 | 532796 | Bus: 532743 ID: 6 Name: EMPEC | 08 N-OK & S-KS | 19W (Sensitivity A) | 170
GEN-2017-068 | 532796 | Bus: 532743 ID: 6 Name: EMPEC | 08 N-OK & S-KS | 21L (Sensitivity A) | 164
GEN-2017-068 | 532796 | Bus: 532743 ID: 6 Name: EMPEC | 08 N-OK & S-KS | 21S | 155
GEN-2017-068 | 532796 | Bus: 532743 ID: 6 Name: EMPEC | 08 N-OK & S-KS | 28S | 155
GEN-2017-068 | 532796 | Bus: 532741 ID: 4 Name: EMPEC | 08 N-OK & S-KS | 19W (Sensitivity A) | 50
GEN-2017-068 | 532796 | Bus: 532741 ID: 4 Name: EMPEC | 08 N-OK & S-KS | 21L (Sensitivity A) | 49
GEN-2017-068 | 532796 | Bus: 532741 ID: 4 Name: EMPEC | 08 N-OK & S-KS | 21S | 44
GEN-2017-068 | 532796 | Bus: 532741 ID: 4 Name: EMPEC | 08 N-OK & S-KS | 28S | 44
GEN-2017-068 | 532796 | Bus: 532741 ID: 3 Name: EMPEC | 08 N-OK & S-KS | 19W (Sensitivity A) | 50
GEN-2017-068 | 532796 | Bus: 532741 ID: 3 Name: EMPEC | 08 N-OK & S-KS | 21L (Sensitivity A) | 49
GEN-2017-068 | 532796 | Bus: 532741 ID: 3 Name: EMPEC | 08 N-OK & S-KS | 21S | 44
GEN-2017-068 | 532796 | Bus: 532741 ID: 3 Name: EMPEC | 08 N-OK & S-KS | 28S | 44
GEN-2017-068 | 532796 | Bus: 532742 ID: 5 Name: EMPEC | 08 N-OK & S-KS | 19W (Sensitivity A) | 170
GEN-2017-068 | 532796 | Bus: 532742 ID: 5 Name: EMPEC | 08 N-OK & S-KS | 21L (Sensitivity A) | 164
GEN-2017-068 | 532796 | Bus: 532742 ID: 5 Name: EMPEC | 08 N-OK & S-KS | 21S | 155
GEN-2017-068 | 532796 | Bus: 532742 ID: 5 Name: EMPEC | 08 N-OK & S-KS | 28S | 155
GEN-2017-068 | 532796 | Bus: 532740 ID: 2 Name: EMPEC | 08 N-OK & S-KS | 19W (Sensitivity A) | 50
GEN-2017-068 | 532796 | Bus: 532740 ID: 2 Name: EMPEC | 08 N-OK & S-KS | 21L (Sensitivity A) | 49
GEN-2017-068 | 532796 | Bus: 532740 ID: 2 Name: EMPEC | 08 N-OK & S-KS | 21S | 44
GEN-2017-068 | 532796 | Bus: 532740 ID: 2 Name: EMPEC | 08 N-OK & S-KS | 28S | 44
GEN-2017-068 | 532796 | Bus: 532740 ID: 1 Name: EMPEC | 08 N-OK & S-KS | 19W (Sensitivity A) | 50
GEN-2017-068 | 532796 | Bus: 532740 ID: 1 Name: EMPEC | 08 N-OK & S-KS | 21L (Sensitivity A) | 49
GEN-2017-068 | 532796 | Bus: 532740 ID: 1 Name: EMPEC | 08 N-OK & S-KS | 21S | 44
GEN-2017-068 | 532796 | Bus: 532740 ID: 1 Name: EMPEC | 08 N-OK & S-KS | 28S | 44
GEN-2017-068 | 532796 | Bus: 532744 ID: 7 Name: EMPEC | 08 N-OK & S-KS | 19W (Sensitivity A) | 170
GEN-2017-068 | 532796 | Bus: 532744 ID: 7 Name: EMPEC | 08 N-OK & S-KS | 21L (Sensitivity A) | 164
GEN-2017-068 | 532796 | Bus: 532744 ID: 7 Name: EMPEC | 08 N-OK & S-KS | 21S | 155
GEN-2017-068 | 532796 | Bus: 532744 ID: 7 Name: EMPEC | 08 N-OK & S-KS | 28S | 155
GEN-2017-073 | 512629 | Bus: 512688 ID: 2 Name: GRDA | 08 N-OK & S-KS | 19W (Sensitivity B) | 520
GEN-2017-073 | 512629 | Bus: 512688 ID: 2 Name: GRDA | 08 N-OK & S-KS | 21L (Sensitivity B) | 520
GEN-2017-073 | 512629 | Bus: 512688 ID: 2 Name: GRDA | 08 N-OK & S-KS | 21S | 520
GEN-2017-073 | 512629 | Bus: 512688 ID: 2 Name: GRDA | 08 N-OK & S-KS | 28S | 520
GEN-2017-073 | 512629 | Bus: 512614 ID: 1 Name: GEN-2013-028 | 08 N-OK & S-KS | 19W (Sensitivity B) | 360
GEN-2017-073 | 512629 | Bus: 512614 ID: 1 Name: GEN-2013-028 | 08 N-OK & S-KS | 21L (Sensitivity B) | 360
GEN-2017-073 | 512629 | Bus: 512614 ID: 1 Name: GEN-2013-028 | 08 N-OK & S-KS | 21S | 324.6
GEN-2017-073 | 512629 | Bus: 512614 ID: 1 Name: GEN-2013-028 | 08 N-OK & S-KS | 28S | 324.6
GEN-2017-073 | 512629 | Bus: 512615 ID: 1 Name: GEN-2013-028 | 08 N-OK & S-KS | 19W (Sensitivity B) | 199.5
GEN-2017-073 | 512629 | Bus: 512615 ID: 1 Name: GEN-2013-028 | 08 N-OK & S-KS | 21L (Sensitivity B) | 199.5
GEN-2017-073 | 512629 | Bus: 512615 ID: 1 Name: GEN-2013-028 | 08 N-OK & S-KS | 21S | 191.8
GEN-2017-073 | 512629 | Bus: 512615 ID: 1 Name: GEN-2013-028 | 08 N-OK & S-KS | 28S | 191.8
GEN-2017-073 | 512629 | Bus: 512608 ID: 1 Name: Salinas Units | 08 N-OK & S-KS | 19W (Sensitivity B) | 43
GEN-2017-073 | 512629 | Bus: 512608 ID: 1 Name: Salinas Units | 08 N-OK & S-KS | 21L (Sensitivity B) | 43
GEN-2017-073 | 512629 | Bus: 512608 ID: 1 Name: Salinas Units | 08 N-OK & S-KS | 21S | 43
GEN-2017-073 | 512629 | Bus: 512608 ID: 1 Name: Salinas Units | 08 N-OK & S-KS | 28S | 43
GEN-2017-073 | 512629 | Bus: 512609 ID: 2 Name: Salinas Units | 08 N-OK & S-KS | 19W (Sensitivity B) | 43
GEN-2017-073 | 512629 | Bus: 512609 ID: 2 Name: Salinas Units | 08 N-OK & S-KS | 21L (Sensitivity B) | 43
GEN-2017-073 | 512629 | Bus: 512609 ID: 2 Name: Salinas Units | 08 N-OK & S-KS | 21S | 43
GEN-2017-073 | 512629 | Bus: 512609 ID: 2 Name: Salinas Units | 08 N-OK & S-KS | 28S | 43
GEN-2017-073 | 512629 | Bus: 512610 ID: 3 Name: Salinas Units | 08 N-OK & S-KS | 19W (Sensitivity B) | 43
GEN-2017-073 | 512629 | Bus: 512610 ID: 3 Name: Salinas Units | 08 N-OK & S-KS | 21L (Sensitivity B) | 43
GEN-2017-073 | 512629 | Bus: 512610 ID: 3 Name: Salinas Units | 08 N-OK & S-KS | 21S | 43
GEN-2017-073 | 512629 | Bus: 512610 ID: 3 Name: Salinas Units | 08 N-OK & S-KS | 28S | 43
GEN-2017-073 | 512629 | Bus: 512611 ID: 4 Name: Salinas Units | 08 N-OK & S-KS | 19W (Sensitivity B) | 43
GEN-2017-073 | 512629 | Bus: 512611 ID: 4 Name: Salinas Units | 08 N-OK & S-KS | 21L (Sensitivity B) | 43
GEN-2017-073 | 512629 | Bus: 512611 ID: 4 Name: Salinas Units | 08 N-OK & S-KS | 21S | 43
GEN-2017-073 | 512629 | Bus: 512611 ID: 4 Name: Salinas Units | 08 N-OK & S-KS | 28S | 43
GEN-2017-073 | 512629 | Bus: 512612 ID: 5 Name: Salinas Units | 08 N-OK & S-KS | 19W (Sensitivity B) | 43
GEN-2017-073 | 512629 | Bus: 512612 ID: 5 Name: Salinas Units | 08 N-OK & S-KS | 21L (Sensitivity B) | 43
GEN-2017-073 | 512629 | Bus: 512612 ID: 5 Name: Salinas Units | 08 N-OK & S-KS | 21S | 43
GEN-2017-073 | 512629 | Bus: 512612 ID: 5 Name: Salinas Units | 08 N-OK & S-KS | 28S | 43
GEN-2017-073 | 512629 | Bus: 512613 ID: 6 Name: Salinas Units | 08 N-OK & S-KS | 19W (Sensitivity B) | 43
GEN-2017-073 | 512629 | Bus: 512613 ID: 6 Name: Salinas Units | 08 N-OK & S-KS | 21L (Sensitivity B) | 43
GEN-2017-073 | 512629 | Bus: 512613 ID: 6 Name: Salinas Units | 08 N-OK & S-KS | 21S | 43
GEN-2017-073 | 512629 | Bus: 512613 ID: 6 Name: Salinas Units | 08 N-OK & S-KS | 28S | 43
GEN-2017-073 | 512629 | Bus: 300020 ID: 1 Name: CHOTST | 08 N-OK & S-KS | 19W (Sensitivity B) | 157
GEN-2017-073 | 512629 | Bus: 300020 ID: 1 Name: CHOTST | 08 N-OK & S-KS | 21L (Sensitivity B) | 0
GEN-2017-073 | 512629 | Bus: 300020 ID: 1 Name: CHOTST | 08 N-OK & S-KS | 21S | 149.1
GEN-2017-073 | 512629 | Bus: 300020 ID: 1 Name: CHOTST | 08 N-OK & S-KS | 28S | 149.1
GEN-2017-073 | 512629 | Bus: 300021 ID: 1 Name: CHOTST | 08 N-OK & S-KS | 19W (Sensitivity B) | 157
GEN-2017-073 | 512629 | Bus: 300021 ID: 1 Name: CHOTST | 08 N-OK & S-KS | 21L (Sensitivity B) | 149.1
GEN-2017-073 | 512629 | Bus: 300021 ID: 1 Name: CHOTST | 08 N-OK & S-KS | 21S | 149.1
GEN-2017-073 | 512629 | Bus: 300021 ID: 1 Name: CHOTST | 08 N-OK & S-KS | 28S | 149.1
GEN-2017-073 | 512629 | Bus: 300024 ID: 1 Name: CHOTST | 08 N-OK & S-KS | 19W (Sensitivity B) | 163.1
GEN-2017-073 | 512629 | Bus: 300024 ID: 1 Name: CHOTST | 08 N-OK & S-KS | 21L (Sensitivity B) | 154.9
GEN-2017-073 | 512629 | Bus: 300024 ID: 1 Name: CHOTST | 08 N-OK & S-KS | 21S | 154.9
GEN-2017-073 | 512629 | Bus: 300024 ID: 1 Name: CHOTST | 08 N-OK & S-KS | 28S | 154.9
GEN-2017-073 | 512629 | Bus: 300032 ID: 1 Name: CHOTST | 08 N-OK & S-KS | 19W (Sensitivity B) | 157
GEN-2017-073 | 512629 | Bus: 300032 ID: 1 Name: CHOTST | 08 N-OK & S-KS | 21L (Sensitivity B) | 149.1
GEN-2017-073 | 512629 | Bus: 300032 ID: 1 Name: CHOTST | 08 N-OK & S-KS | 21S | 149.1
GEN-2017-073 | 512629 | Bus: 300032 ID: 1 Name: CHOTST | 08 N-OK & S-KS | 28S | 149.1
GEN-2017-073 | 512629 | Bus: 300031 ID: 1 Name: CHOTST | 08 N-OK & S-KS | 19W (Sensitivity B) | 163.1
GEN-2017-073 | 512629 | Bus: 300031 ID: 1 Name: CHOTST | 08 N-OK & S-KS | 21L (Sensitivity B) | 154.9
GEN-2017-073 | 512629 | Bus: 300031 ID: 1 Name: CHOTST | 08 N-OK & S-KS | 21S | 154.9
GEN-2017-073 | 512629 | Bus: 300031 ID: 1 Name: CHOTST | 08 N-OK & S-KS | 28S | 154.9
GEN-2017-073 | 512629 | Bus: 300033 ID: 1 Name: CHOTST | 08 N-OK & S-KS | 19W (Sensitivity B) | 157
GEN-2017-073 | 512629 | Bus: 300033 ID: 1 Name: CHOTST | 08 N-OK & S-KS | 21L (Sensitivity B) | 149.1
GEN-2017-073 | 512629 | Bus: 300033 ID: 1 Name: CHOTST | 08 N-OK & S-KS | 21S | 149.1
GEN-2017-073 | 512629 | Bus: 300033 ID: 1 Name: CHOTST | 08 N-OK & S-KS | 28S | 149.1
GEN-2017-073 | 512629 | Bus: 512607 ID: 5 Name: PENSA | 08 N-OK & S-KS | 19W (Sensitivity B) | 21
GEN-2017-073 | 512629 | Bus: 512607 ID: 5 Name: PENSA | 08 N-OK & S-KS | 21L (Sensitivity B) | 21
GEN-2017-073 | 512629 | Bus: 512607 ID: 5 Name: PENSA | 08 N-OK & S-KS | 21S | 21
GEN-2017-073 | 512629 | Bus: 512607 ID: 5 Name: PENSA | 08 N-OK & S-KS | 28S | 21
GEN-2017-073 | 512629 | Bus: 512605 ID: 4 Name: PENSA | 08 N-OK & S-KS | 19W (Sensitivity B) | 21
GEN-2017-073 | 512629 | Bus: 512605 ID: 4 Name: PENSA | 08 N-OK & S-KS | 21L (Sensitivity B) | 21
GEN-2017-073 | 512629 | Bus: 512605 ID: 4 Name: PENSA | 08 N-OK & S-KS | 21S | 21
GEN-2017-073 | 512629 | Bus: 512605 ID: 4 Name: PENSA | 08 N-OK & S-KS | 28S | 21
GEN-2017-073 | 512629 | Bus: 512606 ID: 6 Name: PENSA | 08 N-OK & S-KS | 19W (Sensitivity B) | 21
GEN-2017-073 | 512629 | Bus: 512606 ID: 6 Name: PENSA | 08 N-OK & S-KS | 21L (Sensitivity B) | 21
GEN-2017-073 | 512629 | Bus: 512606 ID: 6 Name: PENSA | 08 N-OK & S-KS | 21S | 21
GEN-2017-073 | 512629 | Bus: 512606 ID: 6 Name: PENSA | 08 N-OK & S-KS | 28S | 21
GEN-2017-073 | 512629 | Bus: 512602 ID: 1 Name: PENSA | 08 N-OK & S-KS | 19W (Sensitivity B) | 21
GEN-2017-073 | 512629 | Bus: 512602 ID: 1 Name: PENSA | 08 N-OK & S-KS | 21L (Sensitivity B) | 21
GEN-2017-073 | 512629 | Bus: 512602 ID: 1 Name: PENSA | 08 N-OK & S-KS | 21S | 21
GEN-2017-073 | 512629 | Bus: 512602 ID: 1 Name: PENSA | 08 N-OK & S-KS | 28S | 21
GEN-2017-073 | 512629 | Bus: 512603 ID: 2 Name: PENSA | 08 N-OK & S-KS | 19W (Sensitivity B) | 21
GEN-2017-073 | 512629 | Bus: 512603 ID: 2 Name: PENSA | 08 N-OK & S-KS | 21L (Sensitivity B) | 21
GEN-2017-073 | 512629 | Bus: 512603 ID: 2 Name: PENSA | 08 N-OK & S-KS | 21S | 21
GEN-2017-073 | 512629 | Bus: 512603 ID: 2 Name: PENSA | 08 N-OK & S-KS | 28S | 21
GEN-2017-073 | 512629 | Bus: 512604 ID: 3 Name: PENSA | 08 N-OK & S-KS | 19W (Sensitivity B) | 21
GEN-2017-073 | 512629 | Bus: 512604 ID: 3 Name: PENSA | 08 N-OK & S-KS | 21L (Sensitivity B) | 21
GEN-2017-073 | 512629 | Bus: 512604 ID: 3 Name: PENSA | 08 N-OK & S-KS | 21S | 21
GEN-2017-073 | 512629 | Bus: 512604 ID: 3 Name: PENSA | 08 N-OK & S-KS | 28S | 21
GEN-2017-092 | 588839 | Bus: 515226 ID: 1 Name: Muskogee | 08 N-OK & S-KS | 19W (Sensitivity B) | 551
GEN-2017-092 | 588839 | Bus: 515226 ID: 1 Name: Muskogee | 08 N-OK & S-KS | 21L (Sensitivity B) | 551
GEN-2017-092 | 588839 | Bus: 515226 ID: 1 Name: Muskogee | 08 N-OK & S-KS | 21S | 551
GEN-2017-092 | 588839 | Bus: 515226 ID: 1 Name: Muskogee | 08 N-OK & S-KS | 28S | 551
GEN-2017-092 | 588839 | Bus: 515225 ID: 1 Name: Muskogee | 08 N-OK & S-KS | 19W (Sensitivity B) | 557
GEN-2017-092 | 588839 | Bus: 515225 ID: 1 Name: Muskogee | 08 N-OK & S-KS | 21L (Sensitivity B) | 557
GEN-2017-092 | 588839 | Bus: 515225 ID: 1 Name: Muskogee | 08 N-OK & S-KS | 21S | 557
GEN-2017-092 | 588839 | Bus: 515225 ID: 1 Name: Muskogee | 08 N-OK & S-KS | 28S | 557
GEN-2017-092 | 588839 | Bus: 515223 ID: 1 Name: Muskogee | 08 N-OK & S-KS | 19W (Sensitivity B) | 567
GEN-2017-092 | 588839 | Bus: 515223 ID: 1 Name: Muskogee | 08 N-OK & S-KS | 21L (Sensitivity B) | 567
GEN-2017-092 | 588839 | Bus: 515223 ID: 1 Name: Muskogee | 08 N-OK & S-KS | 21S | 567
GEN-2017-092 | 588839 | Bus: 515223 ID: 1 Name: Muskogee | 08 N-OK & S-KS | 28S | 567
GEN-2017-071 | 515417 | Bus: 505612 ID: 1 Name: Keystone | 08 N-OK & S-KS | 19W (Sensitivity A) | 35
GEN-2017-071 | 515417 | Bus: 505612 ID: 1 Name: Keystone | 08 N-OK & S-KS | 21L (Sensitivity A) | 35
GEN-2017-071 | 515417 | Bus: 505612 ID: 1 Name: Keystone | 08 N-OK & S-KS | 21S | 35
GEN-2017-071 | 515417 | Bus: 505612 ID: 1 Name: Keystone | 08 N-OK & S-KS | 28S | 35
GEN-2017-072 | 515417 | Bus: 505612 ID: 2 Name: Keystone | 08 N-OK & S-KS | 19W (Sensitivity A) | 35
GEN-2017-072 | 515417 | Bus: 505612 ID: 2 Name: Keystone | 08 N-OK & S-KS | 21L (Sensitivity A) | 35
GEN-2017-072 | 515417 | Bus: 505612 ID: 2 Name: Keystone | 08 N-OK & S-KS | 21S | 35
GEN-2017-072 | 515417 | Bus: 505612 ID: 2 Name: Keystone | 08 N-OK & S-KS | 28S | 35
GEN-2017-074 | 510419 | None | 08 N-OK & S-KS | None | None
GEN-2017-077 | 589154 | None | 08 N-OK & S-KS | None | None
GEN-2017-086 | 532798 | Bus: 588363 ID: 1 Name: Gen 16-153 | 08 N-OK & S-KS | 19W (Sensitivity A) | 134
GEN-2017-086 | 532798 | Bus: 588363 ID: 1 Name: Gen 16-153 | 08 N-OK & S-KS | 21L (Sensitivity A) | 134
GEN-2017-086 | 532798 | Bus: 588363 ID: 1 Name: Gen 16-153 | 08 N-OK & S-KS | 21S | 134
GEN-2017-086 | 532798 | Bus: 588363 ID: 1 Name: Gen 16-153 | 08 N-OK & S-KS | 28S | 134
GEN-2017-086 | 532798 | Bus: 539114 ID: 1 Name: GEN-2006-021 | 08 N-OK & S-KS | 19W (Sensitivity A) | 50
GEN-2017-086 | 532798 | Bus: 539114 ID: 1 Name: GEN-2006-021 | 08 N-OK & S-KS | 21L (Sensitivity A) | 50
GEN-2017-086 | 532798 | Bus: 539114 ID: 1 Name: GEN-2006-021 | 08 N-OK & S-KS | 21S | 50
GEN-2017-086 | 532798 | Bus: 539114 ID: 1 Name: GEN-2006-021 | 08 N-OK & S-KS | 28S | 50
GEN-2017-086 | 532798 | Bus: 578521 ID: 1 Name: GEN-2006-021 | 08 N-OK & S-KS | 19W (Sensitivity A) | 44
GEN-2017-086 | 532798 | Bus: 578521 ID: 1 Name: GEN-2006-021 | 08 N-OK & S-KS | 21L (Sensitivity A) | 44
GEN-2017-086 | 532798 | Bus: 578521 ID: 1 Name: GEN-2006-021 | 08 N-OK & S-KS | 21S | 44
GEN-2017-086 | 532798 | Bus: 578521 ID: 1 Name: GEN-2006-021 | 08 N-OK & S-KS | 28S | 44
GEN-2017-086 | 532798 | Bus: 588637 ID: 1 Name: GEN-2017-018 | 08 N-OK & S-KS | 19W (Sensitivity A) | 94.5
GEN-2017-086 | 532798 | Bus: 588637 ID: 1 Name: GEN-2017-018 | 08 N-OK & S-KS | 21L (Sensitivity A) | 94.5
GEN-2017-086 | 532798 | Bus: 588637 ID: 1 Name: GEN-2017-018 | 08 N-OK & S-KS | 21S | 94.5
GEN-2017-086 | 532798 | Bus: 588637 ID: 1 Name: GEN-2017-018 | 08 N-OK & S-KS | 28S | 94.5
GEN-2017-086 | 532798 | Bus: 588633 ID: 1 Name: GEN-2017-018 | 08 N-OK & S-KS | 19W (Sensitivity A) | 94.5
GEN-2017-086 | 532798 | Bus: 588633 ID: 1 Name: GEN-2017-018 | 08 N-OK & S-KS | 21L (Sensitivity A) | 94.5
GEN-2017-086 | 532798 | Bus: 588633 ID: 1 Name: GEN-2017-018 | 08 N-OK & S-KS | 21S | 94.5
GEN-2017-086 | 532798 | Bus: 588633 ID: 1 Name: GEN-2017-018 | 08 N-OK & S-KS | 28S | 94.5
GEN-2017-040 | 588839 | Bus: 515226 ID: 1 Name: Muskogee | 08 N-OK & S-KS | 19W (Sensitivity A) | 551
GEN-2017-040 | 588839 | Bus: 515226 ID: 1 Name: Muskogee | 08 N-OK & S-KS | 21L (Sensitivity A) | 551
GEN-2017-040 | 588839 | Bus: 515226 ID: 1 Name: Muskogee | 08 N-OK & S-KS | 21S | 551
GEN-2017-040 | 588839 | Bus: 515226 ID: 1 Name: Muskogee | 08 N-OK & S-KS | 28S | 551
GEN-2017-040 | 588839 | Bus: 515225 ID: 1 Name: Muskogee | 08 N-OK & S-KS | 19W (Sensitivity A) | 557
GEN-2017-040 | 588839 | Bus: 515225 ID: 1 Name: Muskogee | 08 N-OK & S-KS | 21L (Sensitivity A) | 557
GEN-2017-040 | 588839 | Bus: 515225 ID: 1 Name: Muskogee | 08 N-OK & S-KS | 21S | 557
GEN-2017-040 | 588839 | Bus: 515225 ID: 1 Name: Muskogee | 08 N-OK & S-KS | 28S | 557
GEN-2017-040 | 588839 | Bus: 515223 ID: 1 Name: Muskogee | 08 N-OK & S-KS | 19W (Sensitivity A) | 567
GEN-2017-040 | 588839 | Bus: 515223 ID: 1 Name: Muskogee | 08 N-OK & S-KS | 21L (Sensitivity A) | 567
GEN-2017-040 | 588839 | Bus: 515223 ID: 1 Name: Muskogee | 08 N-OK & S-KS | 21S | 567
GEN-2017-040 | 588839 | Bus: 515223 ID: 1 Name: Muskogee | 08 N-OK & S-KS | 28S | 567
GEN-2017-060 | 547479 | Bus: 547651 ID: 1 Name: L1G382 | 12 W-ARK | 19W | 82
GEN-2017-060 | 547479 | Bus: 547651 ID: 1 Name: L1G382 | 12 W-ARK | 21L | 82
GEN-2017-060 | 547479 | Bus: 547651 ID: 1 Name: L1G382 | 12 W-ARK | 21S | 82
GEN-2017-060 | 547479 | Bus: 547651 ID: 1 Name: L1G382 | 12 W-ARK | 28S | 0
GEN-2017-060 | 547479 | Bus: 547653 ID: 1 Name: GEN-2001-030/GEN-2016-013 | 12 W-ARK | 19W | 60
GEN-2017-060 | 547479 | Bus: 547653 ID: 1 Name: GEN-2001-030/GEN-2016-013 | 12 W-ARK | 21L | 60
GEN-2017-060 | 547479 | Bus: 547653 ID: 1 Name: GEN-2001-030/GEN-2016-013 | 12 W-ARK | 21S | 60
GEN-2017-060 | 547479 | Bus: 547653 ID: 1 Name: GEN-2001-030/GEN-2016-013 | 12 W-ARK | 28S | 60
GEN-2017-060 | 547479 | Bus: 547652 ID: 1 Name: L3G382 | 12 W-ARK | 19W | 82
GEN-2017-060 | 547479 | Bus: 547652 ID: 1 Name: L3G382 | 12 W-ARK | 21L | 82
GEN-2017-060 | 547479 | Bus: 547652 ID: 1 Name: L3G382 | 12 W-ARK | 21S | 82
GEN-2017-060 | 547479 | Bus: 547652 ID: 1 Name: L3G382 | 12 W-ARK | 28S | 82
GEN-2017-060 | 547479 | Bus: 505490 ID: 1 Name: Carthage | 12 W-ARK | 19W | 20
GEN-2017-060 | 547479 | Bus: 505490 ID: 1 Name: Carthage | 12 W-ARK | 21L | 20
GEN-2017-060 | 547479 | Bus: 505490 ID: 1 Name: Carthage | 12 W-ARK | 21S | 20
GEN-2017-060 | 547479 | Bus: 505490 ID: 1 Name: Carthage | 12 W-ARK | 28S | 20
GEN-2017-060 | 547479 | Bus: 547649 ID: 1 Name: A1G349 | 12 W-ARK | 19W | 198
GEN-2017-060 | 547479 | Bus: 547649 ID: 1 Name: A1G349 | 12 W-ARK | 21L | 198
GEN-2017-060 | 547479 | Bus: 547649 ID: 1 Name: A1G349 | 12 W-ARK | 21S | 198
GEN-2017-060 | 547479 | Bus: 547649 ID: 1 Name: A1G349 | 12 W-ARK | 28S | 198
GEN-2017-076 | 506944 | Bus: 509410 ID: 1 Name: Matison | 12 W-ARK | 19W | 78.8
GEN-2017-076 | 506944 | Bus: 509410 ID: 1 Name: Matison | 12 W-ARK | 21L | 78.8
GEN-2017-076 | 506944 | Bus: 509410 ID: 1 Name: Matison | 12 W-ARK | 21S | 78.8
GEN-2017-076 | 506944 | Bus: 509410 ID: 1 Name: Matison | 12 W-ARK | 28S | 71.8
GEN-2017-076 | 506944 | Bus: 509411 ID: 1 Name: Matison | 12 W-ARK | 19W | 78
GEN-2017-076 | 506944 | Bus: 509411 ID: 1 Name: Matison | 12 W-ARK | 21L | 78
GEN-2017-076 | 506944 | Bus: 509411 ID: 1 Name: Matison | 12 W-ARK | 21S | 78
GEN-2017-076 | 506944 | Bus: 509411 ID: 1 Name: Matison | 12 W-ARK | 28S | 71
GEN-2017-076 | 506944 | Bus: 509412 ID: 1 Name: Matison | 12 W-ARK | 19W | 79.8
GEN-2017-076 | 506944 | Bus: 509412 ID: 1 Name: Matison | 12 W-ARK | 21L | 79.8
GEN-2017-076 | 506944 | Bus: 509412 ID: 1 Name: Matison | 12 W-ARK | 21S | 79.8
GEN-2017-076 | 506944 | Bus: 509412 ID: 1 Name: Matison | 12 W-ARK | 28S | 71.8
GEN-2017-076 | 506944 | Bus: 509413 ID: 1 Name: Matison | 12 W-ARK | 19W | 80
GEN-2017-076 | 506944 | Bus: 509413 ID: 1 Name: Matison | 12 W-ARK | 21L | 80
GEN-2017-076 | 506944 | Bus: 509413 ID: 1 Name: Matison | 12 W-ARK | 21S | 80
GEN-2017-076 | 506944 | Bus: 509413 ID: 1 Name: Matison | 12 W-ARK | 28S | 71
GEN-2017-076 | 506944 | Bus: 509394 ID: 1 Name: Flint Creek | 12 W-ARK | 19W | 562.2
GEN-2017-076 | 506944 | Bus: 509394 ID: 1 Name: Flint Creek | 12 W-ARK | 21L | 562.2
GEN-2017-076 | 506944 | Bus: 509394 ID: 1 Name: Flint Creek | 12 W-ARK | 21S | 562.2
GEN-2017-076 | 506944 | Bus: 509394 ID: 1 Name: Flint Creek | 12 W-ARK | 28S | 562.2
GEN-2017-082 | 547476 | Bus: 588503 ID: 1 Name: GEN-2017-005 | 12 W-ARK | 19W | 195
GEN-2017-082 | 547476 | Bus: 588503 ID: 1 Name: GEN-2017-005 | 12 W-ARK | 21L | 195
GEN-2017-082 | 547476 | Bus: 588503 ID: 1 Name: GEN-2017-005 | 12 W-ARK | 21S | 195
GEN-2017-082 | 547476 | Bus: 588503 ID: 1 Name: GEN-2017-005 | 12 W-ARK | 28S | 195
GEN-2017-082 | 547476 | Bus: 533774 ID: 1 Name: sheffield | 12 W-ARK | 19W | 1.6
GEN-2017-082 | 547476 | Bus: 533774 ID: 1 Name: sheffield | 12 W-ARK | 21L | 1.6
GEN-2017-082 | 547476 | Bus: 533774 ID: 1 Name: sheffield | 12 W-ARK | 21S | 1.6
GEN-2017-082 | 547476 | Bus: 533774 ID: 1 Name: sheffield | 12 W-ARK | 28S | 1.6
GEN-2017-082 | 547476 | Bus: 533774 ID: 2 Name: sheffield | 12 W-ARK | 19W | 1.95
GEN-2017-082 | 547476 | Bus: 533774 ID: 2 Name: sheffield | 12 W-ARK | 21L | 1.95
GEN-2017-082 | 547476 | Bus: 533774 ID: 2 Name: sheffield | 12 W-ARK | 21S | 1.95
GEN-2017-082 | 547476 | Bus: 533774 ID: 2 Name: sheffield | 12 W-ARK | 28S | 1.95
GEN-2017-082 | 547476 | Bus: 547651 ID: 1 Name: L1G382 | 12 W-ARK | 19W | 82
GEN-2017-082 | 547476 | Bus: 547651 ID: 1 Name: L1G382 | 12 W-ARK | 21L | 82
GEN-2017-082 | 547476 | Bus: 547651 ID: 1 Name: L1G382 | 12 W-ARK | 21S | 82
GEN-2017-082 | 547476 | Bus: 547651 ID: 1 Name: L1G382 | 12 W-ARK | 28S | 0
GEN-2017-082 | 547476 | Bus: 547653 ID: 1 Name: L2G382 | 12 W-ARK | 19W | 60
GEN-2017-082 | 547476 | Bus: 547653 ID: 1 Name: L2G382 | 12 W-ARK | 21L | 60
GEN-2017-082 | 547476 | Bus: 547653 ID: 1 Name: L2G382 | 12 W-ARK | 21S | 60
GEN-2017-082 | 547476 | Bus: 547653 ID: 1 Name: L2G382 | 12 W-ARK | 28S | 60
GEN-2017-082 | 547476 | Bus: 547652 ID: 1 Name: L3G382 | 12 W-ARK | 19W | 82
GEN-2017-082 | 547476 | Bus: 547652 ID: 1 Name: L3G382 | 12 W-ARK | 21L | 82
GEN-2017-082 | 547476 | Bus: 547652 ID: 1 Name: L3G382 | 12 W-ARK | 21S | 82
GEN-2017-082 | 547476 | Bus: 547652 ID: 1 Name: L3G382 | 12 W-ARK | 28S | 82
GEN-2017-082 | 547476 | Bus: 547654 ID: 1 Name: G01-030&040_G16-013&-14 | 12 W-ARK | 19W | 60
GEN-2017-082 | 547476 | Bus: 547654 ID: 1 Name: G01-030&040_G16-013&-14 | 12 W-ARK | 21L | 60
GEN-2017-082 | 547476 | Bus: 547654 ID: 1 Name: G01-030&040_G16-013&-14 | 12 W-ARK | 21S | 60
GEN-2017-082 | 547476 | Bus: 547654 ID: 1 Name: G01-030&040_G16-013&-14 | 12 W-ARK | 28S | 60
GEN-2017-082 | 547476 | Bus: 505490 ID: 1 Name: Carthage | 12 W-ARK | 19W | 20
GEN-2017-082 | 547476 | Bus: 505490 ID: 1 Name: Carthage | 12 W-ARK | 21L | 20
GEN-2017-082 | 547476 | Bus: 505490 ID: 1 Name: Carthage | 12 W-ARK | 21S | 20
GEN-2017-082 | 547476 | Bus: 505490 ID: 1 Name: Carthage | 12 W-ARK | 28S | 20
GEN-2017-082 | 547476 | Bus: 533761 ID: 1 Name: Girard | 12 W-ARK | 19W | 1.4
GEN-2017-082 | 547476 | Bus: 533761 ID: 1 Name: Girard | 12 W-ARK | 21L | 1.4
GEN-2017-082 | 547476 | Bus: 533761 ID: 1 Name: Girard | 12 W-ARK | 21S | 1.4
GEN-2017-082 | 547476 | Bus: 533761 ID: 1 Name: Girard | 12 W-ARK | 28S | 1.4
GEN-2017-082 | 547476 | Bus: 533761 ID: 4 Name: Girard | 12 W-ARK | 19W | 2
GEN-2017-082 | 547476 | Bus: 533761 ID: 4 Name: Girard | 12 W-ARK | 21L | 2
GEN-2017-082 | 547476 | Bus: 533761 ID: 4 Name: Girard | 12 W-ARK | 21S | 2
GEN-2017-082 | 547476 | Bus: 533761 ID: 4 Name: Girard | 12 W-ARK | 28S | 2
GEN-2017-082 | 547476 | Bus: 533761 ID: 6 Name: Girard | 12 W-ARK | 19W | 3.5
GEN-2017-082 | 547476 | Bus: 533761 ID: 6 Name: Girard | 12 W-ARK | 21L | 3.5
GEN-2017-082 | 547476 | Bus: 533761 ID: 6 Name: Girard | 12 W-ARK | 21S | 3.5
GEN-2017-082 | 547476 | Bus: 533761 ID: 6 Name: Girard | 12 W-ARK | 28S | 3.5
GEN-2017-082 | 547476 | Bus: 533761 ID: 7 Name: Girard | 12 W-ARK | 19W | 3.8
GEN-2017-082 | 547476 | Bus: 533761 ID: 7 Name: Girard | 12 W-ARK | 21L | 3.8
GEN-2017-082 | 547476 | Bus: 533761 ID: 7 Name: Girard | 12 W-ARK | 21S | 3.8
GEN-2017-082 | 547476 | Bus: 533761 ID: 7 Name: Girard | 12 W-ARK | 28S | 3.8
GEN-2017-082 | 547476 | Bus: 547658 ID: 1 Name: Stateline | 12 W-ARK | 19W | 188
GEN-2017-082 | 547476 | Bus: 547658 ID: 1 Name: Stateline | 12 W-ARK | 21L | 188
GEN-2017-082 | 547476 | Bus: 547658 ID: 1 Name: Stateline | 12 W-ARK | 21S | 188
GEN-2017-082 | 547476 | Bus: 547658 ID: 1 Name: Stateline | 12 W-ARK | 28S | 188
GEN-2017-082 | 547476 | Bus: 547656 ID: 1 Name: Stateline | 12 W-ARK | 19W | 167
GEN-2017-082 | 547476 | Bus: 547656 ID: 1 Name: Stateline | 12 W-ARK | 21L | 167
GEN-2017-082 | 547476 | Bus: 547656 ID: 1 Name: Stateline | 12 W-ARK | 21S | 167
GEN-2017-082 | 547476 | Bus: 547656 ID: 1 Name: Stateline | 12 W-ARK | 28S | 167
GEN-2017-082 | 547476 | Bus: 547657 ID: 1 Name: Stateline | 12 W-ARK | 19W | 173
GEN-2017-082 | 547476 | Bus: 547657 ID: 1 Name: Stateline | 12 W-ARK | 21L | 173
GEN-2017-082 | 547476 | Bus: 547657 ID: 1 Name: Stateline | 12 W-ARK | 21S | 173
GEN-2017-082 | 547476 | Bus: 547657 ID: 1 Name: Stateline | 12 W-ARK | 28S | 173
GEN-2017-082 | 547476 | Bus: 547655 ID: 1 Name: Stateline | 12 W-ARK | 19W | 94
GEN-2017-082 | 547476 | Bus: 547655 ID: 1 Name: Stateline | 12 W-ARK | 21L | 94
GEN-2017-082 | 547476 | Bus: 547655 ID: 1 Name: Stateline | 12 W-ARK | 21S | 94
GEN-2017-082 | 547476 | Bus: 547655 ID: 1 Name: Stateline | 12 W-ARK | 28S | 94
GEN-2017-082 | 547476 | Bus: 547655 ID: 1 Name: Stateline | 12 W-ARK | 19W | 94
GEN-2017-082 | 547476 | Bus: 547655 ID: 1 Name: Stateline | 12 W-ARK | 21L | 94
GEN-2017-082 | 547476 | Bus: 547655 ID: 1 Name: Stateline | 12 W-ARK | 21S | 94
GEN-2017-082 | 547476 | Bus: 547655 ID: 1 Name: Stateline | 12 W-ARK | 28S | 94
GEN-2017-030 | 588736 | Bus: 541171 ID: 1 Name: Lakeridge | 13 NE-KS & NW-MO | 19W | 20.4
GEN-2017-030 | 588736 | Bus: 541171 ID: 1 Name: Lakeridge | 13 NE-KS & NW-MO | 21L | 20.4
GEN-2017-030 | 588736 | Bus: 541171 ID: 1 Name: Lakeridge | 13 NE-KS & NW-MO | 21S | 20.4
GEN-2017-030 | 588736 | Bus: 541171 ID: 1 Name: Lakeridge | 13 NE-KS & NW-MO | 28S | 20.4
GEN-2017-030 | 588736 | Bus: 541172 ID: 2 Name: Lakeridge | 13 NE-KS & NW-MO | 19W | 21.9
GEN-2017-030 | 588736 | Bus: 541172 ID: 2 Name: Lakeridge | 13 NE-KS & NW-MO | 21L | 21.9
GEN-2017-030 | 588736 | Bus: 541172 ID: 2 Name: Lakeridge | 13 NE-KS & NW-MO | 21S | 21.9
GEN-2017-030 | 588736 | Bus: 541172 ID: 2 Name: Lakeridge | 13 NE-KS & NW-MO | 28S | 21.9
GEN-2017-030 | 588736 | Bus: 541173 ID: 3 Name: Lakeridge | 13 NE-KS & NW-MO | 19W | 13.1
GEN-2017-030 | 588736 | Bus: 541173 ID: 3 Name: Lakeridge | 13 NE-KS & NW-MO | 21L | 13.1
GEN-2017-030 | 588736 | Bus: 541173 ID: 3 Name: Lakeridge | 13 NE-KS & NW-MO | 21S | 13.1
GEN-2017-030 | 588736 | Bus: 541173 ID: 3 Name: Lakeridge | 13 NE-KS & NW-MO | 28S | 13.1
GEN-2017-030 | 588736 | Bus: 541175 ID: 5 Name: Lakeridge | 13 NE-KS & NW-MO | 19W | 69.4
GEN-2017-030 | 588736 | Bus: 541175 ID: 5 Name: Lakeridge | 13 NE-KS & NW-MO | 21L | 69.4
GEN-2017-030 | 588736 | Bus: 541175 ID: 5 Name: Lakeridge | 13 NE-KS & NW-MO | 21S | 69.4
GEN-2017-030 | 588736 | Bus: 541175 ID: 5 Name: Lakeridge | 13 NE-KS & NW-MO | 28S | 69.4
GEN-2017-030 | 588736 | Bus: 541176 ID: 6 Name: Lakeridge | 13 NE-KS & NW-MO | 19W | 20.9
GEN-2017-030 | 588736 | Bus: 541176 ID: 6 Name: Lakeridge | 13 NE-KS & NW-MO | 21L | 20.9
GEN-2017-030 | 588736 | Bus: 541176 ID: 6 Name: Lakeridge | 13 NE-KS & NW-MO | 21S | 20.9
GEN-2017-030 | 588736 | Bus: 541176 ID: 6 Name: Lakeridge | 13 NE-KS & NW-MO | 28S | 20.9
GEN-2017-030 | 588736 | Bus: 541177 ID: 7 Name: Lakeridge | 13 NE-KS & NW-MO | 19W | 20.4
GEN-2017-030 | 588736 | Bus: 541177 ID: 7 Name: Lakeridge | 13 NE-KS & NW-MO | 21L | 20.4
GEN-2017-030 | 588736 | Bus: 541177 ID: 7 Name: Lakeridge | 13 NE-KS & NW-MO | 21S | 20.4
GEN-2017-030 | 588736 | Bus: 541177 ID: 7 Name: Lakeridge | 13 NE-KS & NW-MO | 28S | 20.4
GEN-2017-030 | 588736 | Bus: 542962 ID: 2 Name: GEN-2011-011 | 13 NE-KS & NW-MO | 19W | 954.5
GEN-2017-030 | 588736 | Bus: 542962 ID: 2 Name: GEN-2011-011 | 13 NE-KS & NW-MO | 21L | 954.5
GEN-2017-030 | 588736 | Bus: 542962 ID: 2 Name: GEN-2011-011 | 13 NE-KS & NW-MO | 21S | 954.5
GEN-2017-030 | 588736 | Bus: 542962 ID: 2 Name: GEN-2011-011 | 13 NE-KS & NW-MO | 28S | 954.5
GEN-2017-030 | 588736 | Bus: 640009 ID: 1 Name: Cooper | 13 NE-KS & NW-MO | 19W | 874.4
GEN-2017-030 | 588736 | Bus: 640009 ID: 1 Name: Cooper | 13 NE-KS & NW-MO | 21L | 874.4
GEN-2017-030 | 588736 | Bus: 640009 ID: 1 Name: Cooper | 13 NE-KS & NW-MO | 21S | 874.4
GEN-2017-030 | 588736 | Bus: 640009 ID: 1 Name: Cooper | 13 NE-KS & NW-MO | 28S | 874.4
GEN-2017-090 | 541240 | Bus: 541167 ID: 3 Name: S Harp | 13 NE-KS & NW-MO | 19W | 96.7
GEN-2017-090 | 541240 | Bus: 541167 ID: 3 Name: S Harp | 13 NE-KS & NW-MO | 21L | 96.7
GEN-2017-090 | 541240 | Bus: 541167 ID: 3 Name: S Harp | 13 NE-KS & NW-MO | 21S | 96.7
GEN-2017-090 | 541240 | Bus: 541167 ID: 3 Name: S Harp | 13 NE-KS & NW-MO | 28S | 96.7
GEN-2017-090 | 541240 | Bus: 541166 ID: 2 Name: S Harp | 13 NE-KS & NW-MO | 19W | 97.5
GEN-2017-090 | 541240 | Bus: 541166 ID: 2 Name: S Harp | 13 NE-KS & NW-MO | 21L | 97.5
GEN-2017-090 | 541240 | Bus: 541166 ID: 2 Name: S Harp | 13 NE-KS & NW-MO | 21S | 97.5
GEN-2017-090 | 541240 | Bus: 541166 ID: 2 Name: S Harp | 13 NE-KS & NW-MO | 28S | 97.5
GEN-2017-090 | 541240 | Bus: 541165 ID: 1 Name: S Harp | 13 NE-KS & NW-MO | 19W | 97.9
GEN-2017-090 | 541240 | Bus: 541165 ID: 1 Name: S Harp | 13 NE-KS & NW-MO | 21L | 97.9
GEN-2017-090 | 541240 | Bus: 541165 ID: 1 Name: S Harp | 13 NE-KS & NW-MO | 21S | 97.9
GEN-2017-090 | 541240 | Bus: 541165 ID: 1 Name: S Harp | 13 NE-KS & NW-MO | 28S | 97.9
GEN-2017-090 | 541240 | Bus: 541159 ID: 1 Name: Nevada | 13 NE-KS & NW-MO | 19W | 19.4
GEN-2017-090 | 541240 | Bus: 541159 ID: 1 Name: Nevada | 13 NE-KS & NW-MO | 21L | 19.4
GEN-2017-090 | 541240 | Bus: 541159 ID: 1 Name: Nevada | 13 NE-KS & NW-MO | 21S | 19.4
GEN-2017-090 | 541240 | Bus: 541159 ID: 1 Name: Nevada | 13 NE-KS & NW-MO | 28S | 19.4
GEN-2017-090 | 541240 | Bus: 300690 ID: 1 Name: Butlere | 13 NE-KS & NW-MO | 19W | 11.6
GEN-2017-090 | 541240 | Bus: 300690 ID: 1 Name: Butlere | 13 NE-KS & NW-MO | 21L | 11.6
GEN-2017-090 | 541240 | Bus: 300690 ID: 1 Name: Butlere | 13 NE-KS & NW-MO | 21S | 11.6
GEN-2017-090 | 541240 | Bus: 300690 ID: 1 Name: Butlere | 13 NE-KS & NW-MO | 28S | 11.6
GEN-2016-159 | 635213 | NEAL 3G | 09 - Nebraska | ALL | 544
GEN-2016-159 | 635214 | NEAL 4G | 09 - Nebraska | ALL | 715.1

## Short Circuit Analysis
Gen Number | Region | Group | Bus Number | Bus Name | Bus Voltage (kV) | Request Not In Service 28SP Fault Current 3-Phase (kA) | Request In Service 28SP Fault Current 3-Phase (kA) | Change in Fault Current (kA) | Circuit Breakers Exceeding Capacity | Facilities Required to Interconnect
GEN-2017-013 | North | 04 - Northwest Kansas | 531451 | MINGO 7 | 345 | 6.65 | 6.92 | 0.27
GEN-2017-013 | North | 04 - Northwest Kansas | 531632 | GEN-2016-067 | 345 | 6.65 | 6.92 | 0.27
GEN-2017-013 | North | 04 - Northwest Kansas | 588580 | GEN-2017-013 | 345 | 6.586 | 6.856 | 0.27
GEN-2017-004 | North | 04 - Northwest Kansas | 588490 | GEN-2017-004 | 345 | 7.781 | 8.044 | 0.263
GEN-2017-004 | North | 04 - Northwest Kansas | 588494 | G17-004-TAP | 345 | 9.842 | 10.057 | 0.215
GEN-2017-013 | North | 04 - Northwest Kansas | 531429 | MINGO 3 | 115 | 12.977 | 13.19 | 0.213
GEN-2017-013 | North | 04 - Northwest Kansas | 585030 | GEN-2015-065 | 345 | 6.022 | 6.232 | 0.21
GEN-2017-004 | North | 04 - Northwest Kansas | 532773 | SUMMIT 7 | 345 | 11.842 | 12.038 | 0.196
GEN-2017-013 | North | 04 - Northwest Kansas | 585020 | GEN-2015-064 | 115 | 10.189 | 10.297 | 0.108
GEN-2017-004 | North | 04 - Northwest Kansas | 587894 | G16-112-TAP | 345 | 10.96 | 11.045 | 0.085
GEN-2017-004 | North | 04 - Northwest Kansas | 532873 | SUMMIT 6 | 230 | 14.501 | 14.573 | 0.072
GEN-2017-013 | North | 04 - Northwest Kansas | 531465 | SETAB 7 | 345 | 7.153 | 7.219 | 0.066
GEN-2017-013 | North | 04 - Northwest Kansas | 640325 | REDWILO3 | 345 | 9.465 | 9.515 | 0.05
GEN-2017-004 | North | 04 - Northwest Kansas | 587884 | G16-111-TAP | 345 | 11.222 | 11.262 | 0.04
GEN-2017-004 | North | 04 - Northwest Kansas | 533381 | SUMMIT 3 | 115 | 18.425 | 18.459 | 0.034
GEN-2017-004 | North | 04 - Northwest Kansas | 539805 | ELMCREEK7 | 345 | 6.021 | 6.054 | 0.033
GEN-2017-004 | North | 04 - Northwest Kansas | 587910 | GEN-2016-114 | 345 | 10.034 | 10.062 | 0.028
GEN-2017-004 | North | 04 - Northwest Kansas | 532767 | GEARY 7 | 345 | 10.354 | 10.382 | 0.028
GEN-2017-004 | North | 04 - Northwest Kansas | 539639 | ELMCREK6 | 230 | 8.401 | 8.422 | 0.021
GEN-2017-013 | North | 04 - Northwest Kansas | 531449 | HOLCOMB7 | 345 | 10.027 | 10.047 | 0.02
GEN-2017-013 | North | 04 - Northwest Kansas | 640096 | CALAMS 7 | 115 | 3.459 | 3.478 | 0.019
GEN-2017-013 | North | 04 - Northwest Kansas | 523853 | FINNEY 7 | 345 | 9.916 | 9.934 | 0.018
GEN-2017-004 | North | 04 - Northwest Kansas | 587980 | GEN-2016-122 | 345 | 5.164 | 5.173 | 0.009
GEN-2017-004 | North | 04 - Northwest Kansas | 532766 | JEC N 7 | 345 | 23.952 | 23.961 | 0.009
GEN-2017-013 | North | 04 - Northwest Kansas | 640183 | GENTLMN3 | 345 | 18.223 | 18.231 | 0.008
GEN-2017-004 | North | 04 - Northwest Kansas | 532771 | RENO 7 | 345 | 12.577 | 12.584 | 0.007
GEN-2017-004 | North | 04 - Northwest Kansas | 530599 | SMKYP2 6 | 230 | 6.655 | 6.662 | 0.007
GEN-2017-004 | North | 04 - Northwest Kansas | 530592 | SMOKYHL6 | 230 | 7.182 | 7.189 | 0.007
GEN-2017-004 | North | 04 - Northwest Kansas | 587890 | GEN-2016-112 | 345 | 4.64 | 4.646 | 0.006
GEN-2017-004 | North | 04 - Northwest Kansas | 530593 | SMKYP1 6 | 230 | 6.219 | 6.225 | 0.006
GEN-2017-004 | North | 04 - Northwest Kansas | 539637 | MRWYP16 | 230 | 7.502 | 7.507 | 0.005
GEN-2017-013 | North | 04 - Northwest Kansas | 530561 | KNOLL 3 | 115 | 12.462 | 12.467 | 0.005
GEN-2017-004 | North | 04 - Northwest Kansas | 533372 | PHILIPS3 | 115 | 12.958 | 12.961 | 0.003
GEN-2017-004 | North | 04 - Northwest Kansas | 587880 | GEN-2016-111 | 345 | 7.094 | 7.096 | 0.002
GEN-2017-004 | North | 04 - Northwest Kansas | 533368 | EXIDE J3 | 115 | 12.898 | 12.9 | 0.002
GEN-2017-004 | North | 04 - Northwest Kansas | 532852 | JEC 6 | 230 | 25.007 | 25.008 | 0.001
GEN-2017-013 | North | 04 - Northwest Kansas | 530558 | KNOLL 6 | 230 | 12.968 | 12.969 | 0.001
GEN-2017-013 | North | 04 - Northwest Kansas | 530584 | POSTROCK6 | 230 | 13.109 | 13.11 | 0.001
GEN-2017-013 | North | 04 - Northwest Kansas | 640252 | KEYSTON3 | 345 | 12.888 | 12.889 | 0.001
GEN-2017-013 | North | 04 - Northwest Kansas | 659131 | LARAMIE_-MB3 | 345 | 7.239 | 7.24 | 0.001
GEN-2017-004 | North | 04 - Northwest Kansas | 539658 | CONCRD6 | 230 | 5.917 | 5.917 | 0
GEN-2017-004 | North | 04 - Northwest Kansas | 532872 | EMCPHER6 | 230 | 9.37 | 9.37 | 0
GEN-2017-004 | North | 04 - Northwest Kansas | 530561 | KNOLL 3 | 115 | 12.467 | 12.467 | 0
GEN-2017-013 | North | 04 - Northwest Kansas | 530555 | COLBY 3 | 115 | 6.163 | 6.163 | 0
GEN-2017-004 | North | 04 - Northwest Kansas | 533371 | NORTHVW3 | 115 | 12.079 | 12.078 | -0.001
GEN-2017-013 | North | 04 - Northwest Kansas | 587874 | G16-110-TAP | 345 | 6.44 | 6.439 | -0.001
GEN-2017-004 | North | 04 - Northwest Kansas | 539634 | MRWYP26 | 230 | 6.334 | 6.332 | -0.002
GEN-2017-004 | North | 04 - Northwest Kansas | 533379 | SO GATE3 | 115 | 11.06 | 11.058 | -0.002
GEN-2017-004 | North | 04 - Northwest Kansas | 533378 | SMOKYHLLS3 | 115 | 11.533 | 11.531 | -0.002
GEN-2017-013 | North | 04 - Northwest Kansas | 530702 | BUCKEYE_230 | 230 | 9.42 | 9.418 | -0.002
GEN-2017-013 | North | 04 - Northwest Kansas | 531501 | BUCKNER7 | 345 | 9.195 | 9.193 | -0.002
GEN-2017-004 | North | 04 - Northwest Kansas | 533336 | GEARY 3 | 115 | 19.209 | 19.206 | -0.003
GEN-2017-013 | North | 04 - Northwest Kansas | 530553 | S HAYS 3 | 115 | 9.335 | 9.332 | -0.003
GEN-2017-013 | North | 04 - Northwest Kansas | 530582 | S HAYS6 | 230 | 9.882 | 9.879 | -0.003
GEN-2017-013 | North | 04 - Northwest Kansas | 530583 | POSTROCK7 | 345 | 9.904 | 9.901 | -0.003
GEN-2017-013 | North | 04 - Northwest Kansas | 531469 | SPERVIL7 | 345 | 13.944 | 13.941 | -0.003
GEN-2017-013 | North | 04 - Northwest Kansas | 640184 | GENTLMN4 | 230 | 20.104 | 20.101 | -0.003
GEN-2017-004 | North | 04 - Northwest Kansas | 533370 | NORTHST3 | 115 | 10.788 | 10.784 | -0.004
GEN-2017-004 | North | 04 - Northwest Kansas | 533367 | EXIDE 3 | 115 | 10.891 | 10.887 | -0.004
GEN-2017-013 | North | 04 - Northwest Kansas | 530610 | SHAYS_230 | 230 | 4.193 | 4.189 | -0.004
GEN-2017-013 | North | 04 - Northwest Kansas | 539803 | IRONWOOD7 | 345 | 13.347 | 13.343 | -0.004
GEN-2017-013 | North | 04 - Northwest Kansas | 588650 | GEN-2017-021 | 345 | 9.841 | 9.837 | -0.004
GEN-2017-013 | North | 04 - Northwest Kansas | 588654 | G17-021-TAP | 345 | 10.308 | 10.304 | -0.004
GEN-2017-013 | North | 04 - Northwest Kansas | 589370 | GEN-2017-099 | 345 | 9.833 | 9.829 | -0.004
GEN-2017-013 | North | 04 - Northwest Kansas | 589484 | G16-049-TAP | 345 | 9.066 | 9.062 | -0.004
GEN-2017-013 | North | 04 - Northwest Kansas | 659135 | STEGALL_-MB3 | 345 | 5.334 | 5.33 | -0.004
GEN-2017-004 | North | 04 - Northwest Kansas | 532875 | GEN-2015-06 | 9230 | 6.636 | 6.631 | -0.005
GEN-2017-004 | North | 04 - Northwest Kansas | 532874 | UNIONRG6 | 230 | 9.047 | 9.042 | -0.005
GEN-2017-013 | North | 04 - Northwest Kansas | 640359 | STAPLETON 7 | 115 | 4.217 | 4.212 | -0.005
GEN-2017-013 | North | 04 - Northwest Kansas | 640381 | THEDFRD7 | 115 | 9.079 | 9.074 | -0.005
GEN-2017-013 | North | 04 - Northwest Kansas | 659133 | SIDNEY__-MB3 | 345 | 7.866 | 7.861 | -0.005
GEN-2017-013 | North | 04 - Northwest Kansas | 659425 | SD.LS-KS-MB3 | 345 | 7.866 | 7.861 | -0.005
GEN-2017-013 | North | 04 - Northwest Kansas | 659426 | SD.LS-LR-MB3 | 345 | 7.866 | 7.861 | -0.005
GEN-2017-004 | North | 04 - Northwest Kansas | 539679 | GRTBEND6 | 230 | 8.67 | 8.664 | -0.006
GEN-2017-004 | North | 04 - Northwest Kansas | 533417 | EMCPHER3 | 115 | 15.19 | 15.184 | -0.006
GEN-2017-004 | North | 04 - Northwest Kansas | 533360 | TCHOPE 3 | 115 | 3.427 | 3.421 | -0.006
GEN-2017-004 | North | 04 - Northwest Kansas | 532796 | WICHITA7 | 345 | 24.716 | 24.71 | -0.006
GEN-2017-013 | North | 04 - Northwest Kansas | 531504 | CIMWD2 7 | 345 | 7.323 | 7.317 | -0.006
GEN-2017-013 | North | 04 - Northwest Kansas | 539695 | SPEARVL6 | 230 | 12.742 | 12.736 | -0.006
GEN-2017-013 | North | 04 - Northwest Kansas | 640520 | ANTELOPE 3 | 345 | 8.955 | 8.949 | -0.006
GEN-2017-004 | North | 04 - Northwest Kansas | 539669 | JEWELL 3 | 115 | 3.152 | 3.145 | -0.007
GEN-2017-004 | North | 04 - Northwest Kansas | 539657 | CONCORD3 | 115 | 7.642 | 7.635 | -0.007
GEN-2017-004 | North | 04 - Northwest Kansas | 533427 | REFINRY3 | 115 | 14.624 | 14.617 | -0.007
GEN-2017-004 | North | 04 - Northwest Kansas | 533359 | UNIONRG3 | 115 | 3.86 | 3.853 | -0.007
GEN-2017-004 | North | 04 - Northwest Kansas | 532871 | CIRCLE 6 | 230 | 10.053 | 10.046 | -0.007
GEN-2017-013 | North | 04 - Northwest Kansas | 530592 | SMOKYHL6 | 230 | 7.189 | 7.182 | -0.007
GEN-2017-013 | North | 04 - Northwest Kansas | 531502 | CIMRRN 7 | 345 | 7.322 | 7.315 | -0.007
GEN-2017-013 | North | 04 - Northwest Kansas | 659134 | SIDNEY___TS4 | 230 | 7.119 | 7.112 | -0.007
GEN-2017-004 | North | 04 - Northwest Kansas | 539650 | BELOIT 3 | 115 | 3.217 | 3.209 | -0.008
GEN-2017-004 | North | 04 - Northwest Kansas | 533426 | MANVILE3 | 115 | 11.693 | 11.685 | -0.008
GEN-2017-004 | North | 04 - Northwest Kansas | 530686 | RICE 6 | 230 | 4.928 | 4.92 | -0.008
GEN-2017-004 | North | 04 - Northwest Kansas | 530584 | POSTROCK6 | 230 | 13.11 | 13.102 | -0.008
GEN-2017-004 | North | 04 - Northwest Kansas | 530558 | KNOLL 6 | 230 | 12.969 | 12.961 | -0.008
GEN-2017-013 | North | 04 - Northwest Kansas | 523118 | BUFF_DUNES 7 | 345 | 6.155 | 6.147 | -0.008
GEN-2017-013 | North | 04 - Northwest Kansas | 539679 | GRTBEND6 | 230 | 8.678 | 8.67 | -0.008
GEN-2017-013 | North | 04 - Northwest Kansas | 640302 | OGALALA4 | 230 | 8.235 | 8.227 | -0.008
GEN-2017-013 | North | 04 - Northwest Kansas | 640500 | THEDFRD3 | 345 | 5.422 | 5.414 | -0.008
GEN-2017-013 | North | 04 - Northwest Kansas | 652832 | GRPRAR1-LNX3 | 345 | 8.138 | 8.13 | -0.008
GEN-2017-013 | North | 04 - Northwest Kansas | 659210 | SIDNEY__-MB4 | 230 | 7.795 | 7.787 | -0.008
GEN-2017-004 | North | 04 - Northwest Kansas | 533323 | CLAYCTR3 | 115 | 2.995 | 2.986 | -0.009
GEN-2017-013 | North | 04 - Northwest Kansas | 640101 | CAMBRIG8 | 69 | 2.322 | 2.313 | -0.009
GEN-2017-013 | North | 04 - Northwest Kansas | 640238 | JEFFREY7 | 115 | 6.179 | 6.17 | -0.009
GEN-2017-013 | North | 04 - Northwest Kansas | 640288 | N.PLATT8 | 69 | 5.255 | 5.246 | -0.009
GEN-2017-013 | North | 04 - Northwest Kansas | 641244 | ATHEY 7 | 115 | 3.214 | 3.205 | -0.009
GEN-2017-004 | North | 04 - Northwest Kansas | 532865 | NMANHT6 | 230 | 9.287 | 9.277 | -0.01
GEN-2017-004 | North | 04 - Northwest Kansas | 532861 | EMANHAT6 | 230 | 10.179 | 10.169 | -0.01
GEN-2017-013 | North | 04 - Northwest Kansas | 531423 | GARDNCY2 | 69 | 3.566 | 3.556 | -0.01
GEN-2017-013 | North | 04 - Northwest Kansas | 584650 | GEN-2015-023 | 345 | 8.9 | 8.89 | -0.01
GEN-2017-013 | North | 04 - Northwest Kansas | 587350 | GEN-2016-050 | 345 | 6.555 | 6.545 | -0.01
GEN-2017-013 | North | 04 - Northwest Kansas | 587850 | GEN-2016-106 | 345 | 9.047 | 9.037 | -0.01
GEN-2017-013 | North | 04 - Northwest Kansas | 640168 | ENDERS 8 | 69 | 3.187 | 3.177 | -0.01
GEN-2017-013 | North | 04 - Northwest Kansas | 640267 | MAXWELS7 | 115 | 6.785 | 6.775 | -0.01
GEN-2017-004 | North | 04 - Northwest Kansas | 532862 | MCDOWEL6 | 230 | 7.083 | 7.072 | -0.011
GEN-2017-004 | North | 04 - Northwest Kansas | 532770 | MORRIS 7 | 345 | 12.928 | 12.917 | -0.011
GEN-2017-013 | North | 04 - Northwest Kansas | 560082 | G16-050-TAP | 345 | 7.303 | 7.292 | -0.011
GEN-2017-013 | North | 04 - Northwest Kansas | 588750 | GEN-2017-032 | 345 | 3.166 | 3.155 | -0.011
GEN-2017-013 | North | 04 - Northwest Kansas | 588754 | G17-032-TAP | 345 | 3.166 | 3.155 | -0.011
GEN-2017-013 | North | 04 - Northwest Kansas | 599950 | LAMAR7 | 345 | 2.559 | 2.548 | -0.011
GEN-2017-013 | North | 04 - Northwest Kansas | 640167 | ENDERS 7 | 115 | 3.957 | 3.946 | -0.011
GEN-2017-013 | North | 04 - Northwest Kansas | 640510 | HOLT.CO3 | 345 | 9.969 | 9.958 | -0.011
GEN-2017-004 | North | 04 - Northwest Kansas | 533361 | AEC 3 | 115 | 7.732 | 7.72 | -0.012
GEN-2017-013 | North | 04 - Northwest Kansas | 539759 | SPRVL 3 | 115 | 11.866 | 11.854 | -0.012
GEN-2017-013 | North | 04 - Northwest Kansas | 640271 | MCCOOL 3 | 345 | 10.686 | 10.674 | -0.012
GEN-2017-013 | North | 04 - Northwest Kansas | 640286 | N.PLATT4 | 230 | 13.479 | 13.467 | -0.012
GEN-2017-013 | North | 04 - Northwest Kansas | 659800 | GRANTNB_-TS7 | 115 | 6.634 | 6.622 | -0.012
GEN-2017-004 | North | 04 - Northwest Kansas | 533365 | EABILEN3 | 115 | 7.945 | 7.932 | -0.013
GEN-2017-004 | North | 04 - Northwest Kansas | 532768 | EMPEC 7 | 345 | 17.587 | 17.574 | -0.013
GEN-2017-013 | North | 04 - Northwest Kansas | 640312 | PAULINE3 | 345 | 8.66 | 8.647 | -0.013
GEN-2017-013 | North | 04 - Northwest Kansas | 640366 | STOCKVL8 | 69 | 3.43 | 3.417 | -0.013
GEN-2017-004 | North | 04 - Northwest Kansas | 539656 | CLIFTON3 | 115 | 4.775 | 4.761 | -0.014
GEN-2017-013 | North | 04 - Northwest Kansas | 530557 | BEACH 3 | 115 | 3.743 | 3.729 | -0.014
GEN-2017-013 | North | 04 - Northwest Kansas | 531409 | ARNOLD3 | 115 | 2.744 | 2.73 | -0.014
GEN-2017-013 | North | 04 - Northwest Kansas | 531464 | SETAB 3 | 115 | 10.504 | 10.49 | -0.014
GEN-2017-013 | North | 04 - Northwest Kansas | 640093 | C.CREEK4 | 230 | 7.118 | 7.104 | -0.014
GEN-2017-013 | North | 04 - Northwest Kansas | 640255 | KINGSLY7 | 115 | 9.852 | 9.838 | -0.014
GEN-2017-004 | North | 04 - Northwest Kansas | 533362 | CHAPMAN3 | 115 | 11.156 | 11.141 | -0.015
GEN-2017-004 | North | 04 - Northwest Kansas | 533328 | FT JCT 3 | 115 | 15.293 | 15.278 | -0.015
GEN-2017-013 | North | 04 - Northwest Kansas | 531444 | GOODCTY3 | 115 | 2.161 | 2.146 | -0.015
GEN-2017-013 | North | 04 - Northwest Kansas | 640194 | GOSPER 7 | 115 | 4.5 | 4.485 | -0.015
GEN-2017-004 | North | 04 - Northwest Kansas | 533413 | CIRCLE 3 | 115 | 23.732 | 23.716 | -0.016
GEN-2017-004 | North | 04 - Northwest Kansas | 533344 | WJCCTYW3 | 115 | 13.664 | 13.648 | -0.016
GEN-2017-013 | North | 04 - Northwest Kansas | 531360 | DIGHTNT3 | 115 | 3.629 | 3.613 | -0.016
GEN-2017-013 | North | 04 - Northwest Kansas | 531408 | PIERCVL3 | 115 | 3.861 | 3.845 | -0.016
GEN-2017-013 | North | 04 - Northwest Kansas | 531411 | GOVE 3 | 115 | 2.808 | 2.792 | -0.016
GEN-2017-013 | North | 04 - Northwest Kansas | 531443 | GODLNDT3 | 115 | 2.692 | 2.676 | -0.016
GEN-2017-013 | North | 04 - Northwest Kansas | 531489 | ONEOK 3 | 115 | 1.966 | 1.95 | -0.016
GEN-2017-013 | North | 04 - Northwest Kansas | 640100 | CAMBRIG7 | 115 | 4.343 | 4.327 | -0.016
GEN-2017-013 | North | 04 - Northwest Kansas | 640365 | STOCKVL7 | 115 | 4.798 | 4.782 | -0.016
GEN-2017-004 | North | 04 - Northwest Kansas | 533416 | RENO 3 | 115 | 27.124 | 27.107 | -0.017
GEN-2017-004 | North | 04 - Northwest Kansas | 533342 | WJCCTY 3 | 115 | 13.757 | 13.74 | -0.017
GEN-2017-004 | North | 04 - Northwest Kansas | 533330 | JCTCTY 3 | 115 | 13.023 | 13.006 | -0.017
GEN-2017-013 | North | 04 - Northwest Kansas | 531351 | BREWSTR3 | 115 | 3.176 | 3.159 | -0.017
GEN-2017-013 | North | 04 - Northwest Kansas | 531353 | GOODLND3 | 115 | 2.707 | 2.69 | -0.017
GEN-2017-013 | North | 04 - Northwest Kansas | 531357 | RULETON3 | 115 | 2.625 | 2.608 | -0.017
GEN-2017-013 | North | 04 - Northwest Kansas | 531440 | WILLIAM3 | 115 | 3.765 | 3.748 | -0.017
GEN-2017-013 | North | 04 - Northwest Kansas | 587680 | GEN-2016-074 | 345 | 6.628 | 6.611 | -0.017
GEN-2017-013 | North | 04 - Northwest Kansas | 640065 | AXTELL 3 | 345 | 9.814 | 9.797 | -0.017
GEN-2017-013 | North | 04 - Northwest Kansas | 640265 | MALONEY7 | 115 | 11.525 | 11.508 | -0.017
GEN-2017-013 | North | 04 - Northwest Kansas | 640304 | OGALALANPPD7 | 115 | 15.924 | 15.907 | -0.017
GEN-2017-013 | North | 04 - Northwest Kansas | 659801 | OGALALA_-TS7 | 115 | 15.924 | 15.907 | -0.017
GEN-2017-004 | North | 04 - Northwest Kansas | 532863 | MORRIS 6 | 230 | 14.054 | 14.036 | -0.018
GEN-2017-013 | North | 04 - Northwest Kansas | 530559 | PH RUN 3 | 115 | 4.642 | 4.624 | -0.018
GEN-2017-013 | North | 04 - Northwest Kansas | 531476 | SWNDTAP3 | 115 | 7.709 | 7.691 | -0.018
GEN-2017-013 | North | 04 - Northwest Kansas | 640082 | BEVERLY7 | 115 | 5.129 | 5.111 | -0.018
GEN-2017-013 | North | 04 - Northwest Kansas | 640083 | BEVERLY8 | 69 | 4.514 | 4.496 | -0.018
GEN-2017-013 | North | 04 - Northwest Kansas | 523097 | HITCHLAND 7 | 345 | 15.314 | 15.295 | -0.019
GEN-2017-013 | North | 04 - Northwest Kansas | 530682 | SEGNTP 3 | 115 | 4.388 | 4.369 | -0.019
GEN-2017-013 | North | 04 - Northwest Kansas | 531363 | MANNING3 | 115 | 4.073 | 4.054 | -0.019
GEN-2017-013 | North | 04 - Northwest Kansas | 531392 | PIONTAP3 | 115 | 6.562 | 6.543 | -0.019
GEN-2017-013 | North | 04 - Northwest Kansas | 531400 | PK_GOAB3 | 115 | 4.891 | 4.872 | -0.019
GEN-2017-013 | North | 04 - Northwest Kansas | 531487 | MCDONLD3 | 115 | 2.341 | 2.322 | -0.019
GEN-2017-013 | North | 04 - Northwest Kansas | 531488 | BVERVLLY | 115 | 2.435 | 2.416 | -0.019
GEN-2017-013 | North | 04 - Northwest Kansas | 640253 | KEYSTON7 | 115 | 16.617 | 16.598 | -0.019
GEN-2017-004 | North | 04 - Northwest Kansas | 533343 | PEIL 3 | 115 | 10.552 | 10.532 | -0.02
GEN-2017-004 | North | 04 - Northwest Kansas | 533341 | STAGGHL3 | 115 | 9.819 | 9.799 | -0.02
GEN-2017-004 | North | 04 - Northwest Kansas | 533333 | KSU W 3 | 115 | 12.011 | 11.991 | -0.02
GEN-2017-013 | North | 04 - Northwest Kansas | 523823 | CARPENTER 7 | 345 | 6.708 | 6.688 | -0.02
GEN-2017-013 | North | 04 - Northwest Kansas | 530683 | SEGUIN 3 | 115 | 4.172 | 4.152 | -0.02
GEN-2017-013 | North | 04 - Northwest Kansas | 531220 | LUDELLT3 | 115 | 2.613 | 2.593 | -0.02
GEN-2017-013 | North | 04 - Northwest Kansas | 531412 | GRINNEL3 | 115 | 3.785 | 3.765 | -0.02
GEN-2017-013 | North | 04 - Northwest Kansas | 531512 | HARBNGR7 | 345 | 6.687 | 6.667 | -0.02
GEN-2017-013 | North | 04 - Northwest Kansas | 640326 | REDWILO7 | 115 | 13.422 | 13.402 | -0.02
GEN-2017-013 | North | 04 - Northwest Kansas | 653571 | GR ISLD3 | 345 | 12.825 | 12.805 | -0.02
GEN-2017-013 | North | 04 - Northwest Kansas | 653871 | GR ISLD-LNX3 | 345 | 12.699 | 12.679 | -0.02
GEN-2017-004 | North | 04 - Northwest Kansas | 533347 | NMANHT3 | 115 | 12.922 | 12.901 | -0.021
GEN-2017-004 | North | 04 - Northwest Kansas | 533335 | MCDOWEL3 | 115 | 18.668 | 18.647 | -0.021
GEN-2017-004 | North | 04 - Northwest Kansas | 533326 | EMANHAT3 | 115 | 13.678 | 13.657 | -0.021
GEN-2017-013 | North | 04 - Northwest Kansas | 530556 | HOXIE 3 | 115 | 3.609 | 3.588 | -0.021
GEN-2017-013 | North | 04 - Northwest Kansas | 531362 | MANNGT 3 | 115 | 5.106 | 5.085 | -0.021
GEN-2017-013 | North | 04 - Northwest Kansas | 531364 | ATWODSW3 | 115 | 2.707 | 2.686 | -0.021
GEN-2017-013 | North | 04 - Northwest Kansas | 531369 | NATWOOD3 | 115 | 2.582 | 2.561 | -0.021
GEN-2017-013 | North | 04 - Northwest Kansas | 531433 | SCOTCTY3 | 115 | 8.965 | 8.944 | -0.021
GEN-2017-013 | North | 04 - Northwest Kansas | 640270 | MCCOOK 8 | 69 | 4.929 | 4.908 | -0.021
GEN-2017-004 | North | 04 - Northwest Kansas | 533305 | MORRIS 3 | 115 | 12.609 | 12.587 | -0.022
GEN-2017-013 | North | 04 - Northwest Kansas | 530554 | ATWOOD 3 | 115 | 3.051 | 3.029 | -0.022
GEN-2017-013 | North | 04 - Northwest Kansas | 531432 | PILE 3 | 115 | 6.542 | 6.52 | -0.022
GEN-2017-013 | North | 04 - Northwest Kansas | 531434 | SELKIRK3 | 115 | 3.818 | 3.796 | -0.022
GEN-2017-013 | North | 04 - Northwest Kansas | 531493 | GANO 3 | 115 | 6.872 | 6.85 | -0.022
GEN-2017-004 | North | 04 - Northwest Kansas | 532765 | HOYT 7 | 345 | 15.972 | 15.949 | -0.023
GEN-2017-013 | North | 04 - Northwest Kansas | 531428 | LEOTI 3 | 115 | 4.17 | 4.147 | -0.023
GEN-2017-013 | North | 04 - Northwest Kansas | 640287 | N.PLATT7 | 115 | 18.746 | 18.723 | -0.023
GEN-2017-004 | North | 04 - Northwest Kansas | 532851 | AUBURN 6 | 230 | 13.114 | 13.09 | -0.024
GEN-2017-013 | North | 04 - Northwest Kansas | 530644 | COLBY 2 | 69 | 3.602 | 3.578 | -0.024
GEN-2017-013 | North | 04 - Northwest Kansas | 531445 | GRDNCTY3 | 115 | 14.373 | 14.349 | -0.024
GEN-2017-013 | North | 04 - Northwest Kansas | 531480 | KSAVWTP3 | 115 | 13.825 | 13.801 | -0.024
GEN-2017-013 | North | 04 - Northwest Kansas | 640374 | SWEET W3 | 345 | 11.109 | 11.085 | -0.024
GEN-2017-004 | North | 04 - Northwest Kansas | 532772 | STRANGR7 | 345 | 25.661 | 25.636 | -0.025
GEN-2017-013 | North | 04 - Northwest Kansas | 640200 | GR ISLD4 | 230 | 17.205 | 17.18 | -0.025
GEN-2017-013 | North | 04 - Northwest Kansas | 640269 | MCCOOK 7 | 115 | 9.734 | 9.709 | -0.025
GEN-2017-004 | North | 04 - Northwest Kansas | 533340 | SMANHAT3 | 115 | 12.272 | 12.246 | -0.026
GEN-2017-013 | North | 04 - Northwest Kansas | 531393 | PLYMELL3 | 115 | 7.651 | 7.623 | -0.028
GEN-2017-013 | North | 04 - Northwest Kansas | 531420 | FLETCHR3 | 115 | 6.823 | 6.795 | -0.028
GEN-2017-013 | North | 04 - Northwest Kansas | 531485 | CNTRLPL3 | 115 | 5.697 | 5.669 | -0.028
GEN-2017-013 | North | 04 - Northwest Kansas | 640066 | AXTELL 7 | 115 | 14.753 | 14.725 | -0.028
GEN-2017-013 | North | 04 - Northwest Kansas | 531426 | JAMESON3 | 115 | 10.527 | 10.497 | -0.03
GEN-2017-013 | North | 04 - Northwest Kansas | 539800 | CLARKCOUNTY7 | 345 | 13.339 | 13.309 | -0.03
GEN-2017-013 | North | 04 - Northwest Kansas | 531379 | JONES3 | 115 | 11.033 | 11 | -0.033
GEN-2017-004 | North | 04 - Northwest Kansas | 532856 | SWISVAL6 | 230 | 21.138 | 21.101 | -0.037
GEN-2017-004 | North | 04 - Northwest Kansas | 533163 | HOYT 3 | 115 | 23.038 | 22.999 | -0.039
GEN-2017-013 | North | 04 - Northwest Kansas | 531448 | HOLCOMB3 | 115 | 21.961 | 21.913 | -0.048
GEN-2016-103 | North | 15 - Eastern South Dakota | 560074 | G16-017_TAP | 345 | 5.823 | 6.309 | 0.486
GEN-2016-103 | North | 15 - Eastern South Dakota | 587030 | GEN-2016-004 | 230 | 7.6 | 7.594 | -0.006
GEN-2016-103 | North | 15 - Eastern South Dakota | 587130 | GEN-2016-017 | 345 | 5.817 | 6.302 | 0.485
GEN-2016-103 | North | 15 - Eastern South Dakota | 587750 | GEN-2016-092 | 345 | 5.263 | 5.645 | 0.382
GEN-2016-103 | North | 15 - Eastern South Dakota | 587760 | GEN-2016-094 | 230 | 9.209 | 9.226 | 0.017
GEN-2016-103 | North | 15 - Eastern South Dakota | 587764 | G16-094-TAP | 230 | 9.372 | 9.39 | 0.018
GEN-2016-103 | North | 15 - Eastern South Dakota | 587830 | GEN-2016-103 | 345 | 5.773 | 6.26 | 0.487
GEN-2016-103 | North | 15 - Eastern South Dakota | 588210 | GEN-2016-130 | 345 | 11.356 | 11.359 | 0.003
GEN-2016-103 | North | 15 - Eastern South Dakota | 589320 | GEN-2017-094 | 230 | 10.967 | 10.967 | 0
GEN-2016-103 | North | 15 - Eastern South Dakota | 589324 | G17-094-TAP | 230 | 10.967 | 10.967 | 0
GEN-2016-103 | North | 15 - Eastern South Dakota | 615600 | GRE-COAL CR4 | 230 | 18.481 | 18.479 | -0.002
GEN-2016-103 | North | 15 - Eastern South Dakota | 615900 | GRE-COAL TP4 | 230 | 15.966 | 15.961 | -0.005
GEN-2016-103 | North | 15 - Eastern South Dakota | 615901 | GRE-STANTON4 | 230 | 17.947 | 17.941 | -0.006
GEN-2016-103 | North | 15 - Eastern South Dakota | 640540 | MEADOWGROVE4 | 230 | 5.671 | 5.648 | -0.023
GEN-2016-103 | North | 15 - Eastern South Dakota | 652276 | FTTHOMP8 | 69 | 4.184 | 4.17 | -0.014
GEN-2016-103 | North | 15 - Eastern South Dakota | 652424 | BELFELD3 | 345 | 6.534 | 6.53 | -0.004
GEN-2016-103 | North | 15 - Eastern South Dakota | 652426 | BISMARK4 | 230 | 13.108 | 13.085 | -0.023
GEN-2016-103 | North | 15 - Eastern South Dakota | 652441 | GARRISN4 | 230 | 11.815 | 11.817 | 0.002
GEN-2016-103 | North | 15 - Eastern South Dakota | 652442 | GARRISN7 | 115 | 15.493 | 15.493 | 0
GEN-2016-103 | North | 15 - Eastern South Dakota | 652444 | JAMESTN4 | 230 | 8.032 | 7.994 | -0.038
GEN-2016-103 | North | 15 - Eastern South Dakota | 652456 | WASHBRN4 | 230 | 10.203 | 10.193 | -0.01
GEN-2016-103 | North | 15 - Eastern South Dakota | 652466 | HILKEN 4 | 230 | 7.284 | 7.275 | -0.009
GEN-2016-103 | North | 15 - Eastern South Dakota | 652506 | FTTHOMP3 | 345 | 8.845 | 9.091 | 0.246
GEN-2016-103 | North | 15 - Eastern South Dakota | 652507 | FTTHOMP4 | 230 | 20.338 | 20.552 | 0.214
GEN-2016-103 | North | 15 - Eastern South Dakota | 652509 | FTRANDL4 | 230 | 10.784 | 10.757 | -0.027
GEN-2016-103 | North | 15 - Eastern South Dakota | 652510 | FTRANDL7 | 115 | 12.595 | 12.603 | 0.008
GEN-2016-103 | North | 15 - Eastern South Dakota | 652514 | HURON 4 | 230 | 11.183 | 11.171 | -0.012
GEN-2016-103 | North | 15 - Eastern South Dakota | 652519 | OAHE 4 | 230 | 14.727 | 14.787 | 0.06
GEN-2016-103 | North | 15 - Eastern South Dakota | 652520 | OAHE 7 | 115 | 11.439 | 11.448 | 0.009
GEN-2016-103 | North | 15 - Eastern South Dakota | 652523 | SIOUXFL4 | 230 | 13.209 | 13.158 | -0.051
GEN-2016-103 | North | 15 - Eastern South Dakota | 652526 | UTICAJC4 | 230 | 7.845 | 7.819 | -0.026
GEN-2016-103 | North | 15 - Eastern South Dakota | 652532 | GR PRAIRIE 3 | 345 | 7.712 | 7.61 | -0.102
GEN-2016-103 | North | 15 - Eastern South Dakota | 652540 | BIGBND14 | 230 | 12.254 | 12.285 | 0.031
GEN-2016-103 | North | 15 - Eastern South Dakota | 652541 | BIGBND24 | 230 | 12.132 | 12.184 | 0.052
GEN-2016-103 | North | 15 - Eastern South Dakota | 652565 | SIOUXCY4 | 230 | 19.804 | 19.757 | -0.047
GEN-2016-103 | North | 15 - Eastern South Dakota | 652606 | LETCHER4 | 230 | 4.692 | 4.661 | -0.031
GEN-2016-103 | North | 15 - Eastern South Dakota | 652607 | WESSINGTON 4 | 230 | 6.598 | 6.573 | -0.025
GEN-2016-103 | North | 15 - Eastern South Dakota | 652609 | LETCHER7 | 115 | 5.984 | 5.948 | -0.036
GEN-2016-103 | North | 15 - Eastern South Dakota | 652806 | FTTHOM1-LNX3 | 345 | 8.786 | 9.036 | 0.25
GEN-2016-103 | North | 15 - Eastern South Dakota | 652807 | FTTHOM2-LNX3 | 345 | 8.845 | 9.091 | 0.246
GEN-2016-103 | North | 15 - Eastern South Dakota | 652833 | GRPRAR2-LNX3 | 345 | 7.712 | 7.61 | -0.102
GEN-2016-103 | North | 15 - Eastern South Dakota | 655153 | MOS-AMES-ER8 | 69 | 4.12 | 4.106 | -0.014
GEN-2016-103 | North | 15 - Eastern South Dakota | 655475 | LAKPLAT-ER4 | 230 | 5.64 | 5.611 | -0.029
GEN-2016-103 | North | 15 - Eastern South Dakota | 655476 | LAKPLAT-ER8 | 69 | 4.039 | 4.011 | -0.028
GEN-2016-103 | North | 15 - Eastern South Dakota | 655487 | SULLYBT-ER4 | 230 | 6.529 | 6.536 | 0.007
GEN-2016-103 | North | 15 - Eastern South Dakota | 657756 | SQBUTTE4 | 230 | 22.769 | 22.744 | -0.025
GEN-2016-103 | North | 15 - Eastern South Dakota | 659101 | ANTELOPE-BE3 | 345 | 16.246 | 16.251 | 0.005
GEN-2016-103 | North | 15 - Eastern South Dakota | 659105 | LELAND_O-BE3 | 345 | 16.41 | 16.423 | 0.013
GEN-2016-103 | North | 15 - Eastern South Dakota | 659106 | LELAND_O-BE4 | 230 | 22.916 | 22.92 | 0.004
GEN-2016-103 | North | 15 - Eastern South Dakota | 659108 | LOGAN___-BE4 | 230 | 5.569 | 5.561 | -0.008
GEN-2016-103 | North | 15 - Eastern South Dakota | 659109 | BASIN___-BE7 | 115 | 5.337 | 5.332 | -0.005
GEN-2016-103 | North | 15 - Eastern South Dakota | 659122 | STORLA__-BE4 | 230 | 5.881 | 5.853 | -0.028
GEN-2016-103 | North | 15 - Eastern South Dakota | 659143 | BLAISDEL-BE4 | 230 | 5.386 | 5.381 | -0.005
GEN-2016-103 | North | 15 - Eastern South Dakota | 659155 | LOGAN___-BE7 | 115 | 9.562 | 9.548 | -0.014
GEN-2016-103 | North | 15 - Eastern South Dakota | 659160 | GROTON__-BE3 | 345 | 5.869 | 5.859 | -0.01
GEN-2016-103 | North | 15 - Eastern South Dakota | 659182 | CHARL_CK-BE7 | 115 | 13.735 | 13.728 | -0.007
GEN-2016-103 | North | 15 - Eastern South Dakota | 659183 | CHARL_CK-BE3 | 345 | 10.145 | 10.14 | -0.005
GEN-2016-103 | North | 15 - Eastern South Dakota | 659188 | PHILIP_T-BE4 | 230 | 5.241 | 5.232 | -0.009
GEN-2016-103 | North | 15 - Eastern South Dakota | 659199 | BASIN___-BE4 | 230 | 20.867 | 20.868 | 0.001
GEN-2016-103 | North | 15 - Eastern South Dakota | 659212 | DGC_____-BE3 | 345 | 15.521 | 15.525 | 0.004
GEN-2016-103 | North | 15 - Eastern South Dakota | 659218 | COTEAU__-RR3 | 345 | 16.246 | 16.251 | 0.005
GEN-2016-103 | North | 15 - Eastern South Dakota | 659222 | COTEAU_1-RR8 | 69 | 9.544 | 9.539 | -0.005
GEN-2016-103 | North | 15 - Eastern South Dakota | 659233 | DGC_____-BE4 | 230 | 7.179 | 7.176 | -0.003
GEN-2016-103 | North | 15 - Eastern South Dakota | 659295 | SD.PW1__-BE4 | 230 | 5.501 | 5.482 | -0.019
GEN-2016-103 | North | 15 - Eastern South Dakota | 659302 | CHARL_CK-BE4 | 230 | 11.114 | 11.108 | -0.006
GEN-2016-103 | North | 15 - Eastern South Dakota | 659384 | ROUNDUP_-BE3 | 345 | 8.271 | 8.267 | -0.004
GEN-2016-103 | North | 15 - Eastern South Dakota | 659385 | ROUNDUP_-MK7 | 115 | 11.092 | 11.085 | -0.007
GEN-2016-103 | North | 15 - Eastern South Dakota | 659390 | PATENTGT-BE3 | 345 | 7.118 | 7.114 | -0.004
GEN-2016-103 | North | 15 - Eastern South Dakota | 659420 | AV.LS-BD-BE3 | 345 | 16.246 | 16.251 | 0.005
GEN-2016-103 | North | 15 - Eastern South Dakota | 659421 | BD.LS-AV-BE3 | 345 | 4.091 | 4.083 | -0.008
GEN-2016-103 | North | 15 - Eastern South Dakota | 659422 | LO.LS-GR-BE3 | 345 | 16.41 | 16.423 | 0.013
GEN-2016-103 | North | 15 - Eastern South Dakota | 659423 | GR.LS-LO-BE3 | 345 | 5.869 | 5.859 | -0.01
GEN-2016-103 | North | 15 - Eastern South Dakota | 659424 | LO.LS-FT-BE3 | 345 | 16.41 | 16.423 | 0.013
GEN-2017-094 | North | 15 - Eastern South Dakota | 560074 | G16-017_TAP | 345 | 6.317 | 6.309 | -0.008
GEN-2017-094 | North | 15 - Eastern South Dakota | 560347 | G10-051-TAP | 230 | 7.351 | 7.336 | -0.015
GEN-2017-094 | North | 15 - Eastern South Dakota | 563230 | GEN-2015-089 | 230 | 5.374 | 5.358 | -0.016
GEN-2017-094 | North | 15 - Eastern South Dakota | 587130 | GEN-2016-017 | 345 | 6.31 | 6.302 | -0.008
GEN-2017-094 | North | 15 - Eastern South Dakota | 587750 | GEN-2016-092 | 345 | 5.653 | 5.645 | -0.008
GEN-2017-094 | North | 15 - Eastern South Dakota | 587760 | GEN-2016-094 | 230 | 9.213 | 9.226 | 0.013
GEN-2017-094 | North | 15 - Eastern South Dakota | 587764 | G16-094-TAP | 230 | 9.377 | 9.39 | 0.013
GEN-2017-094 | North | 15 - Eastern South Dakota | 587830 | GEN-2016-103 | 345 | 6.268 | 6.26 | -0.008
GEN-2017-094 | North | 15 - Eastern South Dakota | 588590 | GEN-2017-014 | 230 | 5.252 | 5.243 | -0.009
GEN-2017-094 | North | 15 - Eastern South Dakota | 588594 | G17-014-TAP | 230 | 5.252 | 5.243 | -0.009
GEN-2017-094 | North | 15 - Eastern South Dakota | 589320 | GEN-2017-094 | 230 | 10.483 | 10.967 | 0.484
GEN-2017-094 | North | 15 - Eastern South Dakota | 589324 | G17-094-TAP | 230 | 10.483 | 10.967 | 0.484
GEN-2017-094 | North | 15 - Eastern South Dakota | 602004 | SPLT RK4 | 230 | 12.769 | 12.725 | -0.044
GEN-2017-094 | North | 15 - Eastern South Dakota | 602008 | MINVALT4 | 230 | 12.156 | 12.102 | -0.054
GEN-2017-094 | North | 15 - Eastern South Dakota | 602009 | MNVLTAP4 | 230 | 12.122 | 12.068 | -0.054
GEN-2017-094 | North | 15 - Eastern South Dakota | 603009 | GRANT 7 | 115 | 3.912 | 3.897 | -0.015
GEN-2017-094 | North | 15 - Eastern South Dakota | 603012 | LAWRENC7 | 115 | 30.393 | 30.325 | -0.068
GEN-2017-094 | North | 15 - Eastern South Dakota | 603016 | SPLT RK7 | 115 | 38.913 | 38.838 | -0.075
GEN-2017-094 | North | 15 - Eastern South Dakota | 619975 | GRE-WILLMAR4 | 230 | 5.291 | 5.265 | -0.026
GEN-2017-094 | North | 15 - Eastern South Dakota | 620214 | BIGSTON7 | 115 | 2.364 | 2.354 | -0.01
GEN-2017-094 | North | 15 - Eastern South Dakota | 620314 | BIGSTON4 | 230 | 11.985 | 11.944 | -0.041
GEN-2017-094 | North | 15 - Eastern South Dakota | 620322 | BSSOUTH4 | 230 | 11.828 | 11.788 | -0.04
GEN-2017-094 | North | 15 - Eastern South Dakota | 620325 | BROWNSV4 | 230 | 5.389 | 5.365 | -0.024
GEN-2017-094 | North | 15 - Eastern South Dakota | 635223 | PLYMOTH5 | 161 | 20.434 | 20.403 | -0.031
GEN-2017-094 | North | 15 - Eastern South Dakota | 640126 | E.COL. 4 | 230 | 9.614 | 9.584 | -0.03
GEN-2017-094 | North | 15 - Eastern South Dakota | 640131 | COLMB.W4 | 230 | 9.683 | 9.651 | -0.032
GEN-2017-094 | North | 15 - Eastern South Dakota | 640133 | COLMBUS4 | 230 | 11.279 | 11.243 | -0.036
GEN-2017-094 | North | 15 - Eastern South Dakota | 640134 | KELLY 7 | 115 | 17.646 | 17.604 | -0.042
GEN-2017-094 | North | 15 - Eastern South Dakota | 640305 | ONEILL 7 | 115 | 3.991 | 3.981 | -0.01
GEN-2017-094 | North | 15 - Eastern South Dakota | 640343 | SHELCRK4 | 230 | 10.691 | 10.657 | -0.034
GEN-2017-094 | North | 15 - Eastern South Dakota | 640349 | SPENCER7 | 115 | 4.596 | 4.587 | -0.009
GEN-2017-094 | North | 15 - Eastern South Dakota | 640386 | TWIN CH4 | 230 | 8.828 | 8.807 | -0.021
GEN-2017-094 | North | 15 - Eastern South Dakota | 640387 | TWIN CH7 | 115 | 11.246 | 11.22 | -0.026
GEN-2017-094 | North | 15 - Eastern South Dakota | 640540 | MEADOWGROVE4 | 230 | 5.671 | 5.648 | -0.023
GEN-2017-094 | North | 15 - Eastern South Dakota | 648506 | PR BRZ 4 | 230 | 4.436 | 4.422 | -0.014
GEN-2017-094 | North | 15 - Eastern South Dakota | 652209 | SUMMIT-8 | 69 | 2.7 | 2.691 | -0.009
GEN-2017-094 | North | 15 - Eastern South Dakota | 652225 | BROOKNG8 | 69 | 2.954 | 2.943 | -0.011
GEN-2017-094 | North | 15 - Eastern South Dakota | 652235 | SIOUXFL8 | 69 | 3.891 | 3.879 | -0.012
GEN-2017-094 | North | 15 - Eastern South Dakota | 652242 | WATERT18 | 69 | 3.911 | 3.896 | -0.015
GEN-2017-094 | North | 15 - Eastern South Dakota | 652243 | FAITH 7 | 115 | 2.393 | 2.389 | -0.004
GEN-2017-094 | North | 15 - Eastern South Dakota | 652249 | ARMOUR 8 | 69 | 2.481 | 2.475 | -0.006
GEN-2017-094 | North | 15 - Eastern South Dakota | 652259 | EAGLEBE8 | 69 | 1.695 | 1.692 | -0.003
GEN-2017-094 | North | 15 - Eastern South Dakota | 652260 | EAGLEBW8 | 69 | 2.204 | 2.201 | -0.003
GEN-2017-094 | North | 15 - Eastern South Dakota | 652276 | FTTHOMP8 | 69 | 4.181 | 4.17 | -0.011
GEN-2017-094 | North | 15 - Eastern South Dakota | 652284 | HURON 8 | 69 | 3.687 | 3.684 | -0.003
GEN-2017-094 | North | 15 - Eastern South Dakota | 652398 | VFODNES4 | 230 | 6.737 | 6.713 | -0.024
GEN-2017-094 | North | 15 - Eastern South Dakota | 652455 | ROBERTSCTY7 | 115 | 3.151 | 3.14 | -0.011
GEN-2017-094 | North | 15 - Eastern South Dakota | 652474 | AURORA 7 | 115 | 4.4 | 4.384 | -0.016
GEN-2017-094 | North | 15 - Eastern South Dakota | 652475 | BONESTL7 | 115 | 3.562 | 3.559 | -0.003
GEN-2017-094 | North | 15 - Eastern South Dakota | 652476 | EAGLEBT7 | 115 | 2.006 | 2.003 | -0.003
GEN-2017-094 | North | 15 - Eastern South Dakota | 652478 | GREGORY7 | 115 | 2.181 | 2.176 | -0.005
GEN-2017-094 | North | 15 - Eastern South Dakota | 652481 | MIDLAND7 | 115 | 3.49 | 3.483 | -0.007
GEN-2017-094 | North | 15 - Eastern South Dakota | 652484 | NUNDRWD4 | 230 | 3.972 | 3.963 | -0.009
GEN-2017-094 | North | 15 - Eastern South Dakota | 652486 | PHILIP 4 | 230 | 4.023 | 4.015 | -0.008
GEN-2017-094 | North | 15 - Eastern South Dakota | 652487 | PHILIP 7 | 115 | 5.904 | 5.888 | -0.016
GEN-2017-094 | North | 15 - Eastern South Dakota | 652489 | PIERRE 7 | 115 | 8.247 | 8.248 | 0.001
GEN-2017-094 | North | 15 - Eastern South Dakota | 652491 | IRVSIMM7 | 115 | 8.207 | 8.208 | 0.001
GEN-2017-094 | North | 15 - Eastern South Dakota | 652501 | ARMOUR 7 | 115 | 4.186 | 4.176 | -0.01
GEN-2017-094 | North | 15 - Eastern South Dakota | 652502 | BERSFRD7 | 115 | 3.929 | 3.924 | -0.005
GEN-2017-094 | North | 15 - Eastern South Dakota | 652504 | BROOKNG7 | 115 | 7.112 | 7.089 | -0.023
GEN-2017-094 | North | 15 - Eastern South Dakota | 652505 | FLANDRU7 | 115 | 4.06 | 4.046 | -0.014
GEN-2017-094 | North | 15 - Eastern South Dakota | 652506 | FTTHOMP3 | 345 | 9.1 | 9.091 | -0.009
GEN-2017-094 | North | 15 - Eastern South Dakota | 652507 | FTTHOMP4 | 230 | 20.396 | 20.552 | 0.156
GEN-2017-094 | North | 15 - Eastern South Dakota | 652509 | FTRANDL4 | 230 | 10.787 | 10.757 | -0.03
GEN-2017-094 | North | 15 - Eastern South Dakota | 652510 | FTRANDL7 | 115 | 12.596 | 12.603 | 0.007
GEN-2017-094 | North | 15 - Eastern South Dakota | 652512 | GROTON 7 | 115 | 16.158 | 16.145 | -0.013
GEN-2017-094 | North | 15 - Eastern South Dakota | 652513 | HANLON 4 | 230 | 5.573 | 5.545 | -0.028
GEN-2017-094 | North | 15 - Eastern South Dakota | 652514 | HURON 4 | 230 | 10.938 | 11.171 | 0.233
GEN-2017-094 | North | 15 - Eastern South Dakota | 652515 | HURON 7 | 115 | 15.438 | 15.59 | 0.152
GEN-2017-094 | North | 15 - Eastern South Dakota | 652518 | MTVERN 7 | 115 | 4.335 | 4.317 | -0.018
GEN-2017-094 | North | 15 - Eastern South Dakota | 652519 | OAHE 4 | 230 | 14.743 | 14.787 | 0.044
GEN-2017-094 | North | 15 - Eastern South Dakota | 652520 | OAHE 7 | 115 | 11.442 | 11.448 | 0.006
GEN-2017-094 | North | 15 - Eastern South Dakota | 652522 | SUMMIT-7 | 115 | 4.691 | 4.676 | -0.015
GEN-2017-094 | North | 15 - Eastern South Dakota | 652523 | SIOUXFL4 | 230 | 13.203 | 13.158 | -0.045
GEN-2017-094 | North | 15 - Eastern South Dakota | 652524 | SIOUXFL7 | 115 | 26.721 | 26.655 | -0.066
GEN-2017-094 | North | 15 - Eastern South Dakota | 652525 | TYNDALL7 | 115 | 3.869 | 3.861 | -0.008
GEN-2017-094 | North | 15 - Eastern South Dakota | 652526 | UTICAJC4 | 230 | 7.843 | 7.819 | -0.024
GEN-2017-094 | North | 15 - Eastern South Dakota | 652528 | WOONSKT7 | 115 | 5.287 | 5.273 | -0.014
GEN-2017-094 | North | 15 - Eastern South Dakota | 652529 | WATERTN3 | 345 | 9.907 | 9.895 | -0.012
GEN-2017-094 | North | 15 - Eastern South Dakota | 652530 | WATERTN4 | 230 | 13.846 | 13.834 | -0.012
GEN-2017-094 | North | 15 - Eastern South Dakota | 652531 | WATERTN7 | 115 | 12.311 | 12.277 | -0.034
GEN-2017-094 | North | 15 - Eastern South Dakota | 652532 | GR PRAIRIE 3 | 345 | 7.677 | 7.609 | -0.068
GEN-2017-094 | North | 15 - Eastern South Dakota | 652537 | WHITE 3 | 345 | 17.64 | 17.612 | -0.028
GEN-2017-094 | North | 15 - Eastern South Dakota | 652538 | WHITE 7 | 115 | 9.106 | 9.082 | -0.024
GEN-2017-094 | North | 15 - Eastern South Dakota | 652540 | BIGBND14 | 230 | 12.264 | 12.285 | 0.021
GEN-2017-094 | North | 15 - Eastern South Dakota | 652541 | BIGBND24 | 230 | 12.158 | 12.184 | 0.026
GEN-2017-094 | North | 15 - Eastern South Dakota | 652550 | GRANITF4 | 230 | 12.266 | 12.211 | -0.055
GEN-2017-094 | North | 15 - Eastern South Dakota | 652551 | GRANITF7 | 115 | 16.529 | 16.459 | -0.07
GEN-2017-094 | North | 15 - Eastern South Dakota | 652552 | SIOUXCY2 | 230 | 19.8 | 19.756 | -0.044
GEN-2017-094 | North | 15 - Eastern South Dakota | 652554 | MORRIS 4 | 230 | 4.46 | 4.439 | -0.021
GEN-2017-094 | North | 15 - Eastern South Dakota | 652561 | DENISON5 | 161 | 5.468 | 5.456 | -0.012
GEN-2017-094 | North | 15 - Eastern South Dakota | 652563 | SPENCER5 | 161 | 9.468 | 9.46 | -0.008
GEN-2017-094 | North | 15 - Eastern South Dakota | 652564 | SIOUXCY3 | 345 | 15.084 | 15.062 | -0.022
GEN-2017-094 | North | 15 - Eastern South Dakota | 652565 | SIOUXCY4 | 230 | 19.8 | 19.756 | -0.044
GEN-2017-094 | North | 15 - Eastern South Dakota | 652566 | SIOUXCY5 | 161 | 20.87 | 20.838 | -0.032
GEN-2017-094 | North | 15 - Eastern South Dakota | 652567 | DENISON4 | 230 | 4.395 | 4.385 | -0.01
GEN-2017-094 | North | 15 - Eastern South Dakota | 652568 | GROTONSOUTH7 | 115 | 16.198 | 16.185 | -0.013
GEN-2017-094 | North | 15 - Eastern South Dakota | 652574 | SIOUXCY8 | 69 | 17.95 | 17.922 | -0.028
GEN-2017-094 | North | 15 - Eastern South Dakota | 652582 | APPLEDORN 4 | 230 | 6.903 | 6.869 | -0.034
GEN-2017-094 | North | 15 - Eastern South Dakota | 652583 | DENISON8 | 69 | 11.211 | 11.189 | -0.022
GEN-2017-094 | North | 15 - Eastern South Dakota | 652600 | ASH TAP | 115 | 8.682 | 8.684 | 0.002
GEN-2017-094 | North | 15 - Eastern South Dakota | 652604 | APPLEDORN 8 | 69 | 2.499 | 2.486 | -0.013
GEN-2017-094 | North | 15 - Eastern South Dakota | 652606 | LETCHER4 | 230 | 4.686 | 4.661 | -0.025
GEN-2017-094 | North | 15 - Eastern South Dakota | 652607 | WESSINGTON 4 | 230 | 6.592 | 6.573 | -0.019
GEN-2017-094 | North | 15 - Eastern South Dakota | 652609 | LETCHER7 | 115 | 5.979 | 5.948 | -0.031
GEN-2017-094 | North | 15 - Eastern South Dakota | 652614 | CARPENTER 4 | 230 | 6.914 | 6.957 | 0.043
GEN-2017-094 | North | 15 - Eastern South Dakota | 652626 | UTICAJC7 | 115 | 8.903 | 8.875 | -0.028
GEN-2017-094 | North | 15 - Eastern South Dakota | 652630 | WATERTNCAP 4 | 230 | 13.689 | 13.676 | -0.013
GEN-2017-094 | North | 15 - Eastern South Dakota | 652806 | FTTHOM1-LNX3 | 345 | 9.045 | 9.036 | -0.009
GEN-2017-094 | North | 15 - Eastern South Dakota | 652807 | FTTHOM2-LNX3 | 345 | 9.1 | 9.091 | -0.009
GEN-2017-094 | North | 15 - Eastern South Dakota | 652829 | WATERTN-LNX3 | 345 | 9.902 | 9.89 | -0.012
GEN-2017-094 | North | 15 - Eastern South Dakota | 652833 | GRPRAR2-LNX3 | 345 | 7.677 | 7.609 | -0.068
GEN-2017-094 | North | 15 - Eastern South Dakota | 655040 | MOS-ASTR-ER8 | 69 | 1.221 | 1.216 | -0.005
GEN-2017-094 | North | 15 - Eastern South Dakota | 655054 | MOS-RDFL-ER8 | 69 | 2.058 | 2.056 | -0.002
GEN-2017-094 | North | 15 - Eastern South Dakota | 655055 | SW311-ER8 | 69 | 1.178 | 1.176 | -0.002
GEN-2017-094 | North | 15 - Eastern South Dakota | 655056 | SW313-ER8 | 69 | 1.582 | 1.575 | -0.007
GEN-2017-094 | North | 15 - Eastern South Dakota | 655058 | MOS-HRON-ER8 | 69 | 2.654 | 2.65 | -0.004
GEN-2017-094 | North | 15 - Eastern South Dakota | 655059 | MOS-ASHT-ER8 | 69 | 1.634 | 1.632 | -0.002
GEN-2017-094 | North | 15 - Eastern South Dakota | 655063 | SW341-ER8 | 69 | 3.633 | 3.63 | -0.003
GEN-2017-094 | North | 15 - Eastern South Dakota | 655064 | SW343-ER8 | 69 | 3.607 | 3.604 | -0.003
GEN-2017-094 | North | 15 - Eastern South Dakota | 655066 | SW352-ER8 | 69 | 3.671 | 3.668 | -0.003
GEN-2017-094 | North | 15 - Eastern South Dakota | 655067 | SW353-ER8 | 69 | 3.675 | 3.672 | -0.003
GEN-2017-094 | North | 15 - Eastern South Dakota | 655072 | SW373-ER8 | 69 | 2.313 | 2.303 | -0.01
GEN-2017-094 | North | 15 - Eastern South Dakota | 655073 | MOS-CRPN-ER8 | 69 | 2.481 | 2.471 | -0.01
GEN-2017-094 | North | 15 - Eastern South Dakota | 655079 | MOS-KLKP-ER8 | 69 | 0.76 | 0.755 | -0.005
GEN-2017-094 | North | 15 - Eastern South Dakota | 655080 | MOS-HLTP-ER8 | 69 | 1.303 | 1.295 | -0.008
GEN-2017-094 | North | 15 - Eastern South Dakota | 655108 | MOS-RVLE-ER8 | 69 | 3.874 | 3.859 | -0.015
GEN-2017-094 | North | 15 - Eastern South Dakota | 655111 | SW714-ER8 | 69 | 3.275 | 3.262 | -0.013
GEN-2017-094 | North | 15 - Eastern South Dakota | 655153 | MOS-AMES-ER8 | 69 | 4.117 | 4.106 | -0.011
GEN-2017-094 | North | 15 - Eastern South Dakota | 655158 | MOS-HYDE-ER8 | 69 | 3.055 | 3.051 | -0.004
GEN-2017-094 | North | 15 - Eastern South Dakota | 655236 | MORNINGS-ER8 | 69 | 1.869 | 1.866 | -0.003
GEN-2017-094 | North | 15 - Eastern South Dakota | 655238 | FRANKFRT-ER8 | 69 | 2.092 | 2.09 | -0.002
GEN-2017-094 | North | 15 - Eastern South Dakota | 655250 | CHMBRLAN-ER8 | 69 | 1.579 | 1.569 | -0.01
GEN-2017-094 | North | 15 - Eastern South Dakota | 655294 | MORITZ-ER8 | 69 | 2.033 | 2.025 | -0.008
GEN-2017-094 | North | 15 - Eastern South Dakota | 655328 | BIGBEND-ER8 | 69 | 3.077 | 3.069 | -0.008
GEN-2017-094 | North | 15 - Eastern South Dakota | 655329 | GANNVALL-ER8 | 69 | 0.839 | 0.836 | -0.003
GEN-2017-094 | North | 15 - Eastern South Dakota | 655334 | OKOBOJO-ER8 | 69 | 2.445 | 2.444 | -0.001
GEN-2017-094 | North | 15 - Eastern South Dakota | 655352 | AMES-ER8 | 69 | 1.294 | 1.29 | -0.004
GEN-2017-094 | North | 15 - Eastern South Dakota | 655355 | WOONSKT-ER8 | 69 | 3.598 | 3.584 | -0.014
GEN-2017-094 | North | 15 - Eastern South Dakota | 655373 | MOS-SLY2-ER8 | 69 | 2.452 | 2.451 | -0.001
GEN-2017-094 | North | 15 - Eastern South Dakota | 655377 | SW1145-ER7 | 115 | 25.36 | 25.297 | -0.063
GEN-2017-094 | North | 15 - Eastern South Dakota | 655384 | NWPS8645-ER8 | 69 | 2.02 | 2.017 | -0.003
GEN-2017-094 | North | 15 - Eastern South Dakota | 655385 | MOS-LKPL-ER8 | 69 | 4.02 | 3.997 | -0.023
GEN-2017-094 | North | 15 - Eastern South Dakota | 655386 | MOS-RVR1-ER8 | 69 | 2.086 | 2.074 | -0.012
GEN-2017-094 | North | 15 - Eastern South Dakota | 655412 | CRPNTR-ER8 | 69 | 2.877 | 2.867 | -0.01
GEN-2017-094 | North | 15 - Eastern South Dakota | 655417 | ROSWELL-ER7 | 115 | 2.591 | 2.576 | -0.015
GEN-2017-094 | North | 15 - Eastern South Dakota | 655418 | FREEMAN-ER7 | 115 | 2.593 | 2.584 | -0.009
GEN-2017-094 | North | 15 - Eastern South Dakota | 655419 | SW561-ER7 | 115 | 5.029 | 5.023 | -0.006
GEN-2017-094 | North | 15 - Eastern South Dakota | 655457 | BRISTOL-ER7 | 115 | 4.569 | 4.559 | -0.01
GEN-2017-094 | North | 15 - Eastern South Dakota | 655462 | ARLNGTN-ER7 | 115 | 4.291 | 4.275 | -0.016
GEN-2017-094 | North | 15 - Eastern South Dakota | 655463 | ARLNGTN-ER8 | 69 | 2.662 | 2.651 | -0.011
GEN-2017-094 | North | 15 - Eastern South Dakota | 655465 | BLAIR-ER4 | 230 | 9.183 | 9.147 | -0.036
GEN-2017-094 | North | 15 - Eastern South Dakota | 655466 | BLAIR-ER8 | 69 | 2.452 | 2.443 | -0.009
GEN-2017-094 | North | 15 - Eastern South Dakota | 655468 | VFODNES-ER7 | 115 | 4.927 | 4.908 | -0.019
GEN-2017-094 | North | 15 - Eastern South Dakota | 655469 | VFODNES-ER8 | 69 | 4.147 | 4.13 | -0.017
GEN-2017-094 | North | 15 - Eastern South Dakota | 655475 | LAKPLAT-ER4 | 230 | 5.636 | 5.611 | -0.025
GEN-2017-094 | North | 15 - Eastern South Dakota | 655476 | LAKPLAT-ER8 | 69 | 4.035 | 4.011 | -0.024
GEN-2017-094 | North | 15 - Eastern South Dakota | 655481 | REDFELD-ER7 | 115 | 4.121 | 4.12 | -0.001
GEN-2017-094 | North | 15 - Eastern South Dakota | 655482 | REDFELD-ER8 | 69 | 2.825 | 2.822 | -0.003
GEN-2017-094 | North | 15 - Eastern South Dakota | 655484 | RASMUSN-ER4 | 230 | 6.643 | 6.623 | -0.02
GEN-2017-094 | North | 15 - Eastern South Dakota | 655485 | RASMUSN-ER8 | 69 | 3.242 | 3.231 | -0.011
GEN-2017-094 | North | 15 - Eastern South Dakota | 655487 | SULLYBT-ER4 | 230 | 6.531 | 6.536 | 0.005
GEN-2017-094 | North | 15 - Eastern South Dakota | 655488 | SULLYBT-ER8 | 69 | 2.456 | 2.455 | -0.001
GEN-2017-094 | North | 15 - Eastern South Dakota | 655490 | WHTSWAN-ER7 | 115 | 12.285 | 12.292 | 0.007
GEN-2017-094 | North | 15 - Eastern South Dakota | 655493 | HANLON-ER7 | 115 | 3.836 | 3.815 | -0.021
GEN-2017-094 | North | 15 - Eastern South Dakota | 655494 | HANLON1-ER8 | 69 | 2.956 | 2.939 | -0.017
GEN-2017-094 | North | 15 - Eastern South Dakota | 655495 | HANLON2-ER8 | 69 | 2.959 | 2.942 | -0.017
GEN-2017-094 | North | 15 - Eastern South Dakota | 655499 | CARPENTR-ER8 | 69 | 3.244 | 3.233 | -0.011
GEN-2017-094 | North | 15 - Eastern South Dakota | 655510 | SB.LS-WK-ER4 | 230 | 6.531 | 6.536 | 0.005
GEN-2017-094 | North | 15 - Eastern South Dakota | 655765 | WHITLOCK_-RM | 230 | 4.567 | 4.568 | 0.001
GEN-2017-094 | North | 15 - Eastern South Dakota | 658088 | WTREAST7 | 115 | 9.545 | 9.516 | -0.029
GEN-2017-094 | North | 15 - Eastern South Dakota | 658090 | WTRTNPP | 115 | 9.016 | 8.988 | -0.028
GEN-2017-094 | North | 15 - Eastern South Dakota | 658092 | WTRWEST7 | 115 | 8.362 | 8.336 | -0.026
GEN-2017-094 | North | 15 - Eastern South Dakota | 658094 | WTRPELI7 | 115 | 8.496 | 8.469 | -0.027
GEN-2017-094 | North | 15 - Eastern South Dakota | 658120 | GARFLD 7 | 115 | 7.16 | 7.161 | 0.001
GEN-2017-094 | North | 15 - Eastern South Dakota | 659120 | BROADLND-BE3 | 345 | 4.057 | 4.083 | 0.026
GEN-2017-094 | North | 15 - Eastern South Dakota | 659122 | STORLA__-BE4 | 230 | 5.875 | 5.853 | -0.022
GEN-2017-094 | North | 15 - Eastern South Dakota | 659123 | STORLA__-BE7 | 115 | 6.609 | 6.585 | -0.024
GEN-2017-094 | North | 15 - Eastern South Dakota | 659160 | GROTON__-BE3 | 345 | 5.865 | 5.859 | -0.006
GEN-2017-094 | North | 15 - Eastern South Dakota | 659165 | G09_001IST | 345 | 6.093 | 6.086 | -0.007
GEN-2017-094 | North | 15 - Eastern South Dakota | 659187 | GROTON__-BE7 | 115 | 16.179 | 16.166 | -0.013
GEN-2017-094 | North | 15 - Eastern South Dakota | 659188 | PHILIP_T-BE4 | 230 | 5.24 | 5.231 | -0.009
GEN-2017-094 | North | 15 - Eastern South Dakota | 659205 | BROADLND-BE4 | 230 | 9.925 | 10.105 | 0.18
GEN-2017-094 | North | 15 - Eastern South Dakota | 659275 | GROTON_G-BE7 | 115 | 15.846 | 15.833 | -0.013
GEN-2017-094 | North | 15 - Eastern South Dakota | 659295 | SD.PW1__-BE4 | 230 | 5.497 | 5.482 | -0.015
GEN-2017-094 | North | 15 - Eastern South Dakota | 659310 | ORDWAY__-BE7 | 115 | 6.966 | 6.957 | -0.009
GEN-2017-094 | North | 15 - Eastern South Dakota | 659311 | PAHOJA__-BE4 | 230 | 7.279 | 7.25 | -0.029
GEN-2017-094 | North | 15 - Eastern South Dakota | 659420 | AV.LS-BD-BE3 | 345 | 16.248 | 16.251 | 0.003
GEN-2017-094 | North | 15 - Eastern South Dakota | 659421 | BD.LS-AV-BE3 | 345 | 4.057 | 4.083 | 0.026
GEN-2017-094 | North | 15 - Eastern South Dakota | 659424 | LO.LS-FT-BE3 | 345 | 16.424 | 16.423 | -0.001
GEN-2017-094 | North | 15 - Eastern South Dakota | 659472 | CROCKER_-UA3 | 345 | 5.266 | 5.26 | -0.006
GEN-2017-094 | North | 15 - Eastern South Dakota | 659716 | MAPLETAP-LO7 | 115 | 12.67 | 12.634 | -0.036
GEN-2017-094 | North | 15 - Eastern South Dakota | 659735 | CLEVELND-LO4 | 230 | 4.848 | 4.827 | -0.021
GEN-2017-094 | North | 15 - Eastern South Dakota | 659900 | EAGLE___-NI4 | 230 | 7.175 | 7.149 | -0.026
GEN-2017-094 | North | 15 - Eastern South Dakota | 660002 | REDFLD 7 | 115 | 4.003 | 4.002 | -0.001
GEN-2017-094 | North | 15 - Eastern South Dakota | 660003 | HURONWP7 | 115 | 10.144 | 10.206 | 0.062
GEN-2017-094 | North | 15 - Eastern South Dakota | 660004 | MITCHEL7 | 115 | 5.714 | 5.689 | -0.025
GEN-2017-094 | North | 15 - Eastern South Dakota | 660005 | TRIPP 7 | 115 | 3.981 | 3.968 | -0.013
GEN-2017-094 | North | 15 - Eastern South Dakota | 660007 | MENNOJT7 | 115 | 6.578 | 6.556 | -0.022
GEN-2017-094 | North | 15 - Eastern South Dakota | 660008 | MITCLNW7 | 115 | 5.323 | 5.3 | -0.023
GEN-2017-094 | North | 15 - Eastern South Dakota | 660009 | BTAP WP7 | 115 | 14.986 | 15.127 | 0.141
GEN-2017-094 | North | 15 - Eastern South Dakota | 660012 | HURON WP 8 | 69 | 6.055 | 6.065 | 0.01
GEN-2017-094 | North | 15 - Eastern South Dakota | 660026 | NAPA JCT7 | 115 | 8.409 | 8.386 | -0.023
GEN-2017-094 | North | 15 - Eastern South Dakota | 660040 | DAKOTACCESS7 | 115 | 4.477 | 4.477 | 0
GEN-2017-010 | North | 16 - Western North Dakota | 588550 | GEN-2017-010 | 230 | 3.927 | 4.311 | 0.384
GEN-2017-010 | North | 16 - Western North Dakota | 652219 | MI CTYE8 | 60 | 3.669 | 3.67 | 0.001
GEN-2017-010 | North | 16 - Western North Dakota | 652395 | SHIRLEY TAP | 115 | 3.057 | 3.065 | 0.008
GEN-2017-010 | North | 16 - Western North Dakota | 652402 | MI CTYW4 | 230 | 14.135 | 14.135 | 0
GEN-2017-010 | North | 16 - Western North Dakota | 652403 | DAWSONC4 | 230 | 3.987 | 4.01 | 0.023
GEN-2017-010 | North | 16 - Western North Dakota | 652404 | DAWSONC7 | 115 | 7.49 | 7.528 | 0.038
GEN-2017-010 | North | 16 - Western North Dakota | 652405 | FTPECK 4 | 230 | 2.204 | 2.205 | 0.001
GEN-2017-010 | North | 16 - Western North Dakota | 652411 | MI CTYE4 | 230 | 2.683 | 2.699 | 0.016
GEN-2017-010 | North | 16 - Western North Dakota | 652412 | MI CTYE7 | 115 | 3.86 | 3.875 | 0.015
GEN-2017-010 | North | 16 - Western North Dakota | 652424 | BELFELD3 | 345 | 6.358 | 6.393 | 0.035
GEN-2017-010 | North | 16 - Western North Dakota | 652425 | BELFELD4 | 230 | 8.803 | 8.895 | 0.092
GEN-2017-010 | North | 16 - Western North Dakota | 652450 | MT WEST4 | 230 | 14.241 | 14.241 | 0
GEN-2017-010 | North | 16 - Western North Dakota | 652468 | HEBRON 4 | 230 | 5.223 | 5.202 | -0.021
GEN-2017-010 | North | 16 - Western North Dakota | 652480 | MAURINE7 | 115 | 4.137 | 4.093 | -0.044
GEN-2017-010 | North | 16 - Western North Dakota | 652497 | MAURINE4 | 230 | 2.894 | 2.862 | -0.032
GEN-2017-010 | North | 16 - Western North Dakota | 652616 | MINGUSVILLE4 | 230 | 3.662 | 3.676 | 0.014
GEN-2017-010 | North | 16 - Western North Dakota | 652884 | NUNDRWD-LNX3 | 230 | 3.97 | 3.945 | -0.025
GEN-2017-010 | North | 16 - Western North Dakota | 655730 | CENTIPED-UM7 | 115 | 2.972 | 2.955 | -0.017
GEN-2017-010 | North | 16 - Western North Dakota | 659101 | ANTELOPE-BE3 | 345 | 16.054 | 16.036 | -0.018
GEN-2017-010 | North | 16 - Western North Dakota | 659124 | DICKINSN-BE4 | 230 | 6.689 | 6.703 | 0.014
GEN-2017-010 | North | 16 - Western North Dakota | 659125 | DICKINSON 7 | 115 | 7.997 | 7.979 | -0.018
GEN-2017-010 | North | 16 - Western North Dakota | 659182 | CHARL_CK-BE7 | 115 | 13.584 | 13.559 | -0.025
GEN-2017-010 | North | 16 - Western North Dakota | 659183 | CHARL_CK-BE3 | 345 | 9.96 | 9.972 | 0.012
GEN-2017-010 | North | 16 - Western North Dakota | 659247 | MEDORA__-UM4 | 230 | 4.944 | 4.963 | 0.019
GEN-2017-010 | North | 16 - Western North Dakota | 659249 | MILES_DC-BED | 230 | 14.135 | 14.135 | 0
GEN-2017-010 | North | 16 - Western North Dakota | 659263 | LITTL_MS-BE7 | 115 | 1.9 | 1.914 | 0.014
GEN-2017-010 | North | 16 - Western North Dakota | 659265 | LITTL_MS-BE4 | 230 | 3.323 | 3.486 | 0.163
GEN-2017-010 | North | 16 - Western North Dakota | 659266 | RHAME___-BE4 | 230 | 4.007 | 4.387 | 0.38
GEN-2017-010 | North | 16 - Western North Dakota | 659267 | RHAME___-BE7 | 115 | 2.046 | 2.055 | 0.009
GEN-2017-010 | North | 16 - Western North Dakota | 659302 | CHARL_CK-BE4 | 230 | 10.939 | 10.934 | -0.005
GEN-2017-010 | North | 16 - Western North Dakota | 659306 | S.HEART_-RR7 | 115 | 2.292 | 2.276 | -0.016
GEN-2017-010 | North | 16 - Western North Dakota | 659309 | S.HEART_-RR4 | 230 | 8.803 | 8.895 | 0.092
GEN-2017-010 | North | 16 - Western North Dakota | 659339 | BOWMAN__-BE4 | 230 | 3.556 | 3.745 | 0.189
GEN-2017-010 | North | 16 - Western North Dakota | 659340 | BOWMAN__-BE7 | 115 | 3.417 | 3.395 | -0.022
GEN-2017-010 | North | 16 - Western North Dakota | 659341 | NBURR___-GE7 | 115 | 1.794 | 1.769 | -0.025
GEN-2017-010 | North | 16 - Western North Dakota | 659350 | BISON___-GE7 | 115 | 1.487 | 1.448 | -0.039
GEN-2017-010 | North | 16 - Western North Dakota | 659351 | BISON___-GE4 | 230 | 2.823 | 2.809 | -0.014
GEN-2017-010 | North | 16 - Western North Dakota | 659352 | BISON___-GE8 | 69 | 1.989 | 1.947 | -0.042
GEN-2017-010 | North | 16 - Western North Dakota | 659384 | ROUNDUP_-BE3 | 345 | 8.155 | 8.148 | -0.007
GEN-2017-010 | North | 16 - Western North Dakota | 659390 | PATENTGT-BE3 | 345 | 6.986 | 6.979 | -0.007
GEN-2017-010 | North | 16 - Western North Dakota | 659400 | ND.SUN._-PP4 | 230 | 4.697 | 4.678 | -0.019
GEN-2017-010 | North | 16 - Western North Dakota | 659442 | 32STREET-RR7 | 115 | 1.922 | 1.908 | -0.014
GEN-2017-010 | North | 16 - Western North Dakota | 659448 | DAGLUM__-BE4 | 230 | 6.079 | 6.198 | 0.119
GEN-2017-010 | North | 16 - Western North Dakota | 659450 | BRADYWND 4 | 230 | 3.419 | 3.436 | 0.017
GEN-2017-010 | North | 16 - Western North Dakota | 659535 | BEAVRHIL-GW4 | 230 | 3.662 | 3.676 | 0.014
GEN-2017-010 | North | 16 - Western North Dakota | 661004 | BAKER 4 | 230 | 3.175 | 3.288 | 0.113
GEN-2017-010 | North | 16 - Western North Dakota | 661005 | BAKER 7 | 115 | 3.831 | 3.853 | 0.022
GEN-2017-010 | North | 16 - Western North Dakota | 661019 | MATHSON7 | 115 | 7.269 | 7.247 | -0.022
GEN-2017-010 | North | 16 - Western North Dakota | 661024 | WDICKSN7 | 115 | 6.156 | 6.131 | -0.025
GEN-2017-010 | North | 16 - Western North Dakota | 661032 | GLENDCT7 | 115 | 6.337 | 6.361 | 0.024
GEN-2017-010 | North | 16 - Western North Dakota | 661033 | CABINCR7 | 115 | 3.314 | 3.322 | 0.008
GEN-2017-010 | North | 16 - Western North Dakota | 661047 | HETINGR4 | 230 | 3.437 | 3.493 | 0.056
GEN-2017-010 | North | 16 - Western North Dakota | 661048 | HETINGR7 | 115 | 3.281 | 3.269 | -0.012
GEN-2017-010 | North | 16 - Western North Dakota | 661050 | GASCOYN7 | 115 | 1.825 | 1.808 | -0.017
GEN-2017-010 | North | 16 - Western North Dakota | 661053 | MANDAN 4 | 230 | 15.041 | 14.974 | -0.067
GEN-2017-010 | North | 16 - Western North Dakota | 661070 | N ENGLN7 | 115 | 3.581 | 3.561 | -0.02
GEN-2017-010 | North | 16 - Western North Dakota | 661300 | BAKER 8 | 60 | 5.024 | 5.016 | -0.008
GEN-2017-048 | North | 16 - Western North Dakota | 584870 | GEN-2015-046 | 345 | 4.503 | 4.619 | 0.116
GEN-2017-048 | North | 16 - Western North Dakota | 587030 | GEN-2016-004 | 230 | 7.496 | 7.463 | -0.033
GEN-2017-048 | North | 16 - Western North Dakota | 588870 | GEN-2017-048 | 230 | 4.327 | 5.262 | 0.935
GEN-2017-048 | North | 16 - Western North Dakota | 588874 | G17-048-TAP | 230 | 6.646 | 7.464 | 0.818
GEN-2017-048 | North | 16 - Western North Dakota | 603023 | MALLARD7 | 115 | 9.355 | 9.28 | -0.075
GEN-2017-048 | North | 16 - Western North Dakota | 615901 | GRE-STANTON4 | 230 | 17.86 | 17.837 | -0.023
GEN-2017-048 | North | 16 - Western North Dakota | 652216 | WATFORD4 | 230 | 6.301 | 6.309 | 0.008
GEN-2017-048 | North | 16 - Western North Dakota | 652391 | WILLISTON27 | 115 | 16.112 | 16.327 | 0.215
GEN-2017-048 | North | 16 - Western North Dakota | 652400 | WILISTN4 | 230 | 9.715 | 9.987 | 0.272
GEN-2017-048 | North | 16 - Western North Dakota | 652408 | WATFORD7 | 115 | 7.492 | 7.473 | -0.019
GEN-2017-048 | North | 16 - Western North Dakota | 652421 | WILISTN7 | 115 | 16.118 | 16.332 | 0.214
GEN-2017-048 | North | 16 - Western North Dakota | 652441 | GARRISN4 | 230 | 11.795 | 11.801 | 0.006
GEN-2017-048 | North | 16 - Western North Dakota | 652456 | WASHBRN4 | 230 | 10.055 | 10 | -0.055
GEN-2017-048 | North | 16 - Western North Dakota | 652651 | FAIRVIEW 7 | 115 | 4.697 | 4.682 | -0.015
GEN-2017-048 | North | 16 - Western North Dakota | 655641 | BERTHOLD-CP7 | 115 | 5.506 | 5.448 | -0.058
GEN-2017-048 | North | 16 - Western North Dakota | 655657 | SW.MINOT-CP7 | 115 | 7.249 | 7.184 | -0.065
GEN-2017-048 | North | 16 - Western North Dakota | 655791 | SPRINGLK-LY7 | 115 | 1.905 | 1.896 | -0.009
GEN-2017-048 | North | 16 - Western North Dakota | 655792 | NOHLEY -LY7 | 115 | 3.381 | 3.368 | -0.013
GEN-2017-048 | North | 16 - Western North Dakota | 655793 | MARLEY -LY7 | 115 | 5.603 | 5.597 | -0.006
GEN-2017-048 | North | 16 - Western North Dakota | 655840 | CHRRYCRK-MK7 | 115 | 7.492 | 7.473 | -0.019
GEN-2017-048 | North | 16 - Western North Dakota | 655879 | OASIS___-MK7 | 115 | 4.331 | 4.311 | -0.02
GEN-2017-048 | North | 16 - Western North Dakota | 655897 | COYOTCHR-MK7 | 115 | 5.394 | 5.373 | -0.021
GEN-2017-048 | North | 16 - Western North Dakota | 655902 | PLSNTV_T-MW7 | 115 | 5.662 | 5.637 | -0.025
GEN-2017-048 | North | 16 - Western North Dakota | 655909 | HESS GAS-MW7 | 115 | 9.101 | 9.187 | 0.086
GEN-2017-048 | North | 16 - Western North Dakota | 655916 | PALERMO -MW7 | 115 | 5.205 | 5.158 | -0.047
GEN-2017-048 | North | 16 - Western North Dakota | 655917 | STANLEY -MW7 | 115 | 4.643 | 4.597 | -0.046
GEN-2017-048 | North | 16 - Western North Dakota | 655918 | PALGASPL-MW7 | 115 | 4.589 | 4.542 | -0.047
GEN-2017-048 | North | 16 - Western North Dakota | 655922 | W.BANK__-MW7 | 115 | 6.448 | 6.474 | 0.026
GEN-2017-048 | North | 16 - Western North Dakota | 655923 | FARMVALE-MW7 | 115 | 4.204 | 4.191 | -0.013
GEN-2017-048 | North | 16 - Western North Dakota | 655924 | STATELIN-MW7 | 115 | 13.293 | 13.354 | 0.061
GEN-2017-048 | North | 16 - Western North Dakota | 655925 | JUDSON -MW7 | 115 | 13.251 | 13.363 | 0.112
GEN-2017-048 | North | 16 - Western North Dakota | 655926 | SW.WLSTN-MW7 | 115 | 7.899 | 7.912 | 0.013
GEN-2017-048 | North | 16 - Western North Dakota | 655930 | WHTEARTH-MW7 | 115 | 9.505 | 9.602 | 0.097
GEN-2017-048 | North | 16 - Western North Dakota | 655931 | BLKTLTAP-MW7 | 115 | 5.311 | 5.312 | 0.001
GEN-2017-048 | North | 16 - Western North Dakota | 655933 | N.MISRDG-MW7 | 115 | 9.345 | 9.396 | 0.051
GEN-2017-048 | North | 16 - Western North Dakota | 655934 | N.WLST_T-MW7 | 115 | 9.285 | 9.339 | 0.054
GEN-2017-048 | North | 16 - Western North Dakota | 655935 | NW.WLSTN-MW7 | 115 | 9.249 | 9.297 | 0.048
GEN-2017-048 | North | 16 - Western North Dakota | 655940 | MONT -MW7 | 115 | 11.593 | 11.663 | 0.07
GEN-2017-048 | North | 16 - Western North Dakota | 655941 | STRNDAHL-MW7 | 115 | 5.125 | 5.119 | -0.006
GEN-2017-048 | North | 16 - Western North Dakota | 655942 | N.TWELVE-MW7 | 115 | 5.81 | 5.826 | 0.016
GEN-2017-048 | North | 16 - Western North Dakota | 655943 | FARMVL_T-MW7 | 115 | 6.388 | 6.416 | 0.028
GEN-2017-048 | North | 16 - Western North Dakota | 655944 | PLAZA -MW7 | 115 | 3.965 | 3.931 | -0.034
GEN-2017-048 | North | 16 - Western North Dakota | 655945 | WHEELS_T-MW7 | 115 | 7.714 | 7.81 | 0.096
GEN-2017-048 | North | 16 - Western North Dakota | 655946 | POWERSLK-MW7 | 115 | 4.324 | 4.291 | -0.033
GEN-2017-048 | North | 16 - Western North Dakota | 655947 | PWRSLKTP-MW7 | 115 | 6.444 | 6.433 | -0.011
GEN-2017-048 | North | 16 - Western North Dakota | 655948 | LIBERTY -MW7 | 115 | 5.919 | 5.897 | -0.022
GEN-2017-048 | North | 16 - Western North Dakota | 655949 | BLAISDEL-MW7 | 115 | 6.679 | 6.635 | -0.044
GEN-2017-048 | North | 16 - Western North Dakota | 655952 | TIOGA.N_-MW7 | 115 | 9.132 | 9.22 | 0.088
GEN-2017-048 | North | 16 - Western North Dakota | 655953 | W.BANK_T-MW7 | 115 | 7.407 | 7.447 | 0.04
GEN-2017-048 | North | 16 - Western North Dakota | 655954 | ELLISVIL-MW7 | 115 | 4.929 | 4.934 | 0.005
GEN-2017-048 | North | 16 - Western North Dakota | 655955 | ZAHL -MW7 | 115 | 4.915 | 4.915 | 0
GEN-2017-048 | North | 16 - Western North Dakota | 655959 | EPPING -MW7 | 115 | 6.906 | 6.965 | 0.059
GEN-2017-048 | North | 16 - Western North Dakota | 659105 | LELAND_O-BE3 | 345 | 16.185 | 16.135 | -0.05
GEN-2017-048 | North | 16 - Western North Dakota | 659106 | LELAND_O-BE4 | 230 | 22.621 | 22.557 | -0.064
GEN-2017-048 | North | 16 - Western North Dakota | 659108 | LOGAN___-BE4 | 230 | 5.493 | 5.46 | -0.033
GEN-2017-048 | North | 16 - Western North Dakota | 659112 | CULBRTSN-UM7 | 115 | 4.472 | 4.473 | 0.001
GEN-2017-048 | North | 16 - Western North Dakota | 659138 | NESET___-BE4 | 230 | 8.87 | 9.376 | 0.506
GEN-2017-048 | North | 16 - Western North Dakota | 659139 | NESET___-BE7 | 115 | 10.002 | 10.122 | 0.12
GEN-2017-048 | North | 16 - Western North Dakota | 659143 | BLAISDEL-BE4 | 230 | 5.216 | 5.227 | 0.011
GEN-2017-048 | North | 16 - Western North Dakota | 659144 | BLAISDEL-BE7 | 115 | 6.881 | 6.838 | -0.043
GEN-2017-048 | North | 16 - Western North Dakota | 659151 | RICHLAND-BE7 | 115 | 5.235 | 5.222 | -0.013
GEN-2017-048 | North | 16 - Western North Dakota | 659155 | LOGAN___-BE7 | 115 | 9.459 | 9.387 | -0.072
GEN-2017-048 | North | 16 - Western North Dakota | 659183 | CHARL_CK-BE3 | 345 | 9.948 | 9.972 | 0.024
GEN-2017-048 | North | 16 - Western North Dakota | 659199 | BASIN___-BE4 | 230 | 20.601 | 20.539 | -0.062
GEN-2017-048 | North | 16 - Western North Dakota | 659262 | CULBSN.E-BE7 | 115 | 5.859 | 5.865 | 0.006
GEN-2017-048 | North | 16 - Western North Dakota | 659269 | CULB_GEN-BE7 | 115 | 5.811 | 5.82 | 0.009
GEN-2017-048 | North | 16 - Western North Dakota | 659302 | CHARL_CK-BE4 | 230 | 10.929 | 10.934 | 0.005
GEN-2017-048 | North | 16 - Western North Dakota | 659308 | KENASTON-BE7 | 115 | 3.173 | 3.129 | -0.044
GEN-2017-048 | North | 16 - Western North Dakota | 659333 | JUDSON__-BE3 | 345 | 6.72 | 6.872 | 0.152
GEN-2017-048 | North | 16 - Western North Dakota | 659334 | JUDSON__-BE4 | 230 | 9.589 | 9.838 | 0.249
GEN-2017-048 | North | 16 - Western North Dakota | 659336 | TANDE___-BE3 | 345 | 5.564 | 5.773 | 0.209
GEN-2017-048 | North | 16 - Western North Dakota | 659337 | TANDE___-BE4 | 230 | 8.75 | 9.223 | 0.473
GEN-2017-048 | North | 16 - Western North Dakota | 659362 | WHEELOCK-BE4 | 230 | 6.56 | 7.048 | 0.488
GEN-2017-048 | North | 16 - Western North Dakota | 659363 | WHEELOCK-BE7 | 115 | 7.917 | 8.038 | 0.121
GEN-2017-048 | North | 16 - Western North Dakota | 659390 | PATENTGT-BE3 | 345 | 6.914 | 6.979 | 0.065
GEN-2017-048 | North | 16 - Western North Dakota | 659404 | BURKE___-PP3 | 345 | 4.869 | 5.017 | 0.148
GEN-2017-048 | North | 16 - Western North Dakota | 659427 | TN.LS-JD-BE3 | 345 | 5.564 | 5.773 | 0.209
GEN-2017-048 | North | 16 - Western North Dakota | 661052 | KENMARE7 | 115 | 3.107 | 3.064 | -0.043
GEN-2017-048 | North | 16 - Western North Dakota | 661080 | STANLEY7 | 115 | 3.558 | 3.517 | -0.041
GEN-2017-048 | North | 16 - Western North Dakota | 661084 | TIOGA4 4 | 230 | 8.87 | 9.376 | 0.506
GEN-2017-048 | North | 16 - Western North Dakota | 661085 | TIOGA4 7 | 115 | 9.635 | 9.742 | 0.107
GEN-2017-048 | North | 16 - Western North Dakota | 661086 | TIOGA7 7 | 115 | 7.974 | 8.019 | 0.045
GEN-2017-048 | North | 16 - Western North Dakota | 661087 | RAY JCT7 | 115 | 5.184 | 5.169 | -0.015
GEN-2017-048 | North | 16 - Western North Dakota | 661089 | LTLMUDY7 | 115 | 6.442 | 6.441 | -0.001
GEN-2017-048 | North | 16 - Western North Dakota | 661281 | LIGNITE7 | 115 | 1.511 | 1.484 | -0.027
GEN-2017-048 | North | 16 - Western North Dakota | 672501 | BD 6 | 138 | 13.893 | 13.893 | 0
GEN-2017-048 | North | 16 - Western North Dakota | 672601 | BD 4 | 230 | 14.645 | 14.659 | 0.014
GEN-2017-048 | North | 16 - Western North Dakota | 672602 | BDX 4 | 230 | 5.464 | 5.433 | -0.031
GEN-2017-048 | North | 16 - Western North Dakota | 672603 | BDV 4 | 230 | 5.468 | 5.436 | -0.032
GEN-2017-048 | North | 16 - Western North Dakota | 672607 | REGINA 4 | 230 | 8.12 | 8.114 | -0.006
GEN-2017-048 | North | 16 - Western North Dakota | 672613 | AUBURNTON 4 | 230 | 5.741 | 5.721 | -0.02
GEN-2017-048 | North | 16 - Western North Dakota | 672621 | SHAND 4 | 230 | 10.193 | 10.194 | 0.001
GEN-2017-048 | North | 16 - Western North Dakota | 673601 | KISBEY TAP 4 | 230 | 5.672 | 5.662 | -0.01
GEN-2017-047 | South | 02 - Hitchland | 515554 | BVRCNTY7 | 345 | 19.13 | 19.18 | 0.05
GEN-2017-047 | South | 02 - Hitchland | 522898 | BEARD-T 2 | 69 | 2.01 | 2.07 | 0.06
GEN-2017-047 | South | 02 - Hitchland | 522910 | ADAMS 2 | 69 | 1.49 | 1.52 | 0.03
GEN-2017-047 | South | 02 - Hitchland | 522912 | Y TAP 3 | 115 | 5.26 | 5.35 | 0.09
GEN-2017-047 | South | 02 - Hitchland | 522917 | ADAMS-T 2 | 69 | 2.05 | 2.1 | 0.05
GEN-2017-047 | South | 02 - Hitchland | 522918 | COLE 2 | 69 | 3.03 | 3.2 | 0.17
GEN-2017-047 | South | 02 - Hitchland | 522927 | JEFFERSON 2 | 69 | 2.25 | 2.3 | 0.05
GEN-2017-047 | South | 02 - Hitchland | 522934 | TURPIN-T 2 | 69 | 2.03 | 2.11 | 0.08
GEN-2017-047 | South | 02 - Hitchland | 522943 | BEARD 2 | 69 | 1.79 | 1.84 | 0.05
GEN-2017-047 | South | 02 - Hitchland | 522957 | POWELL CNR 3 | 115 | 4.41 | 4.47 | 0.06
GEN-2017-047 | South | 02 - Hitchland | 523012 | TC-ANTHY_TP3 | 115 | 2.14 | 2.3 | 0.16
GEN-2017-047 | South | 02 - Hitchland | 523024 | TC-BEAVER 3 | 115 | 1.66 | 1.76 | 0.1
GEN-2017-047 | South | 02 - Hitchland | 523072 | TC-SEABOARD2 | 69 | 6.77 | 6.87 | 0.1
GEN-2017-047 | South | 02 - Hitchland | 523079 | TC-GUYMON_N2 | 69 | 7.18 | 7.28 | 0.1
GEN-2017-047 | South | 02 - Hitchland | 523089 | TC-TXCOUNTY2 | 69 | 9.2 | 9.35 | 0.15
GEN-2017-047 | South | 02 - Hitchland | 523090 | TEXAS_CNTY 3 | 115 | 9.12 | 9.34 | 0.22
GEN-2017-047 | South | 02 - Hitchland | 523093 | HITCHLAND 3 | 115 | 19.11 | 19.35 | 0.24
GEN-2017-047 | South | 02 - Hitchland | 523095 | HITCHLAND 6 | 230 | 16.26 | 16.42 | 0.16
GEN-2017-047 | South | 02 - Hitchland | 523097 | HITCHLAND 7 | 345 | 17.64 | 17.73 | 0.09
GEN-2017-047 | South | 02 - Hitchland | 523103 | NOBLE_WND 3 | 115 | 11.74 | 11.76 | 0.02
GEN-2017-047 | South | 02 - Hitchland | 523106 | TXPHSF 3 | 115 | 4.55 | 4.6 | 0.05
GEN-2017-047 | South | 02 - Hitchland | 523112 | NOVUS1 7 | 345 | 17.28 | 17.37 | 0.09
GEN-2017-047 | South | 02 - Hitchland | 523113 | TC-MCMURRY 3 | 115 | 6.97 | 7.19 | 0.22
GEN-2017-047 | South | 02 - Hitchland | 523120 | COLE 3 | 115 | 4.49 | 5.16 | 0.67
GEN-2017-047 | South | 02 - Hitchland | 523135 | LIPSCOMB 3 | 115 | 2.87 | 2.96 | 0.09
GEN-2017-047 | South | 02 - Hitchland | 523140 | TXFARMS 3 | 115 | 5.52 | 5.71 | 0.19
GEN-2017-047 | South | 02 - Hitchland | 523142 | TC-AGGIE 3 | 115 | 4.35 | 4.91 | 0.56
GEN-2017-047 | South | 02 - Hitchland | 523147 | WADE 3 | 115 | 3.67 | 3.8 | 0.13
GEN-2017-047 | South | 02 - Hitchland | 523154 | OCHILTREE 3 | 115 | 6.47 | 6.83 | 0.36
GEN-2017-047 | South | 02 - Hitchland | 523155 | OCHILTREE 6 | 230 | 4.51 | 4.61 | 0.1
GEN-2017-047 | South | 02 - Hitchland | 523157 | PERRYTON 2 | 69 | 2.52 | 2.57 | 0.05
GEN-2017-047 | South | 02 - Hitchland | 523158 | PERRYTON 3 | 115 | 6.16 | 6.49 | 0.33
GEN-2017-047 | South | 02 - Hitchland | 523160 | FRISCO_WND 3 | 115 | 7.5 | 7.53 | 0.03
GEN-2017-047 | South | 02 - Hitchland | 523174 | GOODWELLWND3 | 115 | 7.09 | 7.12 | 0.03
GEN-2017-047 | South | 02 - Hitchland | 523185 | SPEARMAN 2 | 69 | 4.41 | 4.43 | 0.02
GEN-2017-047 | South | 02 - Hitchland | 523186 | SPEARMAN 3 | 115 | 9.37 | 9.46 | 0.09
GEN-2017-047 | South | 02 - Hitchland | 523195 | HANSFORD 3 | 115 | 10.98 | 11.07 | 0.09
GEN-2017-047 | South | 02 - Hitchland | 523203 | SPEARMNSUB 3 | 115 | 6.51 | 6.61 | 0.1
GEN-2017-047 | South | 02 - Hitchland | 523215 | FREWHELCOL17 | 345 | 10.3 | 10.33 | 0.03
GEN-2017-047 | South | 02 - Hitchland | 523266 | PRINGLE 3 | 115 | 11.73 | 11.78 | 0.05
GEN-2017-047 | South | 02 - Hitchland | 523308 | MOORE_E 3 | 115 | 12.2 | 12.21 | 0.01
GEN-2017-047 | South | 02 - Hitchland | 523309 | MOORE_CNTY 6 | 230 | 7.23 | 7.24 | 0.01
GEN-2017-047 | South | 02 - Hitchland | 523823 | CARPENTER 7 | 345 | 6.94 | 6.95 | 0.01
GEN-2017-047 | South | 02 - Hitchland | 523959 | POTTER_CO 6 | 230 | 22.46 | 22.48 | 0.02
GEN-2017-047 | South | 02 - Hitchland | 523961 | POTTER_CO 7 | 345 | 10.22 | 10.24 | 0.02
GEN-2017-047 | South | 02 - Hitchland | 539672 | E-LIBER3 | 115 | 4.76 | 4.77 | 0.01
GEN-2017-047 | South | 02 - Hitchland | 576395 | GEN-2010-014 | 345 | 12.69 | 12.74 | 0.05
GEN-2017-047 | South | 02 - Hitchland | 588860 | GEN-2017-047 | 115 | 4.39 | 5.06 | 0.67
GEN-2017-047 | South | 02 - Hitchland | 589380 | GEN-2017-100 | 115 | 5.44 | 5.53 | 0.09
GEN-2017-058 | South | 02 - Hitchland | 523309 | MOORE_CNTY 6 | 230 | 7.24 | 7.24 | 0
GEN-2017-058 | South | 02 - Hitchland | 523869 | CHAN+TASCOS6 | 230 | 4.53 | 4.53 | 0
GEN-2017-058 | South | 02 - Hitchland | 523959 | POTTER_CO 6 | 230 | 22.45 | 22.48 | 0.03
GEN-2017-058 | South | 02 - Hitchland | 523961 | POTTER_CO 7 | 345 | 10.23 | 10.24 | 0.01
GEN-2017-058 | South | 02 - Hitchland | 523979 | HARRNG_EST 6 | 230 | 26.35 | 26.37 | 0.02
GEN-2017-058 | South | 02 - Hitchland | 524010 | ROLLHILLS 6 | 230 | 20.16 | 20.19 | 0.03
GEN-2017-058 | South | 02 - Hitchland | 524243 | OUTPOST 3 | 115 | 10.09 | 10.12 | 0.03
GEN-2017-058 | South | 02 - Hitchland | 524266 | BUSHLAND 3 | 115 | 10.01 | 10.03 | 0.02
GEN-2017-058 | South | 02 - Hitchland | 524267 | BUSHLAND 6 | 230 | 11.68 | 11.71 | 0.03
GEN-2017-058 | South | 02 - Hitchland | 524276 | WILDOR_WND 6 | 230 | 5.6 | 5.62 | 0.02
GEN-2017-058 | South | 02 - Hitchland | 524290 | WILDOR2_JUS6 | 230 | 7.64 | 7.66 | 0.02
GEN-2017-058 | South | 02 - Hitchland | 524516 | CANYON_WEST3 | 115 | 6.09 | 6.13 | 0.04
GEN-2017-058 | South | 02 - Hitchland | 524536 | DS-#5&#11 2 | 69 | 3.37 | 3.44 | 0.07
GEN-2017-058 | South | 02 - Hitchland | 524554 | CENTRE_ST 2 | 69 | 4.17 | 4.26 | 0.09
GEN-2017-058 | South | 02 - Hitchland | 524556 | LAPLATA 3 | 115 | 7.41 | 7.58 | 0.17
GEN-2017-058 | South | 02 - Hitchland | 524561 | DS-MTR 2 | 69 | 6.86 | 7.01 | 0.15
GEN-2017-058 | South | 02 - Hitchland | 524567 | NE_HEREFORD3 | 115 | 13.08 | 13.37 | 0.29
GEN-2017-058 | South | 02 - Hitchland | 524573 | NE_HEREFORD2 | 69 | 7.72 | 7.89 | 0.17
GEN-2017-058 | South | 02 - Hitchland | 524575 | DS-#25+ 3 | 115 | 13.47 | 13.66 | 0.19
GEN-2017-058 | South | 02 - Hitchland | 524580 | DS-#9 +2 | 69 | 3.46 | 3.52 | 0.06
GEN-2017-058 | South | 02 - Hitchland | 524590 | DAWN 3 | 115 | 7.14 | 7.22 | 0.08
GEN-2017-058 | South | 02 - Hitchland | 524597 | PANDAHFD 3 | 115 | 11.44 | 11.59 | 0.15
GEN-2017-058 | South | 02 - Hitchland | 524604 | HEREFRD_SB 2 | 69 | 4.87 | 4.95 | 0.08
GEN-2017-058 | South | 02 - Hitchland | 524605 | HEREFRD_NB 2 | 69 | 4.87 | 4.95 | 0.08
GEN-2017-058 | South | 02 - Hitchland | 524606 | HEREFORD 3 | 115 | 15 | 15.24 | 0.24
GEN-2017-058 | South | 02 - Hitchland | 524608 | HERFRD_STH 2 | 69 | 4.87 | 4.95 | 0.08
GEN-2017-058 | South | 02 - Hitchland | 524622 | DEAFSMITH 3 | 115 | 17.62 | 17.88 | 0.26
GEN-2017-058 | South | 02 - Hitchland | 524623 | DEAFSMITH 6 | 230 | 22.26 | 22.38 | 0.12
GEN-2017-058 | South | 02 - Hitchland | 524627 | DEFPLT_SS 6 | 230 | 16.43 | 16.52 | 0.09
GEN-2017-058 | South | 02 - Hitchland | 524629 | DS-#6 3 | 115 | 7.24 | 7.34 | 0.1
GEN-2017-058 | South | 02 - Hitchland | 524633 | DS-#4 +2 | 69 | 3.51 | 3.57 | 0.06
GEN-2017-058 | South | 02 - Hitchland | 524640 | DS-#8 2 | 69 | 2.04 | 2.08 | 0.04
GEN-2017-058 | South | 02 - Hitchland | 524648 | CARGILL 3 | 115 | 4.25 | 4.29 | 0.04
GEN-2017-058 | South | 02 - Hitchland | 524655 | FRIONA 3 | 115 | 4.27 | 4.31 | 0.04
GEN-2017-058 | South | 02 - Hitchland | 524664 | DS-#24 +3 | 115 | 4.44 | 4.47 | 0.03
GEN-2017-058 | South | 02 - Hitchland | 524688 | DS-#3 2 | 69 | 3.04 | 3.05 | 0.01
GEN-2017-058 | South | 02 - Hitchland | 524694 | DS-#22 3 | 115 | 4.74 | 4.76 | 0.02
GEN-2017-058 | South | 02 - Hitchland | 524721 | DS-#15&#19+2 | 69 | 3.65 | 3.67 | 0.02
GEN-2017-058 | South | 02 - Hitchland | 524728 | DS-CASTRO 2 | 69 | 4.39 | 4.42 | 0.03
GEN-2017-058 | South | 02 - Hitchland | 524734 | DS-#21 3 | 115 | 9.7 | 9.76 | 0.06
GEN-2017-058 | South | 02 - Hitchland | 524745 | CASTRO_CNTY2 | 69 | 9.08 | 9.13 | 0.05
GEN-2017-058 | South | 02 - Hitchland | 524746 | CASTRO_CNTY3 | 115 | 10.21 | 10.27 | 0.06
GEN-2017-058 | South | 02 - Hitchland | 524757 | BETHEL_COL13 | 115 | 8.52 | 8.56 | 0.04
GEN-2017-058 | South | 02 - Hitchland | 524909 | ROSEVELT_N 6 | 230 | 9.58 | 9.6 | 0.02
GEN-2017-058 | South | 02 - Hitchland | 525019 | MULSHVLY_TP3 | 115 | 6.6 | 6.63 | 0.03
GEN-2017-058 | South | 02 - Hitchland | 525050 | BC-KELLEY +3 | 115 | 7.93 | 7.97 | 0.04
GEN-2017-058 | South | 02 - Hitchland | 525056 | BC-EARTH 3 | 115 | 8.39 | 8.43 | 0.04
GEN-2017-058 | South | 02 - Hitchland | 525124 | HART_INDUST3 | 115 | 7.93 | 7.95 | 0.02
GEN-2017-058 | South | 02 - Hitchland | 525192 | KRESS_INT 3 | 115 | 12.41 | 12.44 | 0.03
GEN-2017-058 | South | 02 - Hitchland | 525213 | SWISHER 6 | 230 | 10.68 | 10.7 | 0.02
GEN-2017-058 | South | 02 - Hitchland | 525230 | NEWPOT_SS 6 | 230 | 7.3 | 7.31 | 0.01
GEN-2017-058 | South | 02 - Hitchland | 525446 | RKYFORD_TP 3 | 115 | 10.28 | 10.32 | 0.04
GEN-2017-058 | South | 02 - Hitchland | 525454 | HALE_CNTY 3 | 115 | 10.48 | 10.5 | 0.02
GEN-2017-058 | South | 02 - Hitchland | 525460 | NEWHART 3 | 115 | 16.95 | 17 | 0.05
GEN-2017-058 | South | 02 - Hitchland | 525461 | NEWHART 6 | 230 | 11.28 | 11.32 | 0.04
GEN-2017-058 | South | 02 - Hitchland | 525480 | PLANT_X 3 | 115 | 19.15 | 19.24 | 0.09
GEN-2017-058 | South | 02 - Hitchland | 525481 | PLANT_X 6 | 230 | 22.26 | 22.38 | 0.12
GEN-2017-058 | South | 02 - Hitchland | 525524 | TOLK_EAST 6 | 230 | 27.78 | 27.87 | 0.09
GEN-2017-058 | South | 02 - Hitchland | 525531 | TOLK_WEST 6 | 230 | 27.78 | 27.87 | 0.09
GEN-2017-058 | South | 02 - Hitchland | 525543 | TOLK_TAP 6 | 230 | 27.78 | 27.87 | 0.09
GEN-2017-058 | South | 02 - Hitchland | 525586 | NEEDMORE 6 | 230 | 11.48 | 11.51 | 0.03
GEN-2017-058 | South | 02 - Hitchland | 525614 | W_LITLFLDTP3 | 115 | 8.03 | 8.06 | 0.03
GEN-2017-058 | South | 02 - Hitchland | 525637 | LAMB_CNTY 6 | 230 | 5.6 | 5.62 | 0.02
GEN-2017-058 | South | 02 - Hitchland | 525830 | TUCO_INT 6 | 230 | 21.8 | 21.82 | 0.02
GEN-2017-058 | South | 02 - Hitchland | 526434 | SUNDOWN 3 | 115 | 11.96 | 11.99 | 0.03
GEN-2017-058 | South | 02 - Hitchland | 526435 | SUNDOWN 6 | 230 | 11.23 | 11.25 | 0.02
GEN-2017-058 | South | 02 - Hitchland | 526460 | AMOCO_SS 6 | 230 | 9.87 | 9.89 | 0.02
GEN-2017-058 | South | 02 - Hitchland | 526525 | WOLFFORTH 6 | 230 | 13.5 | 13.51 | 0.01
GEN-2017-058 | South | 02 - Hitchland | 588440 | GEN-2016-172 | 115 | 14.32 | 14.36 | 0.04
GEN-2017-058 | South | 02 - Hitchland | 588700 | GEN-2017-026 | 230 | 9.12 | 9.15 | 0.03
GEN-2017-058 | South | 02 - Hitchland | 588960 | GEN-2017-058 | 115 | 7.98 | 8.29 | 0.31
GEN-2017-058 | South | 02 - Hitchland | 589180 | GEN-2017-080 | 230 | 24 | 24.07 | 0.07
GEN-2017-100 | South | 02 - Hitchland | 515554 | BVRCNTY7 | 345 | 19.16 | 19.18 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 515590 | PALDR2W7 | 345 | 16.03 | 16.05 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 515618 | BALKOW 7 | 345 | 15.28 | 15.3 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 515677 | BADGER 7 | 345 | 16.85 | 16.87 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 522905 | STURGIS 2 | 69 | 1.93 | 1.98 | 0.05
GEN-2017-100 | South | 02 - Hitchland | 522912 | Y TAP 3 | 115 | 5.21 | 5.35 | 0.14
GEN-2017-100 | South | 02 - Hitchland | 522918 | COLE 2 | 69 | 3.16 | 3.2 | 0.04
GEN-2017-100 | South | 02 - Hitchland | 522921 | THRASH 2 | 69 | 3.91 | 4.01 | 0.1
GEN-2017-100 | South | 02 - Hitchland | 522927 | JEFFERSON 2 | 69 | 2.25 | 2.3 | 0.05
GEN-2017-100 | South | 02 - Hitchland | 522929 | POWELL CNR 2 | 69 | 4.27 | 4.38 | 0.11
GEN-2017-100 | South | 02 - Hitchland | 522934 | TURPIN-T 2 | 69 | 2.07 | 2.11 | 0.04
GEN-2017-100 | South | 02 - Hitchland | 522944 | STURGIS-T 2 | 69 | 3.61 | 3.7 | 0.09
GEN-2017-100 | South | 02 - Hitchland | 522948 | WEST_TIE 2 | 69 | 4.04 | 4.14 | 0.1
GEN-2017-100 | South | 02 - Hitchland | 522950 | THRALL 2 | 69 | 1.7 | 1.74 | 0.04
GEN-2017-100 | South | 02 - Hitchland | 522954 | HOVEY 3 | 115 | 3.76 | 3.85 | 0.09
GEN-2017-100 | South | 02 - Hitchland | 522957 | POWELL CNR 3 | 115 | 4.36 | 4.47 | 0.11
GEN-2017-100 | South | 02 - Hitchland | 522960 | WEST-TIE 3 | 115 | 3.01 | 3.08 | 0.07
GEN-2017-100 | South | 02 - Hitchland | 523001 | TC-HOVEY 2 | 69 | 6.68 | 6.86 | 0.18
GEN-2017-100 | South | 02 - Hitchland | 523012 | TC-ANTHY_TP3 | 115 | 2.27 | 2.3 | 0.03
GEN-2017-100 | South | 02 - Hitchland | 523024 | TC-BEAVER 3 | 115 | 1.74 | 1.76 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 523044 | TC-ELKHRT_T2 | 69 | 3.2 | 3.28 | 0.08
GEN-2017-100 | South | 02 - Hitchland | 523051 | TC-EVAREG 2 | 69 | 2.9 | 2.97 | 0.07
GEN-2017-100 | South | 02 - Hitchland | 523065 | TC-THOMPSON2 | 69 | 7.15 | 7.35 | 0.2
GEN-2017-100 | South | 02 - Hitchland | 523072 | TC-SEABOARD2 | 69 | 6.69 | 6.87 | 0.18
GEN-2017-100 | South | 02 - Hitchland | 523079 | TC-GUYMON_N2 | 69 | 7.09 | 7.28 | 0.19
GEN-2017-100 | South | 02 - Hitchland | 523089 | TC-TXCOUNTY2 | 69 | 9.1 | 9.35 | 0.25
GEN-2017-100 | South | 02 - Hitchland | 523090 | TEXAS_CNTY 3 | 115 | 9.09 | 9.34 | 0.25
GEN-2017-100 | South | 02 - Hitchland | 523093 | HITCHLAND 3 | 115 | 19.19 | 19.35 | 0.16
GEN-2017-100 | South | 02 - Hitchland | 523095 | HITCHLAND 6 | 230 | 16.36 | 16.42 | 0.06
GEN-2017-100 | South | 02 - Hitchland | 523097 | HITCHLAND 7 | 345 | 17.69 | 17.73 | 0.04
GEN-2017-100 | South | 02 - Hitchland | 523099 | TC-WHITING 3 | 115 | 2.75 | 2.83 | 0.08
GEN-2017-100 | South | 02 - Hitchland | 523103 | NOBLE_WND 3 | 115 | 11.73 | 11.76 | 0.03
GEN-2017-100 | South | 02 - Hitchland | 523106 | TXPHSF 3 | 115 | 4.49 | 4.6 | 0.11
GEN-2017-100 | South | 02 - Hitchland | 523111 | NOVUS1 3 | 115 | 21.03 | 21.06 | 0.03
GEN-2017-100 | South | 02 - Hitchland | 523112 | NOVUS1 7 | 345 | 17.33 | 17.37 | 0.04
GEN-2017-100 | South | 02 - Hitchland | 523113 | TC-MCMURRY 3 | 115 | 7 | 7.19 | 0.19
GEN-2017-100 | South | 02 - Hitchland | 523120 | COLE 3 | 115 | 5.09 | 5.16 | 0.07
GEN-2017-100 | South | 02 - Hitchland | 523130 | NBLWND-HV2 3 | 115 | 5.65 | 5.66 | 0.01
GEN-2017-100 | South | 02 - Hitchland | 523131 | NBLWND-HV3 3 | 115 | 8.81 | 8.83 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 523140 | TXFARMS 3 | 115 | 5.67 | 5.71 | 0.04
GEN-2017-100 | South | 02 - Hitchland | 523142 | TC-AGGIE 3 | 115 | 4.84 | 4.91 | 0.07
GEN-2017-100 | South | 02 - Hitchland | 523147 | WADE 3 | 115 | 3.77 | 3.8 | 0.03
GEN-2017-100 | South | 02 - Hitchland | 523154 | OCHILTREE 3 | 115 | 6.78 | 6.83 | 0.05
GEN-2017-100 | South | 02 - Hitchland | 523155 | OCHILTREE 6 | 230 | 4.59 | 4.61 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 523158 | PERRYTON 3 | 115 | 6.44 | 6.49 | 0.05
GEN-2017-100 | South | 02 - Hitchland | 523160 | FRISCO_WND 3 | 115 | 7.49 | 7.53 | 0.04
GEN-2017-100 | South | 02 - Hitchland | 523161 | RB-CLDWTRTP3 | 115 | 4.25 | 4.26 | 0.01
GEN-2017-100 | South | 02 - Hitchland | 523168 | SHERMAN 3 | 115 | 4.69 | 4.7 | 0.01
GEN-2017-100 | South | 02 - Hitchland | 523174 | GOODWELLWND3 | 115 | 7.07 | 7.12 | 0.05
GEN-2017-100 | South | 02 - Hitchland | 523175 | LASLEY 3 | 115 | 6.15 | 6.17 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 523176 | RB-ELKS 3 | 115 | 6.07 | 6.09 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 523177 | RB-SPURLCK+3 | 115 | 6.12 | 6.13 | 0.01
GEN-2017-100 | South | 02 - Hitchland | 523185 | SPEARMAN 2 | 69 | 4.41 | 4.43 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 523186 | SPEARMAN 3 | 115 | 9.42 | 9.46 | 0.04
GEN-2017-100 | South | 02 - Hitchland | 523195 | HANSFORD 3 | 115 | 11 | 11.07 | 0.07
GEN-2017-100 | South | 02 - Hitchland | 523197 | EXCELN4-HV23 | 115 | 5.03 | 5.05 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 523198 | EXCELN4-HV13 | 115 | 4.46 | 4.48 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 523203 | SPEARMNSUB 3 | 115 | 6.58 | 6.61 | 0.03
GEN-2017-100 | South | 02 - Hitchland | 523215 | FREWHELCOL17 | 345 | 10.31 | 10.33 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 523216 | RB-HOGUE 3 | 115 | 4.31 | 4.32 | 0.01
GEN-2017-100 | South | 02 - Hitchland | 523256 | ETTER 3 | 115 | 6.33 | 6.34 | 0.01
GEN-2017-100 | South | 02 - Hitchland | 523266 | PRINGLE 3 | 115 | 11.76 | 11.78 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 523267 | PRINGLE 6 | 230 | 4.5 | 4.51 | 0.01
GEN-2017-100 | South | 02 - Hitchland | 523277 | VALERO 3 | 115 | 11.03 | 11.04 | 0.01
GEN-2017-100 | South | 02 - Hitchland | 523304 | MOORE_W 3 | 115 | 12.19 | 12.21 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 523308 | MOORE_E 3 | 115 | 12.19 | 12.21 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 523309 | MOORE_CNTY 6 | 230 | 7.23 | 7.24 | 0.01
GEN-2017-100 | South | 02 - Hitchland | 523377 | RIVERVIEW 3 | 115 | 13.59 | 13.6 | 0.01
GEN-2017-100 | South | 02 - Hitchland | 523478 | Q_RYTON_TP 3 | 115 | 11.63 | 11.63 | 0
GEN-2017-100 | South | 02 - Hitchland | 523823 | CARPENTER 7 | 345 | 6.94 | 6.95 | 0.01
GEN-2017-100 | South | 02 - Hitchland | 523853 | FINNEY 7 | 345 | 10.13 | 10.14 | 0.01
GEN-2017-100 | South | 02 - Hitchland | 523869 | CHAN+TASCOS6 | 230 | 4.53 | 4.53 | 0
GEN-2017-100 | South | 02 - Hitchland | 523959 | POTTER_CO 6 | 230 | 22.47 | 22.48 | 0.01
GEN-2017-100 | South | 02 - Hitchland | 523961 | POTTER_CO 7 | 345 | 10.22 | 10.24 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 523979 | HARRNG_EST 6 | 230 | 26.36 | 26.37 | 0.01
GEN-2017-100 | South | 02 - Hitchland | 524010 | ROLLHILLS 6 | 230 | 20.17 | 20.19 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 524267 | BUSHLAND 6 | 230 | 11.71 | 11.71 | 0
GEN-2017-100 | South | 02 - Hitchland | 524296 | SPNSPUR_WND7 | 345 | 5.54 | 5.54 | 0
GEN-2017-100 | South | 02 - Hitchland | 525230 | NEWPOT_SS 6 | 230 | 7.31 | 7.31 | 0
GEN-2017-100 | South | 02 - Hitchland | 531405 | WALKMYR3 | 115 | 9.61 | 9.63 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 531512 | HARBNGR7 | 345 | 6.92 | 6.93 | 0.01
GEN-2017-100 | South | 02 - Hitchland | 539640 | HAYNE3 | 115 | 5.14 | 5.16 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 539646 | KISMET 3 | 115 | 4.98 | 5 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 539652 | CMRIVTP3 | 115 | 5.51 | 5.54 | 0.03
GEN-2017-100 | South | 02 - Hitchland | 539654 | CIM-PLT3 | 115 | 6.04 | 6.07 | 0.03
GEN-2017-100 | South | 02 - Hitchland | 539659 | CUDAHY 3 | 115 | 4 | 4.01 | 0.01
GEN-2017-100 | South | 02 - Hitchland | 539672 | E-LIBER3 | 115 | 4.74 | 4.77 | 0.03
GEN-2017-100 | South | 02 - Hitchland | 539690 | E-PINE 3 | 115 | 4.08 | 4.11 | 0.03
GEN-2017-100 | South | 02 - Hitchland | 539700 | W-LIBER3 | 115 | 3.75 | 3.77 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 539737 | NLIB 3 | 115 | 4.56 | 4.59 | 0.03
GEN-2017-100 | South | 02 - Hitchland | 539749 | N-CIMRN3 | 115 | 5.99 | 6.01 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 539751 | NATBEEF3 | 115 | 4.67 | 4.7 | 0.03
GEN-2017-100 | South | 02 - Hitchland | 539800 | CLARKCOUNTY7 | 345 | 15.65 | 15.66 | 0.01
GEN-2017-100 | South | 02 - Hitchland | 560035 | GRAPEVINE | 345 | 8.57 | 8.57 | 0
GEN-2017-100 | South | 02 - Hitchland | 576395 | GEN-2010-014 | 345 | 12.71 | 12.74 | 0.03
GEN-2017-100 | South | 02 - Hitchland | 576396 | G10-014-XFMR | 115 | 14.61 | 14.64 | 0.03
GEN-2017-100 | South | 02 - Hitchland | 588480 | A16-010_SUB | 345 | 0.67 | 0.69 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 588486 | ASGI2016-010 | 115 | 2.72 | 2.78 | 0.06
GEN-2017-100 | South | 02 - Hitchland | 588860 | GEN-2017-047 | 115 | 5 | 5.06 | 0.06
GEN-2017-100 | South | 02 - Hitchland | 589380 | GEN-2017-100 | 115 | 5.27 | 5.53 | 0.26
GEN-2017-051 | South | 07 - Southwestern Oklahoma | 999600 | TAP_G17-036 | 138 | 7.06 | 7.09 | 0.03
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 511456 | O.K.U.-7 | 345 | 6 | 6 | 0
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 515458 | BORDER 7 | 345 | 4.71 | 4.71 | 0
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 522800 | MU-TULIA 3 | 115 | 5.56 | 5.62 | 0.06
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 522823 | LP-MCDONALD6 | 230 | 14.32 | 14.33 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 522829 | LP-MCDONALD3 | 115 | 13.55 | 13.56 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 522861 | LP-SOUTHEST6 | 230 | 17.35 | 17.36 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 522868 | LP-HOLLY3 | 115 | 17.79 | 17.79 | 0
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 522870 | LP-HOLLY 6 | 230 | 16.99 | 17 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 522888 | LP-WADSWRTH6 | 230 | 12.98 | 12.99 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 523309 | MOORE_CNTY 6 | 230 | 7.08 | 7.08 | 0
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 523339 | FAIN 3 | 115 | 5.35 | 5.36 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 523410 | CRMWA_#4 3 | 115 | 9.58 | 9.59 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 523544 | HUTCH_N 3 | 115 | 15.76 | 15.77 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 523546 | HUTCH_S 3 | 115 | 15.76 | 15.77 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 523551 | HUTCHISON 6 | 230 | 7.37 | 7.37 | 0
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 523770 | GRAPEVINE 3 | 115 | 7.93 | 7.93 | 0
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 523771 | GRAPEVINE 6 | 230 | 5.84 | 5.84 | 0
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 523777 | WHEELER 6 | 230 | 5.98 | 5.98 | 0
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 523817 | MIDSTRM_TP 3 | 115 | 4.02 | 4.02 | 0
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 523869 | CHAN+TASCOS6 | 230 | 4.49 | 4.49 | 0
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 523959 | POTTER_CO 6 | 230 | 21.22 | 21.24 | 0.02
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 523961 | POTTER_CO 7 | 345 | 7.78 | 7.78 | 0
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 523977 | HARRNG_WST 6 | 230 | 25.94 | 25.97 | 0.03
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 523978 | HARRNG_MID 6 | 230 | 25.94 | 25.97 | 0.03
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 523979 | HARRNG_EST 6 | 230 | 25.94 | 25.97 | 0.03
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 524007 | ROLLHILLS 3 | 115 | 19.01 | 19.03 | 0.02
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 524010 | ROLLHILLS 6 | 230 | 19.67 | 19.69 | 0.02
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 524016 | ASARCO 3 | 115 | 22.72 | 22.74 | 0.02
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 524018 | ASARCO_TP 3 | 115 | 24.23 | 24.26 | 0.03
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 524043 | NICHOLS 3 | 115 | 25.53 | 25.55 | 0.02
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 524044 | NICHOLS 6 | 230 | 25.1 | 25.12 | 0.02
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 524058 | WHITAKER 3 | 115 | 20.32 | 20.34 | 0.02
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 524079 | CONWAY 3 | 115 | 5.1 | 5.1 | 0
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 524163 | EAST_PLANT 6 | 230 | 13.88 | 13.9 | 0.02
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 524224 | MANHATTAN 3 | 115 | 17.36 | 17.39 | 0.03
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 524267 | BUSHLAND 6 | 230 | 11.7 | 11.72 | 0.02
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 524322 | GEORGIA 3 | 115 | 17.15 | 17.18 | 0.03
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 524338 | SOUTHEAST 3 | 115 | 11.66 | 11.68 | 0.02
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 524345 | OSAGE 3 | 115 | 13.98 | 14 | 0.02
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 524364 | RANDALL 3 | 115 | 21.5 | 21.54 | 0.04
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 524365 | RANDALL 6 | 230 | 14.67 | 14.69 | 0.02
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 524377 | FARMERS 3 | 115 | 15.75 | 15.77 | 0.02
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 524387 | CRSE_HINDTP3 | 115 | 15.76 | 15.78 | 0.02
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 524397 | ARROWHEAD 3 | 115 | 13.92 | 13.94 | 0.02
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 524404 | OWENSCORN 3 | 115 | 15.36 | 15.38 | 0.02
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 524414 | AMA_SOUTH 3 | 115 | 17.17 | 17.2 | 0.03
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 524415 | AMA_SOUTH 6 | 230 | 13.81 | 13.83 | 0.02
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 524425 | ESTACADO_TP3 | 115 | 13.83 | 13.85 | 0.02
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 524522 | CANYON_E_TP3 | 115 | 6.53 | 6.54 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 524530 | PALO_DURO 3 | 115 | 7.1 | 7.13 | 0.03
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 524544 | SPRING_DRW 3 | 115 | 6.68 | 6.69 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 524622 | DEAFSMITH 3 | 115 | 18.87 | 18.9 | 0.03
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 524623 | DEAFSMITH 6 | 230 | 24.18 | 24.21 | 0.03
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 524627 | DEFPLT_SS 6 | 230 | 17.73 | 17.75 | 0.02
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 524688 | DS-#3 2 | 69 | 3.3 | 3.31 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 524694 | DS-#22 3 | 115 | 5.16 | 5.17 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 524721 | DS-#15&#19+2 | 69 | 3.97 | 3.98 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 524728 | DS-CASTRO 2 | 69 | 4.78 | 4.79 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 524734 | DS-#21 3 | 115 | 10.56 | 10.59 | 0.03
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 524745 | CASTRO_CNTY2 | 69 | 9.88 | 9.91 | 0.03
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 524746 | CASTRO_CNTY3 | 115 | 11.14 | 11.17 | 0.03
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 524757 | BETHEL_COL13 | 115 | 9.36 | 9.38 | 0.02
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 524770 | PLSNT_HILL 6 | 230 | 7.84 | 7.85 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 524875 | OASIS 6 | 230 | 8.85 | 8.85 | 0
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 524908 | ROOSEVELT 3 | 115 | 12.15 | 12.16 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 524909 | ROSEVELT_N 6 | 230 | 10.66 | 10.67 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525018 | MULESHVALLY3 | 115 | 6.54 | 6.55 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525019 | MULSHVLY_TP3 | 115 | 7.07 | 7.08 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525028 | BAILEYCO 3 | 115 | 7.06 | 7.07 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525050 | BC-KELLEY +3 | 115 | 8.55 | 8.57 | 0.02
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525056 | BC-EARTH 3 | 115 | 9.01 | 9.03 | 0.02
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525124 | HART_INDUST3 | 115 | 8.31 | 8.35 | 0.04
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525132 | LC-N_OLTON 2 | 69 | 3.32 | 3.34 | 0.02
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525143 | HAPPY_CTYTP2 | 69 | 4.84 | 4.88 | 0.04
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525153 | HAPPY_INT 2 | 69 | 5.43 | 5.48 | 0.05
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525154 | HAPPY_INT 3 | 115 | 5.81 | 5.87 | 0.06
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525179 | TULIA_TP 3 | 115 | 6.91 | 6.99 | 0.08
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525191 | KRESS_INT 2 | 69 | 4.82 | 4.88 | 0.06
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525192 | KRESS_INT 3 | 115 | 12.93 | 13.11 | 0.18
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525203 | SW-KRESS 2 | 69 | 4.82 | 4.88 | 0.06
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525212 | SWISHER 3 | 115 | 12.43 | 12.64 | 0.21
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525213 | SWISHER 6 | 230 | 11.24 | 11.31 | 0.07
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525224 | KRESS_RURL 2 | 69 | 2.7 | 2.74 | 0.04
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525225 | KRESS_RURAL3 | 115 | 6.43 | 6.51 | 0.08
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525226 | KRS_RURL_TP3 | 115 | 6.94 | 7.02 | 0.08
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525230 | NEWPOT_SS 6 | 230 | 7.46 | 7.49 | 0.03
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525249 | LH-PLW&FNY+2 | 69 | 1.71 | 1.74 | 0.03
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525256 | SW_9748 2 | 69 | 3.34 | 3.37 | 0.03
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525257 | N_PLAINVEW 3 | 115 | 5.66 | 5.71 | 0.05
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525271 | KISER 2 | 69 | 3.75 | 3.79 | 0.04
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525272 | KISER 3 | 115 | 5.68 | 5.73 | 0.05
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525279 | WSTRIDGE_TP3 | 69 | 4.58 | 4.61 | 0.03
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525291 | PLAINVW_TP 2 | 69 | 6.98 | 7.03 | 0.05
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525298 | S_PLAINVEW 2 | 69 | 2.78 | 2.79 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525307 | E_PLAINVEW 2 | 69 | 2.66 | 2.68 | 0.02
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525316 | LH-PROVDNCE2 | 69 | 3.67 | 3.7 | 0.03
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525325 | COX 2 | 69 | 3.67 | 3.7 | 0.03
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525326 | COX 3 | 115 | 6.79 | 6.84 | 0.05
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525339 | AIKEN_RURL 2 | 69 | 2.98 | 3 | 0.02
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525393 | ROCKYFORD 3 | 115 | 9.75 | 9.77 | 0.02
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525404 | LC-OLTON 2 | 69 | 4.84 | 4.87 | 0.03
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525413 | LAMTON 2 | 69 | 5.59 | 5.61 | 0.02
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525414 | LAMTON 3 | 115 | 8.27 | 8.31 | 0.04
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525425 | CORNER 2 | 69 | 3.9 | 3.93 | 0.03
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525432 | SP-HALFWAY+2 | 69 | 6.31 | 6.35 | 0.04
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525440 | LC-S_OLTON+3 | 115 | 7.79 | 7.82 | 0.03
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525446 | RKYFORD_TP 3 | 115 | 10.91 | 10.94 | 0.03
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525453 | HALE_CNTY 2 | 69 | 7.44 | 7.49 | 0.05
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525454 | HALE_CNTY 3 | 115 | 11.01 | 11.09 | 0.08
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525460 | NEWHART 3 | 115 | 17.81 | 17.89 | 0.08
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525461 | NEWHART 6 | 230 | 11.82 | 11.87 | 0.05
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525480 | PLANT_X 3 | 115 | 20.49 | 20.53 | 0.04
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525481 | PLANT_X 6 | 230 | 24.18 | 24.21 | 0.03
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525524 | TOLK_EAST 6 | 230 | 31.28 | 31.31 | 0.03
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525531 | TOLK_WEST 6 | 230 | 31.28 | 31.31 | 0.03
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525543 | TOLK_TAP 6 | 230 | 31.28 | 31.31 | 0.03
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525549 | TOLK 7 | 345 | 12.95 | 12.96 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525586 | NEEDMORE 6 | 230 | 12.54 | 12.55 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525614 | W_LITLFLDTP3 | 115 | 8.55 | 8.56 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525615 | W_LITTLFLD 3 | 115 | 8.1 | 8.11 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525636 | LAMB_CNTY 3 | 115 | 10.19 | 10.2 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525637 | LAMB_CNTY 6 | 230 | 6.01 | 6.02 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525731 | SP-ABERNTHY2 | 69 | 3.2 | 3.21 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525738 | HALECENTER 2 | 69 | 2.61 | 2.62 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525745 | LH-HALECTR 2 | 69 | 2.58 | 2.59 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525779 | FLOYD_CNTY 2 | 69 | 5.86 | 5.88 | 0.02
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525780 | FLOYD_CNTY 3 | 115 | 6.85 | 6.88 | 0.03
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525803 | BLANCO 3 | 115 | 5.61 | 5.63 | 0.02
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525816 | TUCO_INT2 2 | 69 | 4.97 | 4.98 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525826 | TUCO_INT 2 | 69 | 8.44 | 8.45 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525828 | TUCO_INT 3 | 115 | 21.9 | 21.93 | 0.03
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525830 | TUCO_INT 6 | 230 | 28.99 | 29.02 | 0.03
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525832 | TUCO_INT 7 | 345 | 23.66 | 23.68 | 0.02
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525840 | ANTELOPE_1 6 | 230 | 28.68 | 28.71 | 0.03
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525850 | ELK_CT1 | 345 | 23.28 | 23.29 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525853 | LH-WIL&ELN+2 | 69 | 2.7 | 2.71 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525885 | SP-NEWDEAL 2 | 69 | 3.52 | 3.53 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 525926 | CROSBY 3 | 115 | 5.25 | 5.26 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 526076 | STANTON_W 3 | 115 | 9.7 | 9.7 | 0
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 526109 | SP-ERSKINE 3 | 115 | 12.02 | 12.03 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 526146 | INDIANA 3 | 115 | 10.12 | 10.13 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 526159 | CARLISLE 2 | 69 | 2.71 | 2.71 | 0
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 526160 | CARLISLE 3 | 115 | 14.09 | 14.1 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 526161 | CARLISLE 6 | 230 | 14.7 | 14.71 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 526162 | LP-DOUD_TP 3 | 115 | 12.4 | 12.4 | 0
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 526192 | MURPHY 3 | 115 | 11.27 | 11.27 | 0
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 526268 | LUBBCK_STH 3 | 115 | 20.1 | 20.11 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 526269 | LUBBCK_STH 6 | 230 | 19.21 | 19.22 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 526297 | LUBBCK_EST 2 | 69 | 8.48 | 8.48 | 0
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 526298 | LUBBCK_EST 3 | 115 | 16.19 | 16.2 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 526299 | LUBBCK_EST 6 | 230 | 13.84 | 13.85 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 526337 | JONES 6 | 230 | 21.13 | 21.14 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 526434 | SUNDOWN 3 | 115 | 12.54 | 12.55 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 526435 | SUNDOWN 6 | 230 | 11.83 | 11.84 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 526460 | AMOCO_SS 6 | 230 | 10.36 | 10.37 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 526524 | WOLFFORTH 3 | 115 | 12.23 | 12.24 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 526525 | WOLFFORTH 6 | 230 | 14.33 | 14.34 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 526676 | GRASSLAND 3 | 115 | 7.53 | 7.53 | 0
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 526677 | GRASSLAND 6 | 230 | 6.83 | 6.83 | 0
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 526679 | CIRRUS_WND 6 | 230 | 5.32 | 5.32 | 0
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 526935 | YOAKUM 6 | 230 | 18.56 | 18.57 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 526936 | YOAKUM_345 | 345 | 9.69 | 9.7 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 527896 | HOBBS_INT 7 | 345 | 9.34 | 9.34 | 0
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 560022 | CRAWFISH_DR | 345 | 23.92 | 23.94 | 0.02
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 560100 | CRAWFISH765 | 765 | 11.17 | 11.17 | 0
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 583340 | GEN-2012-020 | 230 | 11.68 | 11.7 | 0.02
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 587250 | GEN-2016-039 | 115 | 12.43 | 12.64 | 0.21
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 587570 | ASGI1604 | 115 | 7.1 | 7.13 | 0.03
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 588440 | GEN-2016-172 | 115 | 15.02 | 15.09 | 0.07
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 588700 | GEN-2017-026 | 230 | 9.98 | 9.99 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 588970 | GEN-2017-059 | 230 | 10 | 10.01 | 0.01
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 589180 | GEN-2017-080 | 230 | 26.88 | 26.91 | 0.03
GEN-2016-039 | South | 06 - South Texas Panhandle/New Mexico | 599955 | PNM-DC6 | 230 | 10.66 | 10.67 | 0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 522800 | MU-TULIA 3 | 115 | 5.59 | 5.62 | 0.03
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 522823 | LP-MCDONALD6 | 230 | 14.31 | 14.33 | 0.02
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 522870 | LP-HOLLY 6 | 230 | 16.98 | 17 | 0.02
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 523095 | HITCHLAND 6 | 230 | 15.05 | 15.05 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 523097 | HITCHLAND 7 | 345 | 15.39 | 15.39 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 523221 | XIT_INTG 6 | 230 | 3.35 | 3.35 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 523267 | PRINGLE 6 | 230 | 4.49 | 4.49 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 523308 | MOORE_E 3 | 115 | 12.01 | 12.01 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 523309 | MOORE_CNTY 6 | 230 | 7.08 | 7.08 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 523551 | HUTCHISON 6 | 230 | 7.37 | 7.37 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 523771 | GRAPEVINE 6 | 230 | 5.84 | 5.84 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 523869 | CHAN+TASCOS6 | 230 | 4.49 | 4.49 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 523959 | POTTER_CO 6 | 230 | 21.13 | 21.24 | 0.11
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 523961 | POTTER_CO 7 | 345 | 7.77 | 7.78 | 0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 523977 | HARRNG_WST 6 | 230 | 25.85 | 25.97 | 0.12
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 523978 | HARRNG_MID 6 | 230 | 25.85 | 25.97 | 0.12
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 523979 | HARRNG_EST 6 | 230 | 25.85 | 25.97 | 0.12
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524007 | ROLLHILLS 3 | 115 | 19 | 19.03 | 0.03
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524010 | ROLLHILLS 6 | 230 | 19.61 | 19.69 | 0.08
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524043 | NICHOLS 3 | 115 | 25.5 | 25.55 | 0.05
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524044 | NICHOLS 6 | 230 | 25.01 | 25.12 | 0.11
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524266 | BUSHLAND 3 | 115 | 10.1 | 10.11 | 0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524267 | BUSHLAND 6 | 230 | 11.68 | 11.72 | 0.04
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524290 | WILDOR2_JUS6 | 230 | 7.63 | 7.64 | 0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524296 | SPNSPUR_WND7 | 345 | 4.72 | 4.72 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524364 | RANDALL 3 | 115 | 21.47 | 21.54 | 0.07
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524365 | RANDALL 6 | 230 | 14.63 | 14.69 | 0.06
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524377 | FARMERS 3 | 115 | 15.74 | 15.77 | 0.03
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524397 | ARROWHEAD 3 | 115 | 13.92 | 13.94 | 0.02
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524404 | OWENSCORN 3 | 115 | 15.36 | 15.38 | 0.02
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524414 | AMA_SOUTH 3 | 115 | 17.17 | 17.2 | 0.03
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524415 | AMA_SOUTH 6 | 230 | 13.77 | 13.83 | 0.06
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524530 | PALO_DURO 3 | 115 | 7.12 | 7.13 | 0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524544 | SPRING_DRW 3 | 115 | 6.69 | 6.69 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524556 | LAPLATA 3 | 115 | 7.92 | 7.93 | 0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524567 | NE_HEREFORD3 | 115 | 13.98 | 14.04 | 0.06
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524573 | NE_HEREFORD2 | 69 | 8.24 | 8.25 | 0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524575 | DS-#25+ 3 | 115 | 14.32 | 14.38 | 0.06
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524597 | PANDAHFD 3 | 115 | 12.14 | 12.18 | 0.04
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524604 | HEREFRD_SB 2 | 69 | 5.19 | 5.19 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524605 | HEREFRD_NB 2 | 69 | 5.19 | 5.19 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524606 | HEREFORD 3 | 115 | 16.01 | 16.09 | 0.08
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524622 | DEAFSMITH 3 | 115 | 18.79 | 18.9 | 0.11
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524623 | DEAFSMITH 6 | 230 | 23.91 | 24.21 | 0.3
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524627 | DEFPLT_SS 6 | 230 | 17.59 | 17.75 | 0.16
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524629 | DS-#6 3 | 115 | 7.75 | 7.76 | 0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524679 | DIMMIT_S_TP2 | 69 | 3.26 | 3.26 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524680 | DIMIT_SOUTH2 | 69 | 3.2 | 3.2 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524681 | DIMMIT_EAST2 | 69 | 3.12 | 3.12 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524688 | DS-#3 2 | 69 | 3.31 | 3.31 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524694 | DS-#22 3 | 115 | 5.14 | 5.17 | 0.03
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524721 | DS-#15&#19+2 | 69 | 3.97 | 3.98 | 0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524728 | DS-CASTRO 2 | 69 | 4.78 | 4.79 | 0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524734 | DS-#21 3 | 115 | 10.43 | 10.59 | 0.16
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524745 | CASTRO_CNTY2 | 69 | 9.83 | 9.91 | 0.08
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524746 | CASTRO_CNTY3 | 115 | 10.97 | 11.17 | 0.2
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524757 | BETHEL_COL13 | 115 | 9.26 | 9.38 | 0.12
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524770 | PLSNT_HILL 6 | 230 | 7.84 | 7.85 | 0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524875 | OASIS 6 | 230 | 8.85 | 8.85 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524908 | ROOSEVELT 3 | 115 | 12.15 | 12.16 | 0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 524909 | ROSEVELT_N 6 | 230 | 10.65 | 10.67 | 0.02
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525018 | MULESHVALLY3 | 115 | 6.55 | 6.55 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525019 | MULSHVLY_TP3 | 115 | 7.07 | 7.08 | 0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525028 | BAILEYCO 3 | 115 | 7.06 | 7.07 | 0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525050 | BC-KELLEY +3 | 115 | 8.5 | 8.57 | 0.07
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525056 | BC-EARTH 3 | 115 | 8.97 | 9.03 | 0.06
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525116 | DS-#12 2 | 69 | 2.65 | 2.65 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525119 | BC-SUNYSIDE2 | 69 | 1.44 | 1.43 | -0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525124 | HART_INDUST3 | 115 | 8.01 | 8.35 | 0.34
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525129 | LC-HART 2 | 69 | 2.78 | 2.78 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525132 | LC-N_OLTON 2 | 69 | 3.33 | 3.34 | 0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525143 | HAPPY_CTYTP2 | 69 | 4.88 | 4.88 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525153 | HAPPY_INT 2 | 69 | 5.48 | 5.48 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525154 | HAPPY_INT 3 | 115 | 5.84 | 5.87 | 0.03
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525179 | TULIA_TP 3 | 115 | 6.94 | 6.99 | 0.05
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525191 | KRESS_INT 2 | 69 | 4.87 | 4.88 | 0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525192 | KRESS_INT 3 | 115 | 12.83 | 13.11 | 0.28
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525203 | SW-KRESS 2 | 69 | 4.87 | 4.88 | 0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525212 | SWISHER 3 | 115 | 12.4 | 12.64 | 0.24
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525213 | SWISHER 6 | 230 | 11.04 | 11.31 | 0.27
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525224 | KRESS_RURL 2 | 69 | 2.74 | 2.74 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525225 | KRESS_RURAL3 | 115 | 6.46 | 6.51 | 0.05
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525226 | KRS_RURL_TP3 | 115 | 6.96 | 7.02 | 0.06
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525230 | NEWPOT_SS 6 | 230 | 7.35 | 7.49 | 0.14
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525249 | LH-PLW&FNY+2 | 69 | 1.74 | 1.74 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525256 | SW_9748 2 | 69 | 3.37 | 3.37 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525257 | N_PLAINVEW 3 | 115 | 5.69 | 5.71 | 0.02
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525271 | KISER 2 | 69 | 3.79 | 3.79 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525272 | KISER 3 | 115 | 5.71 | 5.73 | 0.02
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525279 | WSTRIDGE_TP3 | 69 | 4.61 | 4.61 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525291 | PLAINVW_TP 2 | 69 | 7.01 | 7.03 | 0.02
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525298 | S_PLAINVEW 2 | 69 | 2.8 | 2.79 | -0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525307 | E_PLAINVEW 2 | 69 | 2.68 | 2.68 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525316 | LH-PROVDNCE2 | 69 | 3.7 | 3.7 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525325 | COX 2 | 69 | 3.7 | 3.7 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525326 | COX 3 | 115 | 6.81 | 6.84 | 0.03
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525339 | AIKEN_RURL 2 | 69 | 3 | 3 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525393 | ROCKYFORD 3 | 115 | 9.71 | 9.77 | 0.06
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525397 | OLTON 2 | 69 | 4.53 | 4.54 | 0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525404 | LC-OLTON 2 | 69 | 4.85 | 4.87 | 0.02
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525413 | LAMTON 2 | 69 | 5.59 | 5.61 | 0.02
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525414 | LAMTON 3 | 115 | 8.19 | 8.31 | 0.12
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525425 | CORNER 2 | 69 | 3.93 | 3.93 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525432 | SP-HALFWAY+2 | 69 | 6.34 | 6.35 | 0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525440 | LC-S_OLTON+3 | 115 | 7.75 | 7.82 | 0.07
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525446 | RKYFORD_TP 3 | 115 | 10.86 | 10.94 | 0.08
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525453 | HALE_CNTY 2 | 69 | 7.47 | 7.49 | 0.02
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525454 | HALE_CNTY 3 | 115 | 10.98 | 11.09 | 0.11
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525460 | NEWHART 3 | 115 | 15.62 | 17.89 | 2.27
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525461 | NEWHART 6 | 230 | 11.21 | 11.87 | 0.66
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525480 | PLANT_X 3 | 115 | 20.33 | 20.53 | 0.2
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525481 | PLANT_X 6 | 230 | 23.91 | 24.21 | 0.3
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525524 | TOLK_EAST 6 | 230 | 31.09 | 31.31 | 0.22
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525531 | TOLK_WEST 6 | 230 | 31.09 | 31.31 | 0.22
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525543 | TOLK_TAP 6 | 230 | 31.09 | 31.31 | 0.22
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525549 | TOLK 7 | 345 | 12.93 | 12.96 | 0.03
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525586 | NEEDMORE 6 | 230 | 12.53 | 12.55 | 0.02
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525614 | W_LITLFLDTP3 | 115 | 8.55 | 8.56 | 0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525615 | W_LITTLFLD 3 | 115 | 8.1 | 8.11 | 0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525636 | LAMB_CNTY 3 | 115 | 10.19 | 10.2 | 0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525637 | LAMB_CNTY 6 | 230 | 6.01 | 6.02 | 0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525731 | SP-ABERNTHY2 | 69 | 3.21 | 3.21 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525738 | HALECENTER 2 | 69 | 2.62 | 2.62 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525745 | LH-HALECTR 2 | 69 | 2.59 | 2.59 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525779 | FLOYD_CNTY 2 | 69 | 5.88 | 5.88 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525780 | FLOYD_CNTY 3 | 115 | 6.87 | 6.88 | 0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525803 | BLANCO 3 | 115 | 5.63 | 5.63 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525816 | TUCO_INT2 2 | 69 | 4.98 | 4.98 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525826 | TUCO_INT 2 | 69 | 8.45 | 8.45 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525828 | TUCO_INT 3 | 115 | 21.88 | 21.93 | 0.05
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525830 | TUCO_INT 6 | 230 | 28.9 | 29.02 | 0.12
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525832 | TUCO_INT 7 | 345 | 23.63 | 23.68 | 0.05
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525840 | ANTELOPE_1 6 | 230 | 28.6 | 28.71 | 0.11
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525850 | ELK_CT1 | 345 | 23.25 | 23.29 | 0.04
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525853 | LH-WIL&ELN+2 | 69 | 2.71 | 2.71 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525885 | SP-NEWDEAL 2 | 69 | 3.53 | 3.53 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 525926 | CROSBY 3 | 115 | 5.26 | 5.26 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 526013 | DEAN_INTG 6 | 230 | 8.72 | 8.73 | 0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 526036 | LC-OPDYKE 3 | 115 | 6.37 | 6.37 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 526076 | STANTON_W 3 | 115 | 9.7 | 9.7 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 526146 | INDIANA 3 | 115 | 10.13 | 10.13 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 526160 | CARLISLE 3 | 115 | 14.09 | 14.1 | 0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 526161 | CARLISLE 6 | 230 | 14.7 | 14.71 | 0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 526268 | LUBBCK_STH 3 | 115 | 20.1 | 20.11 | 0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 526269 | LUBBCK_STH 6 | 230 | 19.2 | 19.22 | 0.02
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 526297 | LUBBCK_EST 2 | 69 | 8.48 | 8.48 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 526298 | LUBBCK_EST 3 | 115 | 16.19 | 16.2 | 0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 526299 | LUBBCK_EST 6 | 230 | 13.84 | 13.85 | 0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 526337 | JONES 6 | 230 | 21.12 | 21.14 | 0.02
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 526424 | PACIFIC 3 | 115 | 10.96 | 10.96 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 526434 | SUNDOWN 3 | 115 | 12.54 | 12.55 | 0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 526435 | SUNDOWN 6 | 230 | 11.82 | 11.84 | 0.02
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 526445 | AMOCO_TP 3 | 115 | 11.64 | 11.65 | 0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 526460 | AMOCO_SS 6 | 230 | 10.36 | 10.37 | 0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 526524 | WOLFFORTH 3 | 115 | 12.23 | 12.24 | 0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 526525 | WOLFFORTH 6 | 230 | 14.33 | 14.34 | 0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 526677 | GRASSLAND 6 | 230 | 6.83 | 6.83 | 0
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 526935 | YOAKUM 6 | 230 | 18.56 | 18.57 | 0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 526936 | YOAKUM_345 | 345 | 9.69 | 9.7 | 0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 560022 | CRAWFISH_DR | 345 | 23.89 | 23.94 | 0.05
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 583340 | GEN-2012-020 | 230 | 11.69 | 11.7 | 0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 583840 | GEN-2013-027 | 230 | 11.73 | 11.75 | 0.02
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 587250 | GEN-2016-039 | 115 | 12.4 | 12.64 | 0.24
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 587570 | ASGI1604 | 115 | 7.12 | 7.13 | 0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 588440 | GEN-2016-172 | 115 | 12.73 | 15.09 | 2.36
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 588700 | GEN-2017-026 | 230 | 9.97 | 9.99 | 0.02
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 588800 | GEN-2017-039 | 230 | 10.12 | 10.13 | 0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 588960 | GEN-2017-058 | 115 | 8.58 | 8.6 | 0.02
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 588970 | GEN-2017-059 | 230 | 10 | 10.01 | 0.01
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 589180 | GEN-2017-080 | 230 | 26.75 | 26.91 | 0.16
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 589188 | G17-080-SUB2 | 230 | 15.47 | 15.52 | 0.05
GEN-2016-172 | South | 06 - South Texas Panhandle/New Mexico | 599955 | PNM-DC6 | 230 | 10.65 | 10.67 | 0.02
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 522823 | LP-MCDONALD6 | 230 | 14.32 | 14.33 | 0.01
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 522870 | LP-HOLLY 6 | 230 | 16.99 | 17 | 0.01
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524267 | BUSHLAND 6 | 230 | 11.69 | 11.72 | 0.03
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524415 | AMA_SOUTH 6 | 230 | 13.82 | 13.83 | 0.01
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524472 | LOPEZ 3 | 115 | 2.57 | 2.58 | 0.01
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524477 | CAMPBELL_ST3 | 115 | 2.56 | 2.57 | 0.01
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524486 | CAPROCK 3 | 115 | 3.22 | 3.24 | 0.02
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524502 | NORTON 3 | 115 | 3.51 | 3.54 | 0.03
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524509 | FE-TUCMCARI3 | 115 | 2.74 | 2.76 | 0.02
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524622 | DEAFSMITH 3 | 115 | 18.79 | 18.9 | 0.11
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524623 | DEAFSMITH 6 | 230 | 23.96 | 24.21 | 0.25
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524627 | DEFPLT_SS 6 | 230 | 17.6 | 17.75 | 0.15
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524662 | PARMER_CO 3 | 115 | 4.8 | 4.9 | 0.1
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524669 | DS-#20 3 | 115 | 5.8 | 5.95 | 0.15
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524764 | NORRIS_TP 3 | 115 | 12.03 | 12.69 | 0.66
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524768 | PLSNT_HILL 3 | 115 | 11.57 | 12.33 | 0.76
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524770 | PLSNT_HILL 6 | 230 | 6.9 | 7.85 | 0.95
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524773 | E_CLOVIS 3 | 115 | 9.69 | 10.2 | 0.51
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524776 | N_CLOVIS_TP3 | 115 | 8.66 | 9.07 | 0.41
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524777 | N_CLOVIS 3 | 115 | 7.78 | 8.12 | 0.34
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524783 | W_CLOVIS 2 | 69 | 2.66 | 2.71 | 0.05
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524784 | W_CLOVIS 3 | 115 | 7.33 | 7.62 | 0.29
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524790 | CANNON_TP 3 | 115 | 6.81 | 7.08 | 0.27
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524794 | CANNONAFB 3 | 115 | 6.38 | 6.61 | 0.23
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524797 | PERIMETER 3 | 115 | 7.25 | 7.54 | 0.29
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524801 | NORRIS 3 | 115 | 11.01 | 11.58 | 0.57
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524808 | FE-CLVS_INT3 | 115 | 8.22 | 8.58 | 0.36
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524821 | CURRY 2 | 69 | 4.8 | 4.92 | 0.12
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524822 | CURRY 3 | 115 | 12.07 | 12.73 | 0.66
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524831 | FE-HOLLAND 3 | 115 | 10.02 | 10.56 | 0.54
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524838 | FE-CLOVIS2+3 | 115 | 11.44 | 12.05 | 0.61
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524846 | FARWELL 2 | 69 | 2.33 | 2.37 | 0.04
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524863 | FE-CHZPLT 3 | 115 | 8.6 | 8.98 | 0.38
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524874 | OASIS 3 | 115 | 10.8 | 11.37 | 0.57
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524875 | OASIS 6 | 230 | 8.22 | 8.85 | 0.63
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524885 | SN_JUAN_TAP6 | 230 | 5.11 | 5.22 | 0.11
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524889 | SN_JUAN_WND6 | 230 | 4.88 | 4.98 | 0.1
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524908 | ROOSEVELT 3 | 115 | 11.56 | 12.16 | 0.6
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524909 | ROSEVELT_N 6 | 230 | 9.89 | 10.67 | 0.78
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524923 | PORTALES 2 | 69 | 7.88 | 8.12 | 0.24
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524924 | PORTALES 3 | 115 | 8.08 | 8.42 | 0.34
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524929 | RO-PORT_MTR2 | 69 | 7.88 | 8.12 | 0.24
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524934 | ZODIAC 2 | 69 | 5.85 | 6 | 0.15
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524935 | KILGORE 3 | 115 | 6.61 | 6.85 | 0.24
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524941 | PORTALES#1 2 | 69 | 6.06 | 6.22 | 0.16
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524963 | S_PORTALES 3 | 115 | 6.21 | 6.42 | 0.21
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 524977 | GREYHOUND 3 | 115 | 6.12 | 6.33 | 0.21
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 525019 | MULSHVLY_TP3 | 115 | 7.01 | 7.08 | 0.07
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 525027 | BAILEYCO 2 | 69 | 6.08 | 6.13 | 0.05
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 525028 | BAILEYCO 3 | 115 | 6.99 | 7.07 | 0.08
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 525040 | BAILEY_PMP 3 | 115 | 5.21 | 5.25 | 0.04
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 525056 | BC-EARTH 3 | 115 | 9 | 9.03 | 0.03
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 525212 | SWISHER 3 | 115 | 12.62 | 12.64 | 0.02
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 525213 | SWISHER 6 | 230 | 11.29 | 11.31 | 0.02
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 525230 | NEWPOT_SS 6 | 230 | 7.47 | 7.49 | 0.02
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 525446 | RKYFORD_TP 3 | 115 | 10.89 | 10.94 | 0.05
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 525454 | HALE_CNTY 3 | 115 | 11.07 | 11.09 | 0.02
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 525460 | NEWHART 3 | 115 | 17.85 | 17.89 | 0.04
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 525461 | NEWHART 6 | 230 | 11.84 | 11.87 | 0.03
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 525480 | PLANT_X 3 | 115 | 20.39 | 20.53 | 0.14
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 525481 | PLANT_X 6 | 230 | 23.96 | 24.21 | 0.25
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 525524 | TOLK_EAST 6 | 230 | 30.79 | 31.31 | 0.52
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 525531 | TOLK_WEST 6 | 230 | 30.79 | 31.31 | 0.52
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 525543 | TOLK_TAP 6 | 230 | 30.79 | 31.31 | 0.52
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 525549 | TOLK 7 | 345 | 12.86 | 12.96 | 0.1
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 525586 | NEEDMORE 6 | 230 | 12.47 | 12.55 | 0.08
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 525608 | NEW_AMHERST3 | 115 | 5.58 | 5.62 | 0.04
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 525614 | W_LITLFLDTP3 | 115 | 8.52 | 8.56 | 0.04
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 525635 | LAMB_CNTY 2 | 69 | 6.69 | 6.72 | 0.03
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 525636 | LAMB_CNTY 3 | 115 | 10.15 | 10.2 | 0.05
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 525637 | LAMB_CNTY 6 | 230 | 5.98 | 6.02 | 0.04
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 525780 | FLOYD_CNTY 3 | 115 | 6.87 | 6.88 | 0.01
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 525816 | TUCO_INT2 2 | 69 | 4.97 | 4.98 | 0.01
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 525826 | TUCO_INT 2 | 69 | 8.45 | 8.45 | 0
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 525828 | TUCO_INT 3 | 115 | 21.9 | 21.93 | 0.03
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 525830 | TUCO_INT 6 | 230 | 28.96 | 29.02 | 0.06
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 525832 | TUCO_INT 7 | 345 | 23.64 | 23.68 | 0.04
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 525840 | ANTELOPE_1 6 | 230 | 28.66 | 28.71 | 0.05
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 525850 | ELK_CT1 | 345 | 23.26 | 23.29 | 0.03
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 526012 | DEAN_INTG 3 | 115 | 11.49 | 11.51 | 0.02
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 526013 | DEAN_INTG 6 | 230 | 8.71 | 8.73 | 0.02
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 526020 | HOCKLEY 3 | 115 | 6.04 | 6.05 | 0.01
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 526076 | STANTON_W 3 | 115 | 9.7 | 9.7 | 0
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 526160 | CARLISLE 3 | 115 | 14.09 | 14.1 | 0.01
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 526161 | CARLISLE 6 | 230 | 14.7 | 14.71 | 0.01
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 526269 | LUBBCK_STH 6 | 230 | 19.2 | 19.22 | 0.02
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 526298 | LUBBCK_EST 3 | 115 | 16.19 | 16.2 | 0.01
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 526299 | LUBBCK_EST 6 | 230 | 13.84 | 13.85 | 0.01
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 526337 | JONES 6 | 230 | 21.12 | 21.14 | 0.02
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 526434 | SUNDOWN 3 | 115 | 12.52 | 12.55 | 0.03
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 526435 | SUNDOWN 6 | 230 | 11.81 | 11.84 | 0.03
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 526460 | AMOCO_SS 6 | 230 | 10.35 | 10.37 | 0.02
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 526525 | WOLFFORTH 6 | 230 | 14.33 | 14.34 | 0.01
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 526677 | GRASSLAND 6 | 230 | 6.83 | 6.83 | 0
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 526935 | YOAKUM 6 | 230 | 18.54 | 18.57 | 0.03
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 526936 | YOAKUM_345 | 345 | 9.68 | 9.7 | 0.02
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 527455 | RSWL_SLRCOL3 | 115 | 7.22 | 7.27 | 0.05
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 527470 | CHVS_SLRCOL3 | 115 | 7.06 | 7.11 | 0.05
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 527482 | CHAVES_CNTY3 | 115 | 7.29 | 7.34 | 0.05
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 527483 | CHAVES_CNTY6 | 230 | 4.68 | 4.73 | 0.05
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 527501 | URTON 3 | 115 | 6.14 | 6.18 | 0.04
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 527509 | PRICE_TAP 3 | 115 | 5.75 | 5.79 | 0.04
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 527546 | SAMSON 3 | 115 | 5.81 | 5.84 | 0.03
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 527656 | CROSSROADS 7 | 345 | 17.53 | 17.58 | 0.05
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 527793 | EDDY_STH 3 | 115 | 12.48 | 12.51 | 0.03
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 527798 | EDDY_NTH 3 | 115 | 12.48 | 12.51 | 0.03
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 527799 | EDDY_NORTH 6 | 230 | 9.68 | 9.71 | 0.03
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 527802 | EDDY_CNTY 7 | 345 | 7.7 | 7.72 | 0.02
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 527865 | CUNNIGHM_N 6 | 230 | 14.91 | 14.93 | 0.02
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 528095 | 7-RIVERS 6 | 230 | 6.6 | 6.62 | 0.02
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 560022 | CRAWFISH_DR | 345 | 23.9 | 23.94 | 0.04
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 560756 | CEILO-TAP-N | 69 | 0.84 | 0.85 | 0.01
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 583280 | A12-02&13-05 | 115 | 1.13 | 1.14 | 0.01
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 583340 | GEN-2012-020 | 230 | 11.69 | 11.7 | 0.01
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 583620 | CIELO-TAP-S | 115 | 1.13 | 1.14 | 0.01
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 583840 | GEN-2013-027 | 230 | 11.68 | 11.75 | 0.07
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 583960 | G14034G14035 | 115 | 6.9 | 6.95 | 0.05
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 588520 | GEN-2017-007 | 230 | 3.61 | 4.67 | 1.06
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 588610 | GEN-2017-016 | 115 | 3.36 | 3.39 | 0.03
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 588700 | GEN-2017-026 | 230 | 9.92 | 9.99 | 0.07
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 588800 | GEN-2017-039 | 230 | 10.08 | 10.13 | 0.05
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 588970 | GEN-2017-059 | 230 | 10 | 10.01 | 0.01
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 589180 | GEN-2017-080 | 230 | 26.52 | 26.91 | 0.39
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 589188 | G17-080-SUB2 | 230 | 15.37 | 15.52 | 0.15
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 589250 | GEN-2017-087 | 115 | 8.17 | 8.52 | 0.35
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 599950 | LAMAR7 | 345 | 2.55 | 2.55 | 0
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 599951 | LAMAR 6 | 345 | 57.79 | 57.79 | 0
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 599955 | PNM-DC6 | 230 | 9.89 | 10.67 | 0.78
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 599956 | PNM-DC7 | 345 | 16738.66 | 16738.66 | 0
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 599960 | EPTNP-D6 | 230 | 9.68 | 9.71 | 0.03
GEN-2017-007 | South | 06 - South Texas Panhandle/New Mexico | 599961 | EPTNP 7 | 345 | 16736.82 | 16736.82 | 0
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 524472 | LOPEZ 3 | 115 | 2.54 | 2.58 | 0.04
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 524477 | CAMPBELL_ST3 | 115 | 2.53 | 2.57 | 0.04
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 524486 | CAPROCK 3 | 115 | 3.19 | 3.24 | 0.05
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 524502 | NORTON 3 | 115 | 3.47 | 3.54 | 0.07
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 524509 | FE-TUCMCARI3 | 115 | 2.72 | 2.76 | 0.04
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 524662 | PARMER_CO 3 | 115 | 4.89 | 4.9 | 0.01
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 524669 | DS-#20 3 | 115 | 5.95 | 5.95 | 0
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 524764 | NORRIS_TP 3 | 115 | 12.67 | 12.69 | 0.02
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 524768 | PLSNT_HILL 3 | 115 | 12.31 | 12.33 | 0.02
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 524770 | PLSNT_HILL 6 | 230 | 7.84 | 7.85 | 0.01
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 524773 | E_CLOVIS 3 | 115 | 10.18 | 10.2 | 0.02
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 524776 | N_CLOVIS_TP3 | 115 | 9.05 | 9.07 | 0.02
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 524777 | N_CLOVIS 3 | 115 | 8.11 | 8.12 | 0.01
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 524783 | W_CLOVIS 2 | 69 | 2.7 | 2.71 | 0.01
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 524784 | W_CLOVIS 3 | 115 | 7.61 | 7.62 | 0.01
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 524790 | CANNON_TP 3 | 115 | 7.07 | 7.08 | 0.01
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 524797 | PERIMETER 3 | 115 | 7.53 | 7.54 | 0.01
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 524801 | NORRIS 3 | 115 | 11.56 | 11.58 | 0.02
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 524808 | FE-CLVS_INT3 | 115 | 8.57 | 8.58 | 0.01
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 524821 | CURRY 2 | 69 | 4.91 | 4.92 | 0.01
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 524822 | CURRY 3 | 115 | 12.71 | 12.73 | 0.02
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 524831 | FE-HOLLAND 3 | 115 | 10.55 | 10.56 | 0.01
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 524838 | FE-CLOVIS2+3 | 115 | 12.03 | 12.05 | 0.02
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 524846 | FARWELL 2 | 69 | 2.37 | 2.37 | 0
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 524863 | FE-CHZPLT 3 | 115 | 8.97 | 8.98 | 0.01
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 524874 | OASIS 3 | 115 | 11.35 | 11.37 | 0.02
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 524875 | OASIS 6 | 230 | 8.85 | 8.85 | 0
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 524885 | SN_JUAN_TAP6 | 230 | 5.22 | 5.22 | 0
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 524889 | SN_JUAN_WND6 | 230 | 4.98 | 4.98 | 0
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 524908 | ROOSEVELT 3 | 115 | 12.15 | 12.16 | 0.01
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 524909 | ROSEVELT_N 6 | 230 | 10.66 | 10.67 | 0.01
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 524924 | PORTALES 3 | 115 | 8.41 | 8.42 | 0.01
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 525019 | MULSHVLY_TP3 | 115 | 7.08 | 7.08 | 0
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 525027 | BAILEYCO 2 | 69 | 6.13 | 6.13 | 0
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 525028 | BAILEYCO 3 | 115 | 7.06 | 7.07 | 0.01
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 525040 | BAILEY_PMP 3 | 115 | 5.25 | 5.25 | 0
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 525481 | PLANT_X 6 | 230 | 24.21 | 24.21 | 0
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 525524 | TOLK_EAST 6 | 230 | 31.3 | 31.31 | 0.01
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 525531 | TOLK_WEST 6 | 230 | 31.3 | 31.31 | 0.01
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 525543 | TOLK_TAP 6 | 230 | 31.3 | 31.31 | 0.01
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 525586 | NEEDMORE 6 | 230 | 12.55 | 12.55 | 0
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 525637 | LAMB_CNTY 6 | 230 | 6.02 | 6.02 | 0
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 525830 | TUCO_INT 6 | 230 | 29.02 | 29.02 | 0
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 527483 | CHAVES_CNTY6 | 230 | 4.72 | 4.73 | 0.01
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 560756 | CEILO-TAP-N | 69 | 0.84 | 0.85 | 0.01
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 583280 | A12-02&13-05 | 115 | 1.14 | 1.14 | 0
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 583620 | CIELO-TAP-S | 115 | 1.14 | 1.14 | 0
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 588520 | GEN-2017-007 | 230 | 4.66 | 4.67 | 0.01
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 588610 | GEN-2017-016 | 115 | 3.32 | 3.39 | 0.07
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 588700 | GEN-2017-026 | 230 | 9.98 | 9.99 | 0.01
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 589180 | GEN-2017-080 | 230 | 26.9 | 26.91 | 0.01
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 589250 | GEN-2017-087 | 115 | 8.51 | 8.52 | 0.01
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 599955 | PNM-DC6 | 230 | 10.66 | 10.67 | 0.01
GEN-2017-016 | South | 06 - South Texas Panhandle/New Mexico | 599956 | PNM-DC7 | 345 | 16738.66 | 16738.66 | 0
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 522823 | LP-MCDONALD6 | 230 | 14.32 | 14.33 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 522861 | LP-SOUTHEST6 | 230 | 17.35 | 17.36 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 522870 | LP-HOLLY 6 | 230 | 16.99 | 17 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 523309 | MOORE_CNTY 6 | 230 | 7.08 | 7.08 | 0
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 523869 | CHAN+TASCOS6 | 230 | 4.49 | 4.49 | 0
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 523959 | POTTER_CO 6 | 230 | 21.22 | 21.24 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 523961 | POTTER_CO 7 | 345 | 7.78 | 7.78 | 0
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 523979 | HARRNG_EST 6 | 230 | 25.95 | 25.97 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524010 | ROLLHILLS 6 | 230 | 19.68 | 19.69 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524044 | NICHOLS 6 | 230 | 25.1 | 25.12 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524243 | OUTPOST 3 | 115 | 10.18 | 10.19 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524266 | BUSHLAND 3 | 115 | 10.1 | 10.11 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524267 | BUSHLAND 6 | 230 | 11.69 | 11.72 | 0.03
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524276 | WILDOR_WND 6 | 230 | 5.58 | 5.59 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524290 | WILDOR2_JUS6 | 230 | 7.63 | 7.64 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524365 | RANDALL 6 | 230 | 14.68 | 14.69 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524414 | AMA_SOUTH 3 | 115 | 17.19 | 17.2 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524415 | AMA_SOUTH 6 | 230 | 13.82 | 13.83 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524486 | CAPROCK 3 | 115 | 3.24 | 3.24 | 0
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524502 | NORTON 3 | 115 | 3.54 | 3.54 | 0
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524509 | FE-TUCMCARI3 | 115 | 2.76 | 2.76 | 0
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524556 | LAPLATA 3 | 115 | 7.9 | 7.93 | 0.03
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524567 | NE_HEREFORD3 | 115 | 13.97 | 14.04 | 0.07
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524573 | NE_HEREFORD2 | 69 | 8.22 | 8.25 | 0.03
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524575 | DS-#25+ 3 | 115 | 14.32 | 14.38 | 0.06
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524597 | PANDAHFD 3 | 115 | 12.13 | 12.18 | 0.05
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524604 | HEREFRD_SB 2 | 69 | 5.17 | 5.19 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524605 | HEREFRD_NB 2 | 69 | 5.17 | 5.19 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524606 | HEREFORD 3 | 115 | 16.01 | 16.09 | 0.08
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524622 | DEAFSMITH 3 | 115 | 18.8 | 18.9 | 0.1
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524623 | DEAFSMITH 6 | 230 | 23.91 | 24.21 | 0.3
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524627 | DEFPLT_SS 6 | 230 | 17.58 | 17.75 | 0.17
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524629 | DS-#6 3 | 115 | 7.73 | 7.76 | 0.03
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524662 | PARMER_CO 3 | 115 | 4.88 | 4.9 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524669 | DS-#20 3 | 115 | 5.94 | 5.95 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524694 | DS-#22 3 | 115 | 5.16 | 5.17 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524734 | DS-#21 3 | 115 | 10.56 | 10.59 | 0.03
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524745 | CASTRO_CNTY2 | 69 | 9.89 | 9.91 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524746 | CASTRO_CNTY3 | 115 | 11.14 | 11.17 | 0.03
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524757 | BETHEL_COL13 | 115 | 9.36 | 9.38 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524764 | NORRIS_TP 3 | 115 | 12.64 | 12.69 | 0.05
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524768 | PLSNT_HILL 3 | 115 | 12.28 | 12.33 | 0.05
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524770 | PLSNT_HILL 6 | 230 | 7.81 | 7.85 | 0.04
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524773 | E_CLOVIS 3 | 115 | 10.16 | 10.2 | 0.04
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524776 | N_CLOVIS_TP3 | 115 | 9.04 | 9.07 | 0.03
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524777 | N_CLOVIS 3 | 115 | 8.09 | 8.12 | 0.03
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524783 | W_CLOVIS 2 | 69 | 2.7 | 2.71 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524790 | CANNON_TP 3 | 115 | 7.05 | 7.08 | 0.03
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524797 | PERIMETER 3 | 115 | 7.51 | 7.54 | 0.03
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524801 | NORRIS 3 | 115 | 11.53 | 11.58 | 0.05
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524808 | FE-CLVS_INT3 | 115 | 8.55 | 8.58 | 0.03
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524821 | CURRY 2 | 69 | 4.9 | 4.92 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524822 | CURRY 3 | 115 | 12.67 | 12.73 | 0.06
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524831 | FE-HOLLAND 3 | 115 | 10.52 | 10.56 | 0.04
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524838 | FE-CLOVIS2+3 | 115 | 12 | 12.05 | 0.05
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524846 | FARWELL 2 | 69 | 2.36 | 2.37 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524863 | FE-CHZPLT 3 | 115 | 8.94 | 8.98 | 0.04
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524874 | OASIS 3 | 115 | 11.32 | 11.37 | 0.05
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524875 | OASIS 6 | 230 | 8.81 | 8.85 | 0.04
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524885 | SN_JUAN_TAP6 | 230 | 5.21 | 5.22 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524889 | SN_JUAN_WND6 | 230 | 4.97 | 4.98 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524908 | ROOSEVELT 3 | 115 | 12.11 | 12.16 | 0.05
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524909 | ROSEVELT_N 6 | 230 | 10.6 | 10.67 | 0.07
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524923 | PORTALES 2 | 69 | 8.09 | 8.12 | 0.03
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524924 | PORTALES 3 | 115 | 8.39 | 8.42 | 0.03
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524929 | RO-PORT_MTR2 | 69 | 8.09 | 8.12 | 0.03
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524934 | ZODIAC 2 | 69 | 5.99 | 6 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524935 | KILGORE 3 | 115 | 6.82 | 6.85 | 0.03
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524941 | PORTALES#1 2 | 69 | 6.21 | 6.22 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524963 | S_PORTALES 3 | 115 | 6.4 | 6.42 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 524977 | GREYHOUND 3 | 115 | 6.31 | 6.33 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525018 | MULESHVALLY3 | 115 | 6.53 | 6.55 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525019 | MULSHVLY_TP3 | 115 | 7.06 | 7.08 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525027 | BAILEYCO 2 | 69 | 6.11 | 6.13 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525028 | BAILEYCO 3 | 115 | 7.04 | 7.07 | 0.03
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525040 | BAILEY_PMP 3 | 115 | 5.23 | 5.25 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525050 | BC-KELLEY +3 | 115 | 8.55 | 8.57 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525056 | BC-EARTH 3 | 115 | 9 | 9.03 | 0.03
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525124 | HART_INDUST3 | 115 | 8.34 | 8.35 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525179 | TULIA_TP 3 | 115 | 6.98 | 6.99 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525191 | KRESS_INT 2 | 69 | 4.88 | 4.88 | 0
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525192 | KRESS_INT 3 | 115 | 13.09 | 13.11 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525212 | SWISHER 3 | 115 | 12.62 | 12.64 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525213 | SWISHER 6 | 230 | 11.29 | 11.31 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525226 | KRS_RURL_TP3 | 115 | 7.01 | 7.02 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525230 | NEWPOT_SS 6 | 230 | 7.47 | 7.49 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525272 | KISER 3 | 115 | 5.72 | 5.73 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525291 | PLAINVW_TP 2 | 69 | 7.01 | 7.03 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525298 | S_PLAINVEW 2 | 69 | 2.79 | 2.79 | 0
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525325 | COX 2 | 69 | 3.7 | 3.7 | 0
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525326 | COX 3 | 115 | 6.83 | 6.84 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525393 | ROCKYFORD 3 | 115 | 9.74 | 9.77 | 0.03
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525413 | LAMTON 2 | 69 | 5.6 | 5.61 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525414 | LAMTON 3 | 115 | 8.29 | 8.31 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525432 | SP-HALFWAY+2 | 69 | 6.34 | 6.35 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525440 | LC-S_OLTON+3 | 115 | 7.8 | 7.82 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525446 | RKYFORD_TP 3 | 115 | 10.9 | 10.94 | 0.04
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525453 | HALE_CNTY 2 | 69 | 7.48 | 7.49 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525454 | HALE_CNTY 3 | 115 | 11.07 | 11.09 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525460 | NEWHART 3 | 115 | 17.85 | 17.89 | 0.04
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525461 | NEWHART 6 | 230 | 11.84 | 11.87 | 0.03
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525480 | PLANT_X 3 | 115 | 20.41 | 20.53 | 0.12
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525481 | PLANT_X 6 | 230 | 23.91 | 24.21 | 0.3
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525524 | TOLK_EAST 6 | 230 | 30.57 | 31.31 | 0.74
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525531 | TOLK_WEST 6 | 230 | 30.57 | 31.31 | 0.74
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525543 | TOLK_TAP 6 | 230 | 30.57 | 31.31 | 0.74
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525549 | TOLK 7 | 345 | 12.82 | 12.96 | 0.14
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525586 | NEEDMORE 6 | 230 | 12.45 | 12.55 | 0.1
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525594 | SUDANRURAL 3 | 115 | 5.06 | 5.07 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525599 | LC-SANDHLL+2 | 69 | 3.02 | 3.03 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525607 | NEW_AMHERST2 | 69 | 3.48 | 3.49 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525608 | NEW_AMHERST3 | 115 | 5.6 | 5.62 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525614 | W_LITLFLDTP3 | 115 | 8.53 | 8.56 | 0.03
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525615 | W_LITTLFLD 3 | 115 | 8.08 | 8.11 | 0.03
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525620 | LTFLD_S&CTY2 | 69 | 4.68 | 4.69 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525635 | LAMB_CNTY 2 | 69 | 6.69 | 6.72 | 0.03
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525636 | LAMB_CNTY 3 | 115 | 10.16 | 10.2 | 0.04
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525637 | LAMB_CNTY 6 | 230 | 5.98 | 6.02 | 0.04
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525650 | LC-LTTLFLD+2 | 69 | 5.56 | 5.58 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525657 | W_ANTON_TP 2 | 69 | 4.6 | 4.62 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525687 | LC-LUMSCHAP2 | 69 | 5.19 | 5.2 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525694 | HOBGOOD 2 | 69 | 3.84 | 3.85 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525780 | FLOYD_CNTY 3 | 115 | 6.87 | 6.88 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525816 | TUCO_INT2 2 | 69 | 4.97 | 4.98 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525826 | TUCO_INT 2 | 69 | 8.45 | 8.45 | 0
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525828 | TUCO_INT 3 | 115 | 21.9 | 21.93 | 0.03
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525830 | TUCO_INT 6 | 230 | 28.96 | 29.02 | 0.06
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525832 | TUCO_INT 7 | 345 | 23.64 | 23.68 | 0.04
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525840 | ANTELOPE_1 6 | 230 | 28.66 | 28.71 | 0.05
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 525850 | ELK_CT1 | 345 | 23.26 | 23.29 | 0.03
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 526009 | LC-LEVLND#22 | 69 | 4.67 | 4.68 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 526012 | DEAN_INTG 3 | 115 | 11.49 | 11.51 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 526013 | DEAN_INTG 6 | 230 | 8.71 | 8.73 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 526019 | HOCKLEY 2 | 69 | 5.62 | 5.63 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 526020 | HOCKLEY 3 | 115 | 6.04 | 6.05 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 526036 | LC-OPDYKE 3 | 115 | 6.35 | 6.37 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 526042 | COBLE 2 | 69 | 2.46 | 2.47 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 526048 | LVLNDCTY_TP2 | 69 | 4.67 | 4.68 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 526076 | STANTON_W 3 | 115 | 9.7 | 9.7 | 0
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 526160 | CARLISLE 3 | 115 | 14.09 | 14.1 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 526161 | CARLISLE 6 | 230 | 14.7 | 14.71 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 526268 | LUBBCK_STH 3 | 115 | 20.1 | 20.11 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 526269 | LUBBCK_STH 6 | 230 | 19.2 | 19.22 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 526298 | LUBBCK_EST 3 | 115 | 16.19 | 16.2 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 526299 | LUBBCK_EST 6 | 230 | 13.84 | 13.85 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 526337 | JONES 6 | 230 | 21.12 | 21.14 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 526350 | LEHMAN_TP 3 | 115 | 9.38 | 9.4 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 526352 | LEHMAN 3 | 115 | 7.47 | 7.48 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 526360 | COCHRAN 2 | 69 | 6.87 | 6.88 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 526361 | COCHRAN 3 | 115 | 8.97 | 8.98 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 526424 | PACIFIC 3 | 115 | 10.94 | 10.96 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 526434 | SUNDOWN 3 | 115 | 12.52 | 12.55 | 0.03
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 526435 | SUNDOWN 6 | 230 | 11.81 | 11.84 | 0.03
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 526445 | AMOCO_TP 3 | 115 | 11.63 | 11.65 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 526452 | AMOCO_CRYO 3 | 115 | 7.09 | 7.1 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 526460 | AMOCO_SS 6 | 230 | 10.35 | 10.37 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 526475 | YUMA_INT 3 | 115 | 11.66 | 11.67 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 526484 | LG-LEVELAND3 | 115 | 10.31 | 10.32 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 526524 | WOLFFORTH 3 | 115 | 12.23 | 12.24 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 526525 | WOLFFORTH 6 | 230 | 14.33 | 14.34 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 526677 | GRASSLAND 6 | 230 | 6.83 | 6.83 | 0
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 526736 | TERRY_CNTY 3 | 115 | 11.08 | 11.09 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 526784 | AMOCOWASSON6 | 230 | 14.43 | 14.44 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 526792 | PRENTICE 3 | 115 | 6.27 | 6.27 | 0
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 526928 | PLAINS_INT 3 | 115 | 10.25 | 10.26 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 526934 | YOAKUM 3 | 115 | 17.4 | 17.42 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 526935 | YOAKUM 6 | 230 | 18.55 | 18.57 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 526936 | YOAKUM_345 | 345 | 9.69 | 9.7 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 526944 | LG-PLAINS 3 | 115 | 8.48 | 8.49 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 527009 | BRU_SUB 6 | 230 | 14.64 | 14.65 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 527010 | OXYBRU 6 | 230 | 14.52 | 14.53 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 527011 | XTO_MAHONEY6 | 230 | 14.22 | 14.23 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 527027 | INK_BASIN 3 | 115 | 13.33 | 13.34 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 527028 | INK_BASIN 6 | 230 | 11.12 | 11.13 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 527041 | ARCO_TP 3 | 115 | 13.79 | 13.79 | 0
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 527146 | MUSTANG 3 | 115 | 24.19 | 24.2 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 527149 | MUSTANG 6 | 230 | 16.14 | 16.15 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 527151 | GS-MUSTANG 6 | 230 | 16.14 | 16.15 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 527194 | LG-PLSHILL 3 | 115 | 7.98 | 7.98 | 0
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 527276 | SEMINOLE 6 | 230 | 7.92 | 7.92 | 0
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 527482 | CHAVES_CNTY3 | 115 | 7.33 | 7.34 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 527483 | CHAVES_CNTY6 | 230 | 4.72 | 4.73 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 527654 | RSVLT_CC_W 7 | 345 | 11.32 | 11.35 | 0.03
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 527655 | RSVLT_CC_E 7 | 345 | 13.91 | 13.94 | 0.03
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 527656 | CROSSROADS 7 | 345 | 17.53 | 17.58 | 0.05
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 527799 | EDDY_NORTH 6 | 230 | 9.7 | 9.71 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 527802 | EDDY_CNTY 7 | 345 | 7.71 | 7.72 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 527894 | HOBBS_INT 6 | 230 | 17.05 | 17.06 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 527896 | HOBBS_INT 7 | 345 | 9.33 | 9.34 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 560022 | CRAWFISH_DR | 345 | 23.9 | 23.94 | 0.04
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 560100 | CRAWFISH765 | 765 | 11.15 | 11.17 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 560102 | CROSSRDS765 | 765 | 7.99 | 8.01 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 583340 | GEN-2012-020 | 230 | 11.68 | 11.7 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 583840 | GEN-2013-027 | 230 | 11.66 | 11.75 | 0.09
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 584560 | GEN-2015-014 | 115 | 6.47 | 6.48 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 587250 | GEN-2016-039 | 115 | 12.62 | 12.64 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 588000 | GEN-2016-123 | 345 | 16.86 | 16.91 | 0.05
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 588440 | GEN-2016-172 | 115 | 15.06 | 15.09 | 0.03
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 588520 | GEN-2017-007 | 230 | 4.65 | 4.67 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 588610 | GEN-2017-016 | 115 | 3.39 | 3.39 | 0
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 588700 | GEN-2017-026 | 230 | 9.2 | 9.99 | 0.79
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 588800 | GEN-2017-039 | 230 | 10.06 | 10.13 | 0.07
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 588960 | GEN-2017-058 | 115 | 8.56 | 8.6 | 0.04
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 588970 | GEN-2017-059 | 230 | 10 | 10.01 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 589160 | GEN-2017-078 | 345 | 10.86 | 10.88 | 0.02
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 589180 | GEN-2017-080 | 230 | 26.35 | 26.91 | 0.56
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 589188 | G17-080-SUB2 | 230 | 15.31 | 15.52 | 0.21
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 599950 | LAMAR7 | 345 | 2.55 | 2.55 | 0
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 599951 | LAMAR 6 | 345 | 57.79 | 57.79 | 0
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 599955 | PNM-DC6 | 230 | 10.6 | 10.67 | 0.07
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 599956 | PNM-DC7 | 345 | 16738.66 | 16738.66 | 0
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 599960 | EPTNP-D6 | 230 | 9.7 | 9.71 | 0.01
GEN-2017-026 | South | 06 - South Texas Panhandle/New Mexico | 599961 | EPTNP 7 | 345 | 16736.82 | 16736.82 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 510907 | PITTSB-7 | 345 | 14.43 | 14.44 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511422 | FLETCHR4 | 138 | 8.32 | 8.34 | 0.02
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511423 | FLE TAP4 | 138 | 9.13 | 9.15 | 0.02
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511428 | LG-YEAR4 | 138 | 12.2 | 12.25 | 0.05
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511431 | LWS S4 | 138 | 11.35 | 11.4 | 0.05
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511436 | COMANC-2 | 69 | 10.11 | 10.13 | 0.02
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511437 | COMANC-4 | 138 | 18.69 | 18.79 | 0.1
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511439 | LWSTAP 4 | 138 | 11.84 | 11.89 | 0.05
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511451 | CYRIL--2 | 69 | 4.77 | 4.78 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511453 | DUNCAN-4 | 138 | 6.68 | 6.69 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511456 | O.K.U.-7 | 345 | 5.56 | 6 | 0.44
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511461 | FT.SILL2 | 69 | 6.1 | 6.12 | 0.02
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511466 | L.E.S.-2 | 69 | 17.11 | 17.17 | 0.06
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511467 | L.E.S.-4 | 138 | 25.39 | 25.58 | 0.19
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511468 | L.E.S.-7 | 345 | 13.53 | 13.76 | 0.23
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511469 | LGORE-N2 | 69 | 8.24 | 8.26 | 0.02
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511470 | LGORE-S2 | 69 | 7.15 | 7.17 | 0.02
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511471 | LWS-NTP4 | 138 | 11.97 | 12.02 | 0.05
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511473 | PO.HILL2 | 69 | 5.97 | 5.99 | 0.02
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511474 | SHERID4 | 138 | 12.65 | 12.7 | 0.05
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511477 | S.W.S.-4 | 138 | 36.36 | 36.4 | 0.04
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511486 | ELGINJT4 | 138 | 10.32 | 10.35 | 0.03
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511487 | ELGINJT2 | 69 | 8.74 | 8.76 | 0.02
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511488 | 112GORE4 | 138 | 13 | 13.06 | 0.06
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511494 | COMMTAP4 | 138 | 22.2 | 22.35 | 0.15
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511503 | LAW WC2 | 69 | 4.67 | 4.68 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511509 | 53CACHE4 | 138 | 12 | 12.06 | 0.06
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511510 | LAIRGST4 | 138 | 12.59 | 12.64 | 0.05
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511512 | RPPAPER4 | 138 | 12.26 | 12.31 | 0.05
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511524 | L-DISTP2 | 69 | 9.34 | 9.36 | 0.02
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511537 | ARTVLTP4 | 138 | 12.02 | 12.08 | 0.06
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511538 | ARTVILL4 | 138 | 8.71 | 8.74 | 0.03
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511553 | CHISHOLM7 | 345 | 5.81 | 5.82 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511563 | ELSWORTH 4 | 138 | 10.24 | 10.27 | 0.03
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511565 | OKLAUN HVDC7 | 345 | 5.54 | 5.98 | 0.44
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511568 | TERRYRD7 | 345 | 10.19 | 10.27 | 0.08
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511571 | RUSHSPR7 | 345 | 6.53 | 6.57 | 0.04
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 514785 | WOODWRD4 | 138 | 13.28 | 13.28 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 514796 | IODINE-4 | 138 | 7.48 | 7.48 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 514801 | MINCO 7 | 345 | 18.52 | 18.55 | 0.03
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 514808 | JOHNCO 4 | 138 | 15.44 | 15.46 | 0.02
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 514809 | JOHNCO 7 | 345 | 10.14 | 10.15 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 514901 | CIMARON7 | 345 | 35.49 | 35.51 | 0.02
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515045 | SEMINOL7 | 345 | 33.65 | 33.68 | 0.03
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515135 | SUNNYSD4 | 138 | 18.99 | 19.02 | 0.03
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515136 | SUNNYSD7 | 345 | 11.36 | 11.39 | 0.03
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515137 | UNIROY 4 | 138 | 12.74 | 12.76 | 0.02
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515144 | LONEGRV4 | 138 | 13.7 | 13.72 | 0.02
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515164 | ROCKYPT4 | 138 | 10.63 | 10.64 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515375 | WWRDEHV7 | 345 | 20.17 | 20.17 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515376 | WWRDEHV4 | 138 | 24.55 | 24.55 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515394 | KEENAN 4 | 138 | 9.05 | 9.05 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515398 | OUSPRT 4 | 138 | 9.63 | 9.63 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515407 | TATONGA7 | 345 | 16.97 | 16.98 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515425 | WWDPST 4 | 138 | 17.79 | 17.79 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515444 | MCNOWND7 | 345 | 18.46 | 18.49 | 0.03
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515448 | CRSRDSW7 | 345 | 11.91 | 11.91 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515458 | BORDER 7 | 345 | 4.71 | 4.71 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515497 | MATHWSN7 | 345 | 33.94 | 33.96 | 0.02
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515549 | MNCWND37 | 345 | 12.66 | 12.68 | 0.02
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515561 | CARTRCO4 | 138 | 9.91 | 9.92 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515582 | SLNGWND7 | 345 | 7.45 | 7.45 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515585 | MAMTHPW7 | 345 | 13.48 | 13.48 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515599 | G07621119-20 | 345 | 13.41 | 13.42 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515677 | BADGER 7 | 345 | 14.39 | 14.39 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515800 | GRACMNT7 | 345 | 17.51 | 17.58 | 0.07
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515802 | GRACMNT4 | 138 | 30.3 | 30.35 | 0.05
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515852 | DGRASSE7 | 345 | 14.79 | 14.79 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515853 | DGRASSE4 | 138 | 15.6 | 15.6 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 520814 | ANADARK4 | 138 | 32.75 | 32.78 | 0.03
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 521089 | WASHITA4 | 138 | 31.11 | 31.15 | 0.04
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 521157 | HUGO 7 | 345 | 11.54 | 11.54 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 522823 | LP-MCDONALD6 | 230 | 14.32 | 14.33 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 522870 | LP-HOLLY 6 | 230 | 16.99 | 17 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 524415 | AMA_SOUTH 6 | 230 | 13.83 | 13.83 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 524909 | ROSEVELT_N 6 | 230 | 10.67 | 10.67 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 525212 | SWISHER 3 | 115 | 12.63 | 12.64 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 525213 | SWISHER 6 | 230 | 11.31 | 11.31 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 525454 | HALE_CNTY 3 | 115 | 11.08 | 11.09 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 525461 | NEWHART 6 | 230 | 11.87 | 11.87 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 525481 | PLANT_X 6 | 230 | 24.21 | 24.21 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 525524 | TOLK_EAST 6 | 230 | 31.3 | 31.31 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 525543 | TOLK_TAP 6 | 230 | 31.3 | 31.31 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 525549 | TOLK 7 | 345 | 12.96 | 12.96 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 525780 | FLOYD_CNTY 3 | 115 | 6.87 | 6.88 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 525816 | TUCO_INT2 2 | 69 | 4.97 | 4.98 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 525826 | TUCO_INT 2 | 69 | 8.45 | 8.45 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 525828 | TUCO_INT 3 | 115 | 21.91 | 21.93 | 0.02
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 525830 | TUCO_INT 6 | 230 | 28.97 | 29.02 | 0.05
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 525832 | TUCO_INT 7 | 345 | 23.61 | 23.68 | 0.07
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 525840 | ANTELOPE_1 6 | 230 | 28.67 | 28.71 | 0.04
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 525850 | ELK_CT1 | 345 | 23.22 | 23.29 | 0.07
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 526013 | DEAN_INTG 6 | 230 | 8.72 | 8.73 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 526076 | STANTON_W 3 | 115 | 9.7 | 9.7 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 526160 | CARLISLE 3 | 115 | 14.09 | 14.1 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 526161 | CARLISLE 6 | 230 | 14.7 | 14.71 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 526269 | LUBBCK_STH 6 | 230 | 19.21 | 19.22 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 526298 | LUBBCK_EST 3 | 115 | 16.19 | 16.2 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 526299 | LUBBCK_EST 6 | 230 | 13.84 | 13.85 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 526337 | JONES 6 | 230 | 21.13 | 21.14 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 526460 | AMOCO_SS 6 | 230 | 10.37 | 10.37 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 526525 | WOLFFORTH 6 | 230 | 14.34 | 14.34 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 526677 | GRASSLAND 6 | 230 | 6.83 | 6.83 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 526934 | YOAKUM 3 | 115 | 17.41 | 17.42 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 526935 | YOAKUM 6 | 230 | 18.56 | 18.57 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 526936 | YOAKUM_345 | 345 | 9.69 | 9.7 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 527009 | BRU_SUB 6 | 230 | 14.65 | 14.65 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 527028 | INK_BASIN 6 | 230 | 11.13 | 11.13 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 527149 | MUSTANG 6 | 230 | 16.15 | 16.15 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 527655 | RSVLT_CC_E 7 | 345 | 13.93 | 13.94 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 527656 | CROSSROADS 7 | 345 | 17.56 | 17.58 | 0.02
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 527802 | EDDY_CNTY 7 | 345 | 7.71 | 7.72 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 527894 | HOBBS_INT 6 | 230 | 17.05 | 17.06 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 527896 | HOBBS_INT 7 | 345 | 9.33 | 9.34 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 527965 | KIOWA 7 | 345 | 8.15 | 8.16 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 529304 | OMDUNCN4 | 138 | 6.9 | 6.91 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 539801 | THISTLE7 | 345 | 16.68 | 16.68 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 560022 | CRAWFISH_DR | 345 | 23.86 | 23.94 | 0.08
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 560071 | G16-003-TAP | 345 | 15.51 | 15.51 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 560078 | G16-037-TAP | 345 | 7.63 | 7.64 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 560088 | G16-063-TAP | 345 | 8.06 | 8.07 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 560100 | CRAWFISH765 | 765 | 11.14 | 11.17 | 0.03
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 560101 | SEMINOLE765 | 765 | 11.92 | 11.93 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 560102 | CROSSRDS765 | 765 | 8 | 8.01 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 560104 | CDSEMMID | 765 | 9.39 | 9.4 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 563259 | GEN-2015-092 | 345 | 6.34 | 6.37 | 0.03
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 563269 | GEN-2015-093 | 345 | 10.03 | 10.06 | 0.03
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 583340 | GEN-2012-020 | 230 | 11.69 | 11.7 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 584780 | GEN-2015-036 | 345 | 7.2 | 7.21 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 585410 | GREAT_WESTRN | 345 | 10.1 | 10.1 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 585430 | PRSIMN_CRK1 | 345 | 11.8 | 11.8 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 587020 | GEN-2016-003 | 345 | 15.51 | 15.51 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 587230 | GEN-2016-037 | 345 | 6.95 | 6.96 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 587430 | GEN-2016-063 | 345 | 7.96 | 7.97 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 587740 | GEN-2016-091 | 345 | 13.4 | 13.48 | 0.08
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 587744 | G16-091-TAP | 345 | 15.1 | 15.19 | 0.09
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 587770 | GEN-2016-095 | 345 | 11.1 | 11.16 | 0.06
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 587790 | GEN-2016-097 | 138 | 9.83 | 9.84 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 587794 | G16-097-TAP | 138 | 12.05 | 12.06 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 588000 | GEN-2016-123 | 345 | 16.89 | 16.91 | 0.02
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 588560 | GEN-2017-011 | 345 | 12.48 | 12.48 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 588760 | GEN-2017-033 | 345 | 3.94 | 4.39 | 0.45
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 588970 | GEN-2017-059 | 230 | 10 | 10.01 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 589030 | GEN-2017-065 | 345 | 5.11 | 5.48 | 0.37
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 589130 | GEN-2017-075 | 345 | 8.05 | 8.06 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 589160 | GEN-2017-078 | 345 | 10.87 | 10.88 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 590001 | OKLEHV24 | 138 | 5.17 | 5.17 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 590003 | OKLEHV14 | 138 | 5.18 | 5.18 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 599891 | OKLAUN 7 | 345 | 4.36 | 4.36 | 0
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 523959 | POTTER_CO 6 | 230 | 21.22 | 21.24 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 524266 | BUSHLAND 3 | 115 | 10.1 | 10.11 | 0.01
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 524267 | BUSHLAND 6 | 230 | 11.7 | 11.72 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 524290 | WILDOR2_JUS6 | 230 | 7.63 | 7.64 | 0.01
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 524415 | AMA_SOUTH 6 | 230 | 13.82 | 13.83 | 0.01
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 524502 | NORTON 3 | 115 | 3.54 | 3.54 | 0
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 524567 | NE_HEREFORD3 | 115 | 13.99 | 14.04 | 0.05
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 524575 | DS-#25+ 3 | 115 | 14.33 | 14.38 | 0.05
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 524606 | HEREFORD 3 | 115 | 16.03 | 16.09 | 0.06
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 524622 | DEAFSMITH 3 | 115 | 18.83 | 18.9 | 0.07
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 524623 | DEAFSMITH 6 | 230 | 24.02 | 24.21 | 0.19
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 524627 | DEFPLT_SS 6 | 230 | 17.64 | 17.75 | 0.11
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 524669 | DS-#20 3 | 115 | 5.94 | 5.95 | 0.01
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 524734 | DS-#21 3 | 115 | 10.57 | 10.59 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 524746 | CASTRO_CNTY3 | 115 | 11.14 | 11.17 | 0.03
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 524764 | NORRIS_TP 3 | 115 | 12.65 | 12.69 | 0.04
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 524768 | PLSNT_HILL 3 | 115 | 12.29 | 12.33 | 0.04
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 524770 | PLSNT_HILL 6 | 230 | 7.82 | 7.85 | 0.03
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 524773 | E_CLOVIS 3 | 115 | 10.17 | 10.2 | 0.03
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 524776 | N_CLOVIS_TP3 | 115 | 9.05 | 9.07 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 524797 | PERIMETER 3 | 115 | 7.52 | 7.54 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 524821 | CURRY 2 | 69 | 4.9 | 4.92 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 524822 | CURRY 3 | 115 | 12.69 | 12.73 | 0.04
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 524831 | FE-HOLLAND 3 | 115 | 10.53 | 10.56 | 0.03
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 524838 | FE-CLOVIS2+3 | 115 | 12.01 | 12.05 | 0.04
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 524863 | FE-CHZPLT 3 | 115 | 8.95 | 8.98 | 0.03
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 524874 | OASIS 3 | 115 | 11.33 | 11.37 | 0.04
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 524875 | OASIS 6 | 230 | 8.82 | 8.85 | 0.03
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 524885 | SN_JUAN_TAP6 | 230 | 5.21 | 5.22 | 0.01
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 524889 | SN_JUAN_WND6 | 230 | 4.97 | 4.98 | 0.01
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 524908 | ROOSEVELT 3 | 115 | 12.12 | 12.16 | 0.04
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 524909 | ROSEVELT_N 6 | 230 | 10.62 | 10.67 | 0.05
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 524923 | PORTALES 2 | 69 | 8.1 | 8.12 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 524924 | PORTALES 3 | 115 | 8.4 | 8.42 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 524935 | KILGORE 3 | 115 | 6.83 | 6.85 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 524977 | GREYHOUND 3 | 115 | 6.31 | 6.33 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525018 | MULESHVALLY3 | 115 | 6.54 | 6.55 | 0.01
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525019 | MULSHVLY_TP3 | 115 | 7.06 | 7.08 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525028 | BAILEYCO 3 | 115 | 7.05 | 7.07 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525050 | BC-KELLEY +3 | 115 | 8.55 | 8.57 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525056 | BC-EARTH 3 | 115 | 9.01 | 9.03 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525124 | HART_INDUST3 | 115 | 8.34 | 8.35 | 0.01
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525192 | KRESS_INT 3 | 115 | 13.09 | 13.11 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525212 | SWISHER 3 | 115 | 12.62 | 12.64 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525213 | SWISHER 6 | 230 | 11.3 | 11.31 | 0.01
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525230 | NEWPOT_SS 6 | 230 | 7.48 | 7.49 | 0.01
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525326 | COX 3 | 115 | 6.83 | 6.84 | 0.01
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525393 | ROCKYFORD 3 | 115 | 9.75 | 9.77 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525414 | LAMTON 3 | 115 | 8.29 | 8.31 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525440 | LC-S_OLTON+3 | 115 | 7.81 | 7.82 | 0.01
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525446 | RKYFORD_TP 3 | 115 | 10.9 | 10.94 | 0.04
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525453 | HALE_CNTY 2 | 69 | 7.48 | 7.49 | 0.01
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525454 | HALE_CNTY 3 | 115 | 11.07 | 11.09 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525460 | NEWHART 3 | 115 | 17.86 | 17.89 | 0.03
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525461 | NEWHART 6 | 230 | 11.85 | 11.87 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525480 | PLANT_X 3 | 115 | 20.45 | 20.53 | 0.08
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525481 | PLANT_X 6 | 230 | 24.02 | 24.21 | 0.19
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525524 | TOLK_EAST 6 | 230 | 30.87 | 31.31 | 0.44
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525531 | TOLK_WEST 6 | 230 | 30.87 | 31.31 | 0.44
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525543 | TOLK_TAP 6 | 230 | 30.87 | 31.31 | 0.44
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525549 | TOLK 7 | 345 | 12.87 | 12.96 | 0.09
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525586 | NEEDMORE 6 | 230 | 11.94 | 12.55 | 0.61
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525594 | SUDANRURAL 3 | 115 | 5.06 | 5.07 | 0.01
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525607 | NEW_AMHERST2 | 69 | 3.48 | 3.49 | 0.01
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525608 | NEW_AMHERST3 | 115 | 5.6 | 5.62 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525614 | W_LITLFLDTP3 | 115 | 8.53 | 8.56 | 0.03
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525615 | W_LITTLFLD 3 | 115 | 8.08 | 8.11 | 0.03
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525620 | LTFLD_S&CTY2 | 69 | 4.68 | 4.69 | 0.01
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525635 | LAMB_CNTY 2 | 69 | 6.7 | 6.72 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525636 | LAMB_CNTY 3 | 115 | 10.17 | 10.2 | 0.03
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525637 | LAMB_CNTY 6 | 230 | 5.99 | 6.02 | 0.03
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525650 | LC-LTTLFLD+2 | 69 | 5.56 | 5.58 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525687 | LC-LUMSCHAP2 | 69 | 5.19 | 5.2 | 0.01
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525828 | TUCO_INT 3 | 115 | 21.91 | 21.93 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525830 | TUCO_INT 6 | 230 | 28.97 | 29.02 | 0.05
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525832 | TUCO_INT 7 | 345 | 23.65 | 23.68 | 0.03
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525840 | ANTELOPE_1 6 | 230 | 28.67 | 28.71 | 0.04
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525850 | ELK_CT1 | 345 | 23.26 | 23.29 | 0.03
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 525978 | SW_6865&67 2 | 69 | 4.38 | 4.39 | 0.01
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 526012 | DEAN_INTG 3 | 115 | 11.45 | 11.51 | 0.06
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 526013 | DEAN_INTG 6 | 230 | 8.64 | 8.73 | 0.09
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 526019 | HOCKLEY 2 | 69 | 5.62 | 5.63 | 0.01
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 526020 | HOCKLEY 3 | 115 | 6.04 | 6.05 | 0.01
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 526036 | LC-OPDYKE 3 | 115 | 6.35 | 6.37 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 526161 | CARLISLE 6 | 230 | 14.7 | 14.71 | 0.01
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 526269 | LUBBCK_STH 6 | 230 | 19.2 | 19.22 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 526337 | JONES 6 | 230 | 21.12 | 21.14 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 526350 | LEHMAN_TP 3 | 115 | 9.35 | 9.4 | 0.05
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 526352 | LEHMAN 3 | 115 | 7.45 | 7.48 | 0.03
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 526360 | COCHRAN 2 | 69 | 6.86 | 6.88 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 526361 | COCHRAN 3 | 115 | 8.95 | 8.98 | 0.03
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 526372 | LG-SUNDOWN 2 | 69 | 2.66 | 2.66 | 0
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 526379 | MIDDLETON 2 | 69 | 4.04 | 4.05 | 0.01
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 526424 | PACIFIC 3 | 115 | 10.93 | 10.96 | 0.03
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 526434 | SUNDOWN 3 | 115 | 12.51 | 12.55 | 0.04
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 526435 | SUNDOWN 6 | 230 | 11.81 | 11.84 | 0.03
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 526445 | AMOCO_TP 3 | 115 | 11.62 | 11.65 | 0.03
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 526460 | AMOCO_SS 6 | 230 | 10.35 | 10.37 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 526524 | WOLFFORTH 3 | 115 | 12.23 | 12.24 | 0.01
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 526525 | WOLFFORTH 6 | 230 | 14.32 | 14.34 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 526736 | TERRY_CNTY 3 | 115 | 11.07 | 11.09 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 526784 | AMOCOWASSON6 | 230 | 14.42 | 14.44 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 526792 | PRENTICE 3 | 115 | 6.26 | 6.27 | 0.01
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 526928 | PLAINS_INT 3 | 115 | 10.24 | 10.26 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 526934 | YOAKUM 3 | 115 | 17.38 | 17.42 | 0.04
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 526935 | YOAKUM 6 | 230 | 18.51 | 18.57 | 0.06
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 526936 | YOAKUM_345 | 345 | 9.68 | 9.7 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 526944 | LG-PLAINS 3 | 115 | 8.47 | 8.49 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 527009 | BRU_SUB 6 | 230 | 14.62 | 14.65 | 0.03
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 527010 | OXYBRU 6 | 230 | 14.5 | 14.53 | 0.03
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 527011 | XTO_MAHONEY6 | 230 | 14.2 | 14.23 | 0.03
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 527018 | BENNETT 3 | 115 | 13.88 | 13.9 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 527027 | INK_BASIN 3 | 115 | 13.32 | 13.34 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 527028 | INK_BASIN 6 | 230 | 11.11 | 11.13 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 527030 | ALRDCRTZ_TP3 | 115 | 12.52 | 12.53 | 0.01
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 527041 | ARCO_TP 3 | 115 | 13.78 | 13.79 | 0.01
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 527047 | OXY_WILRD1 3 | 115 | 11.09 | 11.11 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 527062 | SHELL_CO2 3 | 115 | 16.87 | 16.89 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 527130 | DENVER_N 3 | 115 | 22.57 | 22.6 | 0.03
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 527136 | DENVER_S 3 | 115 | 22.57 | 22.6 | 0.03
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 527146 | MUSTANG 3 | 115 | 24.17 | 24.2 | 0.03
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 527149 | MUSTANG 6 | 230 | 16.12 | 16.15 | 0.03
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 527151 | GS-MUSTANG 6 | 230 | 16.12 | 16.15 | 0.03
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 527194 | LG-PLSHILL 3 | 115 | 7.97 | 7.98 | 0.01
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 527202 | SEAGRAVES 3 | 115 | 9.04 | 9.05 | 0.01
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 527275 | SEMINOLE 3 | 115 | 14.02 | 14.04 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 527276 | SEMINOLE 6 | 230 | 7.91 | 7.92 | 0.01
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 527483 | CHAVES_CNTY6 | 230 | 4.72 | 4.73 | 0.01
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 527655 | RSVLT_CC_E 7 | 345 | 13.92 | 13.94 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 527656 | CROSSROADS 7 | 345 | 17.54 | 17.58 | 0.04
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 527802 | EDDY_CNTY 7 | 345 | 7.71 | 7.72 | 0.01
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 527867 | CUNNIGHM_S 6 | 230 | 14.91 | 14.93 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 527891 | HOBBS_INT 3 | 115 | 30.16 | 30.18 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 527894 | HOBBS_INT 6 | 230 | 17.04 | 17.06 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 527896 | HOBBS_INT 7 | 345 | 9.33 | 9.34 | 0.01
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 527965 | KIOWA 7 | 345 | 8.15 | 8.16 | 0.01
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 528325 | LE-WAITS 3 | 115 | 9.26 | 9.26 | 0
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 528611 | GAINESGENTP6 | 230 | 8.58 | 8.59 | 0.01
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 528626 | LE-PLNSINT 2 | 69 | 3.86 | 3.87 | 0.01
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 560022 | CRAWFISH_DR | 345 | 23.9 | 23.94 | 0.04
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 560102 | CROSSRDS765 | 765 | 8 | 8.01 | 0.01
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 583340 | GEN-2012-020 | 230 | 11.69 | 11.7 | 0.01
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 583840 | GEN-2013-027 | 230 | 11.21 | 11.75 | 0.54
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 584560 | GEN-2015-014 | 115 | 6.45 | 6.48 | 0.03
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 588000 | GEN-2016-123 | 345 | 16.88 | 16.91 | 0.03
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 588440 | GEN-2016-172 | 115 | 15.07 | 15.09 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 588460 | A16-008SUB | 115 | 13.32 | 13.34 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 588520 | GEN-2017-007 | 230 | 4.66 | 4.67 | 0.01
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 588700 | GEN-2017-026 | 230 | 9.93 | 9.99 | 0.06
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 588800 | GEN-2017-039 | 230 | 9.51 | 10.13 | 0.62
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 588970 | GEN-2017-059 | 230 | 10 | 10.01 | 0.01
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 589160 | GEN-2017-078 | 345 | 10.86 | 10.88 | 0.02
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 589180 | GEN-2017-080 | 230 | 26.57 | 26.91 | 0.34
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 589188 | G17-080-SUB2 | 230 | 15.39 | 15.52 | 0.13
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 589400 | GEN-2017-104 | 230 | 6.91 | 6.91 | 0
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 599951 | LAMAR 6 | 345 | 57.79 | 57.79 | 0
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 599955 | PNM-DC6 | 230 | 10.62 | 10.67 | 0.05
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 599956 | PNM-DC7 | 345 | 16738.66 | 16738.66 | 0
GEN-2017-039 | South | 06 - South Texas Panhandle/New Mexico | 599961 | EPTNP 7 | 345 | 16736.82 | 16736.82 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 511456 | O.K.U.-7 | 345 | 6 | 6 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 511467 | L.E.S.-4 | 138 | 25.58 | 25.58 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 511468 | L.E.S.-7 | 345 | 13.76 | 13.76 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 511565 | OKLAUN HVDC7 | 345 | 5.98 | 5.98 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 511568 | TERRYRD7 | 345 | 10.27 | 10.27 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 515375 | WWRDEHV7 | 345 | 20.17 | 20.17 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 515376 | WWRDEHV4 | 138 | 24.55 | 24.55 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 515407 | TATONGA7 | 345 | 16.98 | 16.98 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 515458 | BORDER 7 | 345 | 4.71 | 4.71 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 515599 | G07621119-20 | 345 | 13.41 | 13.42 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 515852 | DGRASSE7 | 345 | 14.79 | 14.79 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 522800 | MU-TULIA 3 | 115 | 5.62 | 5.62 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 522805 | MU-FLOYDADA2 | 69 | 2.35 | 2.35 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 522816 | LP-MACKNZIE3 | 115 | 11.52 | 11.53 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 522820 | LP-NORTHEST3 | 115 | 11.22 | 11.23 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 522821 | LP-NORTHWST3 | 115 | 10.49 | 10.5 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 522823 | LP-MCDONALD6 | 230 | 14.31 | 14.33 | 0.02
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 522824 | LP-XFAB3 | 115 | 10.53 | 10.54 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 522829 | LP-MCDONALD3 | 115 | 13.54 | 13.56 | 0.02
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 522832 | LP-VICKSBRG2 | 69 | 15.53 | 15.55 | 0.02
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 522834 | LP-VICKSBRG3 | 115 | 13.04 | 13.05 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 522835 | LP-THOMPSON3 | 115 | 12.74 | 12.75 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 522846 | LP-COOP3 | 115 | 15.57 | 15.59 | 0.02
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 522848 | LP-CHALKER3 | 115 | 13.68 | 13.7 | 0.02
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 522852 | LP-SLATON3 | 115 | 16.46 | 16.47 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 522858 | LP-SOUTHEST3 | 115 | 17.38 | 17.4 | 0.02
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 522861 | LP-SOUTHEST6 | 230 | 17.34 | 17.36 | 0.02
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 522866 | LP-HOLLY2 | 69 | 13.48 | 13.49 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 522868 | LP-HOLLY3 | 115 | 17.78 | 17.79 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 522870 | LP-HOLLY 6 | 230 | 16.98 | 17 | 0.02
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 522880 | LP-WADSWRTH3 | 115 | 16.43 | 16.44 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 522885 | LP-OLIVER3 | 115 | 12.93 | 12.94 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 522888 | LP-WADSWRTH6 | 230 | 12.97 | 12.99 | 0.02
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 523309 | MOORE_CNTY 6 | 230 | 7.08 | 7.08 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 523339 | FAIN 3 | 115 | 5.35 | 5.36 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 523410 | CRMWA_#4 3 | 115 | 9.59 | 9.59 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 523544 | HUTCH_N 3 | 115 | 15.77 | 15.77 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 523546 | HUTCH_S 3 | 115 | 15.77 | 15.77 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 523551 | HUTCHISON 6 | 230 | 7.37 | 7.37 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 523770 | GRAPEVINE 3 | 115 | 7.93 | 7.93 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 523771 | GRAPEVINE 6 | 230 | 5.84 | 5.84 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 523777 | WHEELER 6 | 230 | 5.98 | 5.98 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 523817 | MIDSTRM_TP 3 | 115 | 4.02 | 4.02 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 523869 | CHAN+TASCOS6 | 230 | 4.49 | 4.49 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 523959 | POTTER_CO 6 | 230 | 21.23 | 21.24 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 523961 | POTTER_CO 7 | 345 | 7.78 | 7.78 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 523977 | HARRNG_WST 6 | 230 | 25.96 | 25.97 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 523978 | HARRNG_MID 6 | 230 | 25.96 | 25.97 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 523979 | HARRNG_EST 6 | 230 | 25.96 | 25.97 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524007 | ROLLHILLS 3 | 115 | 19.03 | 19.03 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524010 | ROLLHILLS 6 | 230 | 19.69 | 19.69 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524016 | ASARCO 3 | 115 | 22.74 | 22.74 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524018 | ASARCO_TP 3 | 115 | 24.25 | 24.26 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524043 | NICHOLS 3 | 115 | 25.55 | 25.55 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524044 | NICHOLS 6 | 230 | 25.11 | 25.12 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524058 | WHITAKER 3 | 115 | 20.34 | 20.34 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524079 | CONWAY 3 | 115 | 5.1 | 5.1 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524163 | EAST_PLANT 6 | 230 | 13.89 | 13.9 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524224 | MANHATTAN 3 | 115 | 17.38 | 17.39 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524266 | BUSHLAND 3 | 115 | 10.11 | 10.11 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524267 | BUSHLAND 6 | 230 | 11.71 | 11.72 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524290 | WILDOR2_JUS6 | 230 | 7.64 | 7.64 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524322 | GEORGIA 3 | 115 | 17.18 | 17.18 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524338 | SOUTHEAST 3 | 115 | 11.68 | 11.68 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524345 | OSAGE 3 | 115 | 13.99 | 14 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524364 | RANDALL 3 | 115 | 21.53 | 21.54 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524365 | RANDALL 6 | 230 | 14.68 | 14.69 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524377 | FARMERS 3 | 115 | 15.77 | 15.77 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524387 | CRSE_HINDTP3 | 115 | 15.78 | 15.78 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524397 | ARROWHEAD 3 | 115 | 13.94 | 13.94 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524404 | OWENSCORN 3 | 115 | 15.38 | 15.38 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524414 | AMA_SOUTH 3 | 115 | 17.19 | 17.2 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524415 | AMA_SOUTH 6 | 230 | 13.83 | 13.83 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524425 | ESTACADO_TP3 | 115 | 13.85 | 13.85 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524502 | NORTON 3 | 115 | 3.54 | 3.54 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524522 | CANYON_E_TP3 | 115 | 6.54 | 6.54 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524530 | PALO_DURO 3 | 115 | 7.13 | 7.13 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524544 | SPRING_DRW 3 | 115 | 6.69 | 6.69 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524567 | NE_HEREFORD3 | 115 | 14.03 | 14.04 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524575 | DS-#25+ 3 | 115 | 14.37 | 14.38 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524606 | HEREFORD 3 | 115 | 16.08 | 16.09 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524622 | DEAFSMITH 3 | 115 | 18.89 | 18.9 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524623 | DEAFSMITH 6 | 230 | 24.2 | 24.21 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524627 | DEFPLT_SS 6 | 230 | 17.74 | 17.75 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524669 | DS-#20 3 | 115 | 5.95 | 5.95 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524694 | DS-#22 3 | 115 | 5.17 | 5.17 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524734 | DS-#21 3 | 115 | 10.58 | 10.59 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524745 | CASTRO_CNTY2 | 69 | 9.9 | 9.91 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524746 | CASTRO_CNTY3 | 115 | 11.16 | 11.17 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524757 | BETHEL_COL13 | 115 | 9.37 | 9.38 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524764 | NORRIS_TP 3 | 115 | 12.68 | 12.69 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524768 | PLSNT_HILL 3 | 115 | 12.32 | 12.33 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524770 | PLSNT_HILL 6 | 230 | 7.84 | 7.85 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524773 | E_CLOVIS 3 | 115 | 10.19 | 10.2 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524776 | N_CLOVIS_TP3 | 115 | 9.07 | 9.07 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524797 | PERIMETER 3 | 115 | 7.53 | 7.54 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524821 | CURRY 2 | 69 | 4.91 | 4.92 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524822 | CURRY 3 | 115 | 12.72 | 12.73 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524831 | FE-HOLLAND 3 | 115 | 10.56 | 10.56 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524838 | FE-CLOVIS2+3 | 115 | 12.04 | 12.05 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524863 | FE-CHZPLT 3 | 115 | 8.97 | 8.98 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524874 | OASIS 3 | 115 | 11.36 | 11.37 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524875 | OASIS 6 | 230 | 8.85 | 8.85 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524885 | SN_JUAN_TAP6 | 230 | 5.22 | 5.22 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524889 | SN_JUAN_WND6 | 230 | 4.98 | 4.98 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524908 | ROOSEVELT 3 | 115 | 12.15 | 12.16 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524909 | ROSEVELT_N 6 | 230 | 10.66 | 10.67 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524923 | PORTALES 2 | 69 | 8.11 | 8.12 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524924 | PORTALES 3 | 115 | 8.41 | 8.42 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524935 | KILGORE 3 | 115 | 6.84 | 6.85 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 524977 | GREYHOUND 3 | 115 | 6.33 | 6.33 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525018 | MULESHVALLY3 | 115 | 6.55 | 6.55 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525019 | MULSHVLY_TP3 | 115 | 7.08 | 7.08 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525028 | BAILEYCO 3 | 115 | 7.06 | 7.07 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525050 | BC-KELLEY +3 | 115 | 8.57 | 8.57 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525056 | BC-EARTH 3 | 115 | 9.02 | 9.03 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525124 | HART_INDUST3 | 115 | 8.34 | 8.35 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525132 | LC-N_OLTON 2 | 69 | 3.33 | 3.34 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525154 | HAPPY_INT 3 | 115 | 5.86 | 5.87 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525179 | TULIA_TP 3 | 115 | 6.98 | 6.99 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525191 | KRESS_INT 2 | 69 | 4.88 | 4.88 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525192 | KRESS_INT 3 | 115 | 13.09 | 13.11 | 0.02
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525203 | SW-KRESS 2 | 69 | 4.88 | 4.88 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525212 | SWISHER 3 | 115 | 12.62 | 12.64 | 0.02
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525213 | SWISHER 6 | 230 | 11.3 | 11.31 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525224 | KRESS_RURL 2 | 69 | 2.74 | 2.74 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525225 | KRESS_RURAL3 | 115 | 6.5 | 6.51 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525226 | KRS_RURL_TP3 | 115 | 7.01 | 7.02 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525230 | NEWPOT_SS 6 | 230 | 7.48 | 7.49 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525257 | N_PLAINVEW 3 | 115 | 5.71 | 5.71 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525271 | KISER 2 | 69 | 3.78 | 3.79 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525272 | KISER 3 | 115 | 5.72 | 5.73 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525279 | WSTRIDGE_TP3 | 69 | 4.61 | 4.61 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525291 | PLAINVW_TP 2 | 69 | 7.02 | 7.03 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525298 | S_PLAINVEW 2 | 69 | 2.79 | 2.79 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525307 | E_PLAINVEW 2 | 69 | 2.68 | 2.68 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525316 | LH-PROVDNCE2 | 69 | 3.69 | 3.7 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525325 | COX 2 | 69 | 3.69 | 3.7 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525326 | COX 3 | 115 | 6.83 | 6.84 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525339 | AIKEN_RURL 2 | 69 | 3 | 3 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525393 | ROCKYFORD 3 | 115 | 9.77 | 9.77 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525404 | LC-OLTON 2 | 69 | 4.86 | 4.87 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525413 | LAMTON 2 | 69 | 5.61 | 5.61 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525414 | LAMTON 3 | 115 | 8.3 | 8.31 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525425 | CORNER 2 | 69 | 3.92 | 3.93 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525432 | SP-HALFWAY+2 | 69 | 6.34 | 6.35 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525440 | LC-S_OLTON+3 | 115 | 7.82 | 7.82 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525446 | RKYFORD_TP 3 | 115 | 10.93 | 10.94 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525453 | HALE_CNTY 2 | 69 | 7.48 | 7.49 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525454 | HALE_CNTY 3 | 115 | 11.07 | 11.09 | 0.02
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525460 | NEWHART 3 | 115 | 17.87 | 17.89 | 0.02
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525461 | NEWHART 6 | 230 | 11.86 | 11.87 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525480 | PLANT_X 3 | 115 | 20.51 | 20.53 | 0.02
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525481 | PLANT_X 6 | 230 | 24.2 | 24.21 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525524 | TOLK_EAST 6 | 230 | 31.29 | 31.31 | 0.02
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525531 | TOLK_WEST 6 | 230 | 31.29 | 31.31 | 0.02
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525543 | TOLK_TAP 6 | 230 | 31.29 | 31.31 | 0.02
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525549 | TOLK 7 | 345 | 12.95 | 12.96 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525586 | NEEDMORE 6 | 230 | 12.54 | 12.55 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525614 | W_LITLFLDTP3 | 115 | 8.55 | 8.56 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525615 | W_LITTLFLD 3 | 115 | 8.1 | 8.11 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525636 | LAMB_CNTY 3 | 115 | 10.2 | 10.2 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525637 | LAMB_CNTY 6 | 230 | 6.01 | 6.02 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525664 | LC-SPD&HART2 | 69 | 2.95 | 2.95 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525723 | CNTYLINE_TP2 | 69 | 2.34 | 2.34 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525724 | COUNTYLINE 2 | 69 | 2.05 | 2.05 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525731 | SP-ABERNTHY2 | 69 | 3.2 | 3.21 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525738 | HALECENTER 2 | 69 | 2.61 | 2.62 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525745 | LH-HALECTR 2 | 69 | 2.58 | 2.59 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525762 | IRICK 2 | 69 | 2.9 | 2.9 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525769 | BARWISE 2 | 69 | 3.64 | 3.65 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525779 | FLOYD_CNTY 2 | 69 | 5.87 | 5.88 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525780 | FLOYD_CNTY 3 | 115 | 6.86 | 6.88 | 0.02
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525790 | FLOYDADA_TP2 | 69 | 2.72 | 2.72 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525797 | S_FLOYDADA 2 | 69 | 2.7 | 2.71 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525803 | BLANCO 3 | 115 | 5.62 | 5.63 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525811 | LH-HARMONY 2 | 69 | 4.67 | 4.68 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525816 | TUCO_INT2 2 | 69 | 4.96 | 4.98 | 0.02
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525826 | TUCO_INT 2 | 69 | 8.43 | 8.45 | 0.02
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525828 | TUCO_INT 3 | 115 | 21.87 | 21.93 | 0.06
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525830 | TUCO_INT 6 | 230 | 28.93 | 29.02 | 0.09
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525832 | TUCO_INT 7 | 345 | 23.64 | 23.68 | 0.04
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525840 | ANTELOPE_1 6 | 230 | 28.63 | 28.71 | 0.08
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525850 | ELK_CT1 | 345 | 23.26 | 23.29 | 0.03
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525853 | LH-WIL&ELN+2 | 69 | 2.7 | 2.71 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525860 | SP-BECTON +2 | 69 | 2.39 | 2.4 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525867 | ALLMON 2 | 69 | 2.33 | 2.34 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525874 | LH-PETERBRG2 | 69 | 2.34 | 2.34 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525885 | SP-NEWDEAL 2 | 69 | 3.52 | 3.53 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525891 | WHITEHEAD 2 | 69 | 2.71 | 2.72 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525892 | MONROE 2 | 69 | 2.81 | 2.82 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525906 | SP-ACUFF +2 | 69 | 2.08 | 2.08 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525915 | SP-CROSBY 2 | 69 | 4.84 | 4.84 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525925 | CROSBY 2 | 69 | 5.4 | 5.41 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525926 | CROSBY 3 | 115 | 5.26 | 5.26 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 525936 | LH-CROSBY +2 | 69 | 3.69 | 3.69 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526012 | DEAN_INTG 3 | 115 | 11.5 | 11.51 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526013 | DEAN_INTG 6 | 230 | 8.72 | 8.73 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526036 | LC-OPDYKE 3 | 115 | 6.36 | 6.37 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526076 | STANTON_W 3 | 115 | 9.69 | 9.7 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526087 | SW_6786_S 2 | 69 | 5.27 | 5.28 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526109 | SP-ERSKINE 3 | 115 | 12.01 | 12.03 | 0.02
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526130 | SP-CARLISLE2 | 69 | 2.22 | 2.23 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526146 | INDIANA 3 | 115 | 10.11 | 10.13 | 0.02
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526159 | CARLISLE 2 | 69 | 2.71 | 2.71 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526160 | CARLISLE 3 | 115 | 14.08 | 14.1 | 0.02
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526161 | CARLISLE 6 | 230 | 14.69 | 14.71 | 0.02
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526162 | LP-DOUD_TP 3 | 115 | 12.39 | 12.4 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526176 | LP-DOUD 3 | 115 | 9.6 | 9.62 | 0.02
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526184 | SW_6878 2 | 69 | 2.28 | 2.28 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526192 | MURPHY 3 | 115 | 11.25 | 11.27 | 0.02
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526199 | SP-FRANKFRD3 | 115 | 10.16 | 10.18 | 0.02
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526205 | IVORY 2 | 69 | 4.13 | 4.13 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526213 | ALLEN 3 | 115 | 11.23 | 11.25 | 0.02
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526221 | BATTON_N 2 | 69 | 1.87 | 1.88 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526236 | LP-WHEELOCK3 | 115 | 9 | 9.01 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526243 | SP-QUAKER 3 | 115 | 10.2 | 10.21 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526249 | ACCO 2 | 69 | 3.36 | 3.36 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526256 | IVORY_TP 2 | 69 | 4.13 | 4.13 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526267 | LUBBCK_STH 2 | 69 | 4.57 | 4.58 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526268 | LUBBCK_STH 3 | 115 | 20.08 | 20.11 | 0.03
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526269 | LUBBCK_STH 6 | 230 | 19.2 | 19.22 | 0.02
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526284 | PLANTERS 2 | 69 | 6.09 | 6.1 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526297 | LUBBCK_EST 2 | 69 | 8.47 | 8.48 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526298 | LUBBCK_EST 3 | 115 | 16.18 | 16.2 | 0.02
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526299 | LUBBCK_EST 6 | 230 | 13.83 | 13.85 | 0.02
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526310 | CLUTTER 2 | 69 | 5.73 | 5.74 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526337 | JONES 6 | 230 | 21.12 | 21.14 | 0.02
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526424 | PACIFIC 3 | 115 | 10.95 | 10.96 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526434 | SUNDOWN 3 | 115 | 12.54 | 12.55 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526435 | SUNDOWN 6 | 230 | 11.83 | 11.84 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526445 | AMOCO_TP 3 | 115 | 11.64 | 11.65 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526460 | AMOCO_SS 6 | 230 | 10.36 | 10.37 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526469 | SP-YUMA 2 | 69 | 3.19 | 3.2 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526475 | YUMA_INT 3 | 115 | 11.66 | 11.67 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526481 | SP-WOLF_TP 3 | 115 | 11.85 | 11.86 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526483 | SP-WOLFORTH3 | 115 | 9.17 | 9.18 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526491 | LG-CLAUENE 3 | 115 | 8.62 | 8.63 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526524 | WOLFFORTH 3 | 115 | 12.22 | 12.24 | 0.02
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526525 | WOLFFORTH 6 | 230 | 14.33 | 14.34 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526535 | SP-MILWAKEE3 | 115 | 10.5 | 10.51 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526562 | SLATON 2 | 69 | 2.61 | 2.61 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526569 | SP-SLATON 2 | 69 | 1.28 | 1.28 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526602 | WOODROW 3 | 115 | 10 | 10.01 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526655 | LYNN_CNTY 2 | 69 | 3.95 | 3.95 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526656 | LYNN_CNTY 3 | 115 | 6.45 | 6.45 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526676 | GRASSLAND 3 | 115 | 7.52 | 7.53 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526677 | GRASSLAND 6 | 230 | 6.83 | 6.83 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526679 | CIRRUS_WND 6 | 230 | 5.32 | 5.32 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526693 | GRAHAM 2 | 69 | 3.56 | 3.57 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526694 | GRAHAM 3 | 115 | 3.01 | 3.01 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526735 | TERRY_CNTY 2 | 69 | 7.42 | 7.43 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526736 | TERRY_CNTY 3 | 115 | 11.08 | 11.09 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526784 | AMOCOWASSON6 | 230 | 14.44 | 14.44 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526792 | PRENTICE 3 | 115 | 6.27 | 6.27 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526928 | PLAINS_INT 3 | 115 | 10.26 | 10.26 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526934 | YOAKUM 3 | 115 | 17.41 | 17.42 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526935 | YOAKUM 6 | 230 | 18.56 | 18.57 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 526936 | YOAKUM_345 | 345 | 9.69 | 9.7 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 527009 | BRU_SUB 6 | 230 | 14.64 | 14.65 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 527010 | OXYBRU 6 | 230 | 14.52 | 14.53 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 527011 | XTO_MAHONEY6 | 230 | 14.23 | 14.23 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 527027 | INK_BASIN 3 | 115 | 13.33 | 13.34 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 527028 | INK_BASIN 6 | 230 | 11.13 | 11.13 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 527041 | ARCO_TP 3 | 115 | 13.79 | 13.79 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 527130 | DENVER_N 3 | 115 | 22.59 | 22.6 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 527146 | MUSTANG 3 | 115 | 24.19 | 24.2 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 527149 | MUSTANG 6 | 230 | 16.15 | 16.15 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 527151 | GS-MUSTANG 6 | 230 | 16.15 | 16.15 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 527194 | LG-PLSHILL 3 | 115 | 7.98 | 7.98 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 527262 | SULPHUR 3 | 115 | 6.02 | 6.02 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 527276 | SEMINOLE 6 | 230 | 7.92 | 7.92 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 527483 | CHAVES_CNTY6 | 230 | 4.72 | 4.73 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 527655 | RSVLT_CC_E 7 | 345 | 13.93 | 13.94 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 527656 | CROSSROADS 7 | 345 | 17.56 | 17.58 | 0.02
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 527802 | EDDY_CNTY 7 | 345 | 7.71 | 7.72 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 527867 | CUNNIGHM_S 6 | 230 | 14.92 | 14.93 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 527891 | HOBBS_INT 3 | 115 | 30.17 | 30.18 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 527894 | HOBBS_INT 6 | 230 | 17.05 | 17.06 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 527896 | HOBBS_INT 7 | 345 | 9.33 | 9.34 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 527965 | KIOWA 7 | 345 | 8.15 | 8.16 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 527966 | KIOWA 3 | 115 | 16.9 | 16.91 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 528027 | RDRUNNER 7 | 345 | 4.82 | 4.82 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 528185 | N_LOVING 7 | 345 | 5.88 | 5.88 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 528611 | GAINESGENTP6 | 230 | 8.58 | 8.59 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 560022 | CRAWFISH_DR | 345 | 23.9 | 23.94 | 0.04
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 560071 | G16-003-TAP | 345 | 15.51 | 15.51 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 560100 | CRAWFISH765 | 765 | 11.16 | 11.17 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 560101 | SEMINOLE765 | 765 | 11.92 | 11.93 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 560102 | CROSSRDS765 | 765 | 8 | 8.01 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 560104 | CDSEMMID | 765 | 9.39 | 9.4 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 581137 | GEN-2011-025 | 115 | 5.62 | 5.63 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 583340 | GEN-2012-020 | 230 | 11.66 | 11.7 | 0.04
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 583840 | GEN-2013-027 | 230 | 11.74 | 11.75 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 587250 | GEN-2016-039 | 115 | 12.62 | 12.64 | 0.02
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 587744 | G16-091-TAP | 345 | 15.19 | 15.19 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 588000 | GEN-2016-123 | 345 | 16.89 | 16.91 | 0.02
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 588440 | GEN-2016-172 | 115 | 15.08 | 15.09 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 588520 | GEN-2017-007 | 230 | 4.67 | 4.67 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 588700 | GEN-2017-026 | 230 | 9.98 | 9.99 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 588760 | GEN-2017-033 | 345 | 4.39 | 4.39 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 588800 | GEN-2017-039 | 230 | 10.12 | 10.13 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 588970 | GEN-2017-059 | 230 | 9.92 | 10.01 | 0.09
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 589030 | GEN-2017-065 | 345 | 5.48 | 5.48 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 589160 | GEN-2017-078 | 345 | 10.87 | 10.88 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 589180 | GEN-2017-080 | 230 | 26.89 | 26.91 | 0.02
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 589188 | G17-080-SUB2 | 230 | 15.51 | 15.52 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 589400 | GEN-2017-104 | 230 | 6.91 | 6.91 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 590001 | OKLEHV24 | 138 | 5.17 | 5.17 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 590003 | OKLEHV14 | 138 | 5.18 | 5.18 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 599891 | OKLAUN 7 | 345 | 4.36 | 4.36 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 599951 | LAMAR 6 | 345 | 57.79 | 57.79 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 599955 | PNM-DC6 | 230 | 10.66 | 10.67 | 0.01
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 599956 | PNM-DC7 | 345 | 16738.66 | 16738.66 | 0
GEN-2017-059 | South | 06 - South Texas Panhandle/New Mexico | 599961 | EPTNP 7 | 345 | 16736.82 | 16736.82 | 0
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 510907 | PITTSB-7 | 345 | 14.43 | 14.44 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 511422 | FLETCHR4 | 138 | 8.32 | 8.34 | 0.02
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 511423 | FLE TAP4 | 138 | 9.12 | 9.15 | 0.03
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 511428 | LG-YEAR4 | 138 | 12.2 | 12.25 | 0.05
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 511431 | LWS S4 | 138 | 11.35 | 11.4 | 0.05
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 511436 | COMANC-2 | 69 | 10.1 | 10.13 | 0.03
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 511437 | COMANC-4 | 138 | 18.72 | 18.79 | 0.07
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 511439 | LWSTAP 4 | 138 | 11.84 | 11.89 | 0.05
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 511451 | CYRIL--2 | 69 | 4.76 | 4.78 | 0.02
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 511453 | DUNCAN-4 | 138 | 6.68 | 6.69 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 511456 | O.K.U.-7 | 345 | 5.86 | 6 | 0.14
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 511461 | FT.SILL2 | 69 | 6.1 | 6.12 | 0.02
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 511466 | L.E.S.-2 | 69 | 17.1 | 17.17 | 0.07
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 511467 | L.E.S.-4 | 138 | 25.47 | 25.58 | 0.11
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 511468 | L.E.S.-7 | 345 | 13.68 | 13.76 | 0.08
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 511469 | LGORE-N2 | 69 | 8.23 | 8.26 | 0.03
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 511470 | LGORE-S2 | 69 | 7.14 | 7.17 | 0.03
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 511471 | LWS-NTP4 | 138 | 11.97 | 12.02 | 0.05
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 511473 | PO.HILL2 | 69 | 5.97 | 5.99 | 0.02
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 511474 | SHERID4 | 138 | 12.65 | 12.7 | 0.05
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 511477 | S.W.S.-4 | 138 | 36.36 | 36.4 | 0.04
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 511486 | ELGINJT4 | 138 | 10.31 | 10.35 | 0.04
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 511487 | ELGINJT2 | 69 | 8.73 | 8.76 | 0.03
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 511488 | 112GORE4 | 138 | 13.01 | 13.06 | 0.05
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 511494 | COMMTAP4 | 138 | 22.25 | 22.35 | 0.1
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 511503 | LAW WC2 | 69 | 4.66 | 4.68 | 0.02
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 511509 | 53CACHE4 | 138 | 12 | 12.06 | 0.06
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 511510 | LAIRGST4 | 138 | 12.59 | 12.64 | 0.05
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 511512 | RPPAPER4 | 138 | 12.26 | 12.31 | 0.05
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 511524 | L-DISTP2 | 69 | 9.33 | 9.36 | 0.03
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 511537 | ARTVLTP4 | 138 | 12.02 | 12.08 | 0.06
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 511538 | ARTVILL4 | 138 | 8.7 | 8.74 | 0.04
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 511553 | CHISHOLM7 | 345 | 5.81 | 5.82 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 511563 | ELSWORTH 4 | 138 | 10.24 | 10.27 | 0.03
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 511565 | OKLAUN HVDC7 | 345 | 5.84 | 5.98 | 0.14
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 511568 | TERRYRD7 | 345 | 10.22 | 10.27 | 0.05
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 511571 | RUSHSPR7 | 345 | 6.54 | 6.57 | 0.03
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 514785 | WOODWRD4 | 138 | 13.28 | 13.28 | 0
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 514796 | IODINE-4 | 138 | 7.48 | 7.48 | 0
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 514801 | MINCO 7 | 345 | 18.53 | 18.55 | 0.02
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 514808 | JOHNCO 4 | 138 | 15.43 | 15.46 | 0.03
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 514809 | JOHNCO 7 | 345 | 10.13 | 10.15 | 0.02
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 514901 | CIMARON7 | 345 | 35.5 | 35.51 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 515045 | SEMINOL7 | 345 | 33.66 | 33.68 | 0.02
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 515135 | SUNNYSD4 | 138 | 18.98 | 19.02 | 0.04
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 515136 | SUNNYSD7 | 345 | 11.36 | 11.39 | 0.03
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 515137 | UNIROY 4 | 138 | 12.74 | 12.76 | 0.02
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 515144 | LONEGRV4 | 138 | 13.69 | 13.72 | 0.03
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 515164 | ROCKYPT4 | 138 | 10.62 | 10.64 | 0.02
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 515375 | WWRDEHV7 | 345 | 20.17 | 20.17 | 0
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 515376 | WWRDEHV4 | 138 | 24.54 | 24.55 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 515394 | KEENAN 4 | 138 | 9.05 | 9.05 | 0
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 515398 | OUSPRT 4 | 138 | 9.63 | 9.63 | 0
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 515407 | TATONGA7 | 345 | 16.97 | 16.98 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 515425 | WWDPST 4 | 138 | 17.79 | 17.79 | 0
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 515444 | MCNOWND7 | 345 | 18.47 | 18.49 | 0.02
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 515448 | CRSRDSW7 | 345 | 11.91 | 11.91 | 0
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 515458 | BORDER 7 | 345 | 4.71 | 4.71 | 0
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 515497 | MATHWSN7 | 345 | 33.94 | 33.96 | 0.02
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 515549 | MNCWND37 | 345 | 12.66 | 12.68 | 0.02
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 515561 | CARTRCO4 | 138 | 9.91 | 9.92 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 515582 | SLNGWND7 | 345 | 7.45 | 7.45 | 0
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 515585 | MAMTHPW7 | 345 | 13.47 | 13.48 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 515599 | G07621119-20 | 345 | 13.41 | 13.42 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 515677 | BADGER 7 | 345 | 14.39 | 14.39 | 0
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 515800 | GRACMNT7 | 345 | 17.54 | 17.58 | 0.04
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 515802 | GRACMNT4 | 138 | 30.3 | 30.35 | 0.05
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 515852 | DGRASSE7 | 345 | 14.79 | 14.79 | 0
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 515853 | DGRASSE4 | 138 | 15.59 | 15.6 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 520814 | ANADARK4 | 138 | 32.75 | 32.78 | 0.03
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 521089 | WASHITA4 | 138 | 31.11 | 31.15 | 0.04
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 521157 | HUGO 7 | 345 | 11.53 | 11.54 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 522823 | LP-MCDONALD6 | 230 | 14.32 | 14.33 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 522870 | LP-HOLLY 6 | 230 | 16.99 | 17 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 524415 | AMA_SOUTH 6 | 230 | 13.83 | 13.83 | 0
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 524909 | ROSEVELT_N 6 | 230 | 10.66 | 10.67 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 525212 | SWISHER 3 | 115 | 12.63 | 12.64 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 525213 | SWISHER 6 | 230 | 11.3 | 11.31 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 525454 | HALE_CNTY 3 | 115 | 11.08 | 11.09 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 525461 | NEWHART 6 | 230 | 11.86 | 11.87 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 525481 | PLANT_X 6 | 230 | 24.2 | 24.21 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 525524 | TOLK_EAST 6 | 230 | 31.29 | 31.31 | 0.02
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 525543 | TOLK_TAP 6 | 230 | 31.29 | 31.31 | 0.02
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 525549 | TOLK 7 | 345 | 12.95 | 12.96 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 525780 | FLOYD_CNTY 3 | 115 | 6.87 | 6.88 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 525816 | TUCO_INT2 2 | 69 | 4.97 | 4.98 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 525826 | TUCO_INT 2 | 69 | 8.44 | 8.45 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 525828 | TUCO_INT 3 | 115 | 21.9 | 21.93 | 0.03
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 525830 | TUCO_INT 6 | 230 | 28.98 | 29.02 | 0.04
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 525832 | TUCO_INT 7 | 345 | 23.63 | 23.68 | 0.05
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 525840 | ANTELOPE_1 6 | 230 | 28.67 | 28.71 | 0.04
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 525850 | ELK_CT1 | 345 | 23.25 | 23.29 | 0.04
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 526013 | DEAN_INTG 6 | 230 | 8.72 | 8.73 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 526076 | STANTON_W 3 | 115 | 9.69 | 9.7 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 526160 | CARLISLE 3 | 115 | 14.09 | 14.1 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 526161 | CARLISLE 6 | 230 | 14.7 | 14.71 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 526269 | LUBBCK_STH 6 | 230 | 19.21 | 19.22 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 526298 | LUBBCK_EST 3 | 115 | 16.19 | 16.2 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 526299 | LUBBCK_EST 6 | 230 | 13.84 | 13.85 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 526337 | JONES 6 | 230 | 21.13 | 21.14 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 526460 | AMOCO_SS 6 | 230 | 10.37 | 10.37 | 0
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 526525 | WOLFFORTH 6 | 230 | 14.33 | 14.34 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 526677 | GRASSLAND 6 | 230 | 6.83 | 6.83 | 0
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 526934 | YOAKUM 3 | 115 | 17.41 | 17.42 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 526935 | YOAKUM 6 | 230 | 18.56 | 18.57 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 526936 | YOAKUM_345 | 345 | 9.69 | 9.7 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 527009 | BRU_SUB 6 | 230 | 14.64 | 14.65 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 527028 | INK_BASIN 6 | 230 | 11.13 | 11.13 | 0
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 527149 | MUSTANG 6 | 230 | 16.15 | 16.15 | 0
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 527655 | RSVLT_CC_E 7 | 345 | 13.93 | 13.94 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 527656 | CROSSROADS 7 | 345 | 17.56 | 17.58 | 0.02
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 527802 | EDDY_CNTY 7 | 345 | 7.71 | 7.72 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 527894 | HOBBS_INT 6 | 230 | 17.05 | 17.06 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 527896 | HOBBS_INT 7 | 345 | 9.33 | 9.34 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 527965 | KIOWA 7 | 345 | 8.15 | 8.16 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 529304 | OMDUNCN4 | 138 | 6.89 | 6.91 | 0.02
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 539801 | THISTLE7 | 345 | 16.68 | 16.68 | 0
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 560022 | CRAWFISH_DR | 345 | 23.89 | 23.94 | 0.05
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 560071 | G16-003-TAP | 345 | 15.51 | 15.51 | 0
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 560078 | G16-037-TAP | 345 | 7.63 | 7.64 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 560088 | G16-063-TAP | 345 | 8.06 | 8.07 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 560100 | CRAWFISH765 | 765 | 11.15 | 11.17 | 0.02
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 560101 | SEMINOLE765 | 765 | 11.92 | 11.93 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 560102 | CROSSRDS765 | 765 | 8 | 8.01 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 560104 | CDSEMMID | 765 | 9.39 | 9.4 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 563259 | GEN-2015-092 | 345 | 6.34 | 6.37 | 0.03
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 563269 | GEN-2015-093 | 345 | 10.04 | 10.06 | 0.02
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 583340 | GEN-2012-020 | 230 | 11.68 | 11.7 | 0.02
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 584780 | GEN-2015-036 | 345 | 7.2 | 7.21 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 585410 | GREAT_WESTRN | 345 | 10.09 | 10.1 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 585430 | PRSIMN_CRK1 | 345 | 11.8 | 11.8 | 0
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 587020 | GEN-2016-003 | 345 | 15.51 | 15.51 | 0
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 587230 | GEN-2016-037 | 345 | 6.95 | 6.96 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 587430 | GEN-2016-063 | 345 | 7.96 | 7.97 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 587740 | GEN-2016-091 | 345 | 13.44 | 13.48 | 0.04
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 587744 | G16-091-TAP | 345 | 15.14 | 15.19 | 0.05
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 587770 | GEN-2016-095 | 345 | 11.12 | 11.16 | 0.04
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 587790 | GEN-2016-097 | 138 | 9.83 | 9.84 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 587794 | G16-097-TAP | 138 | 12.04 | 12.06 | 0.02
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 588000 | GEN-2016-123 | 345 | 16.89 | 16.91 | 0.02
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 588560 | GEN-2017-011 | 345 | 12.48 | 12.48 | 0
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 588760 | GEN-2017-033 | 345 | 4.29 | 4.39 | 0.1
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 588970 | GEN-2017-059 | 230 | 10 | 10.01 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 589030 | GEN-2017-065 | 345 | 5.34 | 5.48 | 0.14
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 589130 | GEN-2017-075 | 345 | 8.05 | 8.06 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 589160 | GEN-2017-078 | 345 | 10.87 | 10.88 | 0.01
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 590001 | OKLEHV24 | 138 | 5.17 | 5.17 | 0
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 590003 | OKLEHV14 | 138 | 5.18 | 5.18 | 0
GEN-2017-065 | South | 06 - South Texas Panhandle/New Mexico | 599891 | OKLAUN 7 | 345 | 4.36 | 4.36 | 0
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 524472 | LOPEZ 3 | 115 | 2.51 | 2.58 | 0.07
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 524477 | CAMPBELL_ST3 | 115 | 2.5 | 2.57 | 0.07
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 524486 | CAPROCK 3 | 115 | 3.14 | 3.24 | 0.1
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 524502 | NORTON 3 | 115 | 3.38 | 3.54 | 0.16
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 524509 | FE-TUCMCARI3 | 115 | 2.68 | 2.76 | 0.08
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 524662 | PARMER_CO 3 | 115 | 4.89 | 4.9 | 0.01
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 524669 | DS-#20 3 | 115 | 5.95 | 5.95 | 0
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 524764 | NORRIS_TP 3 | 115 | 12.67 | 12.69 | 0.02
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 524768 | PLSNT_HILL 3 | 115 | 12.29 | 12.33 | 0.04
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 524770 | PLSNT_HILL 6 | 230 | 7.83 | 7.85 | 0.02
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 524773 | E_CLOVIS 3 | 115 | 10.18 | 10.2 | 0.02
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 524776 | N_CLOVIS_TP3 | 115 | 9.05 | 9.07 | 0.02
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 524777 | N_CLOVIS 3 | 115 | 8.1 | 8.12 | 0.02
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 524783 | W_CLOVIS 2 | 69 | 2.7 | 2.71 | 0.01
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 524784 | W_CLOVIS 3 | 115 | 7.61 | 7.62 | 0.01
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 524790 | CANNON_TP 3 | 115 | 7.07 | 7.08 | 0.01
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 524797 | PERIMETER 3 | 115 | 7.53 | 7.54 | 0.01
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 524801 | NORRIS 3 | 115 | 11.56 | 11.58 | 0.02
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 524808 | FE-CLVS_INT3 | 115 | 8.56 | 8.58 | 0.02
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 524821 | CURRY 2 | 69 | 4.91 | 4.92 | 0.01
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 524822 | CURRY 3 | 115 | 12.7 | 12.73 | 0.03
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 524831 | FE-HOLLAND 3 | 115 | 10.54 | 10.56 | 0.02
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 524838 | FE-CLOVIS2+3 | 115 | 12.03 | 12.05 | 0.02
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 524846 | FARWELL 2 | 69 | 2.37 | 2.37 | 0
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 524863 | FE-CHZPLT 3 | 115 | 8.97 | 8.98 | 0.01
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 524874 | OASIS 3 | 115 | 11.35 | 11.37 | 0.02
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 524875 | OASIS 6 | 230 | 8.84 | 8.85 | 0.01
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 524885 | SN_JUAN_TAP6 | 230 | 5.22 | 5.22 | 0
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 524889 | SN_JUAN_WND6 | 230 | 4.98 | 4.98 | 0
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 524908 | ROOSEVELT 3 | 115 | 12.15 | 12.16 | 0.01
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 524909 | ROSEVELT_N 6 | 230 | 10.66 | 10.67 | 0.01
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 524924 | PORTALES 3 | 115 | 8.41 | 8.42 | 0.01
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 525019 | MULSHVLY_TP3 | 115 | 7.08 | 7.08 | 0
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 525027 | BAILEYCO 2 | 69 | 6.13 | 6.13 | 0
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 525028 | BAILEYCO 3 | 115 | 7.07 | 7.07 | 0
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 525040 | BAILEY_PMP 3 | 115 | 5.25 | 5.25 | 0
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 525481 | PLANT_X 6 | 230 | 24.21 | 24.21 | 0
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 525524 | TOLK_EAST 6 | 230 | 31.3 | 31.31 | 0.01
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 525531 | TOLK_WEST 6 | 230 | 31.3 | 31.31 | 0.01
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 525543 | TOLK_TAP 6 | 230 | 31.3 | 31.31 | 0.01
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 525586 | NEEDMORE 6 | 230 | 12.55 | 12.55 | 0
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 525637 | LAMB_CNTY 6 | 230 | 6.02 | 6.02 | 0
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 525830 | TUCO_INT 6 | 230 | 29.02 | 29.02 | 0
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 527483 | CHAVES_CNTY6 | 230 | 4.72 | 4.73 | 0.01
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 560756 | CEILO-TAP-N | 69 | 0.84 | 0.85 | 0.01
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 583280 | A12-02&13-05 | 115 | 1.14 | 1.14 | 0
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 583620 | CIELO-TAP-S | 115 | 1.14 | 1.14 | 0
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 588520 | GEN-2017-007 | 230 | 4.67 | 4.67 | 0
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 588610 | GEN-2017-016 | 115 | 3.25 | 3.39 | 0.14
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 588700 | GEN-2017-026 | 230 | 9.98 | 9.99 | 0.01
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 589180 | GEN-2017-080 | 230 | 26.9 | 26.91 | 0.01
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 589250 | GEN-2017-087 | 115 | 8.51 | 8.52 | 0.01
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 599955 | PNM-DC6 | 230 | 10.66 | 10.67 | 0.01
GEN-2017-069 | South | 06 - South Texas Panhandle/New Mexico | 599956 | PNM-DC7 | 345 | 16738.66 | 16738.66 | 0
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 511456 | O.K.U.-7 | 345 | 5.99 | 6 | 0.01
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 511468 | L.E.S.-7 | 345 | 13.76 | 13.76 | 0
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 511565 | OKLAUN HVDC7 | 345 | 5.98 | 5.98 | 0
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 515045 | SEMINOL7 | 345 | 33.63 | 33.68 | 0.05
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 515375 | WWRDEHV7 | 345 | 20.17 | 20.17 | 0
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 515458 | BORDER 7 | 345 | 4.71 | 4.71 | 0
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 524623 | DEAFSMITH 6 | 230 | 24.15 | 24.21 | 0.06
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 524627 | DEFPLT_SS 6 | 230 | 17.72 | 17.75 | 0.03
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 524770 | PLSNT_HILL 6 | 230 | 7.84 | 7.85 | 0.01
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 524875 | OASIS 6 | 230 | 8.84 | 8.85 | 0.01
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 524885 | SN_JUAN_TAP6 | 230 | 5.21 | 5.22 | 0.01
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 524889 | SN_JUAN_WND6 | 230 | 4.97 | 4.98 | 0.01
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 524908 | ROOSEVELT 3 | 115 | 12.15 | 12.16 | 0.01
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 524909 | ROSEVELT_N 6 | 230 | 10.65 | 10.67 | 0.02
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 525213 | SWISHER 6 | 230 | 11.3 | 11.31 | 0.01
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 525461 | NEWHART 6 | 230 | 11.86 | 11.87 | 0.01
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 525480 | PLANT_X 3 | 115 | 20.5 | 20.53 | 0.03
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 525481 | PLANT_X 6 | 230 | 24.15 | 24.21 | 0.06
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 525524 | TOLK_EAST 6 | 230 | 31.19 | 31.31 | 0.12
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 525531 | TOLK_WEST 6 | 230 | 31.19 | 31.31 | 0.12
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 525543 | TOLK_TAP 6 | 230 | 31.19 | 31.31 | 0.12
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 525549 | TOLK 7 | 345 | 12.87 | 12.96 | 0.09
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 525586 | NEEDMORE 6 | 230 | 12.53 | 12.55 | 0.02
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 525636 | LAMB_CNTY 3 | 115 | 10.19 | 10.2 | 0.01
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 525637 | LAMB_CNTY 6 | 230 | 6.01 | 6.02 | 0.01
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 525828 | TUCO_INT 3 | 115 | 21.89 | 21.93 | 0.04
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 525830 | TUCO_INT 6 | 230 | 28.9 | 29.02 | 0.12
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 525832 | TUCO_INT 7 | 345 | 23.48 | 23.68 | 0.2
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 525840 | ANTELOPE_1 6 | 230 | 28.6 | 28.71 | 0.11
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 525850 | ELK_CT1 | 345 | 23.1 | 23.29 | 0.19
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 526013 | DEAN_INTG 6 | 230 | 8.72 | 8.73 | 0.01
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 526161 | CARLISLE 6 | 230 | 14.69 | 14.71 | 0.02
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 526337 | JONES 6 | 230 | 21.12 | 21.14 | 0.02
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 526435 | SUNDOWN 6 | 230 | 11.82 | 11.84 | 0.02
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 526936 | YOAKUM_345 | 345 | 9.68 | 9.7 | 0.02
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 527455 | RSWL_SLRCOL3 | 115 | 7.26 | 7.27 | 0.01
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 527470 | CHVS_SLRCOL3 | 115 | 7.1 | 7.11 | 0.01
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 527482 | CHAVES_CNTY3 | 115 | 7.33 | 7.34 | 0.01
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 527483 | CHAVES_CNTY6 | 230 | 4.72 | 4.73 | 0.01
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 527501 | URTON 3 | 115 | 6.17 | 6.18 | 0.01
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 527509 | PRICE_TAP 3 | 115 | 5.78 | 5.79 | 0.01
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 527546 | SAMSON 3 | 115 | 5.83 | 5.84 | 0.01
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 527564 | ROSWLL_INT 3 | 115 | 6.09 | 6.1 | 0.01
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 527597 | TWEEDY 3 | 115 | 5.65 | 5.66 | 0.01
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 527654 | RSVLT_CC_W 7 | 345 | 11.09 | 11.35 | 0.26
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 527655 | RSVLT_CC_E 7 | 345 | 13.56 | 13.94 | 0.38
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 527656 | CROSSROADS 7 | 345 | 16.96 | 17.58 | 0.62
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 527707 | ARTESIA 3 | 115 | 7.4 | 7.41 | 0.01
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 527710 | EAGLE_CREEK2 | 69 | 2.53 | 2.53 | 0
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 527711 | EAGLE_CREEK3 | 115 | 8.04 | 8.06 | 0.02
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 527715 | NAVAJO_2TP 3 | 115 | 7.67 | 7.68 | 0.01
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 527736 | NAVAJO_5TP 3 | 115 | 7.62 | 7.63 | 0.01
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 527777 | ARTSA_CC_TP3 | 115 | 7.25 | 7.27 | 0.02
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 527786 | ATOKA 3 | 115 | 7.72 | 7.73 | 0.01
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 527793 | EDDY_STH 3 | 115 | 12.48 | 12.51 | 0.03
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 527798 | EDDY_NTH 3 | 115 | 12.48 | 12.51 | 0.03
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 527799 | EDDY_NORTH 6 | 230 | 9.68 | 9.71 | 0.03
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 527802 | EDDY_CNTY 7 | 345 | 7.68 | 7.72 | 0.04
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 527808 | CV-8_MILE 2 | 67 | 1.99 | 1.99 | 0
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 527809 | CV-8_MILE 3 | 115 | 5.85 | 5.86 | 0.01
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 527821 | CV-DAYTON +3 | 115 | 7.62 | 7.63 | 0.01
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 527822 | CV-TURKYTRK3 | 115 | 3.74 | 3.75 | 0.01
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 527864 | CUNNINHAM 3 | 115 | 26.72 | 26.74 | 0.02
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 527865 | CUNNIGHM_N 6 | 230 | 14.9 | 14.93 | 0.03
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 527867 | CUNNIGHM_S 6 | 230 | 14.9 | 14.93 | 0.03
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 527894 | HOBBS_INT 6 | 230 | 17.03 | 17.06 | 0.03
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 527962 | POTASH_JCT 3 | 115 | 16.9 | 16.94 | 0.04
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 527963 | POTASH_JCT 6 | 230 | 7.47 | 7.49 | 0.02
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 528070 | CV-AZMESA 3 | 115 | 7.91 | 7.92 | 0.01
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 528093 | 7-RIVERS 2 | 69 | 2.6 | 2.6 | 0
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 528094 | 7-RIVERS 3 | 115 | 8.87 | 8.89 | 0.02
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 528095 | 7-RIVERS 6 | 230 | 6.6 | 6.62 | 0.02
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 528109 | CV-LAKEWOOD3 | 115 | 6.93 | 6.94 | 0.01
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 528132 | OCOTILLO 3 | 115 | 6.53 | 6.54 | 0.01
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 528137 | N_CANAL 3 | 115 | 9.1 | 9.12 | 0.02
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 528160 | CARLSBAD 3 | 115 | 11.64 | 11.66 | 0.02
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 528178 | PECOS 3 | 115 | 12.28 | 12.3 | 0.02
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 528179 | PECOS 6 | 230 | 6.79 | 6.81 | 0.02
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 528226 | HOPI_SUB 3 | 115 | 7.26 | 7.27 | 0.01
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 560022 | CRAWFISH_DR | 345 | 23.73 | 23.94 | 0.21
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 560100 | CRAWFISH765 | 765 | 11.04 | 11.17 | 0.13
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 560101 | SEMINOLE765 | 765 | 11.9 | 11.93 | 0.03
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 560102 | CROSSRDS765 | 765 | 7.79 | 8.01 | 0.22
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 560104 | CDSEMMID | 765 | 9.35 | 9.4 | 0.05
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 583340 | GEN-2012-020 | 230 | 11.67 | 11.7 | 0.03
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 583840 | GEN-2013-027 | 230 | 11.73 | 11.75 | 0.02
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 583960 | G14034G14035 | 115 | 6.94 | 6.95 | 0.01
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 588000 | GEN-2016-123 | 345 | 16.34 | 16.91 | 0.57
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 588700 | GEN-2017-026 | 230 | 9.97 | 9.99 | 0.02
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 588760 | GEN-2017-033 | 345 | 4.39 | 4.39 | 0
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 588800 | GEN-2017-039 | 230 | 10.12 | 10.13 | 0.01
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 588970 | GEN-2017-059 | 230 | 9.99 | 10.01 | 0.02
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 589030 | GEN-2017-065 | 345 | 5.48 | 5.48 | 0
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 589160 | GEN-2017-078 | 345 | 10.25 | 10.88 | 0.63
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 589180 | GEN-2017-080 | 230 | 26.81 | 26.91 | 0.1
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 589188 | G17-080-SUB2 | 230 | 15.48 | 15.52 | 0.04
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 599891 | OKLAUN 7 | 345 | 4.36 | 4.36 | 0
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 599955 | PNM-DC6 | 230 | 10.65 | 10.67 | 0.02
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 599956 | PNM-DC7 | 345 | 16738.66 | 16738.66 | 0
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 599960 | EPTNP-D6 | 230 | 9.68 | 9.71 | 0.03
GEN-2017-078 | South | 06 - South Texas Panhandle/New Mexico | 599961 | EPTNP 7 | 345 | 16736.82 | 16736.82 | 0
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 522823 | LP-MCDONALD6 | 230 | 14.28 | 14.33 | 0.05
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 522861 | LP-SOUTHEST6 | 230 | 17.32 | 17.36 | 0.04
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 522870 | LP-HOLLY 6 | 230 | 16.96 | 17 | 0.04
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 523309 | MOORE_CNTY 6 | 230 | 7.07 | 7.08 | 0.01
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 523869 | CHAN+TASCOS6 | 230 | 4.48 | 4.49 | 0.01
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 523959 | POTTER_CO 6 | 230 | 21.18 | 21.24 | 0.06
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 523961 | POTTER_CO 7 | 345 | 7.76 | 7.78 | 0.02
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 523979 | HARRNG_EST 6 | 230 | 25.91 | 25.97 | 0.06
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524010 | ROLLHILLS 6 | 230 | 19.64 | 19.69 | 0.05
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524044 | NICHOLS 6 | 230 | 25.07 | 25.12 | 0.05
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524243 | OUTPOST 3 | 115 | 10.15 | 10.19 | 0.04
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524266 | BUSHLAND 3 | 115 | 10.06 | 10.11 | 0.05
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524267 | BUSHLAND 6 | 230 | 11.64 | 11.72 | 0.08
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524276 | WILDOR_WND 6 | 230 | 5.55 | 5.59 | 0.04
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524290 | WILDOR2_JUS6 | 230 | 7.59 | 7.64 | 0.05
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524365 | RANDALL 6 | 230 | 14.65 | 14.69 | 0.04
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524414 | AMA_SOUTH 3 | 115 | 17.15 | 17.2 | 0.05
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524415 | AMA_SOUTH 6 | 230 | 13.79 | 13.83 | 0.04
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524486 | CAPROCK 3 | 115 | 3.23 | 3.24 | 0.01
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524502 | NORTON 3 | 115 | 3.52 | 3.54 | 0.02
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524509 | FE-TUCMCARI3 | 115 | 2.75 | 2.76 | 0.01
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524556 | LAPLATA 3 | 115 | 7.82 | 7.93 | 0.11
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524567 | NE_HEREFORD3 | 115 | 13.84 | 14.04 | 0.2
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524573 | NE_HEREFORD2 | 69 | 8.13 | 8.25 | 0.12
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524575 | DS-#25+ 3 | 115 | 14.19 | 14.38 | 0.19
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524597 | PANDAHFD 3 | 115 | 12.02 | 12.18 | 0.16
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524604 | HEREFRD_SB 2 | 69 | 5.11 | 5.19 | 0.08
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524605 | HEREFRD_NB 2 | 69 | 5.11 | 5.19 | 0.08
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524606 | HEREFORD 3 | 115 | 15.86 | 16.09 | 0.23
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524622 | DEAFSMITH 3 | 115 | 18.64 | 18.9 | 0.26
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524623 | DEAFSMITH 6 | 230 | 23.85 | 24.21 | 0.36
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524627 | DEFPLT_SS 6 | 230 | 17.48 | 17.75 | 0.27
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524629 | DS-#6 3 | 115 | 7.65 | 7.76 | 0.11
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524662 | PARMER_CO 3 | 115 | 4.83 | 4.9 | 0.07
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524669 | DS-#20 3 | 115 | 5.87 | 5.95 | 0.08
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524694 | DS-#22 3 | 115 | 5.12 | 5.17 | 0.05
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524734 | DS-#21 3 | 115 | 10.48 | 10.59 | 0.11
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524745 | CASTRO_CNTY2 | 69 | 9.81 | 9.91 | 0.1
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524746 | CASTRO_CNTY3 | 115 | 11.05 | 11.17 | 0.12
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524757 | BETHEL_COL13 | 115 | 9.29 | 9.38 | 0.09
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524764 | NORRIS_TP 3 | 115 | 12.51 | 12.69 | 0.18
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524768 | PLSNT_HILL 3 | 115 | 12.17 | 12.33 | 0.16
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524770 | PLSNT_HILL 6 | 230 | 7.74 | 7.85 | 0.11
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524773 | E_CLOVIS 3 | 115 | 10.06 | 10.2 | 0.14
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524776 | N_CLOVIS_TP3 | 115 | 8.96 | 9.07 | 0.11
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524777 | N_CLOVIS 3 | 115 | 8.02 | 8.12 | 0.1
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524783 | W_CLOVIS 2 | 69 | 2.67 | 2.71 | 0.04
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524790 | CANNON_TP 3 | 115 | 6.98 | 7.08 | 0.1
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524797 | PERIMETER 3 | 115 | 7.43 | 7.54 | 0.11
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524801 | NORRIS 3 | 115 | 11.41 | 11.58 | 0.17
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524808 | FE-CLVS_INT3 | 115 | 8.47 | 8.58 | 0.11
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524821 | CURRY 2 | 69 | 4.85 | 4.92 | 0.07
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524822 | CURRY 3 | 115 | 12.55 | 12.73 | 0.18
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524831 | FE-HOLLAND 3 | 115 | 10.42 | 10.56 | 0.14
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524838 | FE-CLOVIS2+3 | 115 | 11.88 | 12.05 | 0.17
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524846 | FARWELL 2 | 69 | 2.34 | 2.37 | 0.03
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524863 | FE-CHZPLT 3 | 115 | 8.85 | 8.98 | 0.13
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524874 | OASIS 3 | 115 | 11.21 | 11.37 | 0.16
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524875 | OASIS 6 | 230 | 8.73 | 8.85 | 0.12
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524885 | SN_JUAN_TAP6 | 230 | 5.17 | 5.22 | 0.05
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524889 | SN_JUAN_WND6 | 230 | 4.94 | 4.98 | 0.04
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524908 | ROOSEVELT 3 | 115 | 11.98 | 12.16 | 0.18
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524909 | ROSEVELT_N 6 | 230 | 10.51 | 10.67 | 0.16
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524923 | PORTALES 2 | 69 | 8 | 8.12 | 0.12
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524924 | PORTALES 3 | 115 | 8.3 | 8.42 | 0.12
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524929 | RO-PORT_MTR2 | 69 | 8 | 8.12 | 0.12
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524934 | ZODIAC 2 | 69 | 5.92 | 6 | 0.08
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524935 | KILGORE 3 | 115 | 6.75 | 6.85 | 0.1
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524941 | PORTALES#1 2 | 69 | 6.13 | 6.22 | 0.09
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524963 | S_PORTALES 3 | 115 | 6.33 | 6.42 | 0.09
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 524977 | GREYHOUND 3 | 115 | 6.24 | 6.33 | 0.09
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525018 | MULESHVALLY3 | 115 | 6.46 | 6.55 | 0.09
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525019 | MULSHVLY_TP3 | 115 | 6.98 | 7.08 | 0.1
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525027 | BAILEYCO 2 | 69 | 6.04 | 6.13 | 0.09
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525028 | BAILEYCO 3 | 115 | 6.97 | 7.07 | 0.1
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525040 | BAILEY_PMP 3 | 115 | 5.17 | 5.25 | 0.08
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525050 | BC-KELLEY +3 | 115 | 8.47 | 8.57 | 0.1
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525056 | BC-EARTH 3 | 115 | 8.92 | 9.03 | 0.11
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525124 | HART_INDUST3 | 115 | 8.28 | 8.35 | 0.07
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525179 | TULIA_TP 3 | 115 | 6.95 | 6.99 | 0.04
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525191 | KRESS_INT 2 | 69 | 4.85 | 4.88 | 0.03
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525192 | KRESS_INT 3 | 115 | 13.02 | 13.11 | 0.09
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525212 | SWISHER 3 | 115 | 12.55 | 12.64 | 0.09
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525213 | SWISHER 6 | 230 | 11.24 | 11.31 | 0.07
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525226 | KRS_RURL_TP3 | 115 | 6.98 | 7.02 | 0.04
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525230 | NEWPOT_SS 6 | 230 | 7.44 | 7.49 | 0.05
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525272 | KISER 3 | 115 | 5.69 | 5.73 | 0.04
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525291 | PLAINVW_TP 2 | 69 | 6.97 | 7.03 | 0.06
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525298 | S_PLAINVEW 2 | 69 | 2.77 | 2.79 | 0.02
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525325 | COX 2 | 69 | 3.68 | 3.7 | 0.02
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525326 | COX 3 | 115 | 6.79 | 6.84 | 0.05
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525393 | ROCKYFORD 3 | 115 | 9.65 | 9.77 | 0.12
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525413 | LAMTON 2 | 69 | 5.56 | 5.61 | 0.05
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525414 | LAMTON 3 | 115 | 8.22 | 8.31 | 0.09
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525432 | SP-HALFWAY+2 | 69 | 6.3 | 6.35 | 0.05
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525440 | LC-S_OLTON+3 | 115 | 7.74 | 7.82 | 0.08
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525446 | RKYFORD_TP 3 | 115 | 10.79 | 10.94 | 0.15
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525453 | HALE_CNTY 2 | 69 | 7.43 | 7.49 | 0.06
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525454 | HALE_CNTY 3 | 115 | 11 | 11.09 | 0.09
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525460 | NEWHART 3 | 115 | 17.75 | 17.89 | 0.14
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525461 | NEWHART 6 | 230 | 11.78 | 11.87 | 0.09
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525480 | PLANT_X 3 | 115 | 20.24 | 20.53 | 0.29
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525481 | PLANT_X 6 | 230 | 23.85 | 24.21 | 0.36
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525524 | TOLK_EAST 6 | 230 | 30.7 | 31.31 | 0.61
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525531 | TOLK_WEST 6 | 230 | 30.7 | 31.31 | 0.61
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525543 | TOLK_TAP 6 | 230 | 30.7 | 31.31 | 0.61
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525549 | TOLK 7 | 345 | 12.76 | 12.96 | 0.2
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525586 | NEEDMORE 6 | 230 | 12.35 | 12.55 | 0.2
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525594 | SUDANRURAL 3 | 115 | 5 | 5.07 | 0.07
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525599 | LC-SANDHLL+2 | 69 | 2.98 | 3.03 | 0.05
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525607 | NEW_AMHERST2 | 69 | 3.43 | 3.49 | 0.06
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525608 | NEW_AMHERST3 | 115 | 5.53 | 5.62 | 0.09
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525614 | W_LITLFLDTP3 | 115 | 8.43 | 8.56 | 0.13
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525615 | W_LITTLFLD 3 | 115 | 7.99 | 8.11 | 0.12
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525620 | LTFLD_S&CTY2 | 69 | 4.62 | 4.69 | 0.07
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525635 | LAMB_CNTY 2 | 69 | 6.61 | 6.72 | 0.11
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525636 | LAMB_CNTY 3 | 115 | 10.04 | 10.2 | 0.16
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525637 | LAMB_CNTY 6 | 230 | 5.91 | 6.02 | 0.11
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525650 | LC-LTTLFLD+2 | 69 | 5.49 | 5.58 | 0.09
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525657 | W_ANTON_TP 2 | 69 | 4.55 | 4.62 | 0.07
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525687 | LC-LUMSCHAP2 | 69 | 5.12 | 5.2 | 0.08
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525694 | HOBGOOD 2 | 69 | 3.79 | 3.85 | 0.06
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525780 | FLOYD_CNTY 3 | 115 | 6.84 | 6.88 | 0.04
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525816 | TUCO_INT2 2 | 69 | 4.95 | 4.98 | 0.03
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525826 | TUCO_INT 2 | 69 | 8.42 | 8.45 | 0.03
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525828 | TUCO_INT 3 | 115 | 21.84 | 21.93 | 0.09
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525830 | TUCO_INT 6 | 230 | 28.89 | 29.02 | 0.13
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525832 | TUCO_INT 7 | 345 | 23.6 | 23.68 | 0.08
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525840 | ANTELOPE_1 6 | 230 | 28.59 | 28.71 | 0.12
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 525850 | ELK_CT1 | 345 | 23.21 | 23.29 | 0.08
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 526009 | LC-LEVLND#22 | 69 | 4.63 | 4.68 | 0.05
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 526012 | DEAN_INTG 3 | 115 | 11.43 | 11.51 | 0.08
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 526013 | DEAN_INTG 6 | 230 | 8.66 | 8.73 | 0.07
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 526019 | HOCKLEY 2 | 69 | 5.57 | 5.63 | 0.06
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 526020 | HOCKLEY 3 | 115 | 5.99 | 6.05 | 0.06
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 526036 | LC-OPDYKE 3 | 115 | 6.3 | 6.37 | 0.07
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 526042 | COBLE 2 | 69 | 2.44 | 2.47 | 0.03
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 526048 | LVLNDCTY_TP2 | 69 | 4.63 | 4.68 | 0.05
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 526076 | STANTON_W 3 | 115 | 9.67 | 9.7 | 0.03
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 526160 | CARLISLE 3 | 115 | 14.05 | 14.1 | 0.05
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 526161 | CARLISLE 6 | 230 | 14.66 | 14.71 | 0.05
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 526268 | LUBBCK_STH 3 | 115 | 20.06 | 20.11 | 0.05
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 526269 | LUBBCK_STH 6 | 230 | 19.17 | 19.22 | 0.05
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 526298 | LUBBCK_EST 3 | 115 | 16.15 | 16.2 | 0.05
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 526299 | LUBBCK_EST 6 | 230 | 13.81 | 13.85 | 0.04
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 526337 | JONES 6 | 230 | 21.09 | 21.14 | 0.05
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 526350 | LEHMAN_TP 3 | 115 | 9.33 | 9.4 | 0.07
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 526352 | LEHMAN 3 | 115 | 7.43 | 7.48 | 0.05
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 526360 | COCHRAN 2 | 69 | 6.83 | 6.88 | 0.05
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 526361 | COCHRAN 3 | 115 | 8.92 | 8.98 | 0.06
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 526424 | PACIFIC 3 | 115 | 10.88 | 10.96 | 0.08
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 526434 | SUNDOWN 3 | 115 | 12.46 | 12.55 | 0.09
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 526435 | SUNDOWN 6 | 230 | 11.76 | 11.84 | 0.08
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 526445 | AMOCO_TP 3 | 115 | 11.56 | 11.65 | 0.09
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 526452 | AMOCO_CRYO 3 | 115 | 7.05 | 7.1 | 0.05
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 526460 | AMOCO_SS 6 | 230 | 10.31 | 10.37 | 0.06
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 526475 | YUMA_INT 3 | 115 | 11.63 | 11.67 | 0.04
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 526484 | LG-LEVELAND3 | 115 | 10.25 | 10.32 | 0.07
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 526524 | WOLFFORTH 3 | 115 | 12.19 | 12.24 | 0.05
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 526525 | WOLFFORTH 6 | 230 | 14.29 | 14.34 | 0.05
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 526677 | GRASSLAND 6 | 230 | 6.82 | 6.83 | 0.01
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 526736 | TERRY_CNTY 3 | 115 | 11.04 | 11.09 | 0.05
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 526784 | AMOCOWASSON6 | 230 | 14.4 | 14.44 | 0.04
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 526792 | PRENTICE 3 | 115 | 6.25 | 6.27 | 0.02
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 526928 | PLAINS_INT 3 | 115 | 10.22 | 10.26 | 0.04
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 526934 | YOAKUM 3 | 115 | 17.35 | 17.42 | 0.07
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 526935 | YOAKUM 6 | 230 | 18.5 | 18.57 | 0.07
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 526936 | YOAKUM_345 | 345 | 9.66 | 9.7 | 0.04
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 526944 | LG-PLAINS 3 | 115 | 8.45 | 8.49 | 0.04
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 527009 | BRU_SUB 6 | 230 | 14.6 | 14.65 | 0.05
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 527010 | OXYBRU 6 | 230 | 14.48 | 14.53 | 0.05
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 527011 | XTO_MAHONEY6 | 230 | 14.19 | 14.23 | 0.04
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 527027 | INK_BASIN 3 | 115 | 13.3 | 13.34 | 0.04
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 527028 | INK_BASIN 6 | 230 | 11.1 | 11.13 | 0.03
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 527041 | ARCO_TP 3 | 115 | 13.76 | 13.79 | 0.03
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 527146 | MUSTANG 3 | 115 | 24.15 | 24.2 | 0.05
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 527149 | MUSTANG 6 | 230 | 16.11 | 16.15 | 0.04
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 527151 | GS-MUSTANG 6 | 230 | 16.11 | 16.15 | 0.04
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 527194 | LG-PLSHILL 3 | 115 | 7.96 | 7.98 | 0.02
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 527276 | SEMINOLE 6 | 230 | 7.9 | 7.92 | 0.02
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 527482 | CHAVES_CNTY3 | 115 | 7.29 | 7.34 | 0.05
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 527483 | CHAVES_CNTY6 | 230 | 4.69 | 4.73 | 0.04
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 527654 | RSVLT_CC_W 7 | 345 | 11.29 | 11.35 | 0.06
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 527655 | RSVLT_CC_E 7 | 345 | 13.87 | 13.94 | 0.07
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 527656 | CROSSROADS 7 | 345 | 17.48 | 17.58 | 0.1
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 527799 | EDDY_NORTH 6 | 230 | 9.67 | 9.71 | 0.04
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 527802 | EDDY_CNTY 7 | 345 | 7.69 | 7.72 | 0.03
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 527894 | HOBBS_INT 6 | 230 | 17.02 | 17.06 | 0.04
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 527896 | HOBBS_INT 7 | 345 | 9.31 | 9.34 | 0.03
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 560022 | CRAWFISH_DR | 345 | 23.85 | 23.94 | 0.09
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 560100 | CRAWFISH765 | 765 | 11.13 | 11.17 | 0.04
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 560102 | CROSSRDS765 | 765 | 7.97 | 8.01 | 0.04
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 583340 | GEN-2012-020 | 230 | 11.65 | 11.7 | 0.05
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 583840 | GEN-2013-027 | 230 | 11.56 | 11.75 | 0.19
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 584560 | GEN-2015-014 | 115 | 6.43 | 6.48 | 0.05
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 587250 | GEN-2016-039 | 115 | 12.55 | 12.64 | 0.09
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 588000 | GEN-2016-123 | 345 | 16.81 | 16.91 | 0.1
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 588440 | GEN-2016-172 | 115 | 14.98 | 15.09 | 0.11
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 588520 | GEN-2017-007 | 230 | 4.61 | 4.67 | 0.06
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 588610 | GEN-2017-016 | 115 | 3.38 | 3.39 | 0.01
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 588700 | GEN-2017-026 | 230 | 9.8 | 9.99 | 0.19
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 588800 | GEN-2017-039 | 230 | 9.97 | 10.13 | 0.16
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 588960 | GEN-2017-058 | 115 | 8.47 | 8.6 | 0.13
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 588970 | GEN-2017-059 | 230 | 9.97 | 10.01 | 0.04
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 589160 | GEN-2017-078 | 345 | 10.82 | 10.88 | 0.06
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 589180 | GEN-2017-080 | 230 | 26.3 | 26.91 | 0.61
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 589188 | G17-080-SUB2 | 230 | 15 | 15.52 | 0.52
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 599950 | LAMAR7 | 345 | 2.55 | 2.55 | 0
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 599951 | LAMAR 6 | 345 | 57.79 | 57.79 | 0
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 599955 | PNM-DC6 | 230 | 10.51 | 10.67 | 0.16
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 599956 | PNM-DC7 | 345 | 16738.66 | 16738.66 | 0
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 599960 | EPTNP-D6 | 230 | 9.67 | 9.71 | 0.04
GEN-2017-080 | South | 06 - South Texas Panhandle/New Mexico | 599961 | EPTNP 7 | 345 | 16736.82 | 16736.82 | 0
GEN-2017-087 | South | 06 - South Texas Panhandle/New Mexico | 524472 | LOPEZ 3 | 115 | 2.57 | 2.58 | 0.01
GEN-2017-087 | South | 06 - South Texas Panhandle/New Mexico | 524486 | CAPROCK 3 | 115 | 3.22 | 3.24 | 0.02
GEN-2017-087 | South | 06 - South Texas Panhandle/New Mexico | 524502 | NORTON 3 | 115 | 3.52 | 3.54 | 0.02
GEN-2017-087 | South | 06 - South Texas Panhandle/New Mexico | 524509 | FE-TUCMCARI3 | 115 | 2.75 | 2.76 | 0.01
GEN-2017-087 | South | 06 - South Texas Panhandle/New Mexico | 524669 | DS-#20 3 | 115 | 5.84 | 5.95 | 0.11
GEN-2017-087 | South | 06 - South Texas Panhandle/New Mexico | 524764 | NORRIS_TP 3 | 115 | 12.16 | 12.69 | 0.53
GEN-2017-087 | South | 06 - South Texas Panhandle/New Mexico | 524768 | PLSNT_HILL 3 | 115 | 11.59 | 12.33 | 0.74
GEN-2017-087 | South | 06 - South Texas Panhandle/New Mexico | 524770 | PLSNT_HILL 6 | 230 | 7.59 | 7.85 | 0.26
GEN-2017-087 | South | 06 - South Texas Panhandle/New Mexico | 524773 | E_CLOVIS 3 | 115 | 9.75 | 10.2 | 0.45
GEN-2017-087 | South | 06 - South Texas Panhandle/New Mexico | 524776 | N_CLOVIS_TP3 | 115 | 8.21 | 9.07 | 0.86
GEN-2017-087 | South | 06 - South Texas Panhandle/New Mexico | 524777 | N_CLOVIS 3 | 115 | 7.41 | 8.12 | 0.71
GEN-2017-087 | South | 06 - South Texas Panhandle/New Mexico | 524784 | W_CLOVIS 3 | 115 | 6.94 | 7.62 | 0.68
GEN-2017-087 | South | 06 - South Texas Panhandle/New Mexico | 524790 | CANNON_TP 3 | 115 | 6.58 | 7.08 | 0.5
GEN-2017-087 | South | 06 - South Texas Panhandle/New Mexico | 524794 | CANNONAFB 3 | 115 | 6.17 | 6.61 | 0.44
GEN-2017-087 | South | 06 - South Texas Panhandle/New Mexico | 524797 | PERIMETER 3 | 115 | 7.16 | 7.54 | 0.38
GEN-2017-087 | South | 06 - South Texas Panhandle/New Mexico | 524808 | FE-CLVS_INT3 | 115 | 7.63 | 8.58 | 0.95
GEN-2017-087 | South | 06 - South Texas Panhandle/New Mexico | 524821 | CURRY 2 | 69 | 4.84 | 4.92 | 0.08
GEN-2017-087 | South | 06 - South Texas Panhandle/New Mexico | 524822 | CURRY 3 | 115 | 12.2 | 12.73 | 0.53
GEN-2017-087 | South | 06 - South Texas Panhandle/New Mexico | 524831 | FE-HOLLAND 3 | 115 | 10.07 | 10.56 | 0.49
GEN-2017-087 | South | 06 - South Texas Panhandle/New Mexico | 524838 | FE-CLOVIS2+3 | 115 | 11.55 | 12.05 | 0.5
GEN-2017-087 | South | 06 - South Texas Panhandle/New Mexico | 524863 | FE-CHZPLT 3 | 115 | 8.69 | 8.98 | 0.29
GEN-2017-087 | South | 06 - South Texas Panhandle/New Mexico | 524874 | OASIS 3 | 115 | 10.93 | 11.37 | 0.44
GEN-2017-087 | South | 06 - South Texas Panhandle/New Mexico | 524875 | OASIS 6 | 230 | 8.6 | 8.85 | 0.25
GEN-2017-087 | South | 06 - South Texas Panhandle/New Mexico | 524885 | SN_JUAN_TAP6 | 230 | 5.18 | 5.22 | 0.04
GEN-2017-087 | South | 06 - South Texas Panhandle/New Mexico | 524908 | ROOSEVELT 3 | 115 | 11.79 | 12.16 | 0.37
GEN-2017-087 | South | 06 - South Texas Panhandle/New Mexico | 524909 | ROSEVELT_N 6 | 230 | 10.37 | 10.67 | 0.3
GEN-2017-087 | South | 06 - South Texas Panhandle/New Mexico | 524924 | PORTALES 3 | 115 | 8.19 | 8.42 | 0.23
GEN-2017-087 | South | 06 - South Texas Panhandle/New Mexico | 525028 | BAILEYCO 3 | 115 | 7.02 | 7.07 | 0.05
GEN-2017-087 | South | 06 - South Texas Panhandle/New Mexico | 525524 | TOLK_EAST 6 | 230 | 31.1 | 31.31 | 0.21
GEN-2017-087 | South | 06 - South Texas Panhandle/New Mexico | 525531 | TOLK_WEST 6 | 230 | 31.1 | 31.31 | 0.21
GEN-2017-087 | South | 06 - South Texas Panhandle/New Mexico | 560756 | CEILO-TAP-N | 69 | 0.84 | 0.85 | 0.01
GEN-2017-087 | South | 06 - South Texas Panhandle/New Mexico | 583280 | A12-02&13-05 | 115 | 1.12 | 1.14 | 0.02
GEN-2017-087 | South | 06 - South Texas Panhandle/New Mexico | 583620 | CIELO-TAP-S | 115 | 1.12 | 1.14 | 0.02
GEN-2017-087 | South | 06 - South Texas Panhandle/New Mexico | 588520 | GEN-2017-007 | 230 | 4.58 | 4.67 | 0.09
GEN-2017-087 | South | 06 - South Texas Panhandle/New Mexico | 588610 | GEN-2017-016 | 115 | 3.37 | 3.39 | 0.02
GEN-2017-087 | South | 06 - South Texas Panhandle/New Mexico | 589250 | GEN-2017-087 | 115 | 7.57 | 8.52 | 0.95
GEN-2017-087 | South | 06 - South Texas Panhandle/New Mexico | 599955 | PNM-DC6 | 230 | 10.37 | 10.67 | 0.3
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 511456 | O.K.U.-7 | 345 | 6 | 6 | 0
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 515458 | BORDER 7 | 345 | 4.71 | 4.71 | 0
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 524885 | SN_JUAN_TAP6 | 230 | 5.2 | 5.22 | 0.02
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 525213 | SWISHER 6 | 230 | 11.31 | 11.31 | 0
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 525481 | PLANT_X 6 | 230 | 24.19 | 24.21 | 0.02
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 525524 | TOLK_EAST 6 | 230 | 31.28 | 31.31 | 0.03
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 525531 | TOLK_WEST 6 | 230 | 31.28 | 31.31 | 0.03
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 525586 | NEEDMORE 6 | 230 | 12.53 | 12.55 | 0.02
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 525828 | TUCO_INT 3 | 115 | 21.91 | 21.93 | 0.02
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 525830 | TUCO_INT 6 | 230 | 28.99 | 29.02 | 0.03
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 525832 | TUCO_INT 7 | 345 | 23.65 | 23.68 | 0.03
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 525840 | ANTELOPE_1 6 | 230 | 28.68 | 28.71 | 0.03
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 525850 | ELK_CT1 | 345 | 23.26 | 23.29 | 0.03
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 526012 | DEAN_INTG 3 | 115 | 11.47 | 11.51 | 0.04
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 526013 | DEAN_INTG 6 | 230 | 8.7 | 8.73 | 0.03
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 526161 | CARLISLE 6 | 230 | 14.7 | 14.71 | 0.01
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 526337 | JONES 6 | 230 | 21.13 | 21.14 | 0.01
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 526350 | LEHMAN_TP 3 | 115 | 9.37 | 9.4 | 0.03
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 526361 | COCHRAN 3 | 115 | 8.96 | 8.98 | 0.02
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 526434 | SUNDOWN 3 | 115 | 12.52 | 12.55 | 0.03
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 526435 | SUNDOWN 6 | 230 | 11.81 | 11.84 | 0.03
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 526460 | AMOCO_SS 6 | 230 | 10.35 | 10.37 | 0.02
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 526525 | WOLFFORTH 6 | 230 | 14.33 | 14.34 | 0.01
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 526736 | TERRY_CNTY 3 | 115 | 11.06 | 11.09 | 0.03
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 526784 | AMOCOWASSON6 | 230 | 14.39 | 14.44 | 0.05
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 526792 | PRENTICE 3 | 115 | 6.25 | 6.27 | 0.02
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 526928 | PLAINS_INT 3 | 115 | 10.22 | 10.26 | 0.04
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 526934 | YOAKUM 3 | 115 | 17.35 | 17.42 | 0.07
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 526935 | YOAKUM 6 | 230 | 18.48 | 18.57 | 0.09
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 526936 | YOAKUM_345 | 345 | 9.64 | 9.7 | 0.06
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 526944 | LG-PLAINS 3 | 115 | 8.46 | 8.49 | 0.03
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527009 | BRU_SUB 6 | 230 | 14.59 | 14.65 | 0.06
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527010 | OXYBRU 6 | 230 | 14.47 | 14.53 | 0.06
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527011 | XTO_MAHONEY6 | 230 | 14.17 | 14.23 | 0.06
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527018 | BENNETT 3 | 115 | 13.85 | 13.9 | 0.05
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527022 | APACHE_ROB 3 | 115 | 9.77 | 9.82 | 0.05
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527024 | ALLRED_SUB 3 | 115 | 10.99 | 11.05 | 0.06
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527027 | INK_BASIN 3 | 115 | 13.26 | 13.34 | 0.08
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527028 | INK_BASIN 6 | 230 | 11.05 | 11.13 | 0.08
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527030 | ALRDCRTZ_TP3 | 115 | 12.47 | 12.53 | 0.06
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527033 | XTO_CORNEL+3 | 115 | 12.62 | 12.69 | 0.07
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527041 | ARCO_TP 3 | 115 | 13.74 | 13.79 | 0.05
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527047 | OXY_WILRD1 3 | 115 | 11.07 | 11.11 | 0.04
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527062 | SHELL_CO2 3 | 115 | 16.83 | 16.89 | 0.06
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527068 | SHELLC3_TP 3 | 115 | 13.31 | 13.37 | 0.06
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527130 | DENVER_N 3 | 115 | 22.52 | 22.6 | 0.08
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527136 | DENVER_S 3 | 115 | 22.52 | 22.6 | 0.08
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527146 | MUSTANG 3 | 115 | 24.12 | 24.2 | 0.08
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527149 | MUSTANG 6 | 230 | 16.09 | 16.15 | 0.06
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527151 | GS-MUSTANG 6 | 230 | 16.09 | 16.15 | 0.06
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527194 | LG-PLSHILL 3 | 115 | 7.95 | 7.98 | 0.03
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527202 | SEAGRAVES 3 | 115 | 9.02 | 9.05 | 0.03
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527275 | SEMINOLE 3 | 115 | 13.98 | 14.04 | 0.06
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527276 | SEMINOLE 6 | 230 | 7.89 | 7.92 | 0.03
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527284 | RUSSELL 3 | 115 | 9.49 | 9.54 | 0.05
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527286 | HIGGEAST 3 | 115 | 10.47 | 10.53 | 0.06
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527325 | OXY_WSEM_TP3 | 115 | 9.38 | 9.43 | 0.05
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527360 | MAPCO 3 | 115 | 10.81 | 10.88 | 0.07
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527362 | JOHNSON_DRW3 | 115 | 11.06 | 11.12 | 0.06
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527363 | HIGG 3 | 115 | 10.64 | 10.7 | 0.06
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527482 | CHAVES_CNTY3 | 115 | 7.29 | 7.34 | 0.05
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527483 | CHAVES_CNTY6 | 230 | 4.69 | 4.73 | 0.04
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527597 | TWEEDY 3 | 115 | 5.62 | 5.66 | 0.04
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527656 | CROSSROADS 7 | 345 | 17.55 | 17.58 | 0.03
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527711 | EAGLE_CREEK3 | 115 | 7.99 | 8.06 | 0.07
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527793 | EDDY_STH 3 | 115 | 12.41 | 12.51 | 0.1
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527798 | EDDY_NTH 3 | 115 | 12.41 | 12.51 | 0.1
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527799 | EDDY_NORTH 6 | 230 | 9.63 | 9.71 | 0.08
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527802 | EDDY_CNTY 7 | 345 | 7.66 | 7.72 | 0.06
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527809 | CV-8_MILE 3 | 115 | 5.81 | 5.86 | 0.05
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527821 | CV-DAYTON +3 | 115 | 7.57 | 7.63 | 0.06
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527864 | CUNNINHAM 3 | 115 | 26.53 | 26.74 | 0.21
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527865 | CUNNIGHM_N 6 | 230 | 14.75 | 14.93 | 0.18
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527867 | CUNNIGHM_S 6 | 230 | 14.75 | 14.93 | 0.18
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527891 | HOBBS_INT 3 | 115 | 29.94 | 30.18 | 0.24
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527894 | HOBBS_INT 6 | 230 | 16.83 | 17.06 | 0.23
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527896 | HOBBS_INT 7 | 345 | 9.25 | 9.34 | 0.09
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527929 | PCA 2 | 69 | 8.24 | 8.31 | 0.07
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527930 | PCA 3 | 115 | 12.07 | 12.17 | 0.1
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527948 | CV-LUSK_TP 3 | 115 | 4.49 | 4.53 | 0.04
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527961 | POTASH_JCT 2 | 69 | 10.23 | 10.33 | 0.1
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527962 | POTASH_JCT 3 | 115 | 16.78 | 16.94 | 0.16
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527963 | POTASH_JCT 6 | 230 | 7.42 | 7.49 | 0.07
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527965 | KIOWA 7 | 345 | 8.08 | 8.16 | 0.08
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527966 | KIOWA 3 | 115 | 16.76 | 16.91 | 0.15
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 527999 | INTREPDW_TP3 | 115 | 13.96 | 14.09 | 0.13
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528017 | SNDRO_CRYO+3 | 115 | 7.86 | 7.93 | 0.07
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528024 | RR_SVC_HV 3 | 115 | 10.04 | 10.13 | 0.09
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528025 | RDRUNNER 3 | 115 | 10.04 | 10.13 | 0.09
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528027 | RDRUNNER 7 | 345 | 4.78 | 4.82 | 0.04
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528040 | BATTLE_AXE 3 | 115 | 3.13 | 3.15 | 0.02
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528094 | 7-RIVERS 3 | 115 | 8.81 | 8.89 | 0.08
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528095 | 7-RIVERS 6 | 230 | 6.56 | 6.62 | 0.06
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528160 | CARLSBAD 3 | 115 | 11.55 | 11.66 | 0.11
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528178 | PECOS 3 | 115 | 12.2 | 12.3 | 0.1
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528179 | PECOS 6 | 230 | 6.74 | 6.81 | 0.07
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528182 | NORTH_LOVNG3 | 115 | 9.95 | 10.04 | 0.09
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528185 | N_LOVING 7 | 345 | 5.83 | 5.88 | 0.05
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528192 | SOUTH_LOVNG3 | 115 | 7.5 | 7.56 | 0.06
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528193 | BLACKRIVER 3 | 115 | 8.77 | 8.85 | 0.08
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528195 | AGAVE_PDURO3 | 115 | 7.07 | 7.13 | 0.06
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528222 | CHINA_DRAW 3 | 115 | 9.01 | 9.09 | 0.08
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528223 | CHINA_DRAW 7 | 345 | 4.57 | 4.61 | 0.04
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528226 | HOPI_SUB 3 | 115 | 7.21 | 7.27 | 0.06
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528230 | AGAVE_RHILL3 | 115 | 9.31 | 9.4 | 0.09
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528231 | AGAVE_RHIL23 | 115 | 8.92 | 9 | 0.08
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528239 | CUSTERMTN 3 | 115 | 7.23 | 7.3 | 0.07
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528317 | ENRON_TP 3 | 115 | 7.01 | 7.07 | 0.06
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528318 | ENRON 3 | 115 | 6.12 | 6.18 | 0.06
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528325 | LE-WAITS 3 | 115 | 9.21 | 9.26 | 0.05
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528333 | LE-WEST_SUB3 | 115 | 9.12 | 9.18 | 0.06
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528334 | LE-NRTH_INT3 | 115 | 9.06 | 9.12 | 0.06
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528341 | LE-SANANDRS3 | 115 | 6.61 | 6.66 | 0.05
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528348 | BUCKEYE_TP 3 | 115 | 8.46 | 8.53 | 0.07
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528353 | MADDOXG23 3 | 115 | 25.25 | 25.44 | 0.19
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528355 | MADDOX 3 | 115 | 25.25 | 25.44 | 0.19
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528385 | BUCKEYE 3 | 115 | 7.64 | 7.7 | 0.06
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528392 | PEARLE 3 | 115 | 6.56 | 6.61 | 0.05
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528394 | QUAHADA 3 | 115 | 8.29 | 8.36 | 0.07
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528399 | LEA_NATIONL3 | 115 | 7.05 | 7.11 | 0.06
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528413 | TAYLOR 3 | 115 | 14.55 | 14.65 | 0.1
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528420 | ZIA 3 | 115 | 6.76 | 6.82 | 0.06
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528422 | DCP_ZIA TP 3 | 115 | 7.22 | 7.28 | 0.06
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528423 | DCP_ZIA 3 | 115 | 6.86 | 6.92 | 0.06
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528433 | BENSING 3 | 115 | 8.31 | 8.37 | 0.06
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528435 | MILLEN 3 | 115 | 11.75 | 11.84 | 0.09
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528442 | NE_HOBBS 3 | 115 | 12.04 | 12.13 | 0.09
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528449 | W_BENDER 3 | 115 | 14.74 | 14.85 | 0.11
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528463 | SANGER_SW 3 | 115 | 15.8 | 15.92 | 0.12
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528470 | E_SANGER 3 | 115 | 12.78 | 12.87 | 0.09
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528480 | OXY_S_HOBBS3 | 115 | 10.71 | 10.79 | 0.08
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528484 | SW_4J44 3 | 115 | 11.28 | 11.37 | 0.09
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528491 | MONUMENT 3 | 115 | 15.3 | 15.42 | 0.12
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528498 | W_HOBBS 3 | 115 | 11.81 | 11.91 | 0.1
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528533 | DRINKARD_TP3 | 115 | 7.84 | 7.92 | 0.08
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528554 | COOPER_RNCH3 | 115 | 6.74 | 6.79 | 0.05
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528568 | MONUMNT_TP 3 | 115 | 10.4 | 10.48 | 0.08
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528575 | OXYPERMIAN 3 | 115 | 15.22 | 15.33 | 0.11
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528581 | BYRD_TP 3 | 115 | 8.15 | 8.22 | 0.07
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528582 | BYRD 3 | 115 | 7.55 | 7.61 | 0.06
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528589 | DRINKARD 3 | 115 | 7.98 | 8.06 | 0.08
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528602 | ANDREWS 3 | 115 | 10.45 | 10.57 | 0.12
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528603 | NA_ENRICH 3 | 115 | 10.27 | 10.39 | 0.12
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528604 | ANDREWS 6 | 230 | 6.56 | 6.64 | 0.08
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528605 | TARGA 3 | 115 | 8.51 | 8.6 | 0.09
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528610 | GAINES_GEN 6 | 230 | 7.07 | 7.16 | 0.09
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528611 | GAINESGENTP6 | 230 | 8.48 | 8.59 | 0.11
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528617 | LE-WAITS 2 | 69 | 3.74 | 3.76 | 0.02
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528618 | LE-LOVINTON2 | 69 | 7.08 | 7.12 | 0.04
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528626 | LE-PLNSINT 2 | 69 | 3.85 | 3.87 | 0.02
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528627 | LE-TXACO_TP3 | 115 | 7.32 | 7.37 | 0.05
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528638 | LE-SAUNDRTP2 | 69 | 3.6 | 3.63 | 0.03
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528675 | LE-FAMARISS2 | 69 | 3.44 | 3.46 | 0.02
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528677 | LE-DSYSRPOI2 | 69 | 4.94 | 4.97 | 0.03
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528679 | LE-TATMGOAB2 | 69 | 4.53 | 4.56 | 0.03
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528699 | LE-GRAY 2 | 69 | 4.14 | 4.17 | 0.03
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528714 | LE-FORT_SW 2 | 69 | 3.52 | 3.54 | 0.02
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528759 | LE-TP51 2 | 69 | 2.45 | 2.46 | 0.01
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528775 | LE-ERF 3 | 115 | 11.06 | 11.12 | 0.06
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 528792 | LE-TEXACO 3 | 115 | 6.64 | 6.69 | 0.05
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 560022 | CRAWFISH_DR | 345 | 23.91 | 23.94 | 0.03
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 560100 | CRAWFISH765 | 765 | 11.16 | 11.17 | 0.01
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 583340 | GEN-2012-020 | 230 | 11.69 | 11.7 | 0.01
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 583840 | GEN-2013-027 | 230 | 11.73 | 11.75 | 0.02
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 584560 | GEN-2015-014 | 115 | 6.46 | 6.48 | 0.02
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 587990 | GEN-2016-121 | 115 | 9.53 | 9.62 | 0.09
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 588460 | A16-008SUB | 115 | 13.26 | 13.34 | 0.08
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 588800 | GEN-2017-039 | 230 | 10.12 | 10.13 | 0.01
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 588970 | GEN-2017-059 | 230 | 10 | 10.01 | 0.01
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 589400 | GEN-2017-104 | 230 | 6.64 | 6.91 | 0.27
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 599960 | EPTNP-D6 | 230 | 9.63 | 9.71 | 0.08
GEN-2017-104 | South | 06 - South Texas Panhandle/New Mexico | 599961 | EPTNP 7 | 345 | 16736.82 | 16736.82 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511421 | VERDEN 4 | 138 | 10.28 | 10.29 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511423 | FLE TAP4 | 138 | 9.22 | 9.23 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511425 | TUTCONT4 | 138 | 10.55 | 10.55 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511437 | COMANC-4 | 138 | 18.75 | 18.8 | 0.05
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511439 | LWSTAP 4 | 138 | 11.95 | 11.98 | 0.03
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511445 | CARNEG-4 | 138 | 8.2 | 8.2 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511446 | CL-AFTP4 | 138 | 6.65 | 6.68 | 0.03
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511456 | O.K.U.-7 | 345 | 5.63 | 5.64 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511458 | ELKCTY-4 | 138 | 10.93 | 11.06 | 0.13
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511459 | ELKCTY-2 | 69 | 7.19 | 7.21 | 0.02
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511466 | L.E.S.-2 | 69 | 17.2 | 17.21 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511467 | L.E.S.-4 | 138 | 25.48 | 25.59 | 0.11
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511468 | L.E.S.-7 | 345 | 13.54 | 13.66 | 0.12
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511474 | SHERID4 | 138 | 12.73 | 12.76 | 0.03
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511476 | S.W.S.-2 | 69 | 4.38 | 4.38 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511477 | S.W.S.-4 | 138 | 36.79 | 36.92 | 0.13
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511483 | NORGE--4 | 138 | 11.82 | 11.83 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511485 | CLINTJC4 | 138 | 6.34 | 6.36 | 0.02
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511486 | ELGINJT4 | 138 | 10.4 | 10.41 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511490 | ELKCITY6 | 230 | 6.53 | 6.66 | 0.13
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511494 | COMMTAP4 | 138 | 22.28 | 22.36 | 0.08
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511511 | FALCNRD4 | 138 | 7.83 | 7.89 | 0.06
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511541 | SWEETWT6 | 230 | 7.9 | 8.14 | 0.24
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511542 | BUFFCK6 | 230 | 6.05 | 6.18 | 0.13
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511544 | DEMPSEY6 | 230 | 5.27 | 5.35 | 0.08
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511547 | ROARK6 | 230 | 4.88 | 4.95 | 0.07
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511553 | CHISHOLM7 | 345 | 5.49 | 5.94 | 0.45
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511557 | CHISHOLM6 | 230 | 8.56 | 8.97 | 0.41
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511563 | ELSWORTH 4 | 138 | 10.33 | 10.34 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511565 | OKLAUN HVDC7 | 345 | 5.61 | 5.62 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511568 | TERRYRD7 | 345 | 10.16 | 10.19 | 0.03
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511571 | RUSHSPR7 | 345 | 6.5 | 6.52 | 0.02
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 514801 | MINCO 7 | 345 | 18.29 | 18.54 | 0.25
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 514819 | EL-RENO4 | 138 | 15.77 | 15.78 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 514820 | JENSENT4 | 138 | 15.67 | 15.68 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 514863 | HAYMAKR4 | 138 | 26.84 | 26.85 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 514879 | NORTWST4 | 138 | 45.02 | 45.04 | 0.02
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 514880 | NORTWST7 | 345 | 33.37 | 33.43 | 0.06
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 514881 | SPRNGCK7 | 345 | 24.08 | 24.1 | 0.02
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 514894 | CZECHAL4 | 138 | 28.4 | 28.41 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 514895 | SARA 4 | 138 | 19.09 | 19.1 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 514898 | CIMARON4 | 138 | 44.07 | 44.12 | 0.05
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 514901 | CIMARON7 | 345 | 34.91 | 35.04 | 0.13
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 514908 | ARCADIA7 | 345 | 30.93 | 30.94 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 514933 | DRAPER 4 | 138 | 40.11 | 40.13 | 0.02
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 514934 | DRAPER 7 | 345 | 21.39 | 21.4 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 515045 | SEMINOL7 | 345 | 27.13 | 27.14 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 515136 | SUNNYSD7 | 345 | 11.25 | 11.26 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 515407 | TATONGA7 | 345 | 16.81 | 16.81 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 515444 | MCNOWND7 | 345 | 18.24 | 18.48 | 0.24
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 515497 | MATHWSN7 | 345 | 33.51 | 33.58 | 0.07
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 515549 | MNCWND37 | 345 | 12.58 | 12.68 | 0.1
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 515600 | KNGFSHR7 | 345 | 12 | 12.01 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 515605 | CANADN7 | 345 | 13.07 | 13.08 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 515610 | FSHRTAP7 | 345 | 17.88 | 17.91 | 0.03
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 515800 | GRACMNT7 | 345 | 17.02 | 17.68 | 0.66
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 515802 | GRACMNT4 | 138 | 30.52 | 30.71 | 0.19
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 515875 | REDNGTN7 | 345 | 18.2 | 18.21 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 515939 | MNCWND47 | 345 | 6.89 | 6.92 | 0.03
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 520422 | SEQUOYAHJ4 | 138 | 24.62 | 24.66 | 0.04
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 520440 | HARPER2 | 69 | 18.71 | 18.72 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 520508 | CLVJCTN2 | 69 | 5.05 | 5.05 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 520509 | CLVJCTS2 | 69 | 4.64 | 4.64 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 520512 | BC SW 4 | 138 | 7.94 | 7.94 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 520513 | BCV SW 4 | 138 | 6.12 | 6.12 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 520514 | BCVI_HVB | 138 | 8.85 | 8.85 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 520810 | ANADARK2 | 69 | 20.24 | 20.25 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 520814 | ANADARK4 | 138 | 33.13 | 33.23 | 0.1
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 520827 | BINGERJ4 | 138 | 8.11 | 8.12 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 520838 | CADDO 2 | 69 | 14.01 | 14.02 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 520867 | CORN TP4 | 138 | 14.57 | 14.58 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 520912 | FLETCH-4 | 138 | 7.35 | 7.35 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 520923 | GEORGIA4 | 138 | 18.07 | 18.1 | 0.03
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 521017 | ONEY 4 | 138 | 11.44 | 11.46 | 0.02
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 521024 | PARADSE4 | 138 | 6.25 | 6.25 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 521027 | PINERDG2 | 69 | 5.01 | 5.01 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 521031 | POCASET4 | 138 | 7.91 | 7.91 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 521072 | TUTLETP4 | 138 | 6.78 | 6.78 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 521088 | WASHITA2 | 69 | 9.76 | 9.76 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 521089 | WASHITA4 | 138 | 31.46 | 31.59 | 0.13
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 521103 | SLKHILLS 4 | 138 | 8.88 | 8.88 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 521116 | REDHLSW4 | 138 | 7.32 | 7.36 | 0.04
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 521129 | CHERRYRD 4 | 138 | 6.63 | 6.63 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 523771 | GRAPEVINE 6 | 230 | 5.77 | 5.8 | 0.03
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 523776 | WHEELER 3 | 115 | 6.58 | 6.62 | 0.04
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 523777 | WHEELER 6 | 230 | 5.98 | 6.06 | 0.08
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 525832 | TUCO_INT 7 | 345 | 12.33 | 12.33 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 560078 | G16-037-TAP | 345 | 6.52 | 7.76 | 1.24
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 563269 | GEN-2015-093 | 345 | 9.92 | 10.12 | 0.2
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 584060 | GEN-2015-057 | 345 | 9.24 | 9.29 | 0.05
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 587230 | GEN-2016-037 | 345 | 5.81 | 7.07 | 1.26
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 587740 | GEN-2016-091 | 345 | 13.28 | 13.56 | 0.28
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 587744 | G16-091-TAP | 345 | 14.9 | 15.26 | 0.36
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 587770 | GEN-2016-095 | 345 | 11.03 | 11.22 | 0.19
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 587794 | G16-097-TAP | 138 | 12.2 | 12.22 | 0.02
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 588760 | GEN-2017-033 | 345 | 4.13 | 4.13 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 589030 | GEN-2017-065 | 345 | 5.15 | 5.15 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 599891 | OKLAUN 7 | 345 | 4.36 | 4.36 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 900001 | TRAVERSE1 | 345 | 7.38 | 7.38 | 0
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511428 | LG-YEAR4 | 138 | 12.28 | 12.37 | 0.09
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511429 | L AIRGS4 | 138 | 11.86 | 11.95 | 0.09
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511430 | LWS N4 | 138 | 10.73 | 10.79 | 0.06
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511432 | R-AMOCO2 | 69 | 3.88 | 3.94 | 0.06
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511435 | SNYDER-4 | 138 | 6.9 | 7.12 | 0.22
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511437 | COMANC-4 | 138 | 18.74 | 18.8 | 0.06
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511438 | DUKE---2 | 69 | 3.49 | 3.56 | 0.07
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511439 | LWSTAP 4 | 138 | 11.9 | 11.98 | 0.08
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511440 | ALTUSJT4 | 138 | 5 | 5.12 | 0.12
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511441 | ALTUSJT2 | 69 | 5.73 | 5.87 | 0.14
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511444 | ROSVTAP2 | 69 | 4.1 | 4.16 | 0.06
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511460 | FREDJC-2 | 69 | 2.89 | 2.98 | 0.09
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511462 | HEADRIK2 | 69 | 4.67 | 4.79 | 0.12
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511465 | HOBART-2 | 69 | 5.75 | 5.81 | 0.06
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511467 | L.E.S.-4 | 138 | 25.51 | 25.59 | 0.08
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511471 | LWS-NTP4 | 138 | 12.02 | 12.1 | 0.08
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511472 | TIPTE T2 | 69 | 3.78 | 3.89 | 0.11
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511475 | SNYDER-2 | 69 | 7.7 | 7.92 | 0.22
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511479 | TIPTCTY2 | 69 | 2.44 | 2.51 | 0.07
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511488 | 112GORE4 | 138 | 13.09 | 13.18 | 0.09
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511494 | COMMTAP4 | 138 | 22.29 | 22.36 | 0.07