Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.26184 | 156.23 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25815 | 156.23 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30685 | 156.23 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27966 | 156.23 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25815 | 156.23 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23992 | 156.23 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30685 | 156.23 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25788 | 156.23 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2046 | 137.68 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22307 | 137.68 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29012 | 137.68 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28643 | 137.68 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33514 | 137.68 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30794 | 137.68 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28643 | 137.68 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21164 | 137.68 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33514 | 137.68 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28616 | 137.68 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20493 | 133.53 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2234 | 133.53 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29046 | 133.53 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28677 | 133.53 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33547 | 133.53 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30828 | 133.53 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28677 | 133.53 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21131 | 133.53 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33547 | 133.53 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2865 | 133.53 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21245 | 126.09 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22979 | 126.09 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29002 | 126.09 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28672 | 126.09 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33895 | 126.09 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31345 | 126.09 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28672 | 126.09 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21887 | 126.09 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33895 | 126.09 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28632 | 126.09 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21164 | 112.91 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23013 | 112.91 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29736 | 112.91 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29381 | 112.91 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34211 | 112.91 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31491 | 112.91 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29381 | 112.91 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20465 | 112.91 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34211 | 112.91 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29352 | 112.91 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2101 | 167.62 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2778 | 167.62 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27396 | 167.62 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32304 | 167.62 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29658 | 167.62 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27396 | 167.62 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23261 | 167.62 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32304 | 167.62 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.27371 | 167.62 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22506 | 152.07 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24206 | 152.07 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30976 | 152.07 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30592 | 152.07 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35499 | 152.07 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32854 | 152.07 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30592 | 152.07 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20066 | 152.07 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35499 | 152.07 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30567 | 152.07 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22519 | 145.33 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24218 | 145.33 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30988 | 145.33 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30604 | 145.33 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35511 | 145.33 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.32866 | 145.33 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30604 | 145.33 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20053 | 145.33 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.35511 | 145.33 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30579 | 145.33 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23579 | 138.59 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.25108 | 138.59 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31046 | 138.59 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30707 | 138.59 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36009 | 138.59 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33482 | 138.59 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30707 | 138.59 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20842 | 138.59 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36009 | 138.59 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30667 | 138.59 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.23262 | 123.43 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.24963 | 123.43 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31753 | 123.43 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31384 | 123.43 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36247 | 123.43 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33601 | 123.43 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31384 | 123.43 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.36247 | 123.43 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31357 | 123.43 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20421 | 135.97 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22268 | 135.97 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28976 | 135.97 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28607 | 135.97 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33478 | 135.97 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30759 | 135.97 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28607 | 135.97 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21193 | 135.97 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33478 | 135.97 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.2858 | 135.97 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20457 | 131.62 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22305 | 131.62 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29013 | 131.62 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28644 | 131.62 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33514 | 131.62 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.30795 | 131.62 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28644 | 131.62 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21157 | 131.62 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33514 | 131.62 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28617 | 131.62 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21205 | 123.97 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22941 | 123.97 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28967 | 123.97 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28637 | 123.97 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33859 | 123.97 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.3131 | 123.97 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28637 | 123.97 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21915 | 123.97 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.33859 | 123.97 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.28597 | 123.97 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.21122 | 111.15 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.22972 | 111.15 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29698 | 111.15 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29342 | 111.15 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.15 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.31453 | 111.15 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29342 | 111.15 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.20497 | 111.15 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.34173 | 111.15 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 |  | 553 | 0.29314 | 111.15 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.26202 | 179.04 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.25833 | 179.04 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.30704 | 179.04 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.27985 | 179.04 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.25833 | 179.04 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.23967 | 179.04 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.30704 | 179.04 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.25806 | 179.04 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.20422 | 158.13 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.22269 | 158.13 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.28977 | 158.13 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.28608 | 158.13 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.33479 | 158.13 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.30759 | 158.13 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.28608 | 158.13 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.21192 | 158.13 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.33479 | 158.13 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.28581 | 158.13 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 553 |  | 0.20458 | 132.37 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 553 |  | 0.22306 | 132.37 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 553 |  | 0.29014 | 132.37 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 553 |  | 0.28645 | 132.37 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 553 |  | 0.33516 | 132.37 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 553 |  | 0.30796 | 132.37 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 553 |  | 0.28645 | 132.37 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 553 |  | 0.21156 | 132.37 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 553 |  | 0.33516 | 132.37 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 553 |  | 0.28618 | 132.37 | System Intact
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.21123 | 129.49 | System Intact
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.22972 | 129.49 | System Intact
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.29699 | 129.49 | System Intact
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.29343 | 129.49 | System Intact
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.34173 | 129.49 | System Intact
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.31453 | 129.49 | System Intact
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.29343 | 129.49 | System Intact
Thermal | 06ALL | 2 | 29SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.20496 | 129.49 | System Intact
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.34173 | 129.49 | System Intact
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 478 |  | 0.29314 | 129.49 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 553 |  | 0.21207 | 124.92 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 553 |  | 0.22942 | 124.92 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 553 |  | 0.28968 | 124.92 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 553 |  | 0.28638 | 124.92 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 553 |  | 0.33861 | 124.92 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 553 |  | 0.31311 | 124.92 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 553 |  | 0.28638 | 124.92 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 553 |  | 0.21914 | 124.92 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 553 |  | 0.33861 | 124.92 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 553 |  | 0.28598 | 124.92 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 126.65 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 126.65 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 126.65 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.65 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.65 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 126.65 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.65 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 126.65 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.65 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 126.65 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 126.61 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 126.61 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 126.61 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.61 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.61 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 126.61 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.61 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 126.61 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.61 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 126.61 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 126.41 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 126.41 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 126.41 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.41 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.41 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 126.41 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.41 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 126.41 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.41 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 126.41 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 126.99 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 126.99 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 126.99 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.99 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.99 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 126.99 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.99 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 126.99 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.99 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 126.99 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 129.03 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 129.03 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 129.03 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 129.03 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 129.03 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 129.03 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 129.03 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 129.03 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 129.03 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 129.03 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.22 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.22 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.22 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.22 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.22 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.22 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.22 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.22 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.22 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.22 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.21 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.21 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.21 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.21 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.21 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.21 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.21 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.21 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.21 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.21 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.09 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.09 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.09 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.09 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.09 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.09 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.09 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.09 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.09 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.09 | P11:230:WERE:JECU1_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.34 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.34 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.34 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.34 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.34 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.34 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.34 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.34 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.34 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.34 | P11:24:AEPW:TURKCOAL
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.21 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.21 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.21 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.21 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.21 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.21 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.21 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.21 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.21 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.21 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 125.79 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 125.79 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 125.79 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 125.79 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 125.79 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 125.79 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 125.79 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 125.79 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 125.79 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 125.79 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.21 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.21 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.21 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.21 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.21 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.21 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.21 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.21 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.21 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.21 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 126.21 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 126.21 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 126.21 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.21 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.21 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 126.21 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.21 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 126.21 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.21 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 126.21 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.21 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.21 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.21 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.21 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.21 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.21 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.21 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.21 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.21 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.21 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.21 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.21 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.21 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.21 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.21 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.21 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.21 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.21 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.21 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.21 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.2 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.2 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.2 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.2 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.2 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.2 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.2 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.2 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20428 | 127.2 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.2 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.2 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28609 | 127.2 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3076 | 127.2 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28609 | 127.2 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.2 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28582 | 127.2 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.99 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.99 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.99 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.99 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.99 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.99 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.99 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.99 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.99 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.99 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 128.04 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 128.04 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 128.04 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 128.04 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 128.04 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 128.04 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 128.04 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 128.04 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 128.04 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 128.04 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.2 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.2 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.2 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.2 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.2 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.2 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.2 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.2 | P11:345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.2 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.2 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.2 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.2 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.2 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.2 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.2 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.2 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.2 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.2 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.2 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.2 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.2 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.2 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.2 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.2 | P11:345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 126.4 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 126.4 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 126.4 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.4 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.4 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 126.4 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.4 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 126.4 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.4 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 126.4 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.1 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.1 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.1 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.1 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.1 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.1 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.1 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.1 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.1 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.1 | P11:345:WERE:JECU2_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.1 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.1 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.1 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.1 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.1 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.1 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.1 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.1 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.1 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.1 | P11:345:WERE:JECU3_GEN::
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20519 | 127.63 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22485 | 127.63 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28983 | 127.63 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28605 | 127.63 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33504 | 127.63 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30786 | 127.63 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28605 | 127.63 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21191 | 127.63 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33504 | 127.63 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28579 | 127.63 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20431 | 125.25 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22281 | 125.25 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28979 | 125.25 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 125.25 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33482 | 125.25 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30764 | 125.25 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 125.25 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21207 | 125.25 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33482 | 125.25 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 125.25 | P12:115:SPS:T13.1.TAYLOR.WHOBBS
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20433 | 122.64 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22282 | 122.64 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28979 | 122.64 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28611 | 122.64 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33483 | 122.64 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30766 | 122.64 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28611 | 122.64 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21208 | 122.64 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33483 | 122.64 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 122.64 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 126.17 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 126.17 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 126.17 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.17 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.17 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 126.17 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.17 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 126.17 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.17 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 126.17 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20508 | 128.97 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22428 | 128.97 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29169 | 128.97 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28814 | 128.97 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33694 | 128.97 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30883 | 128.97 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28814 | 128.97 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21181 | 128.97 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33694 | 128.97 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28784 | 128.97 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20508 | 127.65 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22428 | 127.65 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29169 | 127.65 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28814 | 127.65 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33694 | 127.65 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30883 | 127.65 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28814 | 127.65 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21181 | 127.65 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33694 | 127.65 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28784 | 127.65 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20428 | 126.92 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22278 | 126.92 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28979 | 126.92 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28602 | 126.92 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33481 | 126.92 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 126.92 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28602 | 126.92 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21204 | 126.92 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33481 | 126.92 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28582 | 126.92 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20535 | 127.67 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22383 | 127.67 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29048 | 127.67 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28682 | 127.67 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33548 | 127.67 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30826 | 127.67 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28682 | 127.67 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21184 | 127.67 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33548 | 127.67 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28655 | 127.67 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20498 | 127.46 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22348 | 127.46 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29024 | 127.46 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28657 | 127.46 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33524 | 127.46 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30803 | 127.46 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28657 | 127.46 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21192 | 127.46 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33524 | 127.46 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2863 | 127.46 | P12:115:SPS:T54.1.KIRBY.SHM(520)
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20394 | 127.41 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22218 | 127.41 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29566 | 127.41 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2942 | 127.41 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33617 | 127.41 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30891 | 127.41 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2942 | 127.41 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21128 | 127.41 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33617 | 127.41 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29368 | 127.41 | P12:115:SPS:T58.1.HERFRD.CARGIL
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20394 | 127.72 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22218 | 127.72 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29566 | 127.72 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2942 | 127.72 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33617 | 127.72 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30891 | 127.72 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2942 | 127.72 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21128 | 127.72 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33617 | 127.72 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29368 | 127.72 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21077 | 127.77 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22554 | 127.77 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29093 | 127.77 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28722 | 127.77 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33601 | 127.77 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30883 | 127.77 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28722 | 127.77 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21136 | 127.77 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33601 | 127.77 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28695 | 127.77 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20432 | 126.51 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22281 | 126.51 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28976 | 126.51 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28608 | 126.51 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33478 | 126.51 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30758 | 126.51 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28608 | 126.51 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21207 | 126.51 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33478 | 126.51 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28581 | 126.51 | P12:115:SPS:T71.1.CRLSLE.YUMA
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 125.91 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 125.91 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 125.91 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 125.91 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 125.91 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 125.91 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 125.91 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 125.91 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 125.91 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 125.91 | P12:115:SPS:T91.1.HIGG.RUSSELL
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20456 | 127.2 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22314 | 127.2 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29183 | 127.2 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28804 | 127.2 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33539 | 127.2 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30803 | 127.2 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28804 | 127.2 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21219 | 127.2 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33539 | 127.2 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28781 | 127.2 | P12:115:SPS:V26.1.RSWLL.EDDY_N
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 126.37 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 126.37 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 126.37 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.37 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.37 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 126.37 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.37 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 126.37 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.37 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 126.37 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20349 | 126.44 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21934 | 126.44 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29104 | 126.44 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28741 | 126.44 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.336 | 126.44 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30875 | 126.44 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28741 | 126.44 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21148 | 126.44 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.336 | 126.44 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28713 | 126.44 | P12:115:SPS:V37.1.CASTRO.PLANTX
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20436 | 124.88 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22286 | 124.88 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28982 | 124.88 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28613 | 124.88 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33487 | 124.88 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3077 | 124.88 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28613 | 124.88 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21208 | 124.88 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33487 | 124.88 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28586 | 124.88 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20412 | 126.67 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22289 | 126.67 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29014 | 126.67 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28648 | 126.67 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33513 | 126.67 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30791 | 126.67 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28648 | 126.67 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21189 | 126.67 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33513 | 126.67 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2862 | 126.67 | P12:115:SPS:V52.1.COLTR.BSHLND
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20456 | 127.06 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22324 | 127.06 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29027 | 127.06 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2866 | 127.06 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33543 | 127.06 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30795 | 127.06 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2866 | 127.06 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.06 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33543 | 127.06 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28633 | 127.06 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20444 | 125.04 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22293 | 125.04 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2898 | 125.04 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28612 | 125.04 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3349 | 125.04 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30771 | 125.04 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28612 | 125.04 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21219 | 125.04 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3349 | 125.04 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28584 | 125.04 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20434 | 126.03 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22283 | 126.03 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28979 | 126.03 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28611 | 126.03 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33484 | 126.03 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30767 | 126.03 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28611 | 126.03 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21214 | 126.03 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33484 | 126.03 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28584 | 126.03 | P12:115:SPS:W26.1.CUNGHM.OILCNTR
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.12 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.12 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28981 | 127.12 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28625 | 127.12 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.12 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3076 | 127.12 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28625 | 127.12 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.12 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.12 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28625 | 127.12 | P12:115:SPS:W32.1.PRMTR.FE-CLSIN
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20444 | 127.89 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22426 | 127.89 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29254 | 127.89 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28919 | 127.89 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33699 | 127.89 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30969 | 127.89 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28919 | 127.89 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21097 | 127.89 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33699 | 127.89 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28888 | 127.89 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20428 | 127.08 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22277 | 127.08 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29001 | 127.08 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28676 | 127.08 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33481 | 127.08 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30762 | 127.08 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28676 | 127.08 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21204 | 127.08 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33481 | 127.08 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28633 | 127.08 | P12:115:SPS:W62.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 128.01 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 128.01 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 128.01 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 128.01 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 128.01 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 128.01 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 128.01 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 128.01 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20427 | 127.06 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22277 | 127.06 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29005 | 127.06 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28688 | 127.06 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33482 | 127.06 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30762 | 127.06 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28688 | 127.06 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21204 | 127.06 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33482 | 127.06 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28642 | 127.06 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 125.95 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 125.95 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 125.95 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 125.95 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 125.95 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 125.95 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 125.95 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 125.95 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 125.95 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 125.95 | P12:115:SPS:W68.1.DAMNDBK.SULPHR
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 123.23 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 123.23 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 123.23 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 123.23 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 123.23 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 123.23 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 123.23 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 123.23 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 123.23 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 123.23 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20498 | 127.46 | P12:115:SPS-AEPW:KIRBY3:SHAM3WT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22348 | 127.46 | P12:115:SPS-AEPW:KIRBY3:SHAM3WT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29024 | 127.46 | P12:115:SPS-AEPW:KIRBY3:SHAM3WT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28657 | 127.46 | P12:115:SPS-AEPW:KIRBY3:SHAM3WT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33524 | 127.46 | P12:115:SPS-AEPW:KIRBY3:SHAM3WT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30803 | 127.46 | P12:115:SPS-AEPW:KIRBY3:SHAM3WT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28657 | 127.46 | P12:115:SPS-AEPW:KIRBY3:SHAM3WT
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21192 | 127.46 | P12:115:SPS-AEPW:KIRBY3:SHAM3WT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33524 | 127.46 | P12:115:SPS-AEPW:KIRBY3:SHAM3WT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2863 | 127.46 | P12:115:SPS-AEPW:KIRBY3:SHAM3WT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20418 | 126.41 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22267 | 126.41 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28957 | 126.41 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28589 | 126.41 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33459 | 126.41 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30739 | 126.41 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28589 | 126.41 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2125 | 126.41 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33459 | 126.41 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28562 | 126.41 | P12:138:OKGE-WFEC:BKRBKR168
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20552 | 128.51 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22401 | 128.51 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29066 | 128.51 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28699 | 128.51 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33566 | 128.51 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30844 | 128.51 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28699 | 128.51 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21168 | 128.51 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33566 | 128.51 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28672 | 128.51 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21818 | 136.69 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2365 | 136.69 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29898 | 136.69 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29561 | 136.69 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.34375 | 136.69 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31629 | 136.69 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29561 | 136.69 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20935 | 136.69 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.34375 | 136.69 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2953 | 136.69 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21818 | 133.79 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2365 | 133.79 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29898 | 133.79 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29561 | 133.79 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.34375 | 133.79 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31629 | 133.79 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29561 | 133.79 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20935 | 133.79 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.34375 | 133.79 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2953 | 133.79 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20258 | 129.18 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22092 | 129.18 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29127 | 129.18 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28705 | 129.18 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3378 | 129.18 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30992 | 129.18 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28705 | 129.18 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21115 | 129.18 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3378 | 129.18 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28684 | 129.18 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20403 | 126.31 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22253 | 126.31 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28948 | 126.31 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2858 | 126.31 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3345 | 126.31 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3073 | 126.31 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2858 | 126.31 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21244 | 126.31 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3345 | 126.31 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28553 | 126.31 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20924 | 131.71 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2275 | 131.71 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29381 | 131.71 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29015 | 131.71 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33882 | 131.71 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3117 | 131.71 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29015 | 131.71 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21062 | 131.71 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33882 | 131.71 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28988 | 131.71 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.23603 | 171.59 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2524 | 171.59 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31871 | 171.59 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31492 | 171.59 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.36397 | 171.59 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-033 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21277 | 171.59 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3378 | 171.59 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-065 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21277 | 171.59 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31492 | 171.59 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.36397 | 171.59 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31466 | 171.59 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20408 | 125.82 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22258 | 125.82 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28951 | 125.82 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28582 | 125.82 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33452 | 125.82 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30733 | 125.82 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28582 | 125.82 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21247 | 125.82 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33452 | 125.82 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28555 | 125.82 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20151 | 123.55 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21991 | 123.55 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28628 | 123.55 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28263 | 123.55 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33128 | 123.55 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3041 | 123.55 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28263 | 123.55 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21723 | 123.55 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33128 | 123.55 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28235 | 123.55 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20924 | 132.86 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2275 | 132.86 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29381 | 132.86 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29015 | 132.86 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33882 | 132.86 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3117 | 132.86 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29015 | 132.86 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21062 | 132.86 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33882 | 132.86 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28988 | 132.86 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.23603 | 142.05 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2524 | 142.05 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31871 | 142.05 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31492 | 142.05 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.36397 | 142.05 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3378 | 142.05 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31492 | 142.05 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.36397 | 142.05 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31466 | 142.05 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20579 | 129.33 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22425 | 129.33 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29069 | 129.33 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28703 | 129.33 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33568 | 129.33 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30849 | 129.33 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28703 | 129.33 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21239 | 129.33 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33568 | 129.33 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28676 | 129.33 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20579 | 129.32 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22425 | 129.32 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29069 | 129.32 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28703 | 129.32 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33568 | 129.32 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30848 | 129.32 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28703 | 129.32 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21239 | 129.32 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33568 | 129.32 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28676 | 129.32 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20396 | 125.74 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22241 | 125.74 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28902 | 125.74 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28535 | 125.74 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33402 | 125.74 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30683 | 125.74 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28535 | 125.74 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21377 | 125.74 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33402 | 125.74 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28508 | 125.74 | P12:345:OKGE:BKRBKR171
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20396 | 125.74 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22241 | 125.74 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28902 | 125.74 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28535 | 125.74 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33402 | 125.74 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30683 | 125.74 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28535 | 125.74 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21377 | 125.74 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33402 | 125.74 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28508 | 125.74 | P12:345:OKGE:BKRBKR172
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20826 | 131 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22657 | 131 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29301 | 131 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28935 | 131 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33802 | 131 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31087 | 131 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28935 | 131 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21072 | 131 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33802 | 131 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28908 | 131 | P12:345:OKGE:BKRBKR24
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20559 | 128.45 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22406 | 128.45 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29057 | 128.45 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28691 | 128.45 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33557 | 128.45 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30837 | 128.45 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28691 | 128.45 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21234 | 128.45 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33557 | 128.45 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28664 | 128.45 | P12:345:OKGE:BKRBKR336
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2056 | 128.45 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22406 | 128.45 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29057 | 128.45 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28691 | 128.45 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33557 | 128.45 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30837 | 128.45 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28691 | 128.45 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21234 | 128.45 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33557 | 128.45 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28664 | 128.45 | P12:345:OKGE:BKRBKR336_2
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20189 | 125.36 | P12:345:OKGE:BKRBKR349
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22027 | 125.36 | P12:345:OKGE:BKRBKR349
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28626 | 125.36 | P12:345:OKGE:BKRBKR349
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28263 | 125.36 | P12:345:OKGE:BKRBKR349
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33124 | 125.36 | P12:345:OKGE:BKRBKR349
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30405 | 125.36 | P12:345:OKGE:BKRBKR349
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28263 | 125.36 | P12:345:OKGE:BKRBKR349
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21801 | 125.36 | P12:345:OKGE:BKRBKR349
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33124 | 125.36 | P12:345:OKGE:BKRBKR349
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28235 | 125.36 | P12:345:OKGE:BKRBKR349
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20385 | 126.37 | P12:345:OKGE:BKRBKR357_2
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22234 | 126.37 | P12:345:OKGE:BKRBKR357_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28926 | 126.37 | P12:345:OKGE:BKRBKR357_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28558 | 126.37 | P12:345:OKGE:BKRBKR357_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33428 | 126.37 | P12:345:OKGE:BKRBKR357_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30708 | 126.37 | P12:345:OKGE:BKRBKR357_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28558 | 126.37 | P12:345:OKGE:BKRBKR357_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21273 | 126.37 | P12:345:OKGE:BKRBKR357_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33428 | 126.37 | P12:345:OKGE:BKRBKR357_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28531 | 126.37 | P12:345:OKGE:BKRBKR357_2
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22496 | 140.69 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.24197 | 140.69 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30959 | 140.69 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30575 | 140.69 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.35483 | 140.69 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.32837 | 140.69 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30575 | 140.69 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20097 | 140.69 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.35483 | 140.69 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3055 | 140.69 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20529 | 128.33 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22378 | 128.33 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29069 | 128.33 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28701 | 128.33 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3357 | 128.33 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30851 | 128.33 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28701 | 128.33 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21137 | 128.33 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3357 | 128.33 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28673 | 128.33 | P12:345:OKGE:BKRBKR502
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20529 | 128.33 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22378 | 128.33 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29069 | 128.33 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28701 | 128.33 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3357 | 128.33 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30851 | 128.33 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28701 | 128.33 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21137 | 128.33 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3357 | 128.33 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28673 | 128.33 | P12:345:OKGE:BKRBKR503
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 124.8 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 124.8 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 124.8 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 124.8 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 124.8 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 124.8 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 124.8 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 124.8 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 124.8 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 124.8 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 124.99 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 124.99 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 124.99 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 124.99 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 124.99 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 124.99 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 124.99 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 124.99 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 124.99 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 124.99 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20408 | 125.82 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22258 | 125.82 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28951 | 125.82 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28582 | 125.82 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33452 | 125.82 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30733 | 125.82 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28582 | 125.82 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21247 | 125.82 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33452 | 125.82 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28555 | 125.82 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20151 | 123.55 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21991 | 123.55 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28628 | 123.55 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28263 | 123.55 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33128 | 123.55 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3041 | 123.55 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28263 | 123.55 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21723 | 123.55 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33128 | 123.55 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28235 | 123.55 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20924 | 132.86 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2275 | 132.86 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29381 | 132.86 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29015 | 132.86 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33882 | 132.86 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3117 | 132.86 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29015 | 132.86 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21062 | 132.86 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33882 | 132.86 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28988 | 132.86 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22496 | 140.72 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.24197 | 140.72 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30959 | 140.72 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30575 | 140.72 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.35483 | 140.72 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.32837 | 140.72 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30575 | 140.72 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20097 | 140.72 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.35483 | 140.72 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3055 | 140.72 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20504 | 128.41 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22354 | 128.41 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29042 | 128.41 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28674 | 128.41 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33544 | 128.41 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30824 | 128.41 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28674 | 128.41 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21165 | 128.41 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33544 | 128.41 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28647 | 128.41 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20504 | 128.41 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22354 | 128.41 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29042 | 128.41 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28674 | 128.41 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33544 | 128.41 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30824 | 128.41 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28674 | 128.41 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21165 | 128.41 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33544 | 128.41 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28647 | 128.41 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20978 | 131.34 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2283 | 131.34 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29437 | 131.34 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29075 | 131.34 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33934 | 131.34 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3121 | 131.34 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29075 | 131.34 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20895 | 131.34 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33934 | 131.34 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29047 | 131.34 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.25624 | 135.16 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.27211 | 135.16 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.35957 | 135.16 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.35442 | 135.16 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.37989 | 135.16 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.36735 | 135.16 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.35442 | 135.16 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28553 | 135.16 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.37989 | 135.16 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.35482 | 135.16 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20SP | GEN-2017-104 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29638 | 135.16 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2053 | 127.9 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1)
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22381 | 127.9 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29048 | 127.9 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28682 | 127.9 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33548 | 127.9 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30827 | 127.9 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28682 | 127.9 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21185 | 127.9 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33548 | 127.9 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28654 | 127.9 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1)
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20573 | 128.33 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22423 | 128.33 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29107 | 128.33 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28739 | 128.33 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33608 | 128.33 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30888 | 128.33 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28739 | 128.33 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21103 | 128.33 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33608 | 128.33 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28712 | 128.33 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20537 | 128.17 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22387 | 128.17 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29075 | 128.17 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28707 | 128.17 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33576 | 128.17 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30856 | 128.17 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28707 | 128.17 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21128 | 128.17 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33576 | 128.17 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2868 | 128.17 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20536 | 128.78 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22387 | 128.78 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29053 | 128.78 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28686 | 128.78 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33553 | 128.78 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30831 | 128.78 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28686 | 128.78 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21183 | 128.78 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33553 | 128.78 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28659 | 128.78 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20583 | 128.27 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22433 | 128.27 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29117 | 128.27 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28749 | 128.27 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33618 | 128.27 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30898 | 128.27 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28749 | 128.27 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21093 | 128.27 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33618 | 128.27 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28722 | 128.27 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 126.41 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 126.41 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 126.41 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.41 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.41 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 126.41 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.41 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 126.41 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.41 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 126.41 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 126.98 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 126.98 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 126.98 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.98 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.98 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 126.98 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.98 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 126.98 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.98 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 126.98 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20552 | 128.48 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22401 | 128.48 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29066 | 128.48 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28699 | 128.48 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33566 | 128.48 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30844 | 128.48 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28699 | 128.48 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21168 | 128.48 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33566 | 128.48 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28672 | 128.48 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.34 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.34 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.34 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.34 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.34 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.34 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.34 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.34 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.34 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.34 | P13:138-24:AEPW:TURK 4
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.2 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.2 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.2 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.2 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.2 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.2 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.2 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.2 | P13:18-345:OPPD:NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.21 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.21 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.21 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.21 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.21 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.21 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.21 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.21 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.21 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.21 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.2 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.2 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.2 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.2 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.2 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.2 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.2 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.2 | P13:23-345:OPPD:NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.21 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.21 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.21 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.21 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.21 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.21 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.21 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.21 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.21 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.21 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 126.28 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 126.28 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 126.28 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.28 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.28 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 126.28 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.28 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 126.28 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.28 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 126.28 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.21 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.21 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.21 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.21 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.21 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.21 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.21 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.21 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.21 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.21 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.19 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.19 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.19 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.19 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.19 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.19 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.19 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.19 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.19 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.19 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 125.85 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 125.85 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 125.85 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 125.85 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 125.85 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 125.85 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 125.85 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 125.85 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 125.85 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 125.85 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.21 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.21 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.21 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.21 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.21 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.21 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.21 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.21 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.21 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.21 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.2 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.2 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.2 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.2 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.2 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.2 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.2 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.2 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.2 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.2 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.2 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.2 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.2 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.2 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.2 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.2 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.2 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.2 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.2 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.2 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.2 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.2 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.2 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.2 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.2 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.2 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.2 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.2 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.2 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.2 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.2 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.2 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.25624 | 135.17 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.27211 | 135.17 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.35957 | 135.17 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.35442 | 135.17 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.37989 | 135.17 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.36735 | 135.17 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.35442 | 135.17 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28553 | 135.17 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.37989 | 135.17 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.35482 | 135.17 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-104 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29638 | 135.17 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20413 | 126.15 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22263 | 126.15 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2896 | 126.15 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28591 | 126.15 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33462 | 126.15 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30742 | 126.15 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28591 | 126.15 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21228 | 126.15 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33462 | 126.15 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28564 | 126.15 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20413 | 126.17 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22263 | 126.17 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2896 | 126.17 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28591 | 126.17 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33462 | 126.17 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30742 | 126.17 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28591 | 126.17 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21228 | 126.17 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33462 | 126.17 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28564 | 126.17 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20413 | 126.15 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22263 | 126.15 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2896 | 126.15 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28591 | 126.15 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33462 | 126.15 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30742 | 126.15 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28591 | 126.15 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21228 | 126.15 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33462 | 126.15 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28564 | 126.15 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20402 | 126.36 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22252 | 126.36 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28947 | 126.36 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28578 | 126.36 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33448 | 126.36 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30729 | 126.36 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28578 | 126.36 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21246 | 126.36 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33448 | 126.36 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28551 | 126.36 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20402 | 126.36 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22252 | 126.36 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28947 | 126.36 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28578 | 126.36 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33448 | 126.36 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30729 | 126.36 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28578 | 126.36 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21246 | 126.36 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33448 | 126.36 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28551 | 126.36 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20402 | 126.36 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22252 | 126.36 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28947 | 126.36 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28578 | 126.36 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33448 | 126.36 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30729 | 126.36 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28578 | 126.36 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21246 | 126.36 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33448 | 126.36 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28551 | 126.36 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20936 | 132.03 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22761 | 132.03 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29392 | 132.03 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29026 | 132.03 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33893 | 132.03 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31181 | 132.03 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29026 | 132.03 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21057 | 132.03 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33893 | 132.03 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28999 | 132.03 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.23604 | 171.55 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.25241 | 171.55 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31872 | 171.55 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31493 | 171.55 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.36398 | 171.55 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-033 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21278 | 171.55 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33781 | 171.55 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-065 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21278 | 171.55 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31493 | 171.55 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.36398 | 171.55 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31467 | 171.55 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.23719 | 171.96 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.25352 | 171.96 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31952 | 171.96 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31575 | 171.96 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.36476 | 171.96 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-033 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21372 | 171.96 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33859 | 171.96 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-065 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21372 | 171.96 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31575 | 171.96 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.36476 | 171.96 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31548 | 171.96 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20403 | 126.31 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22253 | 126.31 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28948 | 126.31 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2858 | 126.31 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3345 | 126.31 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3073 | 126.31 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2858 | 126.31 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21244 | 126.31 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3345 | 126.31 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28553 | 126.31 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.23603 | 142.05 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2524 | 142.05 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31871 | 142.05 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31492 | 142.05 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.36397 | 142.05 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3378 | 142.05 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31492 | 142.05 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.36397 | 142.05 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31466 | 142.05 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.23603 | 141.48 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2524 | 141.48 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31871 | 141.48 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31492 | 141.48 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.36397 | 141.48 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3378 | 141.48 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31492 | 141.48 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.36397 | 141.48 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31466 | 141.48 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20246 | 125.77 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22094 | 125.77 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28775 | 125.77 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28408 | 125.77 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33276 | 125.77 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30557 | 125.77 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28408 | 125.77 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21451 | 125.77 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33276 | 125.77 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28381 | 125.77 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20363 | 125.99 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22203 | 125.99 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28862 | 125.99 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28495 | 125.99 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33363 | 125.99 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30646 | 125.99 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28495 | 125.99 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21446 | 125.99 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33363 | 125.99 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28468 | 125.99 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20177 | 123.76 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22014 | 123.76 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28646 | 123.76 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28281 | 123.76 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33146 | 123.76 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30429 | 123.76 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28281 | 123.76 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21728 | 123.76 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33146 | 123.76 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28253 | 123.76 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20151 | 123.55 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21991 | 123.55 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28628 | 123.55 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28263 | 123.55 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33128 | 123.55 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3041 | 123.55 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28263 | 123.55 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21723 | 123.55 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33128 | 123.55 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28235 | 123.55 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20924 | 131.87 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2275 | 131.87 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29381 | 131.87 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29015 | 131.87 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33882 | 131.87 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3117 | 131.87 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29015 | 131.87 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21062 | 131.87 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33882 | 131.87 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28988 | 131.87 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20924 | 131.88 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2275 | 131.88 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29381 | 131.88 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29015 | 131.88 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33882 | 131.88 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3117 | 131.88 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29015 | 131.88 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21062 | 131.88 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33882 | 131.88 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28988 | 131.88 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20924 | 131.84 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2275 | 131.84 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29381 | 131.84 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29015 | 131.84 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33882 | 131.84 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3117 | 131.84 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29015 | 131.84 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21062 | 131.84 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33882 | 131.84 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28988 | 131.84 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20467 | 128.2 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22317 | 128.2 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29014 | 128.2 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28645 | 128.2 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33516 | 128.2 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30796 | 128.2 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28645 | 128.2 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21176 | 128.2 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33516 | 128.2 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28618 | 128.2 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.23 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.23 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.23 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28609 | 127.23 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.23 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3076 | 127.23 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28609 | 127.23 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.23 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.23 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28582 | 127.23 | P23:345:MEC:CBEC 905
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.21 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.21 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.21 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.21 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.21 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.21 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.21 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.21 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.21 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.21 | P23:345:MEC:CBEC 908
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 125.85 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 125.85 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 125.85 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 125.85 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 125.85 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 125.85 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 125.85 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 125.85 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 125.85 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 125.85 | P23:345:MEC:RAUN 0210
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.2 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.2 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.2 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.2 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.2 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.2 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.2 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.2 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.2 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.2 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.2 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.2 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.2 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.2 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.2 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.2 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.2 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.2 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.2 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.2 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.2 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.2 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.2 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.2 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.2 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.2 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.2 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.2 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.2 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.2 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.2 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.2 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2053 | 128.25 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22381 | 128.25 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29048 | 128.25 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28682 | 128.25 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33548 | 128.25 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30827 | 128.25 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28682 | 128.25 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21185 | 128.25 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33548 | 128.25 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28654 | 128.25 | P23:345:SUNC:BU_BRK688
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2053 | 127.88 | P23:345:SUNC:HLC_BRK182
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22381 | 127.88 | P23:345:SUNC:HLC_BRK182
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29048 | 127.88 | P23:345:SUNC:HLC_BRK182
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28682 | 127.88 | P23:345:SUNC:HLC_BRK182
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33548 | 127.88 | P23:345:SUNC:HLC_BRK182
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30827 | 127.88 | P23:345:SUNC:HLC_BRK182
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28682 | 127.88 | P23:345:SUNC:HLC_BRK182
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21185 | 127.88 | P23:345:SUNC:HLC_BRK182
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33548 | 127.88 | P23:345:SUNC:HLC_BRK182
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28654 | 127.88 | P23:345:SUNC:HLC_BRK182
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20965 | 131.3 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22817 | 131.3 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29422 | 131.3 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2906 | 131.3 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33919 | 131.3 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31195 | 131.3 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2906 | 131.3 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20913 | 131.3 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33919 | 131.3 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29032 | 131.3 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21004 | 131.51 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22856 | 131.51 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29462 | 131.51 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29099 | 131.51 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33958 | 131.51 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31234 | 131.51 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29099 | 131.51 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20874 | 131.51 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33958 | 131.51 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29071 | 131.51 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20545 | 128.17 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22396 | 128.17 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29083 | 128.17 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28715 | 128.17 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33584 | 128.17 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30864 | 128.17 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28715 | 128.17 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21121 | 128.17 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33584 | 128.17 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28688 | 128.17 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20573 | 128.33 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22423 | 128.33 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29107 | 128.33 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28739 | 128.33 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33608 | 128.33 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30888 | 128.33 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28739 | 128.33 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21103 | 128.33 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33608 | 128.33 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28712 | 128.33 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20583 | 128.27 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22433 | 128.27 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29117 | 128.27 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28749 | 128.27 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33618 | 128.27 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30898 | 128.27 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28749 | 128.27 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21093 | 128.27 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33618 | 128.27 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28722 | 128.27 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20573 | 128.33 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22423 | 128.33 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29107 | 128.33 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28739 | 128.33 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33608 | 128.33 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30888 | 128.33 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28739 | 128.33 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21103 | 128.33 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33608 | 128.33 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28712 | 128.33 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20583 | 128.27 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22433 | 128.27 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29117 | 128.27 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28749 | 128.27 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33618 | 128.27 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30898 | 128.27 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28749 | 128.27 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21093 | 128.27 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33618 | 128.27 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28722 | 128.27 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20579 | 128.44 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2243 | 128.44 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29113 | 128.44 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28745 | 128.44 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33614 | 128.44 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30894 | 128.44 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28745 | 128.44 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21098 | 128.44 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33614 | 128.44 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28718 | 128.44 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20579 | 128.42 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2243 | 128.42 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29113 | 128.42 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28745 | 128.42 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33614 | 128.42 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30894 | 128.42 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28745 | 128.42 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21098 | 128.42 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33614 | 128.42 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28718 | 128.42 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20579 | 128.44 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2243 | 128.44 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29113 | 128.44 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28745 | 128.44 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33614 | 128.44 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30894 | 128.44 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28745 | 128.44 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21098 | 128.44 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33614 | 128.44 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28718 | 128.44 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20529 | 128.59 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2238 | 128.59 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29047 | 128.59 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28681 | 128.59 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33547 | 128.59 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30826 | 128.59 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28681 | 128.59 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21186 | 128.59 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33547 | 128.59 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28654 | 128.59 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20514 | 128.59 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22363 | 128.59 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2905 | 128.59 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28682 | 128.59 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33552 | 128.59 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30832 | 128.59 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28682 | 128.59 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2116 | 128.59 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33552 | 128.59 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28655 | 128.59 | P23:345:WERE:BUFF_345-534::
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20514 | 128.59 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22363 | 128.59 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2905 | 128.59 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28682 | 128.59 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33552 | 128.59 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30832 | 128.59 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28682 | 128.59 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2116 | 128.59 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33552 | 128.59 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28655 | 128.59 | P23:345:WERE:BUFF_345-543::
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.1 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.1 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.1 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.1 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.1 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.1 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.1 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.1 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.1 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.1 | P23:345:WERE:JEC_345-15::
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.1 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.1 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.1 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.1 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.1 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.1 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.1 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.1 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.1 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.1 | P23:345:WERE:JEC_345-19::
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2043 | 127.1 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2228 | 127.1 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28979 | 127.1 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28611 | 127.1 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33481 | 127.1 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30762 | 127.1 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28611 | 127.1 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21204 | 127.1 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33481 | 127.1 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28584 | 127.1 | P23:345:WERE:JEC_345-20::
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.21 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.21 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.21 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.21 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.21 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.21 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.21 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.21 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.21 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.21 | P23:345:XEL:8N17 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 126.27 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 126.27 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 126.27 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.27 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.27 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 126.27 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.27 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 126.27 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 126.27 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28582 | 126.27 | P23:345:XEL:8N22 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.2 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.2 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.2 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.2 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.2 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.2 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.2 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.2 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 127.2 | P23:345:XEL:8N28 SHC
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 127.19 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 127.19 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 127.19 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.19 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.19 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 127.19 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 127.19 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 127.19 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3348 | 127.19 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28582 | 127.19 | P23:345:XEL:8N8 MNN
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20417 | 125.87 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22267 | 125.87 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28965 | 125.87 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28596 | 125.87 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33467 | 125.87 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30747 | 125.87 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28596 | 125.87 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21221 | 125.87 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33467 | 125.87 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28569 | 125.87 | P23:500:EES-EAI:KEO:B4921
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20416 | 125.77 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22266 | 125.77 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28964 | 125.77 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28595 | 125.77 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33466 | 125.77 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30746 | 125.77 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28595 | 125.77 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21222 | 125.77 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33466 | 125.77 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28568 | 125.77 | P23:500:EES-EAI:KEO:B4941
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20411 | 127.18 | P41:345:OKGE:SB_SEOL7382
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22259 | 127.18 | P41:345:OKGE:SB_SEOL7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28937 | 127.18 | P41:345:OKGE:SB_SEOL7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2857 | 127.18 | P41:345:OKGE:SB_SEOL7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33438 | 127.18 | P41:345:OKGE:SB_SEOL7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30719 | 127.18 | P41:345:OKGE:SB_SEOL7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2857 | 127.18 | P41:345:OKGE:SB_SEOL7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21297 | 127.18 | P41:345:OKGE:SB_SEOL7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33438 | 127.18 | P41:345:OKGE:SB_SEOL7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28543 | 127.18 | P41:345:OKGE:SB_SEOL7382
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20396 | 126.65 | P41:345:OKGE:SB_SEOL7383
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22241 | 126.65 | P41:345:OKGE:SB_SEOL7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28902 | 126.65 | P41:345:OKGE:SB_SEOL7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28535 | 126.65 | P41:345:OKGE:SB_SEOL7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33402 | 126.65 | P41:345:OKGE:SB_SEOL7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30683 | 126.65 | P41:345:OKGE:SB_SEOL7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28535 | 126.65 | P41:345:OKGE:SB_SEOL7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21377 | 126.65 | P41:345:OKGE:SB_SEOL7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33402 | 126.65 | P41:345:OKGE:SB_SEOL7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28508 | 126.65 | P41:345:OKGE:SB_SEOL7383
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20413 | 126.17 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22263 | 126.17 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2896 | 126.17 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28591 | 126.17 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33462 | 126.17 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30742 | 126.17 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28591 | 126.17 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21228 | 126.17 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33462 | 126.17 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28564 | 126.17 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20413 | 126.15 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22263 | 126.15 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2896 | 126.15 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28591 | 126.15 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33462 | 126.15 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30742 | 126.15 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28591 | 126.15 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21228 | 126.15 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33462 | 126.15 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28564 | 126.15 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20402 | 126.36 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22252 | 126.36 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28947 | 126.36 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28578 | 126.36 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33448 | 126.36 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30729 | 126.36 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28578 | 126.36 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21246 | 126.36 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33448 | 126.36 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28551 | 126.36 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20402 | 126.36 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22252 | 126.36 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28947 | 126.36 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28578 | 126.36 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33448 | 126.36 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30729 | 126.36 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28578 | 126.36 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21246 | 126.36 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33448 | 126.36 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28551 | 126.36 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20402 | 126.36 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22252 | 126.36 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28947 | 126.36 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28578 | 126.36 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33448 | 126.36 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30729 | 126.36 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28578 | 126.36 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21246 | 126.36 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33448 | 126.36 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28551 | 126.36 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20936 | 132.03 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22761 | 132.03 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29392 | 132.03 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29026 | 132.03 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33893 | 132.03 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31181 | 132.03 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29026 | 132.03 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21057 | 132.03 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33893 | 132.03 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28999 | 132.03 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.23719 | 171.96 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.25352 | 171.96 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31952 | 171.96 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31575 | 171.96 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.36476 | 171.96 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-033 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21372 | 171.96 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33859 | 171.96 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-065 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21372 | 171.96 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31575 | 171.96 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.36476 | 171.96 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31548 | 171.96 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20403 | 126.31 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22253 | 126.31 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28948 | 126.31 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2858 | 126.31 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3345 | 126.31 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3073 | 126.31 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2858 | 126.31 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21244 | 126.31 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3345 | 126.31 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28553 | 126.31 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.23603 | 142.05 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2524 | 142.05 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31871 | 142.05 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31492 | 142.05 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.36397 | 142.05 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3378 | 142.05 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31492 | 142.05 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.36397 | 142.05 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31466 | 142.05 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.23603 | 141.48 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2524 | 141.48 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31871 | 141.48 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31492 | 141.48 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.36397 | 141.48 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3378 | 141.48 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31492 | 141.48 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.36397 | 141.48 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31466 | 141.48 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20246 | 125.77 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22094 | 125.77 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28775 | 125.77 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28408 | 125.77 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33276 | 125.77 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30557 | 125.77 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28408 | 125.77 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21451 | 125.77 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33276 | 125.77 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28381 | 125.77 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20363 | 125.99 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22203 | 125.99 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28862 | 125.99 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28495 | 125.99 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33363 | 125.99 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30646 | 125.99 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28495 | 125.99 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21446 | 125.99 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33363 | 125.99 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28468 | 125.99 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20177 | 123.76 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22014 | 123.76 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28646 | 123.76 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28281 | 123.76 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33146 | 123.76 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30429 | 123.76 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28281 | 123.76 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21728 | 123.76 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33146 | 123.76 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28253 | 123.76 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20151 | 123.55 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21991 | 123.55 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28628 | 123.55 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28263 | 123.55 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33128 | 123.55 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3041 | 123.55 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28263 | 123.55 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21723 | 123.55 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33128 | 123.55 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28235 | 123.55 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20924 | 131.87 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2275 | 131.87 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29381 | 131.87 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29015 | 131.87 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33882 | 131.87 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3117 | 131.87 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29015 | 131.87 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21062 | 131.87 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33882 | 131.87 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28988 | 131.87 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20924 | 131.88 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2275 | 131.88 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29381 | 131.88 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29015 | 131.88 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33882 | 131.88 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3117 | 131.88 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29015 | 131.88 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21062 | 131.88 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33882 | 131.88 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28988 | 131.88 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20924 | 131.84 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2275 | 131.84 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29381 | 131.84 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29015 | 131.84 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33882 | 131.84 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3117 | 131.84 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29015 | 131.84 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21062 | 131.84 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33882 | 131.84 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28988 | 131.84 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20429 | 126.61 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22279 | 126.61 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28979 | 126.61 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.61 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33481 | 126.61 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30761 | 126.61 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2861 | 126.61 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21204 | 126.61 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33481 | 126.61 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28583 | 126.61 | P42:345:NPPD:BKR-GGS-3304
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20593 | 128.37 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22444 | 128.37 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29127 | 128.37 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2876 | 128.37 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33628 | 128.37 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30908 | 128.37 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2876 | 128.37 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21084 | 128.37 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33628 | 128.37 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28732 | 128.37 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20448 | 128.01 | P42:345:NPPD:BKR-SW-3308
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22298 | 128.01 | P42:345:NPPD:BKR-SW-3308
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28995 | 128.01 | P42:345:NPPD:BKR-SW-3308
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28627 | 128.01 | P42:345:NPPD:BKR-SW-3308
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33497 | 128.01 | P42:345:NPPD:BKR-SW-3308
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30777 | 128.01 | P42:345:NPPD:BKR-SW-3308
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28627 | 128.01 | P42:345:NPPD:BKR-SW-3308
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21192 | 128.01 | P42:345:NPPD:BKR-SW-3308
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33497 | 128.01 | P42:345:NPPD:BKR-SW-3308
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.286 | 128.01 | P42:345:NPPD:BKR-SW-3308
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2019 | 125.35 | P42:345:OKGE:SB_ARIA7381
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22028 | 125.35 | P42:345:OKGE:SB_ARIA7381
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28627 | 125.35 | P42:345:OKGE:SB_ARIA7381
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28264 | 125.35 | P42:345:OKGE:SB_ARIA7381
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33125 | 125.35 | P42:345:OKGE:SB_ARIA7381
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30406 | 125.35 | P42:345:OKGE:SB_ARIA7381
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28264 | 125.35 | P42:345:OKGE:SB_ARIA7381
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.218 | 125.35 | P42:345:OKGE:SB_ARIA7381
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33125 | 125.35 | P42:345:OKGE:SB_ARIA7381
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28236 | 125.35 | P42:345:OKGE:SB_ARIA7381
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22331 | 144.54 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.24224 | 144.54 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30243 | 144.54 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29924 | 144.54 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.34706 | 144.54 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31941 | 144.54 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29924 | 144.54 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20858 | 144.54 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.34706 | 144.54 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2989 | 144.54 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22496 | 140.72 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.24197 | 140.72 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30959 | 140.72 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30575 | 140.72 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.35483 | 140.72 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.32837 | 140.72 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30575 | 140.72 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20097 | 140.72 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.35483 | 140.72 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3055 | 140.72 | P42:345:OKGE:SB_BOER7304
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22496 | 140.69 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.24197 | 140.69 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30959 | 140.69 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30575 | 140.69 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.35483 | 140.69 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.32837 | 140.69 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30575 | 140.69 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20097 | 140.69 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.35483 | 140.69 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3055 | 140.69 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22496 | 140.72 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.24197 | 140.72 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30959 | 140.72 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30575 | 140.72 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.35483 | 140.72 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.32837 | 140.72 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30575 | 140.72 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20097 | 140.72 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.35483 | 140.72 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3055 | 140.72 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20527 | 125.65 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22379 | 125.65 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29044 | 125.65 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28677 | 125.65 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33543 | 125.65 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30822 | 125.65 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28677 | 125.65 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21187 | 125.65 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33543 | 125.65 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2865 | 125.65 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20527 | 125.47 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2238 | 125.47 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29044 | 125.47 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28678 | 125.47 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33544 | 125.47 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30822 | 125.47 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28678 | 125.47 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21187 | 125.47 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33544 | 125.47 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2865 | 125.47 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20826 | 130.18 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22657 | 130.18 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29301 | 130.18 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28935 | 130.18 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33802 | 130.18 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31087 | 130.18 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28935 | 130.18 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21072 | 130.18 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33802 | 130.18 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28908 | 130.18 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20391 | 125.45 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22236 | 125.45 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28894 | 125.45 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28528 | 125.45 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33394 | 125.45 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30675 | 125.45 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28528 | 125.45 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21391 | 125.45 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33394 | 125.45 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.285 | 125.45 | P42:345:OKGE:SB_DRER7382
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20391 | 125.41 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22236 | 125.41 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28894 | 125.41 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28528 | 125.41 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33394 | 125.41 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30675 | 125.41 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28528 | 125.41 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21391 | 125.41 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33394 | 125.41 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.285 | 125.41 | P42:345:OKGE:SB_DRER7383
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20826 | 130.48 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22657 | 130.48 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29301 | 130.48 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28935 | 130.48 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33802 | 130.48 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31087 | 130.48 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28935 | 130.48 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21072 | 130.48 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33802 | 130.48 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28908 | 130.48 | P42:345:OKGE:SB_MICO7301
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20826 | 129.68 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22657 | 129.68 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29301 | 129.68 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28935 | 129.68 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33802 | 129.68 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31087 | 129.68 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28935 | 129.68 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21072 | 129.68 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33802 | 129.68 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28908 | 129.68 | P42:345:OKGE:SB_MICO7312
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20405 | 125.56 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22255 | 125.56 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28946 | 125.56 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28578 | 125.56 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33448 | 125.56 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30728 | 125.56 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28578 | 125.56 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21254 | 125.56 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33448 | 125.56 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28551 | 125.56 | P42:345:OKGE:SB_MUGE7387
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20385 | 125.68 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22234 | 125.68 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28926 | 125.68 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28558 | 125.68 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33428 | 125.68 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30708 | 125.68 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28558 | 125.68 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21273 | 125.68 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33428 | 125.68 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28531 | 125.68 | P42:345:OKGE:SB_OPKY7388
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20385 | 126.16 | P42:345:OKGE:SB_RARD7311
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22234 | 126.16 | P42:345:OKGE:SB_RARD7311
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28926 | 126.16 | P42:345:OKGE:SB_RARD7311
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28558 | 126.16 | P42:345:OKGE:SB_RARD7311
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33428 | 126.16 | P42:345:OKGE:SB_RARD7311
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30708 | 126.16 | P42:345:OKGE:SB_RARD7311
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28558 | 126.16 | P42:345:OKGE:SB_RARD7311
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21273 | 126.16 | P42:345:OKGE:SB_RARD7311
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33428 | 126.16 | P42:345:OKGE:SB_RARD7311
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28531 | 126.16 | P42:345:OKGE:SB_RARD7311
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20385 | 126.37 | P42:345:OKGE:SB_RARD7393
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22234 | 126.37 | P42:345:OKGE:SB_RARD7393
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28926 | 126.37 | P42:345:OKGE:SB_RARD7393
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28558 | 126.37 | P42:345:OKGE:SB_RARD7393
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33428 | 126.37 | P42:345:OKGE:SB_RARD7393
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30708 | 126.37 | P42:345:OKGE:SB_RARD7393
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28558 | 126.37 | P42:345:OKGE:SB_RARD7393
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21273 | 126.37 | P42:345:OKGE:SB_RARD7393
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33428 | 126.37 | P42:345:OKGE:SB_RARD7393
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28531 | 126.37 | P42:345:OKGE:SB_RARD7393
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20381 | 125.86 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22231 | 125.86 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28922 | 125.86 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28553 | 125.86 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33423 | 125.86 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30703 | 125.86 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28553 | 125.86 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21279 | 125.86 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33423 | 125.86 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28526 | 125.86 | P42:345:OKGE:SB_REOW7312
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20376 | 126.3 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22226 | 126.3 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28916 | 126.3 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28547 | 126.3 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33417 | 126.3 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30697 | 126.3 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28547 | 126.3 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21286 | 126.3 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33417 | 126.3 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2852 | 126.3 | P42:345:OKGE:SB_REOW7389
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2012 | 123.28 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2195 | 123.28 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28489 | 123.28 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2813 | 123.28 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.32985 | 123.28 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30268 | 123.28 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2813 | 123.28 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22085 | 123.28 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.32985 | 123.28 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28102 | 123.28 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20088 | 122.47 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21925 | 122.47 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28542 | 122.47 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28178 | 122.47 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33041 | 122.47 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30324 | 122.47 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28178 | 122.47 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21861 | 122.47 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33041 | 122.47 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2815 | 122.47 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20579 | 128.58 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22425 | 128.58 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29069 | 128.58 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28703 | 128.58 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33568 | 128.58 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30849 | 128.58 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28703 | 128.58 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21239 | 128.58 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33568 | 128.58 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28676 | 128.58 | P42:345:OKGE:SB_TAGA7381
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2038 | 126.42 | P42:345:OKGE:SB_WONG7383
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2223 | 126.42 | P42:345:OKGE:SB_WONG7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2892 | 126.42 | P42:345:OKGE:SB_WONG7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28552 | 126.42 | P42:345:OKGE:SB_WONG7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33421 | 126.42 | P42:345:OKGE:SB_WONG7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30701 | 126.42 | P42:345:OKGE:SB_WONG7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28552 | 126.42 | P42:345:OKGE:SB_WONG7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21283 | 126.42 | P42:345:OKGE:SB_WONG7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33421 | 126.42 | P42:345:OKGE:SB_WONG7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28524 | 126.42 | P42:345:OKGE:SB_WONG7383
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20568 | 128.46 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22415 | 128.46 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29064 | 128.46 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28698 | 128.46 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33563 | 128.46 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30844 | 128.46 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28698 | 128.46 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21233 | 128.46 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33563 | 128.46 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28671 | 128.46 | P42:345:OKGE:SB_WWHV7382
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20568 | 128.47 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22415 | 128.47 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29064 | 128.47 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28698 | 128.47 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33563 | 128.47 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30844 | 128.47 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28698 | 128.47 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21233 | 128.47 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33563 | 128.47 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28671 | 128.47 | P42:345:OKGE:SB_WWHV7383
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20978 | 134.51 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2283 | 134.51 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29437 | 134.51 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29075 | 134.51 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33934 | 134.51 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3121 | 134.51 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29075 | 134.51 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20895 | 134.51 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33934 | 134.51 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29047 | 134.51 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22283 | 138.04 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.24183 | 138.04 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30366 | 138.04 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30035 | 138.04 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.34839 | 138.04 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.32087 | 138.04 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30035 | 138.04 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20552 | 138.04 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.34839 | 138.04 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30003 | 138.04 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20431 | 126.49 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22281 | 126.49 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2898 | 126.49 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28611 | 126.49 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33482 | 126.49 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30762 | 126.49 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28611 | 126.49 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21203 | 126.49 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33482 | 126.49 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28584 | 126.49 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20413 | 126.15 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22263 | 126.15 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.2896 | 126.15 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28591 | 126.15 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33462 | 126.15 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30742 | 126.15 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28591 | 126.15 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21228 | 126.15 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33462 | 126.15 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28564 | 126.15 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.23604 | 171.55 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.25241 | 171.55 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31872 | 171.55 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31493 | 171.55 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.36398 | 171.55 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-033 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21278 | 171.55 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33781 | 171.55 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-065 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21278 | 171.55 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31493 | 171.55 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.36398 | 171.55 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.31467 | 171.55 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20467 | 128.2 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22317 | 128.2 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.29014 | 128.2 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28645 | 128.2 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33516 | 128.2 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30796 | 128.2 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28645 | 128.2 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21176 | 128.2 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33516 | 128.2 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28618 | 128.2 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22496 | 140.72 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.24197 | 140.72 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30959 | 140.72 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30575 | 140.72 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.35483 | 140.72 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.32837 | 140.72 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.30575 | 140.72 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20097 | 140.72 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.35483 | 140.72 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3055 | 140.72 | P43:345:SPS:TUCO:NR20_19L
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.20428 | 126.4 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.22278 | 126.4 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28978 | 126.4 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28609 | 126.4 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33479 | 126.4 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.3076 | 126.4 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28609 | 126.4 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.21205 | 126.4 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.33479 | 126.4 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 |  | 553 | 0.28582 | 126.4 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 | 478 |  | 0.20429 | 147.21 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 | 478 |  | 0.22279 | 147.21 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 | 478 |  | 0.28978 | 147.21 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 | 478 |  | 0.2861 | 147.21 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 | 478 |  | 0.3348 | 147.21 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 | 478 |  | 0.30761 | 147.21 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 | 478 |  | 0.2861 | 147.21 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 | 478 |  | 0.21205 | 147.21 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 | 478 |  | 0.3348 | 147.21 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 | 478 |  | 0.28583 | 147.21 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998088 TOLK2 230 2 |  | 553 | 0.21079 | 100.66 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998088 TOLK2 230 2 |  | 553 | 0.21079 | 100.66 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998088 TOLK2 230 2 | 478 |  | 0.06831 | 101.74 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998088 TOLK2 230 2 | 478 |  | 0.09467 | 101.74 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998088 TOLK2 230 2 | 478 |  | 0.17368 | 101.74 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998088 TOLK2 230 2 | 478 |  | 0.16977 | 101.74 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998088 TOLK2 230 2 | 478 |  | 0.20698 | 101.74 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998088 TOLK2 230 2 | 478 |  | 0.1825 | 101.74 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998088 TOLK2 230 2 | 478 |  | 0.16977 | 101.74 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998088 TOLK2 230 2 | 478 |  | 0.07567 | 101.74 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998088 TOLK2 230 2 | 478 |  | 0.20698 | 101.74 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998088 TOLK2 230 2 | 478 |  | 0.16975 | 101.74 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.22066 | 108.82 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21633 | 108.82 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26567 | 108.82 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.23257 | 108.82 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21633 | 108.82 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26567 | 108.82 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21615 | 108.82 | P12:115:SPS:T30.1.LAMB.HOCKLY
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.22066 | 107.47 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21633 | 107.47 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26567 | 107.47 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.23257 | 107.47 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21633 | 107.47 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26567 | 107.47 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21615 | 107.47 | P12:115:SPS:T31.1.HOCKLY.SUNDWN
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.2177 | 106.4 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21297 | 106.4 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26239 | 106.4 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.23045 | 106.4 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21297 | 106.4 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26239 | 106.4 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21301 | 106.4 | P12:115:SPS:T45.1.NORRIS.OASIS
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.22387 | 107.21 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.22169 | 107.21 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26384 | 107.21 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.23184 | 107.21 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.22169 | 107.21 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26384 | 107.21 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.22128 | 107.21 | P12:115:SPS:T59.1.CARGIL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21961 | 108.18 | P12:115:SPS:V08.1.TUCO.HALECTR
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21539 | 108.18 | P12:115:SPS:V08.1.TUCO.HALECTR
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26397 | 108.18 | P12:115:SPS:V08.1.TUCO.HALECTR
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.2317 | 108.18 | P12:115:SPS:V08.1.TUCO.HALECTR
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21539 | 108.18 | P12:115:SPS:V08.1.TUCO.HALECTR
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26397 | 108.18 | P12:115:SPS:V08.1.TUCO.HALECTR
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21521 | 108.18 | P12:115:SPS:V08.1.TUCO.HALECTR
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.22017 | 107.66 | P12:115:SPS:V09.1.HALECTR.PLANTX
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21594 | 107.66 | P12:115:SPS:V09.1.HALECTR.PLANTX
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26444 | 107.66 | P12:115:SPS:V09.1.HALECTR.PLANTX
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.2323 | 107.66 | P12:115:SPS:V09.1.HALECTR.PLANTX
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21594 | 107.66 | P12:115:SPS:V09.1.HALECTR.PLANTX
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26444 | 107.66 | P12:115:SPS:V09.1.HALECTR.PLANTX
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21577 | 107.66 | P12:115:SPS:V09.1.HALECTR.PLANTX
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21837 | 106.36 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21388 | 106.36 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26324 | 106.36 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.23097 | 106.36 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21388 | 106.36 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26324 | 106.36 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21373 | 106.36 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.22027 | 107.16 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21605 | 107.16 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26443 | 107.16 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.2324 | 107.16 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21605 | 107.16 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26443 | 107.16 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21588 | 107.16 | P12:115:SPS:W40.1.WCANYON.DFSMTH
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21767 | 107.53 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26238 | 107.53 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.23044 | 107.53 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26238 | 107.53 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21301 | 107.53 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21802 | 106.58 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21417 | 106.58 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.2624 | 106.58 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.23046 | 106.58 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21417 | 106.58 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.2624 | 106.58 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21379 | 106.58 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.22163 | 114.92 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21731 | 114.92 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26617 | 114.92 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.23401 | 114.92 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21731 | 114.92 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26617 | 114.92 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21714 | 114.92 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.22163 | 112.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21731 | 112.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26617 | 112.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.23401 | 112.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21731 | 112.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26617 | 112.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21714 | 112.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.22002 | 108.62 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21483 | 108.62 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26663 | 108.62 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.23385 | 108.62 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21483 | 108.62 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26663 | 108.62 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21476 | 108.62 | P12:230:SPS:K37.1.TOLK.LAMB
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21599 | 103.95 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21149 | 103.95 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26067 | 103.95 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.2287 | 103.95 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21149 | 103.95 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26067 | 103.95 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21135 | 103.95 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21675 | 105.19 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21223 | 105.19 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26144 | 105.19 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.22949 | 105.19 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21223 | 105.19 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26144 | 105.19 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21209 | 105.19 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21797 | 107.58 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21345 | 107.58 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26267 | 107.58 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.23073 | 107.58 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21345 | 107.58 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26267 | 107.58 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21331 | 107.58 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21783 | 107.62 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21332 | 107.62 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26252 | 107.62 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.23057 | 107.62 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21332 | 107.62 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26252 | 107.62 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21318 | 107.62 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21783 | 107.62 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21332 | 107.62 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26252 | 107.62 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.23057 | 107.62 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21332 | 107.62 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26252 | 107.62 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21318 | 107.62 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21492 | 105.12 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21045 | 105.12 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.25958 | 105.12 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.22758 | 105.12 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21045 | 105.12 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.25958 | 105.12 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.2103 | 105.12 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21767 | 105.51 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21315 | 105.51 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26238 | 105.51 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.23044 | 105.51 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21315 | 105.51 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26238 | 105.51 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21301 | 105.51 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21767 | 105.43 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21315 | 105.43 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26238 | 105.43 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.23044 | 105.43 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21315 | 105.43 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26238 | 105.43 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21301 | 105.43 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21675 | 105.19 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21223 | 105.19 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26144 | 105.19 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.22949 | 105.19 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21223 | 105.19 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26144 | 105.19 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21209 | 105.19 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21797 | 107.58 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21345 | 107.58 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26267 | 107.58 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.23073 | 107.58 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21345 | 107.58 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26267 | 107.58 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21331 | 107.58 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21967 | 108.46 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21518 | 108.46 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26434 | 108.46 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.23237 | 108.46 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21518 | 108.46 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26434 | 108.46 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21504 | 108.46 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.23797 | 111.24 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.23246 | 111.24 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26916 | 111.24 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.24366 | 111.24 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.23246 | 111.24 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26916 | 111.24 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.23272 | 111.24 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21804 | 107.11 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21353 | 107.11 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26273 | 107.11 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.23078 | 107.11 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21353 | 107.11 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26273 | 107.11 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21339 | 107.11 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.23797 | 111.27 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.23246 | 111.27 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26916 | 111.27 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.24366 | 111.27 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.23246 | 111.27 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26916 | 111.27 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.23272 | 111.27 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21599 | 103.94 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21149 | 103.94 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26067 | 103.94 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.2287 | 103.94 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21149 | 103.94 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26067 | 103.94 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21135 | 103.94 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21612 | 104.38 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21163 | 104.38 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26079 | 104.38 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.22881 | 104.38 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21163 | 104.38 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26079 | 104.38 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21148 | 104.38 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21599 | 103.95 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21149 | 103.95 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26067 | 103.95 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.2287 | 103.95 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21149 | 103.95 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26067 | 103.95 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21135 | 103.95 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21704 | 105.63 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21252 | 105.63 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26174 | 105.63 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.22979 | 105.63 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21252 | 105.63 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26174 | 105.63 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21238 | 105.63 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21746 | 105.84 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21294 | 105.84 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26216 | 105.84 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.23021 | 105.84 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21294 | 105.84 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26216 | 105.84 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.2128 | 105.84 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.2168 | 105.14 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21228 | 105.14 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26149 | 105.14 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.22955 | 105.14 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21228 | 105.14 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26149 | 105.14 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21214 | 105.14 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21675 | 105.19 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21223 | 105.19 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26144 | 105.19 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.22949 | 105.19 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21223 | 105.19 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26144 | 105.19 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21209 | 105.19 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21797 | 107.46 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21345 | 107.46 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26267 | 107.46 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.23073 | 107.46 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21345 | 107.46 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26267 | 107.46 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21331 | 107.46 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21797 | 107.46 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21345 | 107.46 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26267 | 107.46 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.23073 | 107.46 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21345 | 107.46 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26267 | 107.46 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21331 | 107.46 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21797 | 107.5 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21345 | 107.5 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26267 | 107.5 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.23073 | 107.5 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21345 | 107.5 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26267 | 107.5 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21331 | 107.5 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21741 | 105.89 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21289 | 105.89 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26211 | 105.89 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.23017 | 105.89 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21289 | 105.89 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26211 | 105.89 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21275 | 105.89 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.2196 | 108.35 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21511 | 108.35 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26427 | 108.35 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.23229 | 108.35 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21511 | 108.35 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26427 | 108.35 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21497 | 108.35 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21976 | 108.45 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21527 | 108.45 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26443 | 108.45 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.23245 | 108.45 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21527 | 108.45 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26443 | 108.45 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21513 | 108.45 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21612 | 104.38 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21163 | 104.38 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26079 | 104.38 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.22881 | 104.38 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21163 | 104.38 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26079 | 104.38 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21148 | 104.38 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21599 | 103.95 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21149 | 103.95 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26067 | 103.95 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.2287 | 103.95 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21149 | 103.95 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26067 | 103.95 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21135 | 103.95 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21704 | 105.63 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21252 | 105.63 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26174 | 105.63 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.22979 | 105.63 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21252 | 105.63 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26174 | 105.63 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21238 | 105.63 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21746 | 105.84 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21294 | 105.84 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26216 | 105.84 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.23021 | 105.84 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21294 | 105.84 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26216 | 105.84 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.2128 | 105.84 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.2168 | 105.14 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21228 | 105.14 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26149 | 105.14 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.22955 | 105.14 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21228 | 105.14 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26149 | 105.14 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21214 | 105.14 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21675 | 105.19 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21223 | 105.19 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26144 | 105.19 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.22949 | 105.19 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21223 | 105.19 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26144 | 105.19 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21209 | 105.19 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21797 | 107.46 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21345 | 107.46 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26267 | 107.46 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.23073 | 107.46 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21345 | 107.46 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26267 | 107.46 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21331 | 107.46 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21797 | 107.46 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21345 | 107.46 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26267 | 107.46 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.23073 | 107.46 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21345 | 107.46 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26267 | 107.46 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21331 | 107.46 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21797 | 107.5 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21345 | 107.5 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26267 | 107.5 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.23073 | 107.5 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21345 | 107.5 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26267 | 107.5 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21331 | 107.5 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21741 | 105.89 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21289 | 105.89 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26211 | 105.89 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.23017 | 105.89 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21289 | 105.89 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26211 | 105.89 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21275 | 105.89 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.2243 | 125.5 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.22012 | 125.5 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26872 | 125.5 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.23638 | 125.5 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.22012 | 125.5 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26872 | 125.5 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21994 | 125.5 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21079 | 100.66 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21079 | 100.66 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21492 | 105.12 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21045 | 105.12 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.25958 | 105.12 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.22758 | 105.12 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21045 | 105.12 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.25958 | 105.12 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.2103 | 105.12 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21492 | 105.12 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21045 | 105.12 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.25958 | 105.12 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.22758 | 105.12 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21045 | 105.12 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.25958 | 105.12 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.2103 | 105.12 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21576 | 105.57 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21126 | 105.57 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26044 | 105.57 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.22848 | 105.57 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21126 | 105.57 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26044 | 105.57 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21112 | 105.57 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21653 | 104.83 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21202 | 104.83 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26122 | 104.83 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.22927 | 104.83 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21202 | 104.83 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26122 | 104.83 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21188 | 104.83 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21967 | 112.85 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21518 | 112.85 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26434 | 112.85 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.23237 | 112.85 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21518 | 112.85 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26434 | 112.85 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21504 | 112.85 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.22475 | 118.57 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.22047 | 118.57 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26926 | 118.57 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.23704 | 118.57 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.22047 | 118.57 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26926 | 118.57 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.2203 | 118.57 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21599 | 103.94 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21149 | 103.94 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26067 | 103.94 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.2287 | 103.94 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21149 | 103.94 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.26067 | 103.94 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 |  | 553 | 0.21135 | 103.94 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 | 478 |  | 0.21767 | 123.37 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 | 478 |  | 0.21315 | 123.37 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 | 478 |  | 0.26238 | 123.37 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 | 478 |  | 0.23044 | 123.37 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 | 478 |  | 0.21315 | 123.37 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 | 478 |  | 0.16605 | 123.37 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 | 478 |  | 0.26238 | 123.37 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 | 478 |  | 0.21301 | 123.37 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 | 478 |  | 0.06831 | 101.74 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-172 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 | 478 |  | 0.09467 | 101.74 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 | 478 |  | 0.17368 | 101.74 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 | 478 |  | 0.16977 | 101.74 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 | 478 |  | 0.20698 | 101.74 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 | 478 |  | 0.1825 | 101.74 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 | 478 |  | 0.16977 | 101.74 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-078 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 | 478 |  | 0.07567 | 101.74 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 | 478 |  | 0.20698 | 101.74 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 | 478 |  | 0.16975 | 101.74 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33558 | 113.99 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33496 | 112.57 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33711 | 114 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.3386 | 111.9 | P12:115:SPS:V08.1.TUCO.HALECTR
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33497 | 113.21 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33512 | 112.92 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33491 | 112.88 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33491 | 112.43 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.337 | 121.52 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.337 | 119.07 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.32942 | 106.37 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33412 | 111.8 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33502 | 114.37 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33502 | 114.36 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.32791 | 110.83 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33491 | 110.51 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33491 | 110.99 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33412 | 111.8 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33656 | 117.03 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.34044 | 134.83 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 699 | 0.37495 | 109.87 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 699 | 0.37403 | 109.61 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33535 | 114.49 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33523 | 114.1 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33523 | 114.05 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33536 | 114.41 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.32942 | 106.37 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.32936 | 107.39 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.32942 | 106.37 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33432 | 112.09 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33466 | 112.57 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33413 | 111.8 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33412 | 111.8 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33463 | 112.48 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33651 | 116.93 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33663 | 117.26 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33525 | 114.27 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33535 | 114.48 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33536 | 114.44 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33535 | 114.49 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33536 | 114.41 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33536 | 114.55 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33536 | 114.51 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33536 | 114.55 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33522 | 113.98 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.32936 | 107.39 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.32942 | 106.37 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33432 | 112.09 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33466 | 112.57 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33413 | 111.8 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33412 | 111.8 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33463 | 112.48 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33539 | 114.48 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33822 | 130.58 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 19WP | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 699 | 0.37134 | 103.77 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24WP | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 699 | 0.37138 | 103.52 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.32791 | 110.83 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.32791 | 110.83 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33509 | 111.52 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33509 | 111.02 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.3339 | 111.49 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33677 | 175.03 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 699 | 0.37696 | 158.86 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33656 | 119.71 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.33976 | 120.4 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 |  | 643 | 0.32942 | 106.37 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 | 559 |  | 0.33491 | 130.29 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 | 615 |  | 0.36531 | 104.63 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998067 UPDATE LATER 230 1 | 615 |  | 0.36473 | 103.09 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998068 SIEM 8743066 230 2 |  | 643 | 0.29368 | 105.9 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998068 SIEM 8743066 230 2 |  | 643 | 0.29368 | 103.77 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998068 SIEM 8743066 230 2 |  | 643 | 0.2933 | 101.99 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998068 SIEM 8743066 230 2 |  | 643 | 0.29668 | 117.53 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998068 SIEM 8743066 230 2 |  | 643 | 0.29326 | 101.91 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998068 SIEM 8743066 230 2 |  | 643 | 0.29336 | 102.19 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998068 SIEM 8743066 230 2 |  | 643 | 0.29474 | 113.8 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998068 SIEM 8743066 230 2 |  | 643 | 0.29348 | 152.57 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998068 SIEM 8743066 230 2 |  | 699 | 0.32851 | 138.45 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998068 SIEM 8743066 230 2 |  | 643 | 0.2933 | 104.32 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998068 SIEM 8743066 230 2 |  | 643 | 0.29609 | 104.93 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998068 SIEM 8743066 230 2 | 559 |  | 0.29187 | 113.56 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34835 | 112.99 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.349 | 114.06 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34836 | 112.3 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34835 | 114.04 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34856 | 114.15 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.3496 | 112.16 | P12:115:SPS:T72.1.YUMA.WOLFTH
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.35221 | 111.65 | P12:115:SPS:V08.1.TUCO.HALECTR
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.352 | 112.32 | P12:115:SPS:V24.1.WOLFTH.TERRY
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34835 | 113.89 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34839 | 112.97 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34835 | 113.55 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34841 | 112.87 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34835 | 113.48 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34835 | 112.18 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34867 | 114.22 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.3512 | 122.66 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.3512 | 120.55 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34244 | 105.86 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34735 | 111.99 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34842 | 114.3 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34842 | 114.3 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34857 | 114.2 | P12:345:OKGE:BKRBKR4193
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34857 | 114.2 | P12:345:OKGE:BKRBKR4194
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34085 | 110.27 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34835 | 112.16 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34835 | 112.09 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34735 | 111.99 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.35051 | 115.75 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34814 | 114.93 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.35342 | 139.47 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34866 | 114.2 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34867 | 114.2 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34814 | 114.95 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34244 | 105.85 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34251 | 106.66 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34244 | 105.86 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34758 | 112.24 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.3481 | 112.45 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34737 | 111.94 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34735 | 111.99 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34803 | 112.45 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.35039 | 115.67 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.35061 | 115.83 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34863 | 114.1 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34251 | 106.66 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34244 | 105.86 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34758 | 112.24 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.3481 | 112.45 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34737 | 111.94 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34735 | 111.99 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34803 | 112.45 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.35265 | 132.08 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34857 | 114.2 | P42:345:OKGE:SB_BAER7318
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34085 | 110.27 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34085 | 110.27 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34603 | 112.31 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34711 | 111.65 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.35051 | 117.36 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.35447 | 122.41 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34244 | 105.85 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.34834 | 112.99 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 | 559 |  | 0.34835 | 130.38 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998078 SIEM 8743066 230 2 |  | 643 | 0.30606 | 106.93 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998078 SIEM 8743066 230 2 |  | 643 | 0.30606 | 105.11 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998078 SIEM 8743066 230 2 |  | 643 | 0.30546 | 100.93 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998078 SIEM 8743066 230 2 |  | 643 | 0.30339 | 100.22 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998078 SIEM 8743066 230 2 |  | 643 | 0.30799 | 121.66 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998078 SIEM 8743066 230 2 |  | 643 | 0.30339 | 100.23 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998078 SIEM 8743066 230 2 |  | 643 | 0.30536 | 100.84 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998078 SIEM 8743066 230 2 |  | 643 | 0.30555 | 101 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998078 SIEM 8743066 230 2 |  | 643 | 0.30732 | 115.11 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998078 SIEM 8743066 230 2 |  | 643 | 0.30546 | 102.33 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998078 SIEM 8743066 230 2 |  | 643 | 0.30891 | 106.71 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998078 SIEM 8743066 230 2 | 559 |  | 0.30357 | 113.68 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.2017 | 107.29 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.20356 | 108.34 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.20171 | 106.59 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.2017 | 108.33 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.2024 | 108.44 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.20244 | 106.44 | P12:115:SPS:T72.1.YUMA.WOLFTH
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.20338 | 106.57 | P12:115:SPS:V24.1.WOLFTH.TERRY
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.20169 | 108.18 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.20175 | 107.26 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.20179 | 107.84 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.20176 | 107.16 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.2017 | 107.79 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.2017 | 106.47 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.20245 | 108.48 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.21076 | 116.75 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.21076 | 114.69 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.20085 | 106.31 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.20202 | 108.54 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.20202 | 108.54 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.20245 | 108.47 | P12:345:OKGE:BKRBKR4193
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.20245 | 108.47 | P12:345:OKGE:BKRBKR4194
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.2017 | 106.49 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.2017 | 106.41 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.20085 | 106.31 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.20484 | 110.09 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.20287 | 109.18 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.22932 | 133.54 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2016-172 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.21024 | 133.54 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.20661 | 133.54 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.20661 | 133.54 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.20239 | 108.43 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.20245 | 108.46 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.20287 | 109.2 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.201 | 106.59 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.20151 | 106.88 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.20087 | 106.29 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.20085 | 106.31 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.20142 | 106.85 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.20475 | 109.98 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.20495 | 110.19 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.20236 | 108.35 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.201 | 106.59 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.20151 | 106.88 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.20087 | 106.29 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.20085 | 106.31 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.20142 | 106.85 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.20256 | 108.26 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.21623 | 125.87 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.20245 | 108.47 | P42:345:OKGE:SB_BAER7318
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.20066 | 105.99 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.20484 | 111.69 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.21467 | 116.66 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 |  | 643 | 0.20169 | 107.29 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 | 559 |  | 0.2017 | 123.8 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-078 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 | 559 |  | 0.03252 | 123.8 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998078 SIEM 8743066 230 2 | 559 |  | 0.17577 | 107.96 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-172 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998078 SIEM 8743066 230 2 | 559 |  | 0.15151 | 107.96 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998078 SIEM 8743066 230 2 | 559 |  | 0.10619 | 107.96 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998078 SIEM 8743066 230 2 | 559 |  | 0.10758 | 107.96 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998078 SIEM 8743066 230 2 | 559 |  | 0.11452 | 107.96 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998078 SIEM 8743066 230 2 | 559 |  | 0.10736 | 107.96 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998078 SIEM 8743066 230 2 | 559 |  | 0.10758 | 107.96 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998078 SIEM 8743066 230 2 | 559 |  | 0.11452 | 107.96 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998078 SIEM 8743066 230 2 | 559 |  | 0.10722 | 107.96 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-104 | 'FROM -> TO' | 525830 TUCO_INT 6 230 998078 SIEM 8743066 230 2 | 559 |  | 0.04136 | 107.96 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33558 | 114.85 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33496 | 113.42 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33711 | 114.85 | P12:115:SPS:T67.1.HAPPY.KRESS
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.3386 | 112.76 | P12:115:SPS:V08.1.TUCO.HALECTR
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33497 | 114.07 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33512 | 113.77 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33491 | 113.75 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33491 | 113.28 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.337 | 122.32 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.337 | 119.89 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.32942 | 105.63 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33412 | 112.62 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33502 | 115.23 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33502 | 115.23 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.32791 | 111.74 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33491 | 111.38 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33491 | 111.86 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33412 | 112.62 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33656 | 117.85 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.34044 | 136.09 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 699 | 0.37495 | 111.29 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 699 | 0.37403 | 110.44 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33535 | 115.34 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33523 | 114.95 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33523 | 114.9 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33536 | 115.26 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.32942 | 105.63 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.32936 | 106.48 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.32942 | 105.63 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33432 | 112.92 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33466 | 113.39 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33413 | 112.6 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33412 | 112.62 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33463 | 113.32 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33651 | 117.75 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33663 | 118.08 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33525 | 115.12 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33535 | 115.33 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33536 | 115.29 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33535 | 115.34 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33536 | 115.26 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33536 | 115.4 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33536 | 115.36 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33536 | 115.4 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33522 | 114.83 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.32936 | 106.48 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.32942 | 105.63 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33432 | 112.92 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33466 | 113.39 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33413 | 112.6 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33412 | 112.62 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33463 | 113.32 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33539 | 115.34 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33822 | 131.51 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 19WP | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 699 | 0.37134 | 104.57 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24WP | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 699 | 0.37138 | 104.06 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.32791 | 111.74 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.32791 | 111.74 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33509 | 112.39 | P42:345:OKGE:SB_BVTY7305
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33509 | 111.89 | P42:345:OKGE:SB_BVTY7387
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.3339 | 112.3 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33677 | 179.17 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 699 | 0.37696 | 163.71 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33656 | 120.51 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.33976 | 121.22 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 |  | 643 | 0.32942 | 105.63 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 | 559 |  | 0.33491 | 131.28 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 | 615 |  | 0.36531 | 104.96 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998067 UPDATE LATER 230 1 | 615 |  | 0.36473 | 103.8 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998068 SIEM 8743066 230 2 |  | 643 | 0.29368 | 106.43 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998068 SIEM 8743066 230 2 |  | 643 | 0.29368 | 104.31 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998068 SIEM 8743066 230 2 |  | 643 | 0.29196 | 100.23 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998068 SIEM 8743066 230 2 |  | 643 | 0.29196 | 100.23 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998068 SIEM 8743066 230 2 |  | 643 | 0.2933 | 102.53 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998068 SIEM 8743066 230 2 |  | 643 | 0.29668 | 118.41 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998068 SIEM 8743066 230 2 |  | 643 | 0.29224 | 100.33 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998068 SIEM 8743066 230 2 |  | 643 | 0.29214 | 100 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998068 SIEM 8743066 230 2 |  | 643 | 0.29226 | 100.27 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998068 SIEM 8743066 230 2 |  | 643 | 0.29326 | 102.44 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998068 SIEM 8743066 230 2 |  | 643 | 0.29336 | 102.72 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998068 SIEM 8743066 230 2 |  | 643 | 0.29215 | 100.15 | P23:345:SUNC:HLC_BRK382
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998068 SIEM 8743066 230 2 |  | 643 | 0.29224 | 100.32 | P23:345:SUNC:MO_BRK182
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998068 SIEM 8743066 230 2 |  | 643 | 0.29226 | 100.29 | P23:345:SUNC:MO_BRK188
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998068 SIEM 8743066 230 2 |  | 643 | 0.29224 | 100.33 | P23:345:SUNC:MO_BRK382
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998068 SIEM 8743066 230 2 |  | 643 | 0.29226 | 100.27 | P23:345:SUNC:MO_BRK388
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998068 SIEM 8743066 230 2 |  | 643 | 0.29226 | 100.38 | P23:345:SUNC:SB_BRK482
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998068 SIEM 8743066 230 2 |  | 643 | 0.29226 | 100.35 | P23:345:SUNC:SB_BRK488
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998068 SIEM 8743066 230 2 |  | 643 | 0.29226 | 100.39 | P23:345:SUNC:SB_BRK582
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998068 SIEM 8743066 230 2 |  | 643 | 0.29228 | 100.33 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998068 SIEM 8743066 230 2 |  | 643 | 0.29474 | 114.44 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998068 SIEM 8743066 230 2 |  | 643 | 0.29348 | 155.86 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998068 SIEM 8743066 230 2 |  | 699 | 0.32851 | 142.67 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998068 SIEM 8743066 230 2 |  | 643 | 0.2933 | 104.85 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998068 SIEM 8743066 230 2 |  | 643 | 0.29609 | 105.47 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998068 SIEM 8743066 230 2 | 559 |  | 0.29187 | 114.2 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34835 | 114.29 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.349 | 115.43 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34836 | 113.54 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34835 | 115.35 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34856 | 115.5 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.3496 | 113.5 | P12:115:SPS:T72.1.YUMA.WOLFTH
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.35221 | 112.8 | P12:115:SPS:V08.1.TUCO.HALECTR
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.352 | 113.59 | P12:115:SPS:V24.1.WOLFTH.TERRY
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34835 | 115.21 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34839 | 114.24 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34835 | 114.86 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34841 | 114.14 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34835 | 114.77 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34835 | 113.42 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34867 | 115.57 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.3512 | 123.95 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.3512 | 121.91 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34244 | 104.52 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34735 | 113.24 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34842 | 115.66 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34842 | 115.66 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34857 | 115.54 | P12:345:OKGE:BKRBKR4193
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34857 | 115.54 | P12:345:OKGE:BKRBKR4194
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34085 | 111.53 | P12:345:OKGE:BKRBKR429
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34835 | 113.44 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34835 | 113.36 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34735 | 113.24 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.35051 | 117.15 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34814 | 116.29 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.35342 | 142.26 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34866 | 115.55 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34867 | 115.55 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34814 | 116.31 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34244 | 104.51 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34251 | 105.16 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34244 | 104.52 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34758 | 113.51 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.3481 | 113.72 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34737 | 113.18 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34735 | 113.24 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34803 | 113.72 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.35039 | 117.08 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.35061 | 117.23 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34863 | 115.44 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34251 | 105.16 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34244 | 104.52 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34758 | 113.51 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.3481 | 113.72 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34737 | 113.18 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34735 | 113.24 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34803 | 113.72 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.35265 | 133.03 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34857 | 115.54 | P42:345:OKGE:SB_BAER7318
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34085 | 111.53 | P42:345:OKGE:SB_BOER7383
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34085 | 111.53 | P42:345:OKGE:SB_BOER7384
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34603 | 113.58 | P42:345:OKGE:SB_SEOL7385
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34711 | 112.88 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.35051 | 118.72 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.35447 | 123.61 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34244 | 104.51 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.34834 | 114.29 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 | 559 |  | 0.34835 | 131.89 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998078 SIEM 8743066 230 2 |  | 643 | 0.30414 | 100.37 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998078 SIEM 8743066 230 2 |  | 643 | 0.30357 | 100.3 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998078 SIEM 8743066 230 2 |  | 643 | 0.30375 | 100.43 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998078 SIEM 8743066 230 2 |  | 643 | 0.30357 | 100.17 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998078 SIEM 8743066 230 2 |  | 643 | 0.30385 | 100.49 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998078 SIEM 8743066 230 2 |  | 643 | 0.30606 | 107.82 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998078 SIEM 8743066 230 2 |  | 643 | 0.30606 | 106.03 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998078 SIEM 8743066 230 2 |  | 643 | 0.30363 | 100.56 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998078 SIEM 8743066 230 2 |  | 643 | 0.30363 | 100.56 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998078 SIEM 8743066 230 2 |  | 643 | 0.30546 | 101.87 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998078 SIEM 8743066 230 2 |  | 643 | 0.30339 | 101.12 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998078 SIEM 8743066 230 2 |  | 643 | 0.30799 | 123.7 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998078 SIEM 8743066 230 2 |  | 643 | 0.30384 | 100.47 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998078 SIEM 8743066 230 2 |  | 643 | 0.30385 | 100.47 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998078 SIEM 8743066 230 2 |  | 643 | 0.30339 | 101.13 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998078 SIEM 8743066 230 2 |  | 643 | 0.30536 | 101.79 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998078 SIEM 8743066 230 2 |  | 643 | 0.30555 | 101.94 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998078 SIEM 8743066 230 2 |  | 643 | 0.30382 | 100.38 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998078 SIEM 8743066 230 2 |  | 643 | 0.30732 | 115.77 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998078 SIEM 8743066 230 2 |  | 643 | 0.30546 | 103.24 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998078 SIEM 8743066 230 2 |  | 643 | 0.30891 | 107.53 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998078 SIEM 8743066 230 2 | 559 |  | 0.30357 | 114.68 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.34999 | 113.69 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.32906 | 100.3 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.24537 | 113.69 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.2244 | 100.3 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2016-172 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.23321 | 113.69 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.21226 | 100.3 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.23746 | 113.69 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.21651 | 100.3 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.23622 | 113.69 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.21528 | 100.3 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.25413 | 113.69 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.23318 | 100.3 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.25303 | 113.69 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.23208 | 100.3 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.23622 | 113.69 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.21528 | 100.3 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.25413 | 113.69 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.23318 | 100.3 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.2361 | 113.69 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.21516 | 100.3 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.34901 | 107.98 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.2297 | 107.98 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20G | GEN-2016-172 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.20798 | 107.98 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.32122 | 136.64 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-059 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 1142.5 | 0.38418 | 121.95 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.22952 | 136.64 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 1142.5 | 0.29248 | 121.95 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.22228 | 136.64 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 1142.5 | 0.28525 | 121.95 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.2601 | 136.64 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 1142.5 | 0.32306 | 121.95 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.25695 | 136.64 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 1142.5 | 0.31991 | 121.95 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.26124 | 136.64 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 1142.5 | 0.32421 | 121.95 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.26745 | 136.64 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 1142.5 | 0.33041 | 121.95 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.25695 | 136.64 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 1142.5 | 0.31991 | 121.95 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.26124 | 136.64 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 1142.5 | 0.32421 | 121.95 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.25741 | 136.64 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 1142.5 | 0.32037 | 121.95 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-104 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.30352 | 136.64 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-104 | 'FROM -> TO' | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 1142.5 | 0.36649 | 121.95 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.2017 | 108.56 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.20356 | 109.68 | P12:115:SPS:T04.1.DFSMTH.CASTRO
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.20171 | 107.79 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.2017 | 109.6 | P12:115:SPS:T21.1.GRSSLND.GRAHAM
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.2024 | 109.75 | P12:115:SPS:T53.1.NICHLS.KIRBY
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.20244 | 107.75 | P12:115:SPS:T72.1.YUMA.WOLFTH
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.20338 | 107.8 | P12:115:SPS:V24.1.WOLFTH.TERRY
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.20169 | 109.46 | P12:115:SPS:V33.1.LUBBS.LYNN
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.20175 | 108.49 | P12:115:SPS:V49.1.YOAKUM.SHLCO2
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.20179 | 109.11 | P12:115:SPS:V55.1.SUNDWN.TERRY
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.20176 | 108.4 | P12:115:SPS:V80A.1.DC_STH.INKBSN
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.2017 | 109.05 | P12:115:SPS:W63.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.2017 | 107.68 | P12:115:SPS:W72.1.CHINA.NLOVN
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.20245 | 109.79 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.21076 | 118.41 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.21076 | 116.25 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.20085 | 107.52 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.20202 | 109.86 | P12:345:OKGE:BKBK443NEW
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.20202 | 109.86 | P12:345:OKGE:BKBK443NEW2
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.20245 | 109.78 | P12:345:OKGE:BKRBKR4193
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.20245 | 109.78 | P12:345:OKGE:BKRBKR4194
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.2017 | 107.73 | P12:345:OKGE:BKRBKR604
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.2017 | 107.65 | P12:345:OKGE:BKRBKR604_2
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.20085 | 107.52 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.20484 | 111.46 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.20287 | 110.51 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.22932 | 136.28 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2016-172 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.21024 | 136.28 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.20661 | 136.28 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.20661 | 136.28 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.20239 | 109.76 | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.20245 | 109.77 | P13:138-230:AEPW:ELKCTY-4
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.20287 | 110.52 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.201 | 107.82 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.20151 | 108.11 | P23:345:AEPW:PITTSBURG CB 3429A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.20087 | 107.5 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.20085 | 107.52 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.20142 | 108.09 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.20475 | 111.34 | P23:345:SUNC:HLC_BRK188
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.20495 | 111.56 | P23:345:SUNC:HLC_BRK282
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.20236 | 109.66 | P23:345:SUNC:SV_BRK188
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.201 | 107.82 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.20151 | 108.11 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.20087 | 107.5 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.20085 | 107.52 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.20142 | 108.09 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.20256 | 109.56 | P42:345:NPPD:BKR-RW-3302
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.21623 | 127.97 | P42:345:OKGE:SB_BAER7314
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.20245 | 109.78 | P42:345:OKGE:SB_BAER7318
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.20066 | 107.18 | P42:345:OKGE:SB_SEOL7386
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.20484 | 113.14 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.21467 | 118.31 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 |  | 643 | 0.20169 | 108.56 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 | 559 |  | 0.2017 | 125.27 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-078 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 | 559 |  | 0.03252 | 125.27 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998078 SIEM 8743066 230 2 | 559 |  | 0.17577 | 108.9 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-172 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998078 SIEM 8743066 230 2 | 559 |  | 0.15151 | 108.9 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998078 SIEM 8743066 230 2 | 559 |  | 0.10619 | 108.9 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998078 SIEM 8743066 230 2 | 559 |  | 0.10758 | 108.9 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998078 SIEM 8743066 230 2 | 559 |  | 0.11452 | 108.9 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998078 SIEM 8743066 230 2 | 559 |  | 0.10736 | 108.9 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998078 SIEM 8743066 230 2 | 559 |  | 0.10758 | 108.9 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998078 SIEM 8743066 230 2 | 559 |  | 0.11452 | 108.9 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998078 SIEM 8743066 230 2 | 559 |  | 0.10722 | 108.9 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-104 | 'FROM -> TO' | 525832 TUCO_INT 7 345 998078 SIEM 8743066 230 2 | 559 |  | 0.04136 | 108.9 | System Intact
Non-Converge | 07ALL | 0 |  |  | '' | None |  |  |  |  | None
Thermal | 07ALL | 2 |  |  | '' | None |  |  |  |  | None
Non-Converge | 08ALL | 0 | 19WP | GEN-2017-009 | '' | Non-Converge |  |  | 0.03251 |  | P23:345:AEPW:RIVERSIDE CB 3413A NBTB
Non-Converge | 08ALL | 0 | 19WP | GEN-2017-022 | '' | Non-Converge |  |  | 0.03618 |  | P23:345:AEPW:RIVERSIDE CB 3413A NBTB
Non-Converge | 08ALL | 0 | 19WP | GEN-2017-071 | '' | Non-Converge |  |  | 0.03896 |  | P23:345:AEPW:RIVERSIDE CB 3413A NBTB
Non-Converge | 08ALL | 0 | 19WP | GEN-2017-072 | '' | Non-Converge |  |  | 0.03896 |  | P23:345:AEPW:RIVERSIDE CB 3413A NBTB
Non-Converge | 08ALL | 0 | 19WP | GEN-2017-074 | '' | Non-Converge |  |  | 0.04008 |  | P23:345:AEPW:RIVERSIDE CB 3413A NBTB
Non-Converge | 08ALL | 0 | 19WP | GEN-2017-077 | '' | Non-Converge |  |  | 0.04778 |  | P23:345:AEPW:RIVERSIDE CB 3413A NBTB
Non-Converge | 08ALL | 0 | 20SP | GEN-2017-068 | '' | Non-Converge |  |  | 0.0522 |  | P23:345:WERE:JEC_345-16::
Non-Converge | 08ALL | 0 | 24SP | GEN-2017-068 | '' | Non-Converge |  |  | 0.04968 |  | P23:345:WERE:JEC_345-16::
Non-Converge | 08ALL | 0 | 29SP | GEN-2017-068 | '' | Non-Converge |  |  | 0.05052 |  | P23:345:WERE:JEC_345-16::
Non-Converge | 08ALL | 0 | 20SP | GEN-2017-086 | '' | Non-Converge |  |  | 0.03919 |  | P23:345:WERE:JEC_345-16::
Non-Converge | 08ALL | 0 | 24SP | GEN-2017-086 | '' | Non-Converge |  |  | 0.03669 |  | P23:345:WERE:JEC_345-16::
Non-Converge | 08ALL | 0 | 29SP | GEN-2017-086 | '' | Non-Converge |  |  | 0.03752 |  | P23:345:WERE:JEC_345-16::
Non-Converge | 08ALL | 0 | 19WP | GEN-2017-068 | '' | Non-Converge |  |  | 0.03214 |  | P23:345:WERE:WOLF_345-50::
Non-Converge | 08ALL | 0 | 24WP | GEN-2017-068 | '' | Non-Converge |  |  | 0.03134 |  | P23:345:WERE:WOLF_345-50::
Non-Converge | 08ALL | 0 | 19WP | GEN-2017-086 | '' | Non-Converge |  |  | 0.03515 |  | P23:345:WERE:WOLF_345-50::
Non-Converge | 08ALL | 0 | 24WP | GEN-2017-086 | '' | Non-Converge |  |  | 0.03504 |  | P23:345:WERE:WOLF_345-50::
Non-Converge | 08ALL | 0 | 19WP | GEN-2017-061 | '' | Non-Converge |  |  | 0.11021 |  | P43:345:GRDA:GRDA CB9580
Non-Converge | 08ALL | 0 | 19WP | GEN-2017-073 | '' | Non-Converge |  |  | 0.08929 |  | P43:345:GRDA:GRDA CB9580
Thermal | 08ALL | 2 | 24L | GEN-2017-073 | 'FROM -> TO' | 505480 BEAVER 5 161 506932 EUREKA 5 161 1 | 247 |  | 0.03115 | 100.41 | System Intact
Thermal | 08ALL | 2 | 24L | GEN-2017-074 | 'FROM -> TO' | 505480 BEAVER 5 161 506932 EUREKA 5 161 1 | 247 |  | 0.03575 | 100.41 | System Intact
Thermal | 08ALL | 2 | 24L | GEN-2017-077 | 'FROM -> TO' | 505480 BEAVER 5 161 506932 EUREKA 5 161 1 | 247 |  | 0.03325 | 100.41 | System Intact
Thermal | 08ALL | 2 | 20SP | GEN-2017-061 | 'FROM -> TO' | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 |  | 0.05264 | 105.47 | System Intact
Thermal | 08ALL | 2 | 20SP | GEN-2017-073 | 'FROM -> TO' | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 |  | 0.11214 | 105.47 | System Intact
Thermal | 08ALL | 2 | 29SP | GEN-2017-061 | 'FROM -> TO' | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 |  | 0.05275 | 102.71 | System Intact
Thermal | 08ALL | 2 | 29SP | GEN-2017-073 | 'FROM -> TO' | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 |  | 0.11225 | 102.71 | System Intact
Thermal | 08ALL | 2 | 24SP | GEN-2017-061 | 'FROM -> TO' | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 |  | 0.05268 | 102.14 | System Intact
Thermal | 08ALL | 2 | 24SP | GEN-2017-073 | 'FROM -> TO' | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 |  | 0.11218 | 102.14 | System Intact
Thermal | 08ALL | 2 | 20SP | GEN-2017-061 | 'FROM -> TO' | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 |  | 0.05264 | 108.72 | System Intact
Thermal | 08ALL | 2 | 20SP | GEN-2017-073 | 'FROM -> TO' | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 |  | 0.11214 | 108.72 | System Intact
Thermal | 08ALL | 2 | 29SP | GEN-2017-061 | 'FROM -> TO' | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 |  | 0.05275 | 106.26 | System Intact
Thermal | 08ALL | 2 | 29SP | GEN-2017-073 | 'FROM -> TO' | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 |  | 0.11225 | 106.26 | System Intact
Thermal | 08ALL | 2 | 24SP | GEN-2017-061 | 'FROM -> TO' | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 |  | 0.05268 | 105.5 | System Intact
Thermal | 08ALL | 2 | 24SP | GEN-2017-073 | 'FROM -> TO' | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 |  | 0.11218 | 105.5 | System Intact
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.65 | P11:001:599:CIMARRON1WIND:365:531603(1)
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.65 | P11:001:599:CIMARRON2WIND:200:531605(1)
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.62 | P11:001:599:SPEARVILLEWIND1:100:539116(1)
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.61 | P11:001:599:SPEARVILLEWIND2:154:539120(1)
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 104.07 | P11:022:NPPD:COOPER1G:1:983
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.83 | P11:022:NPPD:COOPER1G:1:983
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.4 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.16 | P11:023:NPPD:GENTLM1G:1:757
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.32 | P11:024:DPC:ALMA2:6
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.08 | P11:024:DPC:ALMA2:6
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.29 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.11 | P11:024:NPPD:GENTLM2G:2:757
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 104 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.77 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.72 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.88 | P11:115:XEL:HBR #6 7 8
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.65 | P11:115:XEL:HBR #6 7 8
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.88 | P11:115:XEL:RIV COMBINE CYCLE
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.64 | P11:115:XEL:RIV COMBINE CYCLE
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.37 | P11:138:OKGE:BKRBKR_GSU03
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.14 | P11:138:OKGE:BKRBKR_GSU03
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.09 | P11:138:OKGE:BKRBKR_GSU03
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 102.93 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 102.64 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 101.66 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 102.79 | P11:138:WERE:SCWF_GEN::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 102.63 | P11:138:WERE:SCWF_GEN::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 101.53 | P11:138:WERE:SCWF_GEN::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 104.68 | P11:20:GRDA:GRECCTG
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 104.63 | P11:20:GRDA:GRECCTG
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.84 | P11:20:OTP:AUTO-SINGLE:CENTER2G:1
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.6 | P11:20:OTP:AUTO-SINGLE:CENTER2G:1
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.59 | P11:20:OTP:AUTO-SINGLE:CENTER2G:1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.9 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.67 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.64 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.9 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.66 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.64 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.9 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.67 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.64 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.97 | P11:22.8:GRDA:GRDA17
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.72 | P11:22.8:GRDA:GRDA17
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 105.01 | P11:22:AEPW:FLINTCR1
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 104.75 | P11:22:AEPW:FLINTCR1
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 104.02 | P11:22:AEPW:FLINTCR1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 105.34 | P11:22:AEPW:NES3-1
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 105.08 | P11:22:AEPW:NES3-1
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 103.99 | P11:22:AEPW:NES3-1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.87 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.63 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.61 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.86 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.63 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.61 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.58 | P11:230:WERE:DVWF1_GEN::FUTURE
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.35 | P11:230:WERE:DVWF1_GEN::FUTURE
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.31 | P11:230:WERE:DVWF1_GEN::FUTURE
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.29 | P11:230:WERE:DVWF2_GEN::FUTURE
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.06 | P11:230:WERE:DVWF2_GEN::FUTURE
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.01 | P11:230:WERE:DVWF2_GEN::FUTURE
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.63 | P11:230:WERE:JECU1_GEN::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.29 | P11:230:WERE:JECU1_GEN::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.04 | P11:230:WERE:JECU1_GEN::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.65 | P11:24:AEPW:PIRKEY 1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.43 | P11:24:AEPW:SWS3-1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.69 | P11:24:AEPW:TURKCOAL
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.46 | P11:24:AEPW:TURKCOAL
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.32 | P11:24:DPC:AUTO-SINGLE:JPM:6
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.08 | P11:24:DPC:AUTO-SINGLE:JPM:6
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.81 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.6 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.55 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 101.99 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 101.71 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 101.15 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.05 | P11:24:OTP:AUTO-SINGLE:BIGSTN1G:1
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 102.77 | P11:24:OTP:AUTO-SINGLE:BIGSTN1G:1
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 101.81 | P11:24:OTP:AUTO-SINGLE:BIGSTN1G:1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.85 | P11:24:OTP:AUTO-SINGLE:COYOTE1G:1
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.61 | P11:24:OTP:AUTO-SINGLE:COYOTE1G:1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.87 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.63 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.61 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 102.65 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 102.39 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 101.47 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.79 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.59 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.55 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.86 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.64 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.62 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 104.09 | P11:345:MEC-NPPD:COOPER 1
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.84 | P11:345:MEC-NPPD:COOPER 1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.85 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.62 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72707 | 103.87 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72429 | 103.63 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 102.6 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.33 | P11:345:OKGE:BKRBKR_GSU04
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.08 | P11:345:OKGE:BKRBKR_GSU04
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.04 | P11:345:OKGE:BKRBKR_GSU04
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.57 | P11:345:OKGE:BKRBKR_GSU24
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.33 | P11:345:OKGE:BKRBKR_GSU24
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.31 | P11:345:OKGE:BKRBKR_GSU24
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.57 | P11:345:OKGE:BKRBKR_GSU25
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.33 | P11:345:OKGE:BKRBKR_GSU25
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.31 | P11:345:OKGE:BKRBKR_GSU25
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.56 | P11:345:OKGE:BKRBKR_GSU26
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.34 | P11:345:OKGE:BKRBKR_GSU26
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.31 | P11:345:OKGE:BKRBKR_GSU26
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.86 | P11:345:OPPD:NEBCTY1G
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.62 | P11:345:OPPD:NEBCTY1G
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.85 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.62 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.86 | P11:345:OPPD:NEBCTY2G
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.62 | P11:345:OPPD:NEBCTY2G
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.59 | P11:345:OPPD:NEBCTY2G
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 102.95 | P11:345:UMZB:# 16 #: LO IN ND. LELAND OLDS 2
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 102.68 | P11:345:UMZB:# 16 #: LO IN ND. LELAND OLDS 2
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 101.72 | P11:345:UMZB:# 16 #: LO IN ND. LELAND OLDS 2
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.86 | P11:345:UMZB:# 31 #: AVS IN ND. ANTELOPE VALLEY 1
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.63 | P11:345:UMZB:# 31 #: AVS IN ND. ANTELOPE VALLEY 1
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.61 | P11:345:UMZB:# 31 #: AVS IN ND. ANTELOPE VALLEY 1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.86 | P11:345:UMZB:# 32 #: AVS IN ND. ANTELOPE VALLEY 2
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.63 | P11:345:UMZB:# 32 #: AVS IN ND. ANTELOPE VALLEY 2
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.61 | P11:345:UMZB:# 32 #: AVS IN ND. ANTELOPE VALLEY 2
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 102.57 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 102.51 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 101.5 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.69 | P11:345:UMZB:# 5 #: DCS IN SD. DEERCREEK
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 102.88 | P11:345:WERE:FR2WFE1_GEN::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 102.64 | P11:345:WERE:FR2WFE1_GEN::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 101.61 | P11:345:WERE:FR2WFE1_GEN::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 102.89 | P11:345:WERE:FR2WFE2_GEN::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 102.65 | P11:345:WERE:FR2WFE2_GEN::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 101.62 | P11:345:WERE:FR2WFE2_GEN::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 102.9 | P11:345:WERE:FR2WFW1_GEN::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 102.65 | P11:345:WERE:FR2WFW1_GEN::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 101.62 | P11:345:WERE:FR2WFW1_GEN::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 102.91 | P11:345:WERE:FR2WFW2_GEN::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 102.67 | P11:345:WERE:FR2WFW2_GEN::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 101.63 | P11:345:WERE:FR2WFW2_GEN::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.56 | P11:345:WERE:JECU2_GEN::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.28 | P11:345:WERE:JECU2_GEN::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.27 | P11:345:WERE:JECU2_GEN::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.56 | P11:345:WERE:JECU3_GEN::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.28 | P11:345:WERE:JECU3_GEN::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.24 | P11:345:WERE:JECU3_GEN::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.04 | P11:345:WERE:KMWF1_GEN::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 102.81 | P11:345:WERE:KMWF1_GEN::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 101.77 | P11:345:WERE:KMWF1_GEN::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.05 | P11:345:WERE:KMWF2_GEN::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 102.82 | P11:345:WERE:KMWF2_GEN::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 101.78 | P11:345:WERE:KMWF2_GEN::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 102.22 | P11:345:WERE:NSWF_GEN::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 101.99 | P11:345:WERE:NSWF_GEN::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 100.94 | P11:345:WERE:NSWF_GEN::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 102.22 | P11:345:WERE:PTWF_GEN::FUTURE
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 101.99 | P11:345:WERE:PTWF_GEN::FUTURE
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 100.94 | P11:345:WERE:PTWF_GEN::FUTURE
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 102.75 | P11:345:WERE:WVWF_GEN::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 102.54 | P11:345:WERE:WVWF_GEN::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 101.47 | P11:345:WERE:WVWF_GEN::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 105.01 | P11:HV:EES::FLINTCR1:1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 104.71 | P11:HV:EES::JTEC GEN#2 1:2
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 104.32 | P12:069:WERE:MURR-VULC_69::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 104.08 | P12:069:WERE:MURR-VULC_69::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 103.06 | P12:069:WERE:MURR-VULC_69::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.64 | P12:115:SPS:T14.1.MADDOX.TAYLOR
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.88 | P12:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.65 | P12:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72639 | 104.53 | P12:138:AEPW:BV-COM-4:MOUNDRD4
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7236 | 104.29 | P12:138:AEPW:BV-COM-4:MOUNDRD4
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7236 | 103.21 | P12:138:AEPW:BV-COM-4:MOUNDRD4
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72636 | 104.85 | P12:138:AEPW:MOUNDRD4:SHIDLER4
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72355 | 104.61 | P12:138:AEPW:MOUNDRD4:SHIDLER4
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72353 | 103.56 | P12:138:AEPW:MOUNDRD4:SHIDLER4
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72707 | 105.1 | P12:138:OKGE:BKRBKR37
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72428 | 104.88 | P12:138:OKGE:BKRBKR37
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72423 | 103.82 | P12:138:OKGE:BKRBKR37
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.1 | P12:138:OKGE:BKRBKR500_4
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 102.88 | P12:138:OKGE:BKRBKR500_4
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 101.84 | P12:138:OKGE:BKRBKR500_4
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.55 | P12:138:OKGE:BKRBKR601
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.33 | P12:138:OKGE:BKRBKR601
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.3 | P12:138:OKGE:BKRBKR601
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72707 | 103.22 | P12:138:OKGE-WFEC:BKRBKR36
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72429 | 103 | P12:138:OKGE-WFEC:BKRBKR36
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 101.97 | P12:138:OKGE-WFEC:BKRBKR36
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72513 | 102.58 | P12:138:OKGE-WFEC-OMPA-WERE:BKRBKR71
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72824 | 102.57 | P12:138:OKGE-WFEC-OMPA-WERE:BKRBKR71
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7255 | 101.39 | P12:138:OKGE-WFEC-OMPA-WERE:BKRBKR71
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72422 | 105.92 | P12:138:WERE:ALTO-BUTL_138::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72132 | 105.7 | P12:138:WERE:ALTO-BUTL_138::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72135 | 104.64 | P12:138:WERE:ALTO-BUTL_138::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 104.29 | P12:138:WERE:BELA-NORT_138::PRESENT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 104.08 | P12:138:WERE:BELA-NORT_138::PRESENT
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 103.11 | P12:138:WERE:BELA-NORT_138::PRESENT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 102.79 | P12:138:WERE:CRSW-SCWF_138::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 102.63 | P12:138:WERE:CRSW-SCWF_138::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 101.53 | P12:138:WERE:CRSW-SCWF_138::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 103 | P12:138:WERE:HOOV-MURR_138::PRESENT
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72479 | 103.15 | P12:138:WERE:ROSE-WEAV_138::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72712 | 104.26 | P12:138:WFEC:NOEL_WAKITA
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72435 | 104.02 | P12:138:WFEC:NOEL_WAKITA
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72435 | 103.01 | P12:138:WFEC:NOEL_WAKITA
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.6 | P12:138:WFEC:WASHITA_BLCANYON
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72411 | 103.12 | P12:161:AECI:CHOTEAU-MAID
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72692 | 102.93 | P12:161:EES-EAI:M:GRANVW:OSAGE_E:BERRYV:GR_FR2:GRFR_S:HRSN_W:HRSN_S:HRSN_E:EUREKASP:1
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72414 | 102.72 | P12:161:EES-EAI:M:GRANVW:OSAGE_E:BERRYV:GR_FR2:GRFR_S:HRSN_W:HRSN_S:HRSN_E:EUREKASP:1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72663 | 103.31 | P12:161:WERE:LITC-EMDE_161::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72386 | 103.08 | P12:161:WERE:LITC-EMDE_161::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72179 | 104.5 | P12:161:WERE:MARM-KCPL_161::FUTURE
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72459 | 104.5 | P12:161:WERE:MARM-KCPL_161::FUTURE
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72185 | 103.35 | P12:161:WERE:MARM-KCPL_161::FUTURE
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72243 | 100.58 | P12:161:WERE:NSES-EMDE_161::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71971 | 100.26 | P12:161:WERE:NSES-EMDE_161::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.85 | P12:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.61 | P12:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.03 | P12:230:WERE:UNIO-DVWF_230::FUTURE
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 102.8 | P12:230:WERE:UNIO-DVWF_230::FUTURE
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 101.74 | P12:230:WERE:UNIO-DVWF_230::FUTURE
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72475 | 103.14 | P12:345:AECI:SPRTSMN-GRDA1
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72198 | 103.05 | P12:345:AECI:SPRTSMN-GRDA1
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72192 | 101.7 | P12:345:AECI:SPRTSMN-GRDA1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72659 | 103.34 | P12:345:AEPW:CLARKSV7:ONETA--7
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72381 | 103.06 | P12:345:AEPW:CLARKSV7:ONETA--7
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69538 | 110.83 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69279 | 110.28 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.6927 | 107.38 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 08ALL | 2 | 20SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.6954 | 101.94 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72698 | 104.84 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72401 | 104.53 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72423 | 103.28 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72717 | 104.51 | P12:345:AEPW:LYDIA7:VALIANT7
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72723 | 104.54 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72628 | 104.92 | P12:345:AEPW:R.S.S.-7:ONETA--7
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72351 | 104.67 | P12:345:AEPW:R.S.S.-7:ONETA--7
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72363 | 103.43 | P12:345:AEPW:R.S.S.-7:ONETA--7
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72201 | 112.79 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71889 | 112.55 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71838 | 112.09 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 08ALL | 2 | 20SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72238 | 100.86 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72238 | 104.23 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72648 | 103.29 | P12:345:AEPW-OKGE:PITTSB-7:C-RIVER7
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72364 | 103.12 | P12:345:AEPW-OKGE:PITTSB-7:C-RIVER7
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72712 | 104.9 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 104.63 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7243 | 103.62 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7248 | 105.38 | P12:345:AEPW-OKGE:R.S.S.-7:REDBUD7
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72187 | 105.2 | P12:345:AEPW-OKGE:R.S.S.-7:REDBUD7
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72134 | 104.52 | P12:345:AEPW-OKGE:R.S.S.-7:REDBUD7
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72698 | 105.18 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72401 | 104.86 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72423 | 103.6 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72695 | 104.9 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72417 | 104.63 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72411 | 103.36 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72665 | 103.08 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7236 | 102.67 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7239 | 101.47 | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69338 | 108.91 | P12:345:AEPW-WERE:DELWARE7:NEOSHO7
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69079 | 108.19 | P12:345:AEPW-WERE:DELWARE7:NEOSHO7
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69067 | 105.45 | P12:345:AEPW-WERE:DELWARE7:NEOSHO7
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72318 | 107.48 | P12:345:GRDA:GRDA1 -GRECTAP
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72599 | 106.98 | P12:345:GRDA:GRDA1 -GRECTAP
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72322 | 104.94 | P12:345:GRDA:GRDA1 -GRECTAP
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72201 | 112.79 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71889 | 112.55 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71838 | 112.09 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 08ALL | 2 | 20SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72238 | 100.86 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72708 | 103.85 | P12:345:MDU::CENTER:COYOTE:1::::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7243 | 103.6 | P12:345:MDU::CENTER:COYOTE:1::::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72412 | 103.17 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72412 | 103.17 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.66 | P12:345:OKGE:BKBK1501NEW
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.43 | P12:345:OKGE:BKBK1501NEW
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.21 | P12:345:OKGE:BKBK1501NEW
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72848 | 106.01 | P12:345:OKGE:BKBK442NEW
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72577 | 105.71 | P12:345:OKGE:BKBK442NEW
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72576 | 104.71 | P12:345:OKGE:BKBK442NEW
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72848 | 106.98 | P12:345:OKGE:BKBK442NEW2
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72577 | 106.63 | P12:345:OKGE:BKBK442NEW2
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72576 | 105.67 | P12:345:OKGE:BKBK442NEW2
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.06 | P12:345:OKGE:BKBK442NEW3
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 102.83 | P12:345:OKGE:BKBK442NEW3
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 101.8 | P12:345:OKGE:BKBK442NEW3
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72726 | 105.26 | P12:345:OKGE:BKRBKR150
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72438 | 104.97 | P12:345:OKGE:BKRBKR150
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7245 | 104.03 | P12:345:OKGE:BKRBKR150
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.29 | P12:345:OKGE:BKRBKR340
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72711 | 104.68 | P12:345:OKGE:BKRBKR349
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72433 | 104.42 | P12:345:OKGE:BKRBKR349
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7243 | 103.4 | P12:345:OKGE:BKRBKR349
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7402 | 113.74 | P12:345:OKGE:BKRBKR357_1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.74332 | 113.54 | P12:345:OKGE:BKRBKR357_1
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.74126 | 113.4 | P12:345:OKGE:BKRBKR357_1
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7402 | 102.09 | P12:345:OKGE:BKRBKR357_2
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.74332 | 101.95 | P12:345:OKGE:BKRBKR357_2
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.74126 | 101.8 | P12:345:OKGE:BKRBKR357_2
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 102.38 | P12:345:OKGE:BKRBKR357_4
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 102.15 | P12:345:OKGE:BKRBKR357_4
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 101.12 | P12:345:OKGE:BKRBKR357_4
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.4 | P12:345:OKGE:BKRBKR399
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72911 | 106.29 | P12:345:OKGE:BKRBKR400
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72632 | 106.08 | P12:345:OKGE:BKRBKR400
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72652 | 105.21 | P12:345:OKGE:BKRBKR400
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 102.53 | P12:345:OKGE:BKRBKR401
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 102.3 | P12:345:OKGE:BKRBKR401
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 101.27 | P12:345:OKGE:BKRBKR401
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72632 | 104.17 | P12:345:OKGE:BKRBKR421
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72652 | 103.27 | P12:345:OKGE:BKRBKR421
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72471 | 104.2 | P12:345:OKGE:BKRBKR429
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72458 | 103.32 | P12:345:OKGE:BKRBKR429
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.12 | P12:345:OKGE:BKRBKR604
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.54 | P12:345:OKGE:BKRBKR604_2
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.31 | P12:345:OKGE:BKRBKR604_2
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.1 | P12:345:OKGE:BKRBKR604_2
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 101.17 | P12:345:OKGE:BKRBKR605
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 100.93 | P12:345:OKGE:BKRBKR605
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 102.22 | P12:345:OKGE:BKRBKR606
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 102 | P12:345:OKGE:BKRBKR606
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 100.96 | P12:345:OKGE:BKRBKR606
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.27 | P12:345:OKGE:BKRBKR607
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.16 | P12:345:OKGE:BKRBKR608
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 102.93 | P12:345:OKGE:BKRBKR613
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 102.71 | P12:345:OKGE:BKRBKR613
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 101.68 | P12:345:OKGE:BKRBKR613
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72238 | 104.23 | P12:345:OKGE-AEPW:BKRBKR12
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7248 | 105.38 | P12:345:OKGE-AEPW:BKRBKR14
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72187 | 105.2 | P12:345:OKGE-AEPW:BKRBKR14
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72134 | 104.52 | P12:345:OKGE-AEPW:BKRBKR14
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72712 | 104.9 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 104.63 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7243 | 103.62 | P12:345:OKGE-AEPW:BKRBKR20
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72698 | 105.18 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72401 | 104.86 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72423 | 103.6 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72648 | 103.29 | P12:345:OKGE-AEPW:BKRBKR409
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72364 | 103.12 | P12:345:OKGE-AEPW:BKRBKR409
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72471 | 104.2 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72458 | 103.31 | P12:345:OKGE-SPS:BKRBKR430
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7298 | 102.88 | P12:345:OKGE-WERE:BKRBKR422
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72706 | 102.71 | P12:345:OKGE-WERE:BKRBKR422
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72723 | 101.88 | P12:345:OKGE-WERE:BKRBKR422
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72483 | 104.25 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.74574 | 102.94 | P12:345:WERE:BENT-ROSE_345::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.74327 | 102.6 | P12:345:WERE:BENT-ROSE_345::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.74299 | 101.43 | P12:345:WERE:BENT-ROSE_345::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72647 | 104.76 | P12:345:WERE:BENT-WOLF_345::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72357 | 104.36 | P12:345:WERE:BENT-WOLF_345::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72705 | 107.32 | P12:345:WERE:EMPR-SWIS_345::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72413 | 106.97 | P12:345:WERE:EMPR-SWIS_345::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72405 | 106 | P12:345:WERE:EMPR-SWIS_345::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 101.94 | P12:345:WERE:FR2EAST-FR2WEST_345::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 101.7 | P12:345:WERE:FR2EAST-FR2WEST_345::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 100.66 | P12:345:WERE:FR2EAST-FR2WEST_345::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72729 | 105.07 | P12:345:WERE:GEAR-SUMM_345::FUTURE
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7245 | 104.64 | P12:345:WERE:GEAR-SUMM_345::FUTURE
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72461 | 103.67 | P12:345:WERE:GEAR-SUMM_345::FUTURE
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72749 | 107.39 | P12:345:WERE:HOYT-JEC_345::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72445 | 107.18 | P12:345:WERE:HOYT-JEC_345::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7243 | 106.06 | P12:345:WERE:HOYT-JEC_345::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72747 | 106.61 | P12:345:WERE:HOYT-STRA_345::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72444 | 106.35 | P12:345:WERE:HOYT-STRA_345::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72437 | 105.22 | P12:345:WERE:HOYT-STRA_345::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 102.22 | P12:345:WERE:KMWF-NSWF_345::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 101.99 | P12:345:WERE:KMWF-NSWF_345::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 100.95 | P12:345:WERE:KMWF-NSWF_345::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 102.22 | P12:345:WERE:KMWF-PTWF_345::FUTURE
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 101.99 | P12:345:WERE:KMWF-PTWF_345::FUTURE
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 100.95 | P12:345:WERE:KMWF-PTWF_345::FUTURE
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.67588 | 104.77 | P12:345:WERE:N345-LACY_345::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.67893 | 103.49 | P12:345:WERE:N345-LACY_345::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69338 | 108.91 | P12:345:WERE:N345-PSO_345::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69079 | 108.19 | P12:345:WERE:N345-PSO_345::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69067 | 105.45 | P12:345:WERE:N345-PSO_345::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72927 | 107.44 | P12:345:WERE:RENO-WICH_345::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72651 | 107.01 | P12:345:WERE:RENO-WICH_345::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72652 | 106.06 | P12:345:WERE:RENO-WICH_345::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72907 | 105.29 | P12:345:WERE:ROSE-WOLF_345::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72614 | 104.77 | P12:345:WERE:ROSE-WOLF_345::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7255 | 107.59 | P12:345:WERE:SWIS-WGAR_345::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72254 | 107.23 | P12:345:WERE:SWIS-WGAR_345::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72255 | 105.99 | P12:345:WERE:SWIS-WGAR_345::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7298 | 102.88 | P12:345:WERE:VIOL-OGE_345::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72706 | 102.71 | P12:345:WERE:VIOL-OGE_345::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72723 | 101.88 | P12:345:WERE:VIOL-OGE_345::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72777 | 101.83 | P12:345:WERE:VIOL-WICH_345::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72487 | 101.81 | P12:345:WERE:VIOL-WICH_345::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72507 | 100.69 | P12:345:WERE:VIOL-WICH_345::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72925 | 131.72 | P12:345:WERE:WAVS-LACY_345::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72583 | 131.68 | P12:345:WERE:WAVS-LACY_345::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72595 | 130.22 | P12:345:WERE:WAVS-LACY_345::
Thermal | 08ALL | 2 | 20SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72983 | 123.27 | P12:345:WERE:WAVS-LACY_345::
Thermal | 08ALL | 2 | 24SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.73047 | 120.13 | P12:345:WERE:WAVS-LACY_345::
Thermal | 08ALL | 2 | 29SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.73221 | 115.76 | P12:345:WERE:WAVS-LACY_345::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72583 | 127.01 | P12:345:WERE:WAVS-WOLF_345::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72925 | 126.93 | P12:345:WERE:WAVS-WOLF_345::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72595 | 125.43 | P12:345:WERE:WAVS-WOLF_345::
Thermal | 08ALL | 2 | 20SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72983 | 118.43 | P12:345:WERE:WAVS-WOLF_345::
Thermal | 08ALL | 2 | 24SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.73047 | 115.24 | P12:345:WERE:WAVS-WOLF_345::
Thermal | 08ALL | 2 | 29SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.73221 | 111.15 | P12:345:WERE:WAVS-WOLF_345::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 102.75 | P12:345:WERE:WAVS-WVWF_345::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 102.54 | P12:345:WERE:WAVS-WVWF_345::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 101.47 | P12:345:WERE:WAVS-WVWF_345::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 104.21 | P12:EHV:EES::7CALAWY 1:1
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.78 | P12:EHV:EES::7CALAWY 1:1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72615 | 106.82 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72342 | 104.64 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72659 | 103.34 | P12:EHV:EES::CLARKSV7!:ONETA--7:1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 104.89 | P12:HV:EES::FLINTCR5:1
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 103.89 | P12:HV:EES::FLINTCR5:1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 104.59 | P12:HV:EES::JTEC 5:1
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.65 | P12:HV:EES::PIRKEY 4:1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.68 | P12:HV:EES::TURK 4%:1(1)
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72745 | 104.64 | P13:069-138:WERE:WEAV_TX-2_138-69::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72469 | 104.41 | P13:069-138:WERE:WEAV_TX-2_138-69::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72469 | 103.42 | P13:069-138:WERE:WEAV_TX-2_138-69::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 104.03 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.8 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.75 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.65 | P13:138-24:AEPW:PIRKEY 4
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.68 | P13:138-24:AEPW:TURK 4
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.46 | P13:138-24:AEPW:TURK 4
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 104.89 | P13:161-22:AEPW:FLINTCR5
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 104.6 | P13:161-22:AEPW:FLINTCR5
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 103.89 | P13:161-22:AEPW:FLINTCR5
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.86 | P13:18-345:OPPD:NEBCTY1G
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.62 | P13:18-345:OPPD:NEBCTY1G
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.85 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.61 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.9 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.67 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.64 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.86 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.63 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.61 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.09 | P13:230-24:OTP:AUTO-SINGLE:BIGSTON4:BIGSTN1G:1
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 102.81 | P13:230-24:OTP:AUTO-SINGLE:BIGSTON4:BIGSTN1G:1
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 101.85 | P13:230-24:OTP:AUTO-SINGLE:BIGSTON4:BIGSTN1G:1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.85 | P13:23-345:OPPD:NEBCTY2G
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.62 | P13:23-345:OPPD:NEBCTY2G
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.59 | P13:23-345:OPPD:NEBCTY2G
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.85 | P13:24-345:OTP:AUTO-SINGLE:COYOTE1G:COYOTE3:1
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.61 | P13:24-345:OTP:AUTO-SINGLE:COYOTE1G:COYOTE3:1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.87 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.61 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 102.73 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 102.47 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 101.55 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.86 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.63 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.62 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.85 | P13:345:MDU:COYOTE GSU LOSS:COYOTE::1::::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.61 | P13:345:MDU:COYOTE GSU LOSS:COYOTE::1::::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 105.16 | P13:345-22:AEPW:N.E.S.-7_#1
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 104.91 | P13:345-22:AEPW:N.E.S.-7_#1
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 103.83 | P13:345-22:AEPW:N.E.S.-7_#1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.87 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.63 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.61 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.81 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.6 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.56 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 102.06 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 101.79 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 101.22 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.8 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.6 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.56 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72412 | 103.17 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72714 | 104.88 | P21:345:UMZW:# 725 #: GI IN NE. GI-SWEET LINE FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 104.3 | P21:345:UMZW:# 725 #: GI IN NE. GI-SWEET LINE FAULT
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72436 | 103.28 | P21:345:UMZW:# 725 #: GI IN NE. GI-SWEET LINE FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72739 | 104.62 | P22:345:AMMO::OVERTON:1
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72458 | 104.43 | P22:345:AMMO::OVERTON:1
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72457 | 103.46 | P22:345:AMMO::OVERTON:1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.86 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.62 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.85 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.62 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.85 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.62 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.59 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.86 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.62 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.59 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.68 | P23:161-345:KCPL:IATAN_R1-11::IATANU1-IATANT11
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.43 | P23:161-345:KCPL:IATAN_R1-11::IATANU1-IATANT11
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.44 | P23:161-345:KCPL:IATAN_R1-11::IATANU1-IATANT11
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72702 | 104.58 | P23:161-345:KCPL:NASHUA_R9-22::NASHUA-IATAN-NASHT11
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72424 | 104.33 | P23:161-345:KCPL:NASHUA_R9-22::NASHUA-IATAN-NASHT11
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72421 | 103.29 | P23:161-345:KCPL:NASHUA_R9-22::NASHUA-IATAN-NASHT11
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72593 | 103.07 | P23:161-345:KCPL:STILWELL_R5-22::STILWELL-LACYGNE-STILT22
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72315 | 102.92 | P23:161-345:KCPL:STILWELL_R5-22::STILWELL-LACYGNE-STILT22
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72319 | 101.76 | P23:161-345:KCPL:STILWELL_R5-22::STILWELL-LACYGNE-STILT22
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7255 | 103.26 | P23:161-345:KCPL:WGARDNER_R10-11::WGARD-LACYGNE-WGARDT11
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72271 | 103.04 | P23:161-345:KCPL:WGARDNER_R10-11::WGARD-LACYGNE-WGARDT11
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72273 | 101.95 | P23:161-345:KCPL:WGARDNER_R10-11::WGARD-LACYGNE-WGARDT11
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72615 | 106.84 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72338 | 106.72 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72342 | 104.65 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72615 | 106.83 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72338 | 106.73 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72342 | 104.64 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72615 | 106.89 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72338 | 106.73 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72342 | 104.65 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69177 | 110.26 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.68919 | 109.6 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.68907 | 106.53 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 08ALL | 2 | 20SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69178 | 101.36 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69177 | 110.27 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.68919 | 109.61 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.68907 | 106.53 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 08ALL | 2 | 20SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69178 | 101.37 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69177 | 110.05 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.68919 | 109.44 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.68907 | 106.49 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 08ALL | 2 | 20SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69178 | 101.11 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72695 | 104.92 | P23:345:AEPW:FLINT CREEK CB 12420 NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72416 | 104.61 | P23:345:AEPW:FLINT CREEK CB 12420 NBTB
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72409 | 103.34 | P23:345:AEPW:FLINT CREEK CB 12420 NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72695 | 104.92 | P23:345:AEPW:FLINT CREEK CB 12440 NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72416 | 104.61 | P23:345:AEPW:FLINT CREEK CB 12440 NBTB
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72409 | 103.34 | P23:345:AEPW:FLINT CREEK CB 12440 NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72698 | 104.86 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.724 | 104.54 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72423 | 103.29 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72667 | 104.79 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7235 | 104.38 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 105.34 | P23:345:AEPW:NES CB 3413B NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 105.08 | P23:345:AEPW:NES CB 3413B NBTB
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 103.99 | P23:345:AEPW:NES CB 3413B NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72253 | 106.14 | P23:345:AEPW:NES CB 3417B NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71982 | 105.86 | P23:345:AEPW:NES CB 3417B NBTB
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71985 | 104.37 | P23:345:AEPW:NES CB 3417B NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69538 | 110.83 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69279 | 110.28 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.6927 | 107.38 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 08ALL | 2 | 20SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.6954 | 101.94 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72718 | 104.7 | P23:345:AEPW:NW TEXARKANA CB 11810 NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72436 | 104.39 | P23:345:AEPW:NW TEXARKANA CB 11810 NBTB
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72453 | 103.21 | P23:345:AEPW:NW TEXARKANA CB 11810 NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72718 | 104.7 | P23:345:AEPW:NW TEXARKANA CB 11820 NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72436 | 104.39 | P23:345:AEPW:NW TEXARKANA CB 11820 NBTB
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72453 | 103.21 | P23:345:AEPW:NW TEXARKANA CB 11820 NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72665 | 103.08 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7236 | 102.67 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7239 | 101.47 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72665 | 101.96 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7236 | 101.53 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7239 | 100.4 | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72659 | 103.34 | P23:345:AEPW:ONETA CB 3401A NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72381 | 103.06 | P23:345:AEPW:ONETA CB 3401A NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72628 | 104.92 | P23:345:AEPW:ONETA CB 3409A NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72351 | 104.67 | P23:345:AEPW:ONETA CB 3409A NBTB
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72363 | 103.43 | P23:345:AEPW:ONETA CB 3409A NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72712 | 104.9 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 104.63 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7243 | 103.62 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72481 | 105.37 | P23:345:AEPW:RIVERSIDE CB 3401A NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72187 | 105.15 | P23:345:AEPW:RIVERSIDE CB 3401A NBTB
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72134 | 104.48 | P23:345:AEPW:RIVERSIDE CB 3401A NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72481 | 105.47 | P23:345:AEPW:RIVERSIDE CB 3405A NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72187 | 105.27 | P23:345:AEPW:RIVERSIDE CB 3405A NBTB
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72135 | 104.56 | P23:345:AEPW:RIVERSIDE CB 3405A NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72622 | 105.18 | P23:345:AEPW:RIVERSIDE CB 3425A NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72346 | 104.89 | P23:345:AEPW:RIVERSIDE CB 3425A NBTB
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72359 | 103.67 | P23:345:AEPW:RIVERSIDE CB 3425A NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72628 | 104.84 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72351 | 104.82 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72363 | 103.24 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72698 | 104.71 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72401 | 104.4 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72698 | 104.71 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72401 | 104.4 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72698 | 104.71 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72401 | 104.4 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72156 | 105.33 | P23:345:AEPW:TULSA NORTH CB 3409A NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71875 | 105.04 | P23:345:AEPW:TULSA NORTH CB 3409A NBTB
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71867 | 103.89 | P23:345:AEPW:TULSA NORTH CB 3409A NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71887 | 114.58 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71578 | 114.37 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71535 | 113.56 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 08ALL | 2 | 20SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71927 | 102.84 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 08ALL | 2 | 24SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71981 | 100.74 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72723 | 104.54 | P23:345:AEPW:VALLIANT CB 3409A NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72716 | 104.92 | P23:345:AEPW:VALLIANT CB 3417A NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 104.61 | P23:345:AEPW:VALLIANT CB 3417A NBTB
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72456 | 103.39 | P23:345:AEPW:VALLIANT CB 3417A NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72727 | 105.12 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72444 | 104.76 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72462 | 103.58 | P23:345:AEPW:VALLIANT CB 3421A NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72718 | 104.69 | P23:345:AEPW:WELSH CB 11590 NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72436 | 104.38 | P23:345:AEPW:WELSH CB 11590 NBTB
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72453 | 103.2 | P23:345:AEPW:WELSH CB 11590 NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72714 | 104.75 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 104.57 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72433 | 103.64 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72713 | 104.52 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 104.38 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.38 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72098 | 117.19 | P23:345:GRDA:CLEVLND CB10180
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71774 | 117.14 | P23:345:GRDA:CLEVLND CB10180
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71702 | 116.59 | P23:345:GRDA:CLEVLND CB10180
Thermal | 08ALL | 2 | 20SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72147 | 105.14 | P23:345:GRDA:CLEVLND CB10180
Thermal | 08ALL | 2 | 24SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72205 | 103.01 | P23:345:GRDA:CLEVLND CB10180
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72814 | 101.1 | P23:345:GRDA:CLEVLND CB10180
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72531 | 101.03 | P23:345:GRDA:CLEVLND CB10180
Thermal | 08ALL | 2 | 29SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72383 | 100.25 | P23:345:GRDA:CLEVLND CB10180
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72201 | 112.79 | P23:345:GRDA:CLEVLND CB13280
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71889 | 112.55 | P23:345:GRDA:CLEVLND CB13280
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71838 | 112.09 | P23:345:GRDA:CLEVLND CB13280
Thermal | 08ALL | 2 | 20SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72238 | 100.86 | P23:345:GRDA:CLEVLND CB13280
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72459 | 103.28 | P23:345:GRDA:GRDA CB12380
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72173 | 101.73 | P23:345:GRDA:GRDA CB12380
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7226 | 107.44 | P23:345:GRDA:GRDA CB9080
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72541 | 107.04 | P23:345:GRDA:GRDA CB9080
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72265 | 104.98 | P23:345:GRDA:GRDA CB9080
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72399 | 103.58 | P23:345:GRDA:GRDA CB9580
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72399 | 102.16 | P23:345:GRDA:GRDA CB9580
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72592 | 103.57 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72315 | 103.44 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72318 | 102.22 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72592 | 102.97 | P23:345:KCPL:LACYGNE_R4-5::LACYGNE-STILWELL-LACYGT7
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72315 | 102.78 | P23:345:KCPL:LACYGNE_R4-5::LACYGNE-STILWELL-LACYGT7
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72318 | 101.68 | P23:345:KCPL:LACYGNE_R4-5::LACYGNE-STILWELL-LACYGT7
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72681 | 104.73 | P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72402 | 104.49 | P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72398 | 103.48 | P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72373 | 102.93 | P23:345:KCPL:WGARDNER_R10-12::WGARD-STILWELL-LACYGNE
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7209 | 102.85 | P23:345:KCPL:WGARDNER_R10-12::WGARD-STILWELL-LACYGNE
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72092 | 101.73 | P23:345:KCPL:WGARDNER_R10-12::WGARD-STILWELL-LACYGNE
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72703 | 104.55 | P23:345:KCPL-GMO:IATAN_R7-9::IATAN-NASHUA-EASTOWNE
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72425 | 104.3 | P23:345:KCPL-GMO:IATAN_R7-9::IATAN-NASHUA-EASTOWNE
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72422 | 103.25 | P23:345:KCPL-GMO:IATAN_R7-9::IATAN-NASHUA-EASTOWNE
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72612 | 103.32 | P23:345:KCPL-GMO:STILWELL_R2-5::STILWELL-PECULIAR-LACYGNE
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72332 | 103.09 | P23:345:KCPL-GMO:STILWELL_R2-5::STILWELL-PECULIAR-LACYGNE
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72336 | 101.96 | P23:345:KCPL-GMO:STILWELL_R2-5::STILWELL-PECULIAR-LACYGNE
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.67588 | 104.49 | P23:345:KCPL-WERE:LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.67893 | 103.21 | P23:345:KCPL-WERE:LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.67588 | 104.79 | P23:345:KCPL-WERE:LACYGNE_R4-6::LACYGNE-NEOSHO-LACYGT7
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.67893 | 103.52 | P23:345:KCPL-WERE:LACYGNE_R4-6::LACYGNE-NEOSHO-LACYGT7
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72925 | 131.69 | P23:345:KCPL-WERE:LACYGNE_R4-9::LACYGNE-WAVERLY-LACYGT7
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72583 | 131.66 | P23:345:KCPL-WERE:LACYGNE_R4-9::LACYGNE-WAVERLY-LACYGT7
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72595 | 130.19 | P23:345:KCPL-WERE:LACYGNE_R4-9::LACYGNE-WAVERLY-LACYGT7
Thermal | 08ALL | 2 | 20SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72983 | 123.25 | P23:345:KCPL-WERE:LACYGNE_R4-9::LACYGNE-WAVERLY-LACYGT7
Thermal | 08ALL | 2 | 24SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.73047 | 120.11 | P23:345:KCPL-WERE:LACYGNE_R4-9::LACYGNE-WAVERLY-LACYGT7
Thermal | 08ALL | 2 | 29SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.73221 | 115.74 | P23:345:KCPL-WERE:LACYGNE_R4-9::LACYGNE-WAVERLY-LACYGT7
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72145 | 131.02 | P23:345:KCPL-WERE:LACYGNE_R9-10::LACYGNE-WAVERLY-WGARD
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72489 | 130.7 | P23:345:KCPL-WERE:LACYGNE_R9-10::LACYGNE-WAVERLY-WGARD
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72155 | 129.39 | P23:345:KCPL-WERE:LACYGNE_R9-10::LACYGNE-WAVERLY-WGARD
Thermal | 08ALL | 2 | 20SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72573 | 121.39 | P23:345:KCPL-WERE:LACYGNE_R9-10::LACYGNE-WAVERLY-WGARD
Thermal | 08ALL | 2 | 24SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72632 | 118.27 | P23:345:KCPL-WERE:LACYGNE_R9-10::LACYGNE-WAVERLY-WGARD
Thermal | 08ALL | 2 | 29SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72812 | 113.79 | P23:345:KCPL-WERE:LACYGNE_R9-10::LACYGNE-WAVERLY-WGARD
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72543 | 107.68 | P23:345:KCPL-WERE:WGARDNER_R12-13::WGARD-STILWELL-SWISSVALE
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72247 | 107.35 | P23:345:KCPL-WERE:WGARDNER_R12-13::WGARD-STILWELL-SWISSVALE
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72248 | 106.1 | P23:345:KCPL-WERE:WGARDNER_R12-13::WGARD-STILWELL-SWISSVALE
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72415 | 107.08 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72118 | 106.82 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72119 | 105.53 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72708 | 103.85 | P23:345:MDU::COYOTE::5707-5712-5715::::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7243 | 103.6 | P23:345:MDU::COYOTE::5707-5712-5715::::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72412 | 103.17 | P23:345:MEC:BONDURANT 906
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72708 | 103.83 | P23:345:MEC:CBEC 905
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7243 | 103.62 | P23:345:MEC:CBEC 905
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 102.6 | P23:345:MEC:CBEC 905
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.81 | P23:345:MEC:CBEC 908
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.6 | P23:345:MEC:CBEC 908
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.56 | P23:345:MEC:CBEC 908
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72412 | 103.17 | P23:345:MEC:GDMEC 901
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72412 | 103.17 | P23:345:MEC:GDMEC 902
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72412 | 103.17 | P23:345:MEC:MONTEZUMA 901
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.87 | P23:345:MEC:RAUN 0180
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.64 | P23:345:MEC:RAUN 0180
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.61 | P23:345:MEC:RAUN 0180
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 102.07 | P23:345:MEC:RAUN 0210
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 101.8 | P23:345:MEC:RAUN 0210
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 101.22 | P23:345:MEC:RAUN 0210
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72412 | 103.18 | P23:345:MEC:SYCAMORE 901
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72412 | 103.18 | P23:345:MEC:SYCAMORE 902
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.86 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.62 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.85 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.62 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.85 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.62 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.59 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.86 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.62 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.59 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72708 | 103.85 | P23:345:OTP:CENTER 3:3215
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7243 | 103.61 | P23:345:OTP:CENTER 3:3215
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72708 | 103.85 | P23:345:OTP:CENTER 3:3215(1)
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7243 | 103.61 | P23:345:OTP:CENTER 3:3215(1)
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72708 | 103.85 | P23:345:OTP:CENTER 3:3225
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7243 | 103.61 | P23:345:OTP:CENTER 3:3225
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72708 | 103.85 | P23:345:OTP:CENTER 3:3225(1)
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7243 | 103.61 | P23:345:OTP:CENTER 3:3225(1)
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72482 | 103.26 | P23:345:SUNC:HLC_BRK188
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72483 | 104.25 | P23:345:SUNC:MO_BRK188
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72483 | 104.25 | P23:345:SUNC:MO_BRK388
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72722 | 104.96 | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72428 | 104.33 | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72443 | 103.27 | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72722 | 104.96 | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72428 | 104.33 | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72443 | 103.27 | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.74632 | 102.33 | P23:345:WERE:BENT_345-50::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.74384 | 101.92 | P23:345:WERE:BENT_345-50::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.74356 | 100.75 | P23:345:WERE:BENT_345-50::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72705 | 107.34 | P23:345:WERE:EMPR_345-210::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72413 | 106.98 | P23:345:WERE:EMPR_345-210::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72405 | 106.02 | P23:345:WERE:EMPR_345-210::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72732 | 104.97 | P23:345:WERE:GEAR_BKRS::FUTURE
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72453 | 104.59 | P23:345:WERE:GEAR_BKRS::FUTURE
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72465 | 103.61 | P23:345:WERE:GEAR_BKRS::FUTURE
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72755 | 107.66 | P23:345:WERE:HOYT_345_BKRS::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72447 | 107.5 | P23:345:WERE:HOYT_345_BKRS::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72434 | 106.31 | P23:345:WERE:HOYT_345_BKRS::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.55 | P23:345:WERE:JEC_345-15::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.28 | P23:345:WERE:JEC_345-15::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 102.28 | P23:345:WERE:JEC_345-15::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72749 | 106.46 | P23:345:WERE:JEC_345-16::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72445 | 106.24 | P23:345:WERE:JEC_345-16::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7243 | 105.22 | P23:345:WERE:JEC_345-16::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72749 | 107.45 | P23:345:WERE:JEC_345-17::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72446 | 107.23 | P23:345:WERE:JEC_345-17::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72433 | 106.1 | P23:345:WERE:JEC_345-17::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.55 | P23:345:WERE:JEC_345-19::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.28 | P23:345:WERE:JEC_345-19::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 102.24 | P23:345:WERE:JEC_345-19::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72727 | 103.85 | P23:345:WERE:JEC_345-20::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72451 | 103.49 | P23:345:WERE:JEC_345-20::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72456 | 102.43 | P23:345:WERE:JEC_345-20::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69338 | 108.91 | P23:345:WERE:N345_345-20::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69079 | 108.19 | P23:345:WERE:N345_345-20::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69067 | 105.45 | P23:345:WERE:N345_345-20::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.67145 | 103.67 | P23:345:WERE:N345_345-80::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.6745 | 101.86 | P23:345:WERE:N345_345-80::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.67172 | 101.65 | P23:345:WERE:N345_345-80::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72928 | 107.42 | P23:345:WERE:RENO_345-150::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72652 | 106.98 | P23:345:WERE:RENO_345-150::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72653 | 106.03 | P23:345:WERE:RENO_345-150::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72928 | 107.42 | P23:345:WERE:RENO_345-160::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72652 | 106.98 | P23:345:WERE:RENO_345-160::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72653 | 106.03 | P23:345:WERE:RENO_345-160::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72956 | 105.64 | P23:345:WERE:ROSE_345-50::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72665 | 105.11 | P23:345:WERE:ROSE_345-50::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72741 | 106.79 | P23:345:WERE:STRA_345-100::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72438 | 106.58 | P23:345:WERE:STRA_345-100::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 105.44 | P23:345:WERE:STRA_345-100::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72748 | 106.6 | P23:345:WERE:STRA_345-95::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72446 | 106.33 | P23:345:WERE:STRA_345-95::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72439 | 105.21 | P23:345:WERE:STRA_345-95::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72658 | 104.61 | P23:345:WERE:STRA_345-99::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72378 | 104.42 | P23:345:WERE:STRA_345-99::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72375 | 103.37 | P23:345:WERE:STRA_345-99::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72729 | 105.07 | P23:345:WERE:SUMM_345-218::FUTURE
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7245 | 104.64 | P23:345:WERE:SUMM_345-218::FUTURE
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72461 | 103.67 | P23:345:WERE:SUMM_345-218::FUTURE
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72705 | 107.32 | P23:345:WERE:SWIS_345-1::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72413 | 106.97 | P23:345:WERE:SWIS_345-1::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72405 | 106 | P23:345:WERE:SWIS_345-1::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7269 | 107.49 | P23:345:WERE:SWIS_345-2::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72396 | 107.13 | P23:345:WERE:SWIS_345-2::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72389 | 106.17 | P23:345:WERE:SWIS_345-2::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72554 | 107.74 | P23:345:WERE:SWIS_345-5::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72258 | 107.38 | P23:345:WERE:SWIS_345-5::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72258 | 106.14 | P23:345:WERE:SWIS_345-5::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72583 | 128.15 | P23:345:WERE:WAVS_BKRS::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72925 | 128.13 | P23:345:WERE:WAVS_BKRS::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72595 | 126.68 | P23:345:WERE:WAVS_BKRS::
Thermal | 08ALL | 2 | 20SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72983 | 119.6 | P23:345:WERE:WAVS_BKRS::
Thermal | 08ALL | 2 | 24SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.73047 | 116.53 | P23:345:WERE:WAVS_BKRS::
Thermal | 08ALL | 2 | 29SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.73221 | 112.34 | P23:345:WERE:WAVS_BKRS::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72814 | 101.49 | P23:345:WERE:WICH_345-116::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72527 | 101.48 | P23:345:WERE:WICH_345-116::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72543 | 100.34 | P23:345:WERE:WICH_345-116::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.74373 | 105.69 | P23:345:WERE:WICH_345-50::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.74118 | 105.31 | P23:345:WERE:WICH_345-50::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.74111 | 104.63 | P23:345:WERE:WICH_345-50::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72495 | 130.42 | P23:345:WERE:WOLF_345-120::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72843 | 130.27 | P23:345:WERE:WOLF_345-120::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72507 | 128.81 | P23:345:WERE:WOLF_345-120::
Thermal | 08ALL | 2 | 20SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72904 | 122.14 | P23:345:WERE:WOLF_345-120::
Thermal | 08ALL | 2 | 24SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72968 | 119.02 | P23:345:WERE:WOLF_345-120::
Thermal | 08ALL | 2 | 29SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.73149 | 114.67 | P23:345:WERE:WOLF_345-120::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.88 | P23:345:XEL:8N17 SHC
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.65 | P23:345:XEL:8N17 SHC
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.62 | P23:345:XEL:8N17 SHC
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72708 | 102.73 | P23:345:XEL:8N22 SHC
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7243 | 102.46 | P23:345:XEL:8N22 SHC
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 101.54 | P23:345:XEL:8N22 SHC
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72708 | 103.85 | P23:345:XEL:8N28 SHC
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7243 | 103.63 | P23:345:XEL:8N28 SHC
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.61 | P23:345:XEL:8N28 SHC
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72708 | 103.83 | P23:345:XEL:8N8 MNN
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7243 | 103.6 | P23:345:XEL:8N8 MNN
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 102.58 | P23:345:XEL:8N8 MNN
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.9 | P23:345:XEL:8P1 KING
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.67 | P23:345:XEL:8P1 KING
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.64 | P23:345:XEL:8P1 KING
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.9 | P23:345:XEL:8P2 KING
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.67 | P23:345:XEL:8P2 KING
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.64 | P23:345:XEL:8P2 KING
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72447 | 103.25 | P24:345:AMMO::MCCREDIE:1
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72318 | 108.64 | P24:345:GRDA:GRDA CB400T
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72599 | 108.18 | P24:345:GRDA:GRDA CB400T
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72322 | 104.94 | P24:345:GRDA:GRDA CB400T
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72318 | 107.51 | P24:345:GRDA:GRECTP CB100T
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72599 | 106.98 | P24:345:GRDA:GRECTP CB100T
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72322 | 104.94 | P24:345:GRDA:GRECTP CB100T
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 105.34 | P41:345:AEPW:NES CB 3413B NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 105.08 | P41:345:AEPW:NES CB 3413B NBTB+FAULT
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 103.99 | P41:345:AEPW:NES CB 3413B NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72253 | 106.14 | P41:345:AEPW:NES CB 3417B NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71982 | 105.86 | P41:345:AEPW:NES CB 3417B NBTB+FAULT
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71985 | 104.37 | P41:345:AEPW:NES CB 3417B NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72718 | 104.69 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72436 | 104.38 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72453 | 103.2 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72713 | 103.54 | P41:345:OKGE:SB_REUD7381
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72434 | 103.32 | P41:345:OKGE:SB_REUD7381
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72437 | 102.29 | P41:345:OKGE:SB_REUD7381
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72712 | 103.54 | P41:345:OKGE:SB_REUD7383
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72434 | 103.31 | P41:345:OKGE:SB_REUD7383
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72436 | 102.29 | P41:345:OKGE:SB_REUD7383
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.33 | P41:345:OKGE:SB_SOER7382
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.08 | P41:345:OKGE:SB_SOER7382
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.04 | P41:345:OKGE:SB_SOER7382
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72615 | 106.83 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72338 | 106.73 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72342 | 104.64 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72615 | 106.89 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72338 | 106.73 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72342 | 104.65 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69177 | 110.26 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.68919 | 109.6 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.68907 | 106.53 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 08ALL | 2 | 20SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69178 | 101.36 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69177 | 110.27 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.68919 | 109.61 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.68907 | 106.53 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 08ALL | 2 | 20SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69178 | 101.37 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69177 | 110.05 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.68919 | 109.44 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.68907 | 106.49 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 08ALL | 2 | 20SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69178 | 101.11 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72695 | 104.92 | P42:345:AEPW:FLINT CREEK CB 12420 NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72416 | 104.61 | P42:345:AEPW:FLINT CREEK CB 12420 NBTB+FAULT
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72409 | 103.34 | P42:345:AEPW:FLINT CREEK CB 12420 NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72698 | 104.86 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.724 | 104.54 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72423 | 103.29 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72667 | 104.79 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7235 | 104.38 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69538 | 110.83 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69279 | 110.28 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.6927 | 107.38 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 08ALL | 2 | 20SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.6954 | 101.94 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72665 | 103.08 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7236 | 102.67 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7239 | 101.47 | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72665 | 101.96 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7236 | 101.53 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7239 | 100.4 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72659 | 103.34 | P42:345:AEPW:ONETA CB 3401A NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72381 | 103.06 | P42:345:AEPW:ONETA CB 3401A NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72628 | 104.92 | P42:345:AEPW:ONETA CB 3409A NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72351 | 104.67 | P42:345:AEPW:ONETA CB 3409A NBTB+FAULT
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72363 | 103.43 | P42:345:AEPW:ONETA CB 3409A NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72712 | 104.9 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 104.63 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7243 | 103.62 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72481 | 105.37 | P42:345:AEPW:RIVERSIDE CB 3401A NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72187 | 105.15 | P42:345:AEPW:RIVERSIDE CB 3401A NBTB+FAULT
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72134 | 104.48 | P42:345:AEPW:RIVERSIDE CB 3401A NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72481 | 105.47 | P42:345:AEPW:RIVERSIDE CB 3405A NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72187 | 105.27 | P42:345:AEPW:RIVERSIDE CB 3405A NBTB+FAULT
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72135 | 104.56 | P42:345:AEPW:RIVERSIDE CB 3405A NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72628 | 104.84 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72351 | 104.82 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72363 | 103.24 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72698 | 104.71 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72401 | 104.4 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72698 | 104.71 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72401 | 104.4 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72698 | 104.71 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72401 | 104.4 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71887 | 114.58 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71578 | 114.37 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71535 | 113.56 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 08ALL | 2 | 20SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71927 | 102.84 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 08ALL | 2 | 24SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71981 | 100.74 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72723 | 104.54 | P42:345:AEPW:VALLIANT CB 3409A NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72716 | 104.92 | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 104.61 | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72456 | 103.39 | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72727 | 105.12 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72444 | 104.76 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72462 | 103.58 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72201 | 112.79 | P42:345:GRDA:CLEVLND CB13280
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71889 | 112.55 | P42:345:GRDA:CLEVLND CB13280
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71838 | 112.09 | P42:345:GRDA:CLEVLND CB13280
Thermal | 08ALL | 2 | 20SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72238 | 100.86 | P42:345:GRDA:CLEVLND CB13280
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72711 | 104.62 | P42:345:NPPD:BKR-AXT-3306
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7243 | 104.27 | P42:345:NPPD:BKR-AXT-3306
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7274 | 104.78 | P42:345:NPPD:BKR-AXT-3308
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72458 | 104.45 | P42:345:NPPD:BKR-AXT-3308
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72458 | 103.39 | P42:345:NPPD:BKR-AXT-3308
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.29 | P42:345:NPPD:BKR-GGS-3304
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.11 | P42:345:NPPD:BKR-GGS-3304
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72427 | 104.35 | P42:345:NPPD:BKR-GGS-3310
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72707 | 104.67 | P42:345:NPPD:BKR-PLN-3310
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72425 | 104.32 | P42:345:NPPD:BKR-PLN-3310
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 103.2 | P42:345:NPPD:BKR-PLN-3310
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72782 | 104.58 | P42:345:NPPD:BKR-RW-3302
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72499 | 104.44 | P42:345:NPPD:BKR-RW-3302
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72486 | 103.33 | P42:345:NPPD:BKR-RW-3302
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72712 | 104.95 | P42:345:NPPD:BKR-SW-3306
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7243 | 104.32 | P42:345:NPPD:BKR-SW-3306
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72434 | 103.32 | P42:345:NPPD:BKR-SW-3306
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72711 | 104.98 | P42:345:NPPD:BKR-SW-3308
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7243 | 104.33 | P42:345:NPPD:BKR-SW-3308
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72434 | 103.33 | P42:345:NPPD:BKR-SW-3308
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72715 | 104.65 | P42:345:OKGE:SB_ARIA7381
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72437 | 104.38 | P42:345:OKGE:SB_ARIA7381
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72435 | 103.37 | P42:345:OKGE:SB_ARIA7381
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72471 | 104.2 | P42:345:OKGE:SB_BOER7304
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72458 | 103.31 | P42:345:OKGE:SB_BOER7304
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72471 | 104.2 | P42:345:OKGE:SB_BOER7383
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72458 | 103.32 | P42:345:OKGE:SB_BOER7383
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72471 | 104.2 | P42:345:OKGE:SB_BOER7384
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72458 | 103.32 | P42:345:OKGE:SB_BOER7384
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7271 | 103.55 | P42:345:OKGE:SB_BVTY7305
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 103.32 | P42:345:OKGE:SB_BVTY7305
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72433 | 102.11 | P42:345:OKGE:SB_BVTY7305
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72433 | 102.12 | P42:345:OKGE:SB_BVTY7387
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72729 | 105.47 | P42:345:OKGE:SB_CION7382
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72441 | 105.17 | P42:345:OKGE:SB_CION7382
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72453 | 104.26 | P42:345:OKGE:SB_CION7382
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72446 | 102.57 | P42:345:OKGE:SB_CION7384
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72641 | 103.05 | P42:345:OKGE:SB_CRER7309
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72356 | 102.89 | P42:345:OKGE:SB_CRER7309
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72354 | 101.88 | P42:345:OKGE:SB_CRER7309
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72648 | 103.29 | P42:345:OKGE:SB_CRER7389
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72364 | 103.12 | P42:345:OKGE:SB_CRER7389
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72726 | 105.24 | P42:345:OKGE:SB_DRER7384
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72438 | 104.94 | P42:345:OKGE:SB_DRER7384
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7245 | 104 | P42:345:OKGE:SB_DRER7384
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72911 | 103.63 | P42:345:OKGE:SB_HURS7309
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72632 | 103.47 | P42:345:OKGE:SB_HURS7309
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72652 | 102.55 | P42:345:OKGE:SB_HURS7309
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72911 | 103.63 | P42:345:OKGE:SB_HURS7319
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72632 | 103.47 | P42:345:OKGE:SB_HURS7319
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72652 | 102.55 | P42:345:OKGE:SB_HURS7319
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72911 | 103.63 | P42:345:OKGE:SB_HURS7389
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72632 | 103.47 | P42:345:OKGE:SB_HURS7389
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72652 | 102.56 | P42:345:OKGE:SB_HURS7389
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.4 | P42:345:OKGE:SB_MICO7311
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72221 | 104.23 | P42:345:OKGE:SB_MUGE7387
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7402 | 101.92 | P42:345:OKGE:SB_RARD7311
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.74332 | 101.78 | P42:345:OKGE:SB_RARD7311
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.74126 | 101.64 | P42:345:OKGE:SB_RARD7311
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7402 | 109.29 | P42:345:OKGE:SB_RARD7313
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.74332 | 109.16 | P42:345:OKGE:SB_RARD7313
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.74126 | 109.06 | P42:345:OKGE:SB_RARD7313
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7402 | 113.74 | P42:345:OKGE:SB_RARD7383
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.74332 | 113.54 | P42:345:OKGE:SB_RARD7383
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.74126 | 113.41 | P42:345:OKGE:SB_RARD7383
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7402 | 102.08 | P42:345:OKGE:SB_RARD7393
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.74332 | 101.95 | P42:345:OKGE:SB_RARD7393
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.74126 | 101.8 | P42:345:OKGE:SB_RARD7393
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72911 | 101.68 | P42:345:OKGE:SB_REOW7312
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72632 | 101.5 | P42:345:OKGE:SB_REOW7312
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72652 | 100.57 | P42:345:OKGE:SB_REOW7312
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7298 | 102.07 | P42:345:OKGE:SB_REOW7319
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72706 | 101.91 | P42:345:OKGE:SB_REOW7319
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72723 | 101.07 | P42:345:OKGE:SB_REOW7319
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72988 | 105.07 | P42:345:OKGE:SB_REOW7382
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72712 | 104.86 | P42:345:OKGE:SB_REOW7382
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72732 | 104.08 | P42:345:OKGE:SB_REOW7382
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72988 | 102.63 | P42:345:OKGE:SB_REOW7389
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72712 | 102.45 | P42:345:OKGE:SB_REOW7389
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72732 | 101.61 | P42:345:OKGE:SB_REOW7389
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72848 | 105.51 | P42:345:OKGE:SB_RETN7303
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72577 | 105.22 | P42:345:OKGE:SB_RETN7303
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72576 | 104.21 | P42:345:OKGE:SB_RETN7303
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72848 | 105.52 | P42:345:OKGE:SB_RETN7311
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72577 | 105.22 | P42:345:OKGE:SB_RETN7311
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72576 | 104.22 | P42:345:OKGE:SB_RETN7311
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72848 | 105.51 | P42:345:OKGE:SB_RETN7383
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72577 | 105.21 | P42:345:OKGE:SB_RETN7383
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72576 | 104.21 | P42:345:OKGE:SB_RETN7383
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7248 | 105.39 | P42:345:OKGE:SB_REUD7386
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72187 | 105.21 | P42:345:OKGE:SB_REUD7386
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72134 | 104.53 | P42:345:OKGE:SB_REUD7386
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72713 | 104.91 | P42:345:OKGE:SB_SEOL7385
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72433 | 104.64 | P42:345:OKGE:SB_SEOL7385
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 103.64 | P42:345:OKGE:SB_SEOL7385
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72715 | 104.94 | P42:345:OKGE:SB_SEOL7386
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72434 | 104.67 | P42:345:OKGE:SB_SEOL7386
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72433 | 103.66 | P42:345:OKGE:SB_SEOL7386
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7402 | 113.74 | P42:345:OKGE:SB_SOER7383
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.74332 | 113.54 | P42:345:OKGE:SB_SOER7383
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.74126 | 113.4 | P42:345:OKGE:SB_SOER7383
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72429 | 102.16 | P42:345:OKGE:SB_TAGA7386
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72911 | 106.29 | P42:345:OKGE:SB_WONG7313
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72632 | 106.08 | P42:345:OKGE:SB_WONG7313
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72652 | 105.21 | P42:345:OKGE:SB_WONG7313
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72848 | 106.01 | P42:345:OKGE:SB_WONG7315
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72577 | 105.71 | P42:345:OKGE:SB_WONG7315
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72576 | 104.71 | P42:345:OKGE:SB_WONG7315
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72911 | 106.26 | P42:345:OKGE:SB_WONG7383
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72632 | 106.04 | P42:345:OKGE:SB_WONG7383
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72652 | 105.18 | P42:345:OKGE:SB_WONG7383
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72884 | 106.76 | P42:345:OKGE:SB_WONG7385
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72619 | 106.53 | P42:345:OKGE:SB_WONG7385
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72615 | 105.52 | P42:345:OKGE:SB_WONG7385
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.87 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72431 | 103.65 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72432 | 102.6 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72708 | 103.8 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72433 | 103.57 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72434 | 102.53 | P42:345:SPS:FINNEY_OR70_19L
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72718 | 102.99 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72442 | 102.71 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72441 | 101.73 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72707 | 103.26 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72429 | 103.02 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72615 | 106.84 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72338 | 106.72 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72342 | 104.65 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72695 | 104.92 | P43:345:AEPW:FLINT CREEK CB 12440 NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72416 | 104.61 | P43:345:AEPW:FLINT CREEK CB 12440 NBTB+FAULT
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72409 | 103.34 | P43:345:AEPW:FLINT CREEK CB 12440 NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72718 | 104.7 | P43:345:AEPW:NW TEXARKANA CB 11810 NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72436 | 104.39 | P43:345:AEPW:NW TEXARKANA CB 11810 NBTB+FAULT
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72453 | 103.21 | P43:345:AEPW:NW TEXARKANA CB 11810 NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72718 | 104.7 | P43:345:AEPW:NW TEXARKANA CB 11820 NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72436 | 104.39 | P43:345:AEPW:NW TEXARKANA CB 11820 NBTB+FAULT
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72453 | 103.21 | P43:345:AEPW:NW TEXARKANA CB 11820 NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72622 | 105.18 | P43:345:AEPW:RIVERSIDE CB 3425A NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72346 | 104.89 | P43:345:AEPW:RIVERSIDE CB 3425A NBTB+FAULT
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72359 | 103.67 | P43:345:AEPW:RIVERSIDE CB 3425A NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72156 | 105.33 | P43:345:AEPW:TULSA NORTH CB 3409A NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71875 | 105.04 | P43:345:AEPW:TULSA NORTH CB 3409A NBTB+FAULT
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71867 | 103.89 | P43:345:AEPW:TULSA NORTH CB 3409A NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72098 | 117.19 | P43:345:GRDA:CLEVLND CB10180
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71774 | 117.14 | P43:345:GRDA:CLEVLND CB10180
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71702 | 116.59 | P43:345:GRDA:CLEVLND CB10180
Thermal | 08ALL | 2 | 20SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72147 | 105.14 | P43:345:GRDA:CLEVLND CB10180
Thermal | 08ALL | 2 | 24SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72205 | 103.01 | P43:345:GRDA:CLEVLND CB10180
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72814 | 101.1 | P43:345:GRDA:CLEVLND CB10180
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72531 | 101.03 | P43:345:GRDA:CLEVLND CB10180
Thermal | 08ALL | 2 | 29SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72383 | 100.25 | P43:345:GRDA:CLEVLND CB10180
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72459 | 103.28 | P43:345:GRDA:GRDA CB12380
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72173 | 101.73 | P43:345:GRDA:GRDA CB12380
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7226 | 107.44 | P43:345:GRDA:GRDA CB9080
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72541 | 107.04 | P43:345:GRDA:GRDA CB9080
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72265 | 104.98 | P43:345:GRDA:GRDA CB9080
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72399 | 103.58 | P43:345:GRDA:GRDA CB9580
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72399 | 102.16 | P43:345:GRDA:GRDA CB9580
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72471 | 104.2 | P43:345:SPS:TUCO:NR20_19L
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72458 | 103.32 | P43:345:SPS:TUCO:NR20_19L
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72704 | 102.57 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72427 | 102.51 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72427 | 101.49 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72722 | 104.96 | P45:345:UMZW:# 1328 #: GI IN NE.
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72428 | 104.33 | P45:345:UMZW:# 1328 #: GI IN NE.
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72443 | 103.27 | P45:345:UMZW:# 1328 #: GI IN NE.
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72318 | 108.64 | P46:345:GRDA:GRDA CB400T
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72599 | 108.18 | P46:345:GRDA:GRDA CB400T
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72322 | 104.94 | P46:345:GRDA:GRDA CB400T
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72318 | 107.51 | P46:345:GRDA:GRECTP CB100T
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72599 | 106.98 | P46:345:GRDA:GRECTP CB100T
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72322 | 104.94 | P46:345:GRDA:GRECTP CB100T
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72708 | 103.25 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7243 | 103.01 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72709 | 103.26 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7243 | 103.01 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72561 | 103.42 | P55:161-345:KCPL:W.GARDNER_BUS_11::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72282 | 103.26 | P55:161-345:KCPL:W.GARDNER_BUS_11::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72285 | 102.14 | P55:161-345:KCPL:W.GARDNER_BUS_11::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72646 | 104.75 | P55:161-345:KCPL-WERE:CRAIG_BUS_11_345::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72367 | 104.51 | P55:161-345:KCPL-WERE:CRAIG_BUS_11_345::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72364 | 103.42 | P55:161-345:KCPL-WERE:CRAIG_BUS_11_345::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 | 956 |  | 0.72709 | 103.87 | System Intact
Thermal | 08ALL | 2 | 19WP | GEN-2017-068 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 | 956 |  | 0.08723 | 103.87 | System Intact
Thermal | 08ALL | 2 | 19WP | GEN-2017-086 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 | 956 |  | 0.07514 | 103.87 | System Intact
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 | 956 |  | 0.72431 | 103.63 | System Intact
Thermal | 08ALL | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 | 956 |  | 0.08451 | 103.63 | System Intact
Thermal | 08ALL | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 | 956 |  | 0.07306 | 103.63 | System Intact
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 | 956 |  | 0.72432 | 102.61 | System Intact
Thermal | 08ALL | 2 | 20G | GEN-2017-068 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 | 956 |  | 0.08443 | 102.61 | System Intact
Thermal | 08ALL | 2 | 20G | GEN-2017-086 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 | 956 |  | 0.07233 | 102.61 | System Intact
Thermal | 08ALL | 2 | 29SP | GEN-2017-086 | 'FROM -> TO' | 532798 VIOLA 7 345 997930 VIOLA TX-1 138 1 |  | 440 | 0.24396 | 103.76 | P12:345:WERE:VIOL-WICH_345::
Thermal | 08ALL | 2 | 29SP | GEN-2017-086 | 'FROM -> TO' | 532798 VIOLA 7 345 997930 VIOLA TX-1 138 1 |  | 440 | 0.24394 | 104.06 | P23:345:WERE:WICH_345-116::
Thermal | 08ALL | 2 | 24SP | GEN-2017-086 | 'FROM -> TO' | 532798 VIOLA 7 345 997931 VIOLA TX-1 138 1 |  | 440 | 0.24381 | 103.86 | P12:345:WERE:VIOL-WICH_345::
Thermal | 08ALL | 2 | 24SP | GEN-2017-086 | 'FROM -> TO' | 532798 VIOLA 7 345 997931 VIOLA TX-1 138 1 |  | 440 | 0.24379 | 104.22 | P23:345:WERE:WICH_345-116::
Thermal | 08ALL | 2 | 20SP | GEN-2017-086 | 'FROM -> TO' | 532798 VIOLA 7 345 997935 VIOLA TX-1 138 1 |  | 440 | 0.24343 | 104.43 | P12:345:WERE:VIOL-WICH_345::
Thermal | 08ALL | 2 | 20SP | GEN-2017-086 | 'FROM -> TO' | 532798 VIOLA 7 345 997935 VIOLA TX-1 138 1 |  | 440 | 0.2434 | 104.81 | P23:345:WERE:WICH_345-116::
Thermal | 08ALL | 2 | 20SP | GEN-2017-068 | 'FROM -> TO' | 532799 WAVERLY7 345 542981 LACYGNE7 345 1 | 1141 |  | 0.09259 | 108.39 | System Intact
Thermal | 08ALL | 2 | 20SP | GEN-2017-071 | 'FROM -> TO' | 532799 WAVERLY7 345 542981 LACYGNE7 345 1 | 1141 |  | 0.03809 | 108.39 | System Intact
Thermal | 08ALL | 2 | 20SP | GEN-2017-072 | 'FROM -> TO' | 532799 WAVERLY7 345 542981 LACYGNE7 345 1 | 1141 |  | 0.03809 | 108.39 | System Intact
Thermal | 08ALL | 2 | 20SP | GEN-2017-086 | 'FROM -> TO' | 532799 WAVERLY7 345 542981 LACYGNE7 345 1 | 1141 |  | 0.0868 | 108.39 | System Intact
Thermal | 08ALL | 2 | 20G | GEN-2017-068 | 'FROM -> TO' | 532799 WAVERLY7 345 542981 LACYGNE7 345 1 | 1141 |  | 0.08672 | 106.78 | System Intact
Thermal | 08ALL | 2 | 20G | GEN-2017-071 | 'FROM -> TO' | 532799 WAVERLY7 345 542981 LACYGNE7 345 1 | 1141 |  | 0.03248 | 106.78 | System Intact
Thermal | 08ALL | 2 | 20G | GEN-2017-072 | 'FROM -> TO' | 532799 WAVERLY7 345 542981 LACYGNE7 345 1 | 1141 |  | 0.03248 | 106.78 | System Intact
Thermal | 08ALL | 2 | 20G | GEN-2017-086 | 'FROM -> TO' | 532799 WAVERLY7 345 542981 LACYGNE7 345 1 | 1141 |  | 0.08031 | 106.78 | System Intact
Thermal | 08ALL | 2 | 24SP | GEN-2017-068 | 'FROM -> TO' | 532799 WAVERLY7 345 542981 LACYGNE7 345 1 | 1141 |  | 0.09344 | 104.54 | System Intact
Thermal | 08ALL | 2 | 24SP | GEN-2017-071 | 'FROM -> TO' | 532799 WAVERLY7 345 542981 LACYGNE7 345 1 | 1141 |  | 0.03907 | 104.54 | System Intact
Thermal | 08ALL | 2 | 24SP | GEN-2017-072 | 'FROM -> TO' | 532799 WAVERLY7 345 542981 LACYGNE7 345 1 | 1141 |  | 0.03907 | 104.54 | System Intact
Thermal | 08ALL | 2 | 24SP | GEN-2017-086 | 'FROM -> TO' | 532799 WAVERLY7 345 542981 LACYGNE7 345 1 | 1141 |  | 0.08765 | 104.54 | System Intact
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 532938 FRANKLIN5 161 1 |  | 251 | 0.37807 | 113.39 | P12:161:WERE:NSES-EMDE_161::
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 532938 FRANKLIN5 161 1 |  | 251 | 0.3658 | 112.38 | P12:161:WERE:NSES-EMDE_161::
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 532938 FRANKLIN5 161 1 |  | 251 | 0.37847 | 107.64 | P12:161:WERE:NSES-EMDE_161::
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 532938 FRANKLIN5 161 1 |  | 251 | 0.36621 | 106.65 | P12:161:WERE:NSES-EMDE_161::
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 532938 FRANKLIN5 161 1 |  | 251 | 0.38386 | 101.22 | P12:345:WERE:N345-AECI_345::
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36174 | 101.22 | P12:161:AEPW-EMDE:FLINTCR5:DEC3925
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36191 | 100.57 | P12:161:GRDA:MIAMI -KETCHUM
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36219 | 100.71 | P12:161:GRDA:PENSA -KETCHUM
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36148 | 129.13 | P12:161:WERE:NSES-EMDE_161::
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36203 | 124.02 | P12:161:WERE:NSES-EMDE_161::
Thermal | 08ALL | 2 | 20G | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36204 | 101.82 | P12:161:WERE:NSES-EMDE_161::
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 317 | 0.36321 | 100.93 | P12:161:WERE:NSES-EMDE_161::
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36513 | 101.64 | P12:345:AEPW-GRDA:FLINTCR7:TONECE7
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36498 | 105.91 | P12:345:GRDA:FLINTCR-TONECE
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36542 | 101.47 | P12:345:GRDA:FLINTCR-TONECE
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36457 | 101.56 | P12:345:GRDA:GRDA1 -GRECTAP
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.365 | 105.76 | P12:345:GRDA:GRDA1 -TONECE
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36544 | 101.24 | P12:345:GRDA:GRDA1 -TONECE
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.37012 | 113.27 | P12:345:WERE:N345-AECI_345::
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.37068 | 108.98 | P12:345:WERE:N345-AECI_345::
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36505 | 101.68 | P22:345:SPRM-AECI:17
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36401 | 104.68 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36443 | 100.08 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36401 | 104.67 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36443 | 100.06 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36401 | 104.72 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36443 | 100.17 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36513 | 101.63 | P23:345:AEPW:FLINT CREEK CB 12430 NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36513 | 101.99 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36473 | 100.05 | P23:345:GRDA:CLEVLND CB10180
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36461 | 101.58 | P23:345:GRDA:GRDA CB9080
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36499 | 108.36 | P23:345:GRDA:GRDA CB9580
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36498 | 105.91 | P23:345:GRDA:TONNECE CB12070
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36542 | 101.47 | P23:345:GRDA:TONNECE CB12070
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36498 | 105.96 | P23:345:GRDA:TONNECE CB90
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36542 | 101.5 | P23:345:GRDA:TONNECE CB90
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36498 | 105.97 | P23:345:GRDA:TONNECE CB9580
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36542 | 101.55 | P23:345:GRDA:TONNECE CB9580
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.37737 | 107.87 | P23:345:WERE:N345_345-110::
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.3779 | 102.55 | P23:345:WERE:N345_345-110::
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36457 | 103.39 | P24:345:GRDA:GRDA CB400T
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36457 | 101.52 | P24:345:GRDA:GRECTP CB100T
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36401 | 104.67 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36443 | 100.06 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36401 | 104.72 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36443 | 100.17 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36513 | 101.99 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36498 | 105.97 | P42:345:GRDA:TONNECE CB9580
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36542 | 101.55 | P42:345:GRDA:TONNECE CB9580
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36505 | 101.68 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36401 | 104.68 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36443 | 100.08 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36513 | 101.63 | P43:345:AEPW:FLINT CREEK CB 12430 NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36473 | 100.05 | P43:345:GRDA:CLEVLND CB10180
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36461 | 101.58 | P43:345:GRDA:GRDA CB9080
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36499 | 108.36 | P43:345:GRDA:GRDA CB9580
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36498 | 105.91 | P43:345:GRDA:TONNECE CB12070
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36542 | 101.47 | P43:345:GRDA:TONNECE CB12070
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36498 | 105.96 | P43:345:GRDA:TONNECE CB90
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36542 | 101.5 | P43:345:GRDA:TONNECE CB90
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36457 | 103.39 | P46:345:GRDA:GRDA CB400T
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36457 | 101.52 | P46:345:GRDA:GRECTP CB100T
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.36505 | 101.68 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532937 NEOSHO 5 161 547469 RIV4525 161 1 | 205 |  | 0.05175 | 174.51 | System Intact
Thermal | 08ALL | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 532937 NEOSHO 5 161 547469 RIV4525 161 1 | 205 |  | 0.07175 | 174.51 | System Intact
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532937 NEOSHO 5 161 547469 RIV4525 161 1 | 205 |  | 0.05237 | 166.68 | System Intact
Thermal | 08ALL | 2 | 19WP | GEN-2017-022 | 'FROM -> TO' | 532937 NEOSHO 5 161 547469 RIV4525 161 1 | 205 |  | 0.07237 | 166.68 | System Intact
Thermal | 08ALL | 2 | 29SP | GEN-2017-009 | 'FROM -> TO' | 532937 NEOSHO 5 161 547469 RIV4525 161 1 | 205 |  | 0.05209 | 156.82 | System Intact
Thermal | 08ALL | 2 | 29SP | GEN-2017-022 | 'FROM -> TO' | 532937 NEOSHO 5 161 547469 RIV4525 161 1 | 205 |  | 0.07209 | 156.82 | System Intact
Thermal | 08ALL | 2 | 24SP | GEN-2017-009 | 'FROM -> TO' | 532937 NEOSHO 5 161 547469 RIV4525 161 1 | 205 |  | 0.05177 | 154.77 | System Intact
Thermal | 08ALL | 2 | 24SP | GEN-2017-022 | 'FROM -> TO' | 532937 NEOSHO 5 161 547469 RIV4525 161 1 | 205 |  | 0.07177 | 154.77 | System Intact
Thermal | 08ALL | 2 | 20SP | GEN-2017-009 | 'FROM -> TO' | 532937 NEOSHO 5 161 547469 RIV4525 161 1 | 205 |  | 0.05178 | 152.94 | System Intact
Thermal | 08ALL | 2 | 20SP | GEN-2017-022 | 'FROM -> TO' | 532937 NEOSHO 5 161 547469 RIV4525 161 1 | 205 |  | 0.07178 | 152.94 | System Intact
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532937 NEOSHO 5 161 547469 RIV4525 161 1 | 205 |  | 0.05237 | 137.82 | System Intact
Thermal | 08ALL | 2 | 20G | GEN-2017-022 | 'FROM -> TO' | 532937 NEOSHO 5 161 547469 RIV4525 161 1 | 205 |  | 0.07237 | 137.82 | System Intact
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44468 | 101.62 | P11:022:NPPD:COOPER1G:1:983
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44468 | 101.67 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44468 | 105.71 | P11:22:AEPW:FLINTCR1
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.4446 | 100.42 | P11:22:AEPW:FLINTCR1
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44468 | 102.34 | P11:230:WERE:JECU1_GEN::
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44473 | 106.39 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44468 | 101.38 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44473 | 103.21 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44473 | 106.7 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44501 | 100.23 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44473 | 104.3 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44473 | 106.32 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44468 | 101.34 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44473 | 106.78 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44501 | 100.22 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44473 | 106.53 | P11:345:MEC-NPPD:COOPER 1
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44501 | 100.08 | P11:345:MEC-NPPD:COOPER 1
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44473 | 106.51 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44468 | 101.6 | P11:345:OPPD:NEBCTY1G
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44468 | 101.59 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44473 | 106.52 | P11:345:OPPD:NEBCTY2G
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44468 | 101.58 | P11:345:OPPD:NEBCTY2G
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44473 | 106.33 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44468 | 101.31 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44468 | 102.36 | P11:345:WERE:JECU2_GEN::
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44468 | 102.1 | P11:345:WERE:JECU3_GEN::
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.45067 | 103.79 | P12:138:WERE:ALTO-TIOG_138::
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44249 | 111 | P12:161:AEPW-EMDE:FLINTCR5:DEC3925
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44242 | 107 | P12:161:AEPW-EMDE:FLINTCR5:DEC3925
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44277 | 104.31 | P12:161:AEPW-EMDE:FLINTCR5:DEC3925
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44233 | 102.28 | P12:161:AEPW-EMDE:FLINTCR5:DEC3925
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44434 | 103.42 | P12:161:EES-EAI:M:GRANVW:OSAGE_E:BERRYV:GR_FR2:GRFR_S:HRSN_W:HRSN_S:HRSN_E:EUREKASP:1
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44257 | 110.59 | P12:161:GRDA:MIAMI -KETCHUM
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44253 | 106.79 | P12:161:GRDA:MIAMI -KETCHUM
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44285 | 104.29 | P12:161:GRDA:MIAMI -KETCHUM
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44244 | 102.07 | P12:161:GRDA:MIAMI -KETCHUM
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44274 | 110.66 | P12:161:GRDA:PENSA -KETCHUM
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.4427 | 106.79 | P12:161:GRDA:PENSA -KETCHUM
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44302 | 104.28 | P12:161:GRDA:PENSA -KETCHUM
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44262 | 102.03 | P12:161:GRDA:PENSA -KETCHUM
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.56775 | 104.54 | P12:161:WERE:MARM-NSES_161::
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.4425 | 128.35 | P12:161:WERE:NSES-EMDE_161::
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.4425 | 123.12 | P12:161:WERE:NSES-EMDE_161::
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44285 | 121.08 | P12:161:WERE:NSES-EMDE_161::
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44237 | 116.84 | P12:161:WERE:NSES-EMDE_161::
Thermal | 08ALL | 2 | 20SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44245 | 113.29 | P12:161:WERE:NSES-EMDE_161::
Thermal | 08ALL | 2 | 20G | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44299 | 110.39 | P12:161:WERE:NSES-EMDE_161::
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44647 | 104.89 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44453 | 111.02 | P12:345:AEPW-GRDA:FLINTCR7:TONECE7
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44451 | 107.85 | P12:345:AEPW-GRDA:FLINTCR7:TONECE7
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44482 | 104.26 | P12:345:AEPW-GRDA:FLINTCR7:TONECE7
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44442 | 101.66 | P12:345:AEPW-GRDA:FLINTCR7:TONECE7
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44428 | 109.32 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44431 | 103.76 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44458 | 102.87 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44445 | 113.93 | P12:345:GRDA:FLINTCR-TONECE
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44444 | 111.74 | P12:345:GRDA:FLINTCR-TONECE
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44474 | 107.19 | P12:345:GRDA:FLINTCR-TONECE
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44435 | 104.92 | P12:345:GRDA:FLINTCR-TONECE
Thermal | 08ALL | 2 | 20SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44443 | 100.88 | P12:345:GRDA:FLINTCR-TONECE
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44418 | 111.12 | P12:345:GRDA:GRDA1 -GRECTAP
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44415 | 105.85 | P12:345:GRDA:GRDA1 -GRECTAP
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44447 | 103.66 | P12:345:GRDA:GRDA1 -GRECTAP
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44407 | 101.07 | P12:345:GRDA:GRDA1 -GRECTAP
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44446 | 113.83 | P12:345:GRDA:GRDA1 -TONECE
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44445 | 111.78 | P12:345:GRDA:GRDA1 -TONECE
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44475 | 107.09 | P12:345:GRDA:GRDA1 -TONECE
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44436 | 104.8 | P12:345:GRDA:GRDA1 -TONECE
Thermal | 08ALL | 2 | 20SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44444 | 100.77 | P12:345:GRDA:GRDA1 -TONECE
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44428 | 109.32 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44431 | 103.76 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44458 | 102.87 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44517 | 109.19 | P12:345:OKGE:BKRBKR357_1
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44547 | 102.64 | P12:345:OKGE:BKRBKR357_1
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44473 | 108.58 | P12:345:WERE:BUFF-KMWF_345::
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44468 | 103.4 | P12:345:WERE:BUFF-KMWF_345::
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44501 | 101.93 | P12:345:WERE:BUFF-KMWF_345::
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44695 | 116.2 | P12:345:WERE:N345-AECI_345::
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.4473 | 109.59 | P12:345:WERE:N345-AECI_345::
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.4469 | 109.34 | P12:345:WERE:N345-AECI_345::
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44681 | 104.92 | P12:345:WERE:N345-AECI_345::
Thermal | 08ALL | 2 | 20G | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44735 | 103.19 | P12:345:WERE:N345-AECI_345::
Thermal | 08ALL | 2 | 20SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44689 | 101.25 | P12:345:WERE:N345-AECI_345::
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44515 | 104.78 | P12:345:WERE:SWIS-WGAR_345::
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44487 | 103.71 | P12:345:WERE:WAVS-LACY_345::
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44487 | 104.28 | P12:345:WERE:WAVS-WOLF_345::
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44412 | 106.46 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44371 | 104.54 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 08ALL | 2 | 20SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44379 | 100.5 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44468 | 105.21 | P13:161-22:AEPW:FLINTCR5
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44468 | 101.6 | P13:18-345:OPPD:NEBCTY1G
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44468 | 101.6 | P13:23-345:OPPD:NEBCTY2G
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44473 | 106.7 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44468 | 101.76 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44501 | 100.23 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44473 | 104.46 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44473 | 106.7 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44468 | 101.75 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44501 | 100.23 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44473 | 106.41 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44468 | 101.41 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44473 | 103.36 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44473 | 106.37 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44468 | 101.37 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44494 | 109.2 | P22:345:AMMO::OVERTON:1
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44468 | 101.6 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44468 | 101.59 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44468 | 101.6 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44473 | 106.52 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44468 | 101.58 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44449 | 111.18 | P22:345:SPRM-AECI:17
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44445 | 108.19 | P22:345:SPRM-AECI:17
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44479 | 104.63 | P22:345:SPRM-AECI:17
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44438 | 101.87 | P22:345:SPRM-AECI:17
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44473 | 106.84 | P23:161-345:KCPL:IATAN_R1-11::IATANU1-IATANT11
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44468 | 101.91 | P23:161-345:KCPL:IATAN_R1-11::IATANU1-IATANT11
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44501 | 100.39 | P23:161-345:KCPL:IATAN_R1-11::IATANU1-IATANT11
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44471 | 104.23 | P23:161-345:KCPL:STILWELL_R5-22::STILWELL-LACYGNE-STILT22
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44512 | 104.26 | P23:161-345:KCPL:WGARDNER_R10-11::WGARD-LACYGNE-WGARDT11
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44516 | 104.27 | P23:161-345:KCPL:WGARDNER_R8-11::WGARD-CRAIG-WGARDT11
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44384 | 113.35 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.4438 | 111.84 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44412 | 106.55 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44371 | 104.71 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 08ALL | 2 | 20SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44379 | 100.59 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44384 | 113.33 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.4438 | 111.68 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44412 | 106.42 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44371 | 104.79 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 08ALL | 2 | 20SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44379 | 100.6 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44384 | 113.38 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.4438 | 111.69 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44412 | 106.61 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44371 | 104.83 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 08ALL | 2 | 20SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44379 | 100.6 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44647 | 105.01 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44647 | 105.04 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44644 | 100.01 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44647 | 104.98 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44454 | 111.05 | P23:345:AEPW:FLINT CREEK CB 12430 NBTB
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44451 | 108 | P23:345:AEPW:FLINT CREEK CB 12430 NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44482 | 104.27 | P23:345:AEPW:FLINT CREEK CB 12430 NBTB
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44443 | 101.73 | P23:345:AEPW:FLINT CREEK CB 12430 NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44454 | 111.36 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44451 | 108.36 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44482 | 104.54 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44443 | 102.12 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44647 | 104.89 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44416 | 109.66 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.4442 | 104.17 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44446 | 103.24 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44515 | 109.78 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44545 | 103.18 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44412 | 110.87 | P23:345:GRDA:CLEVLND CB10180
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44419 | 105.23 | P23:345:GRDA:CLEVLND CB10180
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44444 | 104.38 | P23:345:GRDA:CLEVLND CB10180
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44408 | 101.03 | P23:345:GRDA:CLEVLND CB10180
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44428 | 109.32 | P23:345:GRDA:CLEVLND CB13280
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44431 | 103.76 | P23:345:GRDA:CLEVLND CB13280
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44458 | 102.87 | P23:345:GRDA:CLEVLND CB13280
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44419 | 111.14 | P23:345:GRDA:GRDA CB9080
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44417 | 105.85 | P23:345:GRDA:GRDA CB9080
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44448 | 103.68 | P23:345:GRDA:GRDA CB9080
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44408 | 101.05 | P23:345:GRDA:GRDA CB9080
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44446 | 115.62 | P23:345:GRDA:GRDA CB9580
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44444 | 112.72 | P23:345:GRDA:GRDA CB9580
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44436 | 106.13 | P23:345:GRDA:GRDA CB9580
Thermal | 08ALL | 2 | 20SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44443 | 101.82 | P23:345:GRDA:GRDA CB9580
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44445 | 113.93 | P23:345:GRDA:TONNECE CB12070
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44444 | 111.74 | P23:345:GRDA:TONNECE CB12070
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44474 | 107.19 | P23:345:GRDA:TONNECE CB12070
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44435 | 104.92 | P23:345:GRDA:TONNECE CB12070
Thermal | 08ALL | 2 | 20SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44443 | 100.88 | P23:345:GRDA:TONNECE CB12070
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44445 | 113.99 | P23:345:GRDA:TONNECE CB90
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44444 | 111.97 | P23:345:GRDA:TONNECE CB90
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44474 | 107.23 | P23:345:GRDA:TONNECE CB90
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44435 | 104.94 | P23:345:GRDA:TONNECE CB90
Thermal | 08ALL | 2 | 20SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44443 | 100.92 | P23:345:GRDA:TONNECE CB90
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44445 | 114.01 | P23:345:GRDA:TONNECE CB9580
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44444 | 112 | P23:345:GRDA:TONNECE CB9580
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44474 | 107.28 | P23:345:GRDA:TONNECE CB9580
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44435 | 104.91 | P23:345:GRDA:TONNECE CB9580
Thermal | 08ALL | 2 | 20SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44443 | 100.95 | P23:345:GRDA:TONNECE CB9580
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44456 | 105.03 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44456 | 104.74 | P23:345:KCPL:LACYGNE_R4-5::LACYGNE-STILWELL-LACYGT7
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44338 | 101.86 | P23:345:KCPL-WERE:LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44487 | 103.72 | P23:345:KCPL-WERE:LACYGNE_R4-9::LACYGNE-WAVERLY-LACYGT7
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44473 | 103.49 | P23:345:KCPL-WERE:LACYGNE_R9-10::LACYGNE-WAVERLY-WGARD
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44515 | 104.81 | P23:345:KCPL-WERE:WGARDNER_R12-13::WGARD-STILWELL-SWISSVALE
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44472 | 106.41 | P23:345:MEC:CBEC 905
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44468 | 101.4 | P23:345:MEC:CBEC 905
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44473 | 106.41 | P23:345:MEC:CBEC 908
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44468 | 101.41 | P23:345:MEC:CBEC 908
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44473 | 103.36 | P23:345:MEC:RAUN 0210
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44468 | 101.6 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44468 | 101.59 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44468 | 101.6 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44473 | 106.52 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44468 | 101.58 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44468 | 102.36 | P23:345:WERE:JEC_345-15::
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44477 | 106.34 | P23:345:WERE:JEC_345-16::
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44468 | 102.11 | P23:345:WERE:JEC_345-19::
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44467 | 102.13 | P23:345:WERE:JEC_345-20::
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.45033 | 113.37 | P23:345:WERE:N345_345-110::
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.45027 | 106.89 | P23:345:WERE:N345_345-110::
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.45066 | 106.67 | P23:345:WERE:N345_345-110::
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.45018 | 101.86 | P23:345:WERE:N345_345-110::
Thermal | 08ALL | 2 | 20G | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.45072 | 100.92 | P23:345:WERE:N345_345-110::
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44515 | 104.74 | P23:345:WERE:SWIS_345-5::
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44487 | 104.23 | P23:345:WERE:WAVS_BKRS::
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44473 | 106.71 | P23:345:XEL:8N17 SHC
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44468 | 101.77 | P23:345:XEL:8N17 SHC
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44501 | 100.26 | P23:345:XEL:8N17 SHC
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44473 | 104.45 | P23:345:XEL:8N22 SHC
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44473 | 106.69 | P23:345:XEL:8N28 SHC
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44468 | 101.75 | P23:345:XEL:8N28 SHC
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44501 | 100.23 | P23:345:XEL:8N28 SHC
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44473 | 106.65 | P23:345:XEL:8N8 MNN
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44501 | 100.19 | P23:345:XEL:8N8 MNN
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44418 | 112.36 | P24:345:GRDA:GRDA CB400T
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44415 | 108.4 | P24:345:GRDA:GRDA CB400T
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44447 | 105.18 | P24:345:GRDA:GRDA CB400T
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44407 | 102.38 | P24:345:GRDA:GRDA CB400T
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44418 | 111.04 | P24:345:GRDA:GRECTP CB100T
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44415 | 105.86 | P24:345:GRDA:GRECTP CB100T
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44447 | 103.66 | P24:345:GRDA:GRECTP CB100T
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44407 | 101.04 | P24:345:GRDA:GRECTP CB100T
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44384 | 113.33 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.4438 | 111.68 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44412 | 106.42 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44371 | 104.79 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 08ALL | 2 | 20SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44379 | 100.6 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44384 | 113.38 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.4438 | 111.69 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44412 | 106.61 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44371 | 104.83 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 08ALL | 2 | 20SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44379 | 100.6 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44647 | 105.01 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44647 | 105.04 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44644 | 100.01 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44647 | 104.98 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44454 | 111.36 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44451 | 108.36 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44482 | 104.54 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44443 | 102.12 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44647 | 104.89 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44416 | 109.66 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.4442 | 104.17 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44446 | 103.24 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44428 | 109.32 | P42:345:GRDA:CLEVLND CB13280
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44431 | 103.76 | P42:345:GRDA:CLEVLND CB13280
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44458 | 102.87 | P42:345:GRDA:CLEVLND CB13280
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44445 | 114.01 | P42:345:GRDA:TONNECE CB9580
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44444 | 112 | P42:345:GRDA:TONNECE CB9580
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44474 | 107.28 | P42:345:GRDA:TONNECE CB9580
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44435 | 104.91 | P42:345:GRDA:TONNECE CB9580
Thermal | 08ALL | 2 | 20SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44443 | 100.95 | P42:345:GRDA:TONNECE CB9580
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44517 | 109.19 | P42:345:OKGE:SB_RARD7383
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44547 | 102.64 | P42:345:OKGE:SB_RARD7383
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44517 | 109.19 | P42:345:OKGE:SB_SOER7383
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44547 | 102.64 | P42:345:OKGE:SB_SOER7383
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44449 | 111.18 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44445 | 108.19 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44479 | 104.63 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44438 | 101.87 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44475 | 103.31 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44384 | 113.35 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.4438 | 111.84 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44412 | 106.55 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44371 | 104.71 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 08ALL | 2 | 20SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44379 | 100.59 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44454 | 111.05 | P43:345:AEPW:FLINT CREEK CB 12430 NBTB+FAULT
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44451 | 108 | P43:345:AEPW:FLINT CREEK CB 12430 NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44482 | 104.27 | P43:345:AEPW:FLINT CREEK CB 12430 NBTB+FAULT
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44443 | 101.73 | P43:345:AEPW:FLINT CREEK CB 12430 NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44412 | 110.87 | P43:345:GRDA:CLEVLND CB10180
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44419 | 105.23 | P43:345:GRDA:CLEVLND CB10180
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44444 | 104.38 | P43:345:GRDA:CLEVLND CB10180
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44408 | 101.03 | P43:345:GRDA:CLEVLND CB10180
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44419 | 111.14 | P43:345:GRDA:GRDA CB9080
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44417 | 105.85 | P43:345:GRDA:GRDA CB9080
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44448 | 103.68 | P43:345:GRDA:GRDA CB9080
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44408 | 101.05 | P43:345:GRDA:GRDA CB9080
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44446 | 115.62 | P43:345:GRDA:GRDA CB9580
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44444 | 112.72 | P43:345:GRDA:GRDA CB9580
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44436 | 106.13 | P43:345:GRDA:GRDA CB9580
Thermal | 08ALL | 2 | 20SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44443 | 101.82 | P43:345:GRDA:GRDA CB9580
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44445 | 113.93 | P43:345:GRDA:TONNECE CB12070
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44444 | 111.74 | P43:345:GRDA:TONNECE CB12070
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44474 | 107.19 | P43:345:GRDA:TONNECE CB12070
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44435 | 104.92 | P43:345:GRDA:TONNECE CB12070
Thermal | 08ALL | 2 | 20SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44443 | 100.88 | P43:345:GRDA:TONNECE CB12070
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44445 | 113.99 | P43:345:GRDA:TONNECE CB90
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44444 | 111.97 | P43:345:GRDA:TONNECE CB90
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44474 | 107.23 | P43:345:GRDA:TONNECE CB90
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44435 | 104.94 | P43:345:GRDA:TONNECE CB90
Thermal | 08ALL | 2 | 20SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44443 | 100.92 | P43:345:GRDA:TONNECE CB90
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44472 | 106.33 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44468 | 101.31 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44418 | 112.36 | P46:345:GRDA:GRDA CB400T
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44415 | 108.4 | P46:345:GRDA:GRDA CB400T
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44447 | 105.18 | P46:345:GRDA:GRDA CB400T
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44407 | 102.38 | P46:345:GRDA:GRDA CB400T
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44418 | 111.04 | P46:345:GRDA:GRECTP CB100T
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44415 | 105.86 | P46:345:GRDA:GRECTP CB100T
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44447 | 103.66 | P46:345:GRDA:GRECTP CB100T
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44407 | 101.04 | P46:345:GRDA:GRECTP CB100T
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44449 | 111.18 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44445 | 108.19 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44479 | 104.63 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44438 | 101.87 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44475 | 103.3 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44476 | 103.28 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44475 | 103.12 | P55:161-345:KCPL:STILWELL_BUS_22_345::
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 |  | 223 | 0.44507 | 103.98 | P55:161-345:KCPL:W.GARDNER_BUS_11::
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 | 220 |  | 0.44473 | 108.15 | System Intact
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 | 220 |  | 0.44468 | 103.15 | System Intact
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 | 220 |  | 0.44501 | 101.67 | System Intact
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 997850 FRAN TX-1 69.0 1 |  | 110 | 0.2704 | 118.85 | P12:161:WERE:FRAN-LITC_161::
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 997851 FRAN TX-1 69.0 1 |  | 110 | 0.27045 | 118.29 | P12:161:WERE:FRAN-LITC_161::
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 997851 FRAN TX-1 69.0 1 |  | 110 | 0.27036 | 114.8 | P12:161:WERE:FRAN-LITC_161::
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 997852 FRAN TX-1 69.0 1 |  | 110 | 0.27059 | 111.76 | P12:161:WERE:FRAN-LITC_161::
Thermal | 08ALL | 2 | 20SP | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 997855 FRAN TX-1 69.0 1 |  | 110 | 0.27041 | 109.64 | P12:161:WERE:FRAN-LITC_161::
Thermal | 08ALL | 2 | 20G | GEN-2017-005 | 'FROM -> TO' | 532938 FRANKLIN5 161 997861 FRAN TX-1 69.0 1 |  | 110 | 0.2707 | 108.74 | P12:161:WERE:FRAN-LITC_161::
Thermal | 08ALL | 2 | 29SP | GEN-2017-086 | 'FROM -> TO' | 533075 VIOLA 4 138 997930 VIOLA TX-1 138 1 |  | 440 | 0.24396 | 102.13 | P12:345:WERE:VIOL-WICH_345::
Thermal | 08ALL | 2 | 29SP | GEN-2017-086 | 'FROM -> TO' | 533075 VIOLA 4 138 997930 VIOLA TX-1 138 1 |  | 440 | 0.24394 | 102.4 | P23:345:WERE:WICH_345-116::
Thermal | 08ALL | 2 | 24SP | GEN-2017-086 | 'FROM -> TO' | 533075 VIOLA 4 138 997931 VIOLA TX-1 138 1 |  | 440 | 0.24381 | 102.26 | P12:345:WERE:VIOL-WICH_345::
Thermal | 08ALL | 2 | 24SP | GEN-2017-086 | 'FROM -> TO' | 533075 VIOLA 4 138 997931 VIOLA TX-1 138 1 |  | 440 | 0.24379 | 102.61 | P23:345:WERE:WICH_345-116::
Thermal | 08ALL | 2 | 20SP | GEN-2017-086 | 'FROM -> TO' | 533075 VIOLA 4 138 997935 VIOLA TX-1 138 1 |  | 440 | 0.24343 | 102.51 | P12:345:WERE:VIOL-WICH_345::
Thermal | 08ALL | 2 | 20SP | GEN-2017-086 | 'FROM -> TO' | 533075 VIOLA 4 138 997935 VIOLA TX-1 138 1 |  | 440 | 0.2434 | 102.86 | P23:345:WERE:WICH_345-116::
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | 533876 FRANKLIN2 69.0 997850 FRAN TX-1 69.0 1 |  | 110 | 0.2704 | 115.26 | P12:161:WERE:FRAN-LITC_161::
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 533876 FRANKLIN2 69.0 997851 FRAN TX-1 69.0 1 |  | 110 | 0.27045 | 114.98 | P12:161:WERE:FRAN-LITC_161::
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | 533876 FRANKLIN2 69.0 997851 FRAN TX-1 69.0 1 |  | 110 | 0.27036 | 112 | P12:161:WERE:FRAN-LITC_161::
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | 533876 FRANKLIN2 69.0 997852 FRAN TX-1 69.0 1 |  | 110 | 0.27059 | 109.22 | P12:161:WERE:FRAN-LITC_161::
Thermal | 08ALL | 2 | 20SP | GEN-2017-005 | 'FROM -> TO' | 533876 FRANKLIN2 69.0 997855 FRAN TX-1 69.0 1 |  | 110 | 0.27041 | 108.24 | P12:161:WERE:FRAN-LITC_161::
Thermal | 08ALL | 2 | 20G | GEN-2017-005 | 'FROM -> TO' | 533876 FRANKLIN2 69.0 997861 FRAN TX-1 69.0 1 |  | 110 | 0.2707 | 107.6 | P12:161:WERE:FRAN-LITC_161::
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | 547476 ASB349 5 161 547477 CJ 366 5 161 1 |  | 223 | 0.31973 | 100.28 | P12:161:EMDE:SCHD_REMOVE_2019::ASB349_CAR(SPA)
Thermal | 08ALL | 2 | 20G | GEN-2017-092 | 'FROM -> TO' | 589305 G17-092XFMR2 34.5 589300 GEN-2017-092 345 1 | 125 |  | 1 | 103.15 | System Intact
Thermal | 08ALL | 2 | 20SP | GEN-2017-092 | 'FROM -> TO' | 589305 G17-092XFMR2 34.5 589300 GEN-2017-092 345 1 | 125 |  | 1 | 102.26 | System Intact
Thermal | 08ALL | 2 | 24WP | GEN-2017-092 | 'FROM -> TO' | 589305 G17-092XFMR2 34.5 589300 GEN-2017-092 345 1 | 125 |  | 1 | 102.21 | System Intact
Thermal | 08ALL | 2 | 19WP | GEN-2017-092 | 'FROM -> TO' | 589305 G17-092XFMR2 34.5 589300 GEN-2017-092 345 1 | 125 |  | 1 | 102.2 | System Intact
Thermal | 08ALL | 2 | 24SP | GEN-2017-092 | 'FROM -> TO' | 589305 G17-092XFMR2 34.5 589300 GEN-2017-092 345 1 | 125 |  | 1 | 102.02 | System Intact
Thermal | 08ALL | 2 | 29SP | GEN-2017-092 | 'FROM -> TO' | 589305 G17-092XFMR2 34.5 589300 GEN-2017-092 345 1 | 125 |  | 1 | 101.78 | System Intact
Non-Converge | 09ALL | 0 | 20G | GEN-2016-159 | '' | Non-Converge |  |  | 0.06853 |  | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT
Non-Converge | 09ALL | 0 | 20G | GEN-2017-008 | '' | Non-Converge |  |  | 0.06268 |  | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT
Non-Converge | 09ALL | 0 | 20G | GEN-2017-031 | '' | Non-Converge |  |  | 0.04137 |  | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT
Non-Converge | 09ALL | 0 | 20G | GEN-2017-055 | '' | Non-Converge |  |  | 0.08634 |  | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT
Non-Converge | 09ALL | 0 | 20G | GEN-2017-085 | '' | Non-Converge |  |  | 0.07328 |  | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT
Non-Converge | 09ALL | 0 | 20G | GEN-2016-159 | '' | Non-Converge |  |  | 0.06853 |  | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS
Non-Converge | 09ALL | 0 | 20G | GEN-2017-008 | '' | Non-Converge |  |  | 0.06268 |  | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS
Non-Converge | 09ALL | 0 | 20G | GEN-2017-031 | '' | Non-Converge |  |  | 0.04137 |  | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS
Non-Converge | 09ALL | 0 | 20G | GEN-2017-055 | '' | Non-Converge |  |  | 0.08634 |  | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS
Non-Converge | 09ALL | 0 | 20G | GEN-2017-085 | '' | Non-Converge |  |  | 0.07328 |  | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS
Non-Converge | 09ALL | 0 | 20G | GEN-2016-159 | '' | Non-Converge |  |  | 0.06853 |  | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Non-Converge | 09ALL | 0 | 20G | GEN-2017-008 | '' | Non-Converge |  |  | 0.06268 |  | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Non-Converge | 09ALL | 0 | 20G | GEN-2017-031 | '' | Non-Converge |  |  | 0.04137 |  | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Non-Converge | 09ALL | 0 | 20G | GEN-2017-055 | '' | Non-Converge |  |  | 0.08634 |  | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Non-Converge | 09ALL | 0 | 20G | GEN-2017-085 | '' | Non-Converge |  |  | 0.07328 |  | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Non-Converge | 09ALL | 0 | 20G | GEN-2016-159 | '' | Non-Converge |  |  | 0.05815 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 20G | GEN-2016-159 | '' | Non-Converge |  |  | 0.05245 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 20G | GEN-2017-008 | '' | Non-Converge |  |  | 0.0766 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 20G | GEN-2017-008 | '' | Non-Converge |  |  | 0.06949 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 20G | GEN-2017-031 | '' | Non-Converge |  |  | 0.15897 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 20G | GEN-2017-031 | '' | Non-Converge |  |  | 0.1445 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 20G | GEN-2017-055 | '' | Non-Converge |  |  | 0.05384 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 20G | GEN-2017-055 | '' | Non-Converge |  |  | 0.04861 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 20G | GEN-2017-085 | '' | Non-Converge |  |  | 0.06354 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 20G | GEN-2017-085 | '' | Non-Converge |  |  | 0.05755 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 20G | GEN-2016-159 | '' | Non-Converge |  |  | 0.06446 |  | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Non-Converge | 09ALL | 0 | 20G | GEN-2017-008 | '' | Non-Converge |  |  | 0.08512 |  | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Non-Converge | 09ALL | 0 | 20G | GEN-2017-031 | '' | Non-Converge |  |  | 0.1882 |  | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Non-Converge | 09ALL | 0 | 20G | GEN-2017-055 | '' | Non-Converge |  |  | 0.05872 |  | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Non-Converge | 09ALL | 0 | 20G | GEN-2017-085 | '' | Non-Converge |  |  | 0.0699 |  | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Non-Converge | 09ALL | 0 | 20G | GEN-2016-159 | '' | Non-Converge |  |  | 0.06853 |  | P14:345:GMO-OPPD:S3458 REACTOR
Non-Converge | 09ALL | 0 | 20G | GEN-2017-008 | '' | Non-Converge |  |  | 0.06268 |  | P14:345:GMO-OPPD:S3458 REACTOR
Non-Converge | 09ALL | 0 | 20G | GEN-2017-031 | '' | Non-Converge |  |  | 0.04137 |  | P14:345:GMO-OPPD:S3458 REACTOR
Non-Converge | 09ALL | 0 | 20G | GEN-2017-055 | '' | Non-Converge |  |  | 0.08634 |  | P14:345:GMO-OPPD:S3458 REACTOR
Non-Converge | 09ALL | 0 | 20G | GEN-2017-085 | '' | Non-Converge |  |  | 0.07328 |  | P14:345:GMO-OPPD:S3458 REACTOR
Non-Converge | 09ALL | 0 | 20G | GEN-2016-159 | '' | Non-Converge |  |  | 0.10105 |  | P23:161-345:GMO-NPPD:STJOE_R5-33::STJOE-COOPER-STJOET22
Non-Converge | 09ALL | 0 | 20G | GEN-2017-008 | '' | Non-Converge |  |  | 0.09701 |  | P23:161-345:GMO-NPPD:STJOE_R5-33::STJOE-COOPER-STJOET22
Non-Converge | 09ALL | 0 | 20G | GEN-2017-031 | '' | Non-Converge |  |  | 0.06245 |  | P23:161-345:GMO-NPPD:STJOE_R5-33::STJOE-COOPER-STJOET22
Non-Converge | 09ALL | 0 | 20G | GEN-2017-055 | '' | Non-Converge |  |  | 0.1246 |  | P23:161-345:GMO-NPPD:STJOE_R5-33::STJOE-COOPER-STJOET22
Non-Converge | 09ALL | 0 | 20G | GEN-2017-085 | '' | Non-Converge |  |  | 0.1128 |  | P23:161-345:GMO-NPPD:STJOE_R5-33::STJOE-COOPER-STJOET22
Non-Converge | 09ALL | 0 | 20G | GEN-2016-159 | '' | Non-Converge |  |  | 0.05243 |  | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON
Non-Converge | 09ALL | 0 | 20G | GEN-2017-008 | '' | Non-Converge |  |  | 0.04038 |  | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON
Non-Converge | 09ALL | 0 | 20G | GEN-2017-055 | '' | Non-Converge |  |  | 0.05692 |  | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON
Non-Converge | 09ALL | 0 | 20G | GEN-2017-085 | '' | Non-Converge |  |  | 0.04891 |  | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON
Non-Converge | 09ALL | 0 | 20G | GEN-2016-159 | '' | Non-Converge |  |  | 0.06009 |  | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT
Non-Converge | 09ALL | 0 | 20G | GEN-2016-159 | '' | Non-Converge |  |  | 0.09696 |  | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT
Non-Converge | 09ALL | 0 | 20G | GEN-2017-008 | '' | Non-Converge |  |  | 0.05089 |  | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT
Non-Converge | 09ALL | 0 | 20G | GEN-2017-008 | '' | Non-Converge |  |  | 0.08537 |  | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT
Non-Converge | 09ALL | 0 | 20G | GEN-2017-031 | '' | Non-Converge |  |  | 0.03456 |  | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT
Non-Converge | 09ALL | 0 | 20G | GEN-2017-031 | '' | Non-Converge |  |  | 0.05714 |  | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT
Non-Converge | 09ALL | 0 | 20G | GEN-2017-055 | '' | Non-Converge |  |  | 0.0668 |  | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT
Non-Converge | 09ALL | 0 | 20G | GEN-2017-055 | '' | Non-Converge |  |  | 0.11146 |  | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT
Non-Converge | 09ALL | 0 | 20G | GEN-2017-085 | '' | Non-Converge |  |  | 0.05938 |  | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT
Non-Converge | 09ALL | 0 | 20G | GEN-2017-085 | '' | Non-Converge |  |  | 0.09925 |  | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT
Non-Converge | 09ALL | 0 | 20G | GEN-2016-159 | '' | Non-Converge |  |  | 0.06584 |  | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER
Non-Converge | 09ALL | 0 | 20G | GEN-2017-008 | '' | Non-Converge |  |  | 0.06101 |  | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER
Non-Converge | 09ALL | 0 | 20G | GEN-2017-031 | '' | Non-Converge |  |  | 0.03987 |  | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER
Non-Converge | 09ALL | 0 | 20G | GEN-2017-055 | '' | Non-Converge |  |  | 0.07859 |  | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER
Non-Converge | 09ALL | 0 | 20G | GEN-2017-085 | '' | Non-Converge |  |  | 0.07125 |  | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER
Non-Converge | 09ALL | 0 | 20G | GEN-2017-055 | '' | Non-Converge |  |  | 0.03393 |  | P23:345:KCPL-GMO:NASHUA_R2-11::NASHUA-HAWTHORN-STJOE
Non-Converge | 09ALL | 0 | 20G | GEN-2017-085 | '' | Non-Converge |  |  | 0.03289 |  | P23:345:KCPL-GMO:NASHUA_R2-11::NASHUA-HAWTHORN-STJOE
Non-Converge | 09ALL | 0 | 20G | GEN-2016-159 | '' | Non-Converge |  |  | 0.03817 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 09ALL | 0 | 20G | GEN-2016-159 | '' | Non-Converge |  |  | 0.05245 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 09ALL | 0 | 20G | GEN-2017-008 | '' | Non-Converge |  |  | 0.05465 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 09ALL | 0 | 20G | GEN-2017-008 | '' | Non-Converge |  |  | 0.06949 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 09ALL | 0 | 20G | GEN-2017-031 | '' | Non-Converge |  |  | 0.08095 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 09ALL | 0 | 20G | GEN-2017-031 | '' | Non-Converge |  |  | 0.1445 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 09ALL | 0 | 20G | GEN-2017-055 | '' | Non-Converge |  |  | 0.03735 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 09ALL | 0 | 20G | GEN-2017-055 | '' | Non-Converge |  |  | 0.04861 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 09ALL | 0 | 20G | GEN-2017-085 | '' | Non-Converge |  |  | 0.04324 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 09ALL | 0 | 20G | GEN-2017-085 | '' | Non-Converge |  |  | 0.05755 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 09ALL | 0 | 20G | GEN-2016-159 | '' | Non-Converge |  |  | 0.03439 |  | P42:345:NPPD:BKR-CPR-3304
Non-Converge | 09ALL | 0 | 20G | GEN-2016-159 | '' | Non-Converge |  |  | 0.10105 |  | P42:345:NPPD:BKR-CPR-3304
Non-Converge | 09ALL | 0 | 20G | GEN-2017-008 | '' | Non-Converge |  |  | 0.09701 |  | P42:345:NPPD:BKR-CPR-3304
Non-Converge | 09ALL | 0 | 20G | GEN-2017-031 | '' | Non-Converge |  |  | 0.06245 |  | P42:345:NPPD:BKR-CPR-3304
Non-Converge | 09ALL | 0 | 20G | GEN-2017-055 | '' | Non-Converge |  |  | 0.1246 |  | P42:345:NPPD:BKR-CPR-3304
Non-Converge | 09ALL | 0 | 20G | GEN-2017-085 | '' | Non-Converge |  |  | 0.1128 |  | P42:345:NPPD:BKR-CPR-3304
Non-Converge | 09ALL | 0 | 20G | GEN-2016-159 | '' | Non-Converge |  |  | 0.04867 |  | P42:345:NPPD:BKR-RW-3302
Non-Converge | 09ALL | 0 | 20G | GEN-2016-159 | '' | Non-Converge |  |  | 0.06446 |  | P42:345:NPPD:BKR-RW-3302
Non-Converge | 09ALL | 0 | 20G | GEN-2017-008 | '' | Non-Converge |  |  | 0.06077 |  | P42:345:NPPD:BKR-RW-3302
Non-Converge | 09ALL | 0 | 20G | GEN-2017-008 | '' | Non-Converge |  |  | 0.08512 |  | P42:345:NPPD:BKR-RW-3302
Non-Converge | 09ALL | 0 | 20G | GEN-2017-031 | '' | Non-Converge |  |  | 0.0419 |  | P42:345:NPPD:BKR-RW-3302
Non-Converge | 09ALL | 0 | 20G | GEN-2017-031 | '' | Non-Converge |  |  | 0.0419 |  | P42:345:NPPD:BKR-RW-3302
Non-Converge | 09ALL | 0 | 20G | GEN-2017-031 | '' | Non-Converge |  |  | 0.1155 |  | P42:345:NPPD:BKR-RW-3302
Non-Converge | 09ALL | 0 | 20G | GEN-2017-031 | '' | Non-Converge |  |  | 0.1882 |  | P42:345:NPPD:BKR-RW-3302
Non-Converge | 09ALL | 0 | 20G | GEN-2017-055 | '' | Non-Converge |  |  | 0.04363 |  | P42:345:NPPD:BKR-RW-3302
Non-Converge | 09ALL | 0 | 20G | GEN-2017-055 | '' | Non-Converge |  |  | 0.05872 |  | P42:345:NPPD:BKR-RW-3302
Non-Converge | 09ALL | 0 | 20G | GEN-2017-085 | '' | Non-Converge |  |  | 0.0528 |  | P42:345:NPPD:BKR-RW-3302
Non-Converge | 09ALL | 0 | 20G | GEN-2017-085 | '' | Non-Converge |  |  | 0.0699 |  | P42:345:NPPD:BKR-RW-3302
Thermal | 09ALL | 2 | 24L | GEN-2016-159 | 'FROM -> TO' | 523959 POTTER_CO 6 230 998123 WAUK 90343-A 230 1 | 516 |  | 0.03241 | 101.18 | System Intact
Thermal | 09ALL | 2 | 24L | GEN-2017-008 | 'FROM -> TO' | 523959 POTTER_CO 6 230 998123 WAUK 90343-A 230 1 | 516 |  | 0.03569 | 101.18 | System Intact
Thermal | 09ALL | 2 | 24L | GEN-2017-031 | 'FROM -> TO' | 523959 POTTER_CO 6 230 998123 WAUK 90343-A 230 1 | 516 |  | 0.03962 | 101.18 | System Intact
Thermal | 09ALL | 2 | 24L | GEN-2017-055 | 'FROM -> TO' | 523959 POTTER_CO 6 230 998123 WAUK 90343-A 230 1 | 516 |  | 0.03223 | 101.18 | System Intact
Thermal | 09ALL | 2 | 24L | GEN-2017-085 | 'FROM -> TO' | 523959 POTTER_CO 6 230 998123 WAUK 90343-A 230 1 | 516 |  | 0.03348 | 101.18 | System Intact
Thermal | 09ALL | 2 | 24L | GEN-2016-159 | 'FROM -> TO' | 523959 POTTER_CO 6 230 998123 WAUK 90343-A 230 1 | 516 |  | 0.03241 | 101.17 | System Intact
Thermal | 09ALL | 2 | 24L | GEN-2017-008 | 'FROM -> TO' | 523959 POTTER_CO 6 230 998123 WAUK 90343-A 230 1 | 516 |  | 0.03569 | 101.17 | System Intact
Thermal | 09ALL | 2 | 24L | GEN-2017-031 | 'FROM -> TO' | 523959 POTTER_CO 6 230 998123 WAUK 90343-A 230 1 | 516 |  | 0.03976 | 101.17 | System Intact
Thermal | 09ALL | 2 | 24L | GEN-2017-055 | 'FROM -> TO' | 523959 POTTER_CO 6 230 998123 WAUK 90343-A 230 1 | 516 |  | 0.03224 | 101.17 | System Intact
Thermal | 09ALL | 2 | 24L | GEN-2017-085 | 'FROM -> TO' | 523959 POTTER_CO 6 230 998123 WAUK 90343-A 230 1 | 516 |  | 0.03348 | 101.17 | System Intact
Thermal | 09ALL | 2 | 24L | GEN-2017-031 | 'FROM -> TO' | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 319 |  | 0.03612 | 115.53 | System Intact
Thermal | 09ALL | 2 | 20G | GEN-2017-008 | 'FROM -> TO' | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 319 |  | 0.03247 | 101.14 | System Intact
Thermal | 09ALL | 2 | 20G | GEN-2017-031 | 'FROM -> TO' | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 319 |  | 0.0441 | 101.14 | System Intact
Thermal | 09ALL | 2 | 24L | GEN-2016-159 | 'FROM -> TO' | 560347 DIXONCO 230 640386 TWIN CH4 230 1 | 320 |  | 0.08624 | 100.16 | System Intact
Thermal | 09ALL | 2 | 20G | GEN-2017-031 | 'FROM -> TO' | 640068 B.SPRGS7 115 640091 BRULE 7 115 1 |  | 109 | 0.49811 | 141.82 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 19WP | GEN-2017-031 | 'FROM -> TO' | 640068 B.SPRGS7 115 640091 BRULE 7 115 1 |  | 109 | 0.49868 | 138.01 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 24WP | GEN-2017-031 | 'FROM -> TO' | 640068 B.SPRGS7 115 640091 BRULE 7 115 1 |  | 109 | 0.5002 | 135.7 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 20SP | GEN-2017-031 | 'FROM -> TO' | 640068 B.SPRGS7 115 640091 BRULE 7 115 1 |  | 109 | 0.50037 | 125.28 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 24SP | GEN-2017-031 | 'FROM -> TO' | 640068 B.SPRGS7 115 640091 BRULE 7 115 1 |  | 109 | 0.50182 | 120.97 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 29SP | GEN-2017-031 | 'FROM -> TO' | 640068 B.SPRGS7 115 640091 BRULE 7 115 1 |  | 109 | 0.50196 | 117.45 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 20G | GEN-2017-031 | 'FROM -> TO' | 640068 B.SPRGS7 115 640091 BRULE 7 115 1 |  | 109 | 0.47896 | 131.44 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 19WP | GEN-2017-031 | 'FROM -> TO' | 640068 B.SPRGS7 115 640091 BRULE 7 115 1 |  | 109 | 0.47951 | 129.22 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 24WP | GEN-2017-031 | 'FROM -> TO' | 640068 B.SPRGS7 115 640091 BRULE 7 115 1 |  | 109 | 0.48076 | 126.69 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 20SP | GEN-2017-031 | 'FROM -> TO' | 640068 B.SPRGS7 115 640091 BRULE 7 115 1 |  | 109 | 0.48113 | 119.57 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 24SP | GEN-2017-031 | 'FROM -> TO' | 640068 B.SPRGS7 115 640091 BRULE 7 115 1 |  | 109 | 0.48232 | 115.48 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 29SP | GEN-2017-031 | 'FROM -> TO' | 640068 B.SPRGS7 115 640091 BRULE 7 115 1 |  | 109 | 0.48246 | 112.03 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 20G | GEN-2017-031 | 'FROM -> TO' | 640091 BRULE 7 115 659801 OGALALA_-TS7 115 1 |  | 120 | 0.49811 | 127.45 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 19WP | GEN-2017-031 | 'FROM -> TO' | 640091 BRULE 7 115 659801 OGALALA_-TS7 115 1 |  | 120 | 0.49868 | 120.3 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 24WP | GEN-2017-031 | 'FROM -> TO' | 640091 BRULE 7 115 659801 OGALALA_-TS7 115 1 |  | 120 | 0.5002 | 118.01 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 20SP | GEN-2017-031 | 'FROM -> TO' | 640091 BRULE 7 115 659801 OGALALA_-TS7 115 1 |  | 120 | 0.50037 | 110.14 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 24SP | GEN-2017-031 | 'FROM -> TO' | 640091 BRULE 7 115 659801 OGALALA_-TS7 115 1 |  | 120 | 0.50182 | 106.12 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 29SP | GEN-2017-031 | 'FROM -> TO' | 640091 BRULE 7 115 659801 OGALALA_-TS7 115 1 |  | 120 | 0.50196 | 102.69 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 20G | GEN-2017-031 | 'FROM -> TO' | 640091 BRULE 7 115 659801 OGALALA_-TS7 115 1 |  | 120 | 0.47896 | 118.02 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 19WP | GEN-2017-031 | 'FROM -> TO' | 640091 BRULE 7 115 659801 OGALALA_-TS7 115 1 |  | 120 | 0.47951 | 112.3 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 24WP | GEN-2017-031 | 'FROM -> TO' | 640091 BRULE 7 115 659801 OGALALA_-TS7 115 1 |  | 120 | 0.48076 | 109.81 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 20SP | GEN-2017-031 | 'FROM -> TO' | 640091 BRULE 7 115 659801 OGALALA_-TS7 115 1 |  | 120 | 0.48113 | 104.95 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 24SP | GEN-2017-031 | 'FROM -> TO' | 640091 BRULE 7 115 659801 OGALALA_-TS7 115 1 |  | 120 | 0.48232 | 101.13 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 20G | GEN-2016-159 | 'FROM -> TO' | 640138 COOPER JOE 345 640139 COOPER 3 345 1 | 1195 |  | 0.11001 | 108.34 | System Intact
Thermal | 09ALL | 2 | 20G | GEN-2017-008 | 'FROM -> TO' | 640138 COOPER JOE 345 640139 COOPER 3 345 1 | 1195 |  | 0.10459 | 108.34 | System Intact
Thermal | 09ALL | 2 | 20G | GEN-2017-031 | 'FROM -> TO' | 640138 COOPER JOE 345 640139 COOPER 3 345 1 | 1195 |  | 0.06676 | 108.34 | System Intact
Thermal | 09ALL | 2 | 20G | GEN-2017-055 | 'FROM -> TO' | 640138 COOPER JOE 345 640139 COOPER 3 345 1 | 1195 |  | 0.1344 | 108.34 | System Intact
Thermal | 09ALL | 2 | 20G | GEN-2017-085 | 'FROM -> TO' | 640138 COOPER JOE 345 640139 COOPER 3 345 1 | 1195 |  | 0.12187 | 108.34 | System Intact
Thermal | 09ALL | 2 | 20SP | GEN-2016-159 | 'FROM -> TO' | 640138 COOPER JOE 345 640139 COOPER 3 345 1 | 1073 |  | 0.11277 | 100.23 | System Intact
Thermal | 09ALL | 2 | 20SP | GEN-2017-008 | 'FROM -> TO' | 640138 COOPER JOE 345 640139 COOPER 3 345 1 | 1073 |  | 0.10733 | 100.23 | System Intact
Thermal | 09ALL | 2 | 20SP | GEN-2017-031 | 'FROM -> TO' | 640138 COOPER JOE 345 640139 COOPER 3 345 1 | 1073 |  | 0.06951 | 100.23 | System Intact
Thermal | 09ALL | 2 | 20SP | GEN-2017-055 | 'FROM -> TO' | 640138 COOPER JOE 345 640139 COOPER 3 345 1 | 1073 |  | 0.13715 | 100.23 | System Intact
Thermal | 09ALL | 2 | 20SP | GEN-2017-085 | 'FROM -> TO' | 640138 COOPER JOE 345 640139 COOPER 3 345 1 | 1073 |  | 0.12461 | 100.23 | System Intact
Thermal | 09ALL | 2 | 20G | GEN-2017-031 | 'FROM -> TO' | 640184 GENTLMN4 230 640302 OGALALA4 230 1 |  | 320 | 0.49684 | 104.72 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 19WP | GEN-2017-031 | 'FROM -> TO' | 640184 GENTLMN4 230 640302 OGALALA4 230 1 |  | 320 | 0.49953 | 100.27 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 29SP | GEN-2016-159 | 'FROM -> TO' | 640226 HOSKINS3 345 997390 HOSKINS T2 230 1 |  | 336 | 0.21225 | 113.9 | P42:345:NPPD:BKR-HOS-3312
Thermal | 09ALL | 2 | 24SP | GEN-2016-159 | 'FROM -> TO' | 640226 HOSKINS3 345 997391 HOSKINS T2 230 1 |  | 336 | 0.21179 | 115.62 | P42:345:NPPD:BKR-HOS-3312
Thermal | 09ALL | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | 640226 HOSKINS3 345 997391 HOSKINS T2 230 1 |  | 336 | 0.21258 | 110.38 | P42:345:NPPD:BKR-HOS-3312
Thermal | 09ALL | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | 640226 HOSKINS3 345 997395 HOSKINS T2 230 1 |  | 336 | 0.21591 | 110.67 | P42:345:NPPD:BKR-HOS-3312
Thermal | 09ALL | 2 | 20SP | GEN-2016-159 | 'FROM -> TO' | 640226 HOSKINS3 345 997398 HOSKINS T2 230 1 |  | 336 | 0.21533 | 111.66 | P42:345:NPPD:BKR-HOS-3312
Thermal | 09ALL | 2 | 29SP | GEN-2016-159 | 'FROM -> TO' | 640227 HOSKINS4 230 997390 HOSKINS T2 230 1 |  | 336 | 0.21225 | 111.83 | P42:345:NPPD:BKR-HOS-3312
Thermal | 09ALL | 2 | 24SP | GEN-2016-159 | 'FROM -> TO' | 640227 HOSKINS4 230 997391 HOSKINS T2 230 1 |  | 336 | 0.21179 | 113.46 | P42:345:NPPD:BKR-HOS-3312
Thermal | 09ALL | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | 640227 HOSKINS4 230 997391 HOSKINS T2 230 1 |  | 336 | 0.21258 | 108.28 | P42:345:NPPD:BKR-HOS-3312
Thermal | 09ALL | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | 640227 HOSKINS4 230 997395 HOSKINS T2 230 1 |  | 336 | 0.21591 | 108.52 | P42:345:NPPD:BKR-HOS-3312
Thermal | 09ALL | 2 | 20SP | GEN-2016-159 | 'FROM -> TO' | 640227 HOSKINS4 230 997398 HOSKINS T2 230 1 |  | 336 | 0.21533 | 109.88 | P42:345:NPPD:BKR-HOS-3312
Thermal | 09ALL | 2 | 20SP | GEN-2017-031 | 'FROM -> TO' | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.22866 | 129.8 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 19WP | GEN-2017-031 | 'FROM -> TO' | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.22321 | 126.6 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 24SP | GEN-2017-031 | 'FROM -> TO' | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.23264 | 126.02 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 20G | GEN-2017-031 | 'FROM -> TO' | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.22091 | 125.82 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 29SP | GEN-2017-031 | 'FROM -> TO' | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.23316 | 124.56 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 24WP | GEN-2017-031 | 'FROM -> TO' | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.22754 | 124.46 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 20SP | GEN-2017-031 | 'FROM -> TO' | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.22121 | 128.33 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 24SP | GEN-2017-031 | 'FROM -> TO' | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.22485 | 125.04 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 19WP | GEN-2017-031 | 'FROM -> TO' | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.21578 | 124.68 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 20G | GEN-2017-031 | 'FROM -> TO' | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.21347 | 124.07 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 29SP | GEN-2017-031 | 'FROM -> TO' | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.22537 | 123.32 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 24WP | GEN-2017-031 | 'FROM -> TO' | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.21977 | 122.86 | P42:345:NPPD:BKR-KEY-3310
Non-Converge | 10ALL | 0 |  |  | '' | None |  |  |  |  | None
Thermal | 10ALL | 2 |  |  | '' | None |  |  |  |  | None
Non-Converge | 12ALL | 0 |  |  | '' | None |  |  |  |  | None
Thermal | 12ALL | 2 |  |  | '' | None |  |  |  |  | None
Non-Converge | 13ALL | 0 | 24L | GEN-2017-030 | '' | Non-Converge |  |  | 0.03532 |  | P12:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 24L | GEN-2017-030 | '' | Non-Converge |  |  | 0.03532 |  | P12:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 19WP | GEN-2017-090 | '' | Non-Converge |  |  | 0.06367 |  | P12:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 20G | GEN-2017-090 | '' | Non-Converge |  |  | 0.06048 |  | P12:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 20SP | GEN-2017-090 | '' | Non-Converge |  |  | 0.06123 |  | P12:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 24L | GEN-2017-090 | '' | Non-Converge |  |  | 0.07505 |  | P12:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 24SP | GEN-2017-090 | '' | Non-Converge |  |  | 0.06216 |  | P12:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 24WP | GEN-2017-090 | '' | Non-Converge |  |  | 0.06519 |  | P12:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 29SP | GEN-2017-090 | '' | Non-Converge |  |  | 0.06178 |  | P12:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 19WP | GEN-2017-090 | '' | Non-Converge |  |  | 0.06367 |  | P12:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 20G | GEN-2017-090 | '' | Non-Converge |  |  | 0.06048 |  | P12:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 20SP | GEN-2017-090 | '' | Non-Converge |  |  | 0.06123 |  | P12:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 24L | GEN-2017-090 | '' | Non-Converge |  |  | 0.07505 |  | P12:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 24SP | GEN-2017-090 | '' | Non-Converge |  |  | 0.06216 |  | P12:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 24WP | GEN-2017-090 | '' | Non-Converge |  |  | 0.06519 |  | P12:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 29SP | GEN-2017-090 | '' | Non-Converge |  |  | 0.06178 |  | P12:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 19WP | GEN-2017-030 | '' | Non-Converge |  |  | 0.03417 |  | P23:345:WERE:WOLF_345-50::
Non-Converge | 13ALL | 0 | 20G | GEN-2017-030 | '' | Non-Converge |  |  | 0.03899 |  | P23:345:WERE:WOLF_345-50::
Non-Converge | 13ALL | 0 | 20SP | GEN-2017-030 | '' | Non-Converge |  |  | 0.03558 |  | P23:345:WERE:WOLF_345-50::
Non-Converge | 13ALL | 0 | 24L | GEN-2017-030 | '' | Non-Converge |  |  | 0.04215 |  | P23:345:WERE:WOLF_345-50::
Non-Converge | 13ALL | 0 | 24SP | GEN-2017-030 | '' | Non-Converge |  |  | 0.03527 |  | P23:345:WERE:WOLF_345-50::
Non-Converge | 13ALL | 0 | 24WP | GEN-2017-030 | '' | Non-Converge |  |  | 0.03425 |  | P23:345:WERE:WOLF_345-50::
Non-Converge | 13ALL | 0 | 29SP | GEN-2017-030 | '' | Non-Converge |  |  | 0.03488 |  | P23:345:WERE:WOLF_345-50::
Non-Converge | 13ALL | 0 | 19WP | GEN-2017-090 | '' | Non-Converge |  |  | 0.03849 |  | P23:345:WERE:WOLF_345-50::
Non-Converge | 13ALL | 0 | 20G | GEN-2017-090 | '' | Non-Converge |  |  | 0.04331 |  | P23:345:WERE:WOLF_345-50::
Non-Converge | 13ALL | 0 | 20SP | GEN-2017-090 | '' | Non-Converge |  |  | 0.03993 |  | P23:345:WERE:WOLF_345-50::
Non-Converge | 13ALL | 0 | 24L | GEN-2017-090 | '' | Non-Converge |  |  | 0.04654 |  | P23:345:WERE:WOLF_345-50::
Non-Converge | 13ALL | 0 | 24SP | GEN-2017-090 | '' | Non-Converge |  |  | 0.03966 |  | P23:345:WERE:WOLF_345-50::
Non-Converge | 13ALL | 0 | 24WP | GEN-2017-090 | '' | Non-Converge |  |  | 0.03864 |  | P23:345:WERE:WOLF_345-50::
Non-Converge | 13ALL | 0 | 29SP | GEN-2017-090 | '' | Non-Converge |  |  | 0.03927 |  | P23:345:WERE:WOLF_345-50::
Non-Converge | 14ALL | 0 |  |  | '' | None |  |  |  |  | None
Thermal | 14ALL | 2 | 19WP | GEN-2017-023 | 'FROM -> TO' | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.31053 | 105.87 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 14ALL | 2 | 19WP | GEN-2017-024 | 'FROM -> TO' | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.2908 | 105.87 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 14ALL | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.31041 | 103.91 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 14ALL | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.29067 | 103.91 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 14ALL | 2 | 19WP | GEN-2017-023 | 'FROM -> TO' | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.30794 | 102.84 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 14ALL | 2 | 19WP | GEN-2017-024 | 'FROM -> TO' | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.28827 | 102.84 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 14ALL | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.3078 | 101.04 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 14ALL | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.28811 | 101.04 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 14ALL | 2 | 19WP | GEN-2017-023 | 'FROM -> TO' | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.30794 | 102.84 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 14ALL | 2 | 19WP | GEN-2017-024 | 'FROM -> TO' | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.28827 | 102.84 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 14ALL | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.3078 | 101.04 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 14ALL | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.28811 | 101.04 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Non-Converge | 15ALL | 0 | 19WP | GEN-2016-103 | '' | Non-Converge |  |  | 0.79522 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 15ALL | 0 | 19WP | GEN-2016-103 | '' | Non-Converge |  |  | 0.79522 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 15ALL | 0 | 20G | GEN-2016-103 | '' | Non-Converge |  |  | 0.7936 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 15ALL | 0 | 20G | GEN-2016-103 | '' | Non-Converge |  |  | 0.7936 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 15ALL | 0 | 20SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.79937 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 15ALL | 0 | 20SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.79937 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 15ALL | 0 | 24L | GEN-2016-103 | '' | Non-Converge |  |  | 0.79232 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 15ALL | 0 | 24L | GEN-2016-103 | '' | Non-Converge |  |  | 0.79232 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 15ALL | 0 | 24SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.80122 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 15ALL | 0 | 24SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.80122 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 15ALL | 0 | 24WP | GEN-2016-103 | '' | Non-Converge |  |  | 0.79659 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 15ALL | 0 | 24WP | GEN-2016-103 | '' | Non-Converge |  |  | 0.79659 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 15ALL | 0 | 29SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.80145 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 15ALL | 0 | 29SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.80145 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 15ALL | 0 | 19WP | GEN-2016-103 | '' | Non-Converge |  |  | 0.27753 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 15ALL | 0 | 19WP | GEN-2016-103 | '' | Non-Converge |  |  | 0.27753 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 15ALL | 0 | 20G | GEN-2016-103 | '' | Non-Converge |  |  | 0.27639 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 15ALL | 0 | 20G | GEN-2016-103 | '' | Non-Converge |  |  | 0.27639 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 15ALL | 0 | 20SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.27849 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 15ALL | 0 | 20SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.27849 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 15ALL | 0 | 24L | GEN-2016-103 | '' | Non-Converge |  |  | 0.27703 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 15ALL | 0 | 24L | GEN-2016-103 | '' | Non-Converge |  |  | 0.27703 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 15ALL | 0 | 24SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.27319 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 15ALL | 0 | 24SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.27319 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 15ALL | 0 | 24WP | GEN-2016-103 | '' | Non-Converge |  |  | 0.27263 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 15ALL | 0 | 24WP | GEN-2016-103 | '' | Non-Converge |  |  | 0.27263 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 15ALL | 0 | 29SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.27331 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 15ALL | 0 | 29SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.27331 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 15ALL | 0 | 19WP | GEN-2016-103 | '' | Non-Converge |  |  | 0.27753 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 15ALL | 0 | 19WP | GEN-2016-103 | '' | Non-Converge |  |  | 0.27753 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 15ALL | 0 | 20G | GEN-2016-103 | '' | Non-Converge |  |  | 0.27639 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 15ALL | 0 | 20G | GEN-2016-103 | '' | Non-Converge |  |  | 0.27639 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 15ALL | 0 | 20SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.27849 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 15ALL | 0 | 20SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.27849 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 15ALL | 0 | 24L | GEN-2016-103 | '' | Non-Converge |  |  | 0.27703 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 15ALL | 0 | 24L | GEN-2016-103 | '' | Non-Converge |  |  | 0.27703 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 15ALL | 0 | 24SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.27319 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 15ALL | 0 | 24SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.27319 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 15ALL | 0 | 24WP | GEN-2016-103 | '' | Non-Converge |  |  | 0.27263 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 15ALL | 0 | 24WP | GEN-2016-103 | '' | Non-Converge |  |  | 0.27263 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 15ALL | 0 | 29SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.27331 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 15ALL | 0 | 29SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.27331 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 115.72 | P11:0:OTP:AUTO-SINGLE:ASH1GEN9:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.69 | P11:0:OTP:AUTO-SINGLE:ASH1GEN9:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.22 | P11:0:XEL:AUTO-SINGLE:G349BUFRG1:W
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.14 | P11:0:XEL:AUTO-SINGLE:G349BUFRG1:W
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.22 | P11:0:XEL:AUTO-SINGLE:G349BUFRG2:W
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.14 | P11:0:XEL:AUTO-SINGLE:G349BUFRG2:W
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.95 | P11:0:XEL:AUTO-SINGLE:G514ECRK2W:W
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.88 | P11:0:XEL:AUTO-SINGLE:G514ECRK2W:W
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.4 | P11:0:XEL:AUTO-SINGLE:J183PROSEW1:W
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.4 | P11:0:XEL:AUTO-SINGLE:J183PROSEW1:W
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.41 | P11:0:XEL:AUTO-SINGLE:J183PROSEW2:W
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.4 | P11:0:XEL:AUTO-SINGLE:J183PROSEW2:W
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116 | P11:0:XEL:AUTO-SINGLE:J290BORDRW:W
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.63 | P11:001:599:IRONWOODWIND1:152:539106(1)
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.63 | P11:001:599:SPEARVILLEWIND2:154:539120(1)
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.7 | P11:001:UMZB:# 26 #: WILT2 IN ND. WILTON 2
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.46 | P11:014:NPPD:CANADY1G:1:128
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.62 | P11:014:UMZB:# 17 #: LSS1 IN ND. LONESOME UNIT1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.14 | P11:014:UMZB:# 17 #: LSS1 IN ND. LONESOME UNIT1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.62 | P11:014:UMZB:# 18 #: LSS2 IN ND. LONESOME UNIT2
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.14 | P11:014:UMZB:# 18 #: LSS2 IN ND. LONESOME UNIT2
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.62 | P11:014:UMZB:# 19 #: LSS3 IN ND. LONESOME UNIT3
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.14 | P11:014:UMZB:# 19 #: LSS3 IN ND. LONESOME UNIT3
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.63 | P11:014:UMZB:# 20 #: PNS1 IN ND. PNS1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.16 | P11:014:UMZB:# 20 #: PNS1 IN ND. PNS1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.63 | P11:014:UMZB:# 21 #: PNS2 IN ND. PNS2
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.16 | P11:014:UMZB:# 21 #: PNS2 IN ND. PNS2
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.63 | P11:014:UMZB:# 22 #: PNS3 IN ND. PNS3
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.16 | P11:014:UMZB:# 22 #: PNS3 IN ND. PNS3
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.6 | P11:014:UMZB:# 2988 #: LSS 4 IN ND. LONESOME CREEK 4
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.13 | P11:014:UMZB:# 2988 #: LSS 4 IN ND. LONESOME CREEK 4
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.6 | P11:014:UMZB:# 2989 #: LSS 5 IN ND. LONESOME CREEK 5
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.13 | P11:014:UMZB:# 2989 #: LSS 5 IN ND. LONESOME CREEK 5
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.7 | P11:014:UMZB:# 39 #: WILT1 IN ND. WILTON 1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.8 | P11:014:UMZB:# 41 #: WILT3 IN ND. WILTON 3
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 117.07 | P11:014:UMZW:# 58 #: FP IN MT. LOSS OF UNIT (4).
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.96 | P11:014:UMZW:# 58 #: FP IN MT. LOSS OF UNIT (4).
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.52 | P11:014:UMZW:# 58 #: FP IN MT. LOSS OF UNIT (4).
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 117.54 | P11:014:UMZW:# 68 #: GA IN ND. LOSS OF UNIT (1).
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 104.5 | P11:014:UMZW:# 68 #: GA IN ND. LOSS OF UNIT (1).
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.97 | P11:014:UMZW:# 68 #: GA IN ND. LOSS OF UNIT (1).
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 117.55 | P11:014:UMZW:# 69 #: GA IN ND. LOSS OF UNIT (2).
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 104.5 | P11:014:UMZW:# 69 #: GA IN ND. LOSS OF UNIT (2).
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.97 | P11:014:UMZW:# 69 #: GA IN ND. LOSS OF UNIT (2).
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 117.16 | P11:014:UMZW:# 70 #: GA IN ND. LOSS OF UNIT (3).
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 104.5 | P11:014:UMZW:# 70 #: GA IN ND. LOSS OF UNIT (3).
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.97 | P11:014:UMZW:# 70 #: GA IN ND. LOSS OF UNIT (3).
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 117.56 | P11:014:UMZW:# 71 #: GA IN ND. LOSS OF UNIT (4).
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 104.53 | P11:014:UMZW:# 71 #: GA IN ND. LOSS OF UNIT (4).
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.98 | P11:014:UMZW:# 71 #: GA IN ND. LOSS OF UNIT (4).
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 117.55 | P11:014:UMZW:# 72 #: GA IN ND. LOSS OF UNIT (5).
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 104.53 | P11:014:UMZW:# 72 #: GA IN ND. LOSS OF UNIT (5).
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.99 | P11:014:UMZW:# 72 #: GA IN ND. LOSS OF UNIT (5).
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.59 | P11:014:UMZW:# 77 #: OA IN SD. LOSS OF UNIT (2).
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.48 | P11:014:UMZW:# 77 #: OA IN SD. LOSS OF UNIT (2).
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.58 | P11:014:UMZW:# 78 #: OA IN SD. LOSS OF UNIT (3).
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.48 | P11:014:UMZW:# 78 #: OA IN SD. LOSS OF UNIT (3).
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.48 | P11:014:UMZW:# 79 #: OA IN SD. LOSS OF UNIT (4).
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.48 | P11:014:UMZW:# 80 #: OA IN SD. LOSS OF UNIT (5).
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.52 | P11:014:UMZW:# 81 #: OA IN SD. LOSS OF UNIT (6).
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 114.22 | P11:014:UMZW:# 83 #: OA IN SD. LOSS OF UNIT (1).
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 100.74 | P11:014:UMZW:# 83 #: OA IN SD. LOSS OF UNIT (1).
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 114.27 | P11:024:DPC:ALMA2:6
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 101.25 | P11:024:DPC:ALMA2:6
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.78 | P11:035:UMZB:# 2983 #: BRADY WIND IN ND. BRADY WIND 2
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.63 | P11:035:UMZB:# 2983 #: BRADY WIND IN ND. BRADY WIND 2
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.17 | P11:035:UMZB:# 2983 #: BRADY WIND IN ND. BRADY WIND 2
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.78 | P11:035:UMZB:# 2984 #: BRADY WIND IN ND. BRADY WIND 1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.63 | P11:035:UMZB:# 2984 #: BRADY WIND IN ND. BRADY WIND 1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.17 | P11:035:UMZB:# 2984 #: BRADY WIND IN ND. BRADY WIND 1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.82 | P11:035:UMZB:# 2985 #: LINDAHL WIND IN ND. LINDAHL WIND
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.64 | P11:035:UMZB:# 2985 #: LINDAHL WIND IN ND. LINDAHL WIND
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.18 | P11:035:UMZB:# 2985 #: LINDAHL WIND IN ND. LINDAHL WIND
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.98 | P11:035:UMZB:# 3562 #: DCW IN SD. DAY COUNTY WIND 1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.91 | P11:035:UMZB:# 3562 #: DCW IN SD. DAY COUNTY WIND 1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.53 | P11:035:UMZB:# 3562 #: DCW IN SD. DAY COUNTY WIND 1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.84 | P11:035:UMZB:# 3563 #: IN ND. ND SUNFLOWER WIND
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.65 | P11:035:UMZB:# 3563 #: IN ND. ND SUNFLOWER WIND
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.19 | P11:035:UMZB:# 3563 #: IN ND. ND SUNFLOWER WIND
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.23 | P11:035:UMZB:# 3564 #: CBW IN SD. CAMBELL COUNTY WIND 1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.24 | P11:035:UMZB:# 3564 #: CBW IN SD. CAMBELL COUNTY WIND 1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 101.79 | P11:035:UMZB:# 3564 #: CBW IN SD. CAMBELL COUNTY WIND 1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.78 | P11:035:UMZW:# 28 #: WWC IN SD. LOSS OF UNIT (WIND).
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.09 | P11:069:UMZB:# 12 #: HY IN SD. HYDE
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.11 | P11:069:UMZB:# 12 #: HY IN SD. HYDE
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 101.63 | P11:069:UMZB:# 12 #: HY IN SD. HYDE
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 104.17 | P11:115:GRIS:PGS
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.76 | P11:115:GRIS:PGS
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 102.34 | P11:115:MDU::HESKETT::2::::
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.59 | P11:115:MDU::HESKETT::3::::
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.4 | P11:115:MDU::LEWIS & CLARK::1::::
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 104.14 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.93 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.56 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.22 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.16 | P11:115:UMZB:# 2 #: CQ IN ND. CULBERTSON GEN
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.86 | P11:115:UMZB:# 34 #: PWN IN ND. NDPRARIE WINDS
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.48 | P11:115:UMZB:# 36 #: GGS2 IN SD. GROTON 2
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 118.03 | P11:115:UMZZ:# 2991 #: BH IN SD. LOSS OF BEETHOVEN WIND FARM
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.7 | P11:115:XEL:HBR #6
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.24 | P11:115:XEL:HBR #6
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.95 | P11:115:XEL:HBR #6 7 8
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.7 | P11:115:XEL:HBR #7
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.24 | P11:115:XEL:HBR #7
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.81 | P11:115:XEL:RIV COMBINE CYCLE
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.59 | P11:13:XEL:AUTO-SINGLE:BLKD72G:2
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.7 | P11:13:XEL:AUTO-SINGLE:HBRS73G:9
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.67 | P11:13:XEL:AUTO-SINGLE:LSPCTG:C
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.75 | P11:138:OKGE:BKRBKR_GSU03
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.58 | P11:138:OKGE:BKRBKR_GSU03
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.19 | P11:138:OKGE:BKRBKR_GSU03
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 117.53 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.92 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.82 | P11:15:XEL:AUTO-SINGLE:MEC-CT1:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 101.94 | P11:16:GRE:AUTO-SINGLE:GRE-CGS82G:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.52 | P11:16:GRE:AUTO-SINGLE:GRE-ER14G:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 104.03 | P11:16:GRE:AUTO-SINGLE:GRE-PVS51G:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 104.02 | P11:16:GRE:AUTO-SINGLE:GRE-PVS52G:2
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.57 | P11:16:XEL:AUTO-SINGLE:RIVRS77G:7
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.08 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 117.86 | P11:18:HAST:255 MW:EGYCTR2G WEC2:LOSS OF WEC 2 GEN
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 104.86 | P11:18:HAST:255 MW:EGYCTR2G WEC2:LOSS OF WEC 2 GEN
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 103.52 | P11:18:HAST:255 MW:EGYCTR2G WEC2:LOSS OF WEC 2 GEN
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 100.46 | P11:18:HAST:255 MW:EGYCTR2G WEC2:LOSS OF WEC 2 GEN
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 101.29 | P11:18:ITCM:EMERYGT1:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 101.29 | P11:18:ITCM:EMERYGT2:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.62 | P11:18:XEL:AUTO-SINGLE:BLKD75G:5
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.68 | P11:18:XEL:AUTO-SINGLE:COLVILL1G:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.68 | P11:18:XEL:AUTO-SINGLE:COLVILLG:2
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.73 | P11:18:XEL:AUTO-SINGLE:FEPCTG:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.61 | P11:18:XEL:AUTO-SINGLE:HBRC71G:7
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.61 | P11:18:XEL:AUTO-SINGLE:HBRC72G:8
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.59 | P11:18:XEL:AUTO-SINGLE:RIVRSIDEG97:9
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.59 | P11:18:XEL:AUTO-SINGLE:RIVRSIDG107:10
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.82 | P11:19:XEL:AUTO-SINGLE:MEC-ST:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 110.48 | P11:20:OTP:AUTO-SINGLE:CENTER2G:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.98 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 104.01 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 117.21 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 104.09 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 117.47 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 104.09 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.75 | P11:22:AEPW:FLINTCR1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.35 | P11:22:AEPW:FLINTCR1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.79 | P11:22:AEPW:NES3-1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.41 | P11:22:AEPW:NES3-1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.39 | P11:22:AEPW:RSS2-1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 101.35 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.87 | P11:22:EES-EAI:ARK_NU:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.7 | P11:22:EES-EAI:ARK_NU:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.31 | P11:22:EES-EAI:ARK_NU:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.84 | P11:22:EES-EAI:ARK_NU:1:D395
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.7 | P11:22:EES-EAI:ARK_NU:1:D395
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.29 | P11:22:EES-EAI:ARK_NU:1:D395
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 114.12 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 113.63 | P11:22:OTP:AUTO-SINGLE:CENTER1G:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 102.69 | P11:22:OTP:AUTO-SINGLE:CENTER1G:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.55 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.38 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 115.64 | P11:230:MDU::TATANKA::W::::
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 115.58 | P11:230:MDU::THUNDER SPIRIT::W::::
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 115.67 | P11:230:UMZB:# 40 #: CRW IN SD. SD PRAIRIE WIND
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 102.78 | P11:230:UMZB:# 40 #: CRW IN SD. SD PRAIRIE WIND
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.58 | P11:230:WERE:JECU1_GEN::
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.21 | P11:230:WERE:JECU1_GEN::
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.07 | P11:24:AEPW:PIRKEY 1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.39 | P11:24:AEPW:RSS1-1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.72 | P11:24:AEPW:TURKCOAL
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.61 | P11:24:AEPW:TURKCOAL
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.2 | P11:24:AEPW:TURKCOAL
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 104.16 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 114.27 | P11:24:DPC:AUTO-SINGLE:JPM:6
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 101.25 | P11:24:DPC:AUTO-SINGLE:JPM:6
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 117.45 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 105.66 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 104.48 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 101.44 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.32 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.19 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 100.99 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 111.72 | P11:24:OTP:AUTO-SINGLE:COYOTE1G:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.56 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 108.06 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 117.59 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 106.09 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 105.06 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 101.77 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.63 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 115.87 | P11:34:ALTW:AUTO-SINGLE:G735_WF5:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 101.41 | P11:34:ALTW:AUTO-SINGLE:G735_WF5:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.91 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24537 | 117.82 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24935 | 103.86 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.75 | P11:345:OKGE:BKRBKR_GSU04
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.58 | P11:345:OKGE:BKRBKR_GSU04
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.19 | P11:345:OKGE:BKRBKR_GSU04
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 101.99 | P11:345:OKGE:BKRBKR_GSU05
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.44 | P11:345:OKGE:BKRBKR_GSU06
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 101.99 | P11:345:OKGE:BKRBKR_GSU06
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.51 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.11 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.51 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.11 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.44 | P11:345:OKGE:BKRBKR_GSU22
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 101.99 | P11:345:OKGE:BKRBKR_GSU22
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.15 | P11:345:OKGE:BKRBKR_GSU24
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.15 | P11:345:OKGE:BKRBKR_GSU25
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.15 | P11:345:OKGE:BKRBKR_GSU26
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.15 | P11:345:OKGE:BKRBKR_GSU27
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.91 | P11:345:OPPD:NEBCTY1G
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.53 | P11:345:OPPD:NEBCTY1G
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.91 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.45 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 117.88 | P11:345:OPPD:NEBCTY2G
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.96 | P11:345:OPPD:NEBCTY2G
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.49 | P11:345:OPPD:NEBCTY2G
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.71 | P11:345:UMZB:# 15 #: LO IN ND. LELAND OLDS 1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 111.33 | P11:345:UMZB:# 16 #: LO IN ND. LELAND OLDS 2
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.67 | P11:345:UMZB:# 31 #: AVS IN ND. ANTELOPE VALLEY 1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 122.39 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 118.06 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 117.72 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 114.75 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2478 | 108 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 15ALL | 2 | 24WP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25852 | 103.06 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 106.38 | P11:345:UMZB:# 5 #: DCS IN SD. DEERCREEK
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.58 | P11:345:WERE:JECU2_GEN::
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.2 | P11:345:WERE:JECU2_GEN::
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.58 | P11:345:WERE:JECU3_GEN::
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.2 | P11:345:WERE:JECU3_GEN::
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24964 | 104.37 | P12:115:MDU:ND:BISCENTRYCE7:CENTURY7:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26232 | 102.69 | P12:115:MDU:ND:BISCENTRYCE7:CENTURY7:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24682 | 117.7 | P12:115:NPPD:1090:AINSWND7:THEDFRD7:BTB
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25011 | 103.98 | P12:115:NPPD:1091:VALENTN7:MISSION7:BTB
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26308 | 102.56 | P12:115:NPPD:1091:VALENTN7:MISSION7:BTB
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2476 | 117.98 | P12:115:NPPD:WAPA6:FTRANDL7:ONEILL 7:BTB
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25165 | 106.64 | P12:115:NPPD:WAPA6:FTRANDL7:ONEILL 7:BTB
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26456 | 105.3 | P12:115:NPPD:WAPA6:FTRANDL7:ONEILL 7:BTB
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26456 | 102.15 | P12:115:NPPD:WAPA6:FTRANDL7:ONEILL 7:BTB
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 118.95 | P12:115:OTP::DONALDS7:TRFALLS7
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 102.9 | P12:115:OTP::DONALDS7:TRFALLS7
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 101.31 | P12:115:OTP::DONALDS7:TRFALLS7
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 115.38 | P12:115:OTP:AUTO-SINGLE:LANGWIN7:LANGDON7:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24541 | 118.61 | P12:115:OTP-MPC::TRFALLS7:WINGER 7
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24941 | 102.98 | P12:115:OTP-MPC::TRFALLS7:WINGER 7
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 101.37 | P12:115:OTP-MPC::TRFALLS7:WINGER 7
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2497 | 104.57 | P12:115:OTP-MRES::HOOT LK7:FERGSFL7
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26237 | 103.23 | P12:115:OTP-MRES::HOOT LK7:FERGSFL7
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24538 | 116.89 | P12:115:UMZ:# 5503 #: IN . PROPER N-1 (LINE) FOR 603023-652440-1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.16 | P12:115:UMZ:# 5537 #: IN . PROPER N-1 (LINE) FOR 652421-659262-1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24538 | 116.88 | P12:115:UMZ:# 5551 #: IN . PROPER N-1 (LINE) FOR 652440-655690-1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26262 | 102.15 | P12:115:UMZ:# 5567 #: IN . PROPER N-1 (LINE) FOR 655490-652525-1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24965 | 104.27 | P12:115:UMZ:# 5576 #: IN . PROPER N-1 (LINE) FOR 652479-659153-1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26242 | 102.95 | P12:115:UMZ:# 5576 #: IN . PROPER N-1 (LINE) FOR 652479-659153-1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25024 | 104.03 | P12:115:UMZ:# 5595 #: IN . PROPER N-1 (LINE) FOR 652501-652510-1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26293 | 102.58 | P12:115:UMZ:# 5595 #: IN . PROPER N-1 (LINE) FOR 652501-652510-1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24618 | 117.41 | P12:115:UMZ:# 5614 #: IN . PROPER N-1 (LINE) FOR 652626-660007-1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.76 | P12:115:UMZ:# 5700 #: IN . PROPER N-1 (LINE) FOR 655946-655947-1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26205 | 102.16 | P12:115:UMZ:# 5798 #: IN . PROPER N-1 (LINE) FOR 659112-659262-1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26205 | 102.16 | P12:115:UMZB:# 2944 #: CQ IN MT. POPLAR - WILLISTON
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25024 | 104.03 | P12:115:UMZW:# 123 #: AR IN SD. MV-AR-FR 115
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26293 | 102.58 | P12:115:UMZW:# 123 #: AR IN SD. MV-AR-FR 115
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24965 | 104.27 | P12:115:UMZW:# 153 #: MS-VE-MR IN SD. VETAL TAP IS A TAP WITH NON-FAULT INTERUPTERS
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26242 | 102.95 | P12:115:UMZW:# 153 #: MS-VE-MR IN SD. VETAL TAP IS A TAP WITH NON-FAULT INTERUPTERS
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24538 | 116.88 | P12:115:UMZW:# 156 #: NEL IN ND. FAULT ON ML-NEL-MX-GA 115 KV
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25169 | 104.46 | P12:115:UMZW:# 1843 #: YJ IN SD. YJ-GP LINE FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26432 | 102.93 | P12:115:UMZW:# 1843 #: YJ IN SD. YJ-GP LINE FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26262 | 102.15 | P12:115:UMZW:# 509 #: TY IN SD. TY-YJ LINE FAULT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24618 | 117.41 | P12:115:UMZZ:# 228 #: MEN IN SD. MENNO JUNCTION IS A TAP (UJ-MEN-TP).
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 115.78 | P12:115:XEL:AUTO-SINGLE:BRKNGCO7:OAKLAKEW7:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 102.71 | P12:115:XEL:AUTO-SINGLE:BRKNGCO7:OAKLAKEW7:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.75 | P12:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.88 | P12:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.87 | P12:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.44 | P12:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.43 | P12:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.47 | P12:115:XEL:AUTO-SINGLE:NSSTAP7:NSSTL7:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 117.06 | P12:115:XEL:AUTO-SINGLE:ODELLWIND7:WOADHILL7:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.98 | P12:115:XEL:AUTO-SINGLE:ODELLWIND7:WOADHILL7:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.46 | P12:115:XEL:AUTO-SINGLE:ODELLWIND7:WOADHILL7:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.16 | P12:115:XEL:AUTO-SINGLE:PROSEWIND7:PROSECAP7:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.26 | P12:115:XEL:AUTO-SINGLE:PROSEWIND7:PROSECAP7:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.43 | P12:115:XEL:AUTO-SINGLE:REDROCK7:NSSJCT7:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.39 | P12:115:XEL:AUTO-SINGLE:REDROCK7:NSSJCT7:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.53 | P12:115:XEL:AUTO-SINGLE:SPLTRK7:ANSON7:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.15 | P12:115:XEL:AUTO-SINGLE:SPLTRK7:PROSECAP7:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.26 | P12:115:XEL:AUTO-SINGLE:SPLTRK7:PROSECAP7:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.87 | P12:115:XEL:AUTO-SINGLE:WILMART7:MEC-115:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.67 | P12:115:XEL:BDS #2 5
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.23 | P12:115:XEL:BDS #2 5
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.66 | P12:115:XEL:BLL GEN 1-4
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.17 | P12:115:XEL:BLL GEN 1-4
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.48 | P12:115:XEL:DLK-HYL
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.05 | P12:115:XEL:DLK-HYL
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.48 | P12:115:XEL:SCO-DLK-HYL-BLL
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.04 | P12:115:XEL:SCO-DLK-HYL-BLL
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.76 | P12:116:UMZB:# 2911 #: LND IN ND. LINDAHL - NESET
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 101.18 | P12:161:ALTW:AUTO-SINGLE:CRYSTLK5:CRYSTLKII5:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 115.68 | P12:161:ALTW:AUTO-SINGLE:FREEBORN5:G870_TAP5:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 102.77 | P12:161:ALTW:AUTO-SINGLE:FREEBORN5:G870_TAP5:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 101.22 | P12:161:ALTW:AUTO-SINGLE:FREEBORN5:G870_TAP5:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.96 | P12:161:XEL:ECL-WHT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.53 | P12:161:XEL:ECL-WHT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 117.15 | P12:161:XEL-GRE:AUTO-SINGLE:GRNDMDOW5:GRE-PLVLLY5:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 104.05 | P12:161:XEL-GRE:AUTO-SINGLE:GRNDMDOW5:GRE-PLVLLY5:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 117.15 | P12:161:XEL-GRE:AUTO-SINGLE:PLSVLLYW5:GRE-PLVLLY5:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 104.06 | P12:161:XEL-GRE:AUTO-SINGLE:PLSVLLYW5:GRE-PLVLLY5:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25017 | 104.57 | P12:230:GRE-WAPA:AUTO-SINGLE:GRE-STANTON4:LELANDO4:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2628 | 103.02 | P12:230:GRE-WAPA:AUTO-SINGLE:GRE-STANTON4:LELANDO4:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 115.65 | P12:230:MDU::TATANKA NORTH:TATANKA SOUTH:1::::
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.7 | P12:230:MDU::TATANKA NORTH:TATANKA SOUTH:1::::
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24516 | 115.6 | P12:230:MIDW-WERE:SMOKYHL6-SUMMIT6
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.23 | P12:230:OTP:AUTO-SINGLE:BARNES4:SIBLEY4:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24956 | 105.03 | P12:230:OTP:AUTO-SINGLE:HANKSON4:WAHPETN4:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26224 | 103.72 | P12:230:OTP:AUTO-SINGLE:HANKSON4:WAHPETN4:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 115.08 | P12:230:OTP:AUTO-SINGLE:PILSBRY4:BARNES4:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.7 | P12:230:OTP:AUTO-SINGLE:PILSBRY4:BARNES4:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.28 | P12:230:OTP:AUTO-SINGLE:PILSBRY4:BARNES4:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 115.83 | P12:230:OTP:AUTO-SINGLE:PILSBRY4:LUVERNE4:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 114.33 | P12:230:OTP:AUTO-SINGLE:PILSBRY4:MAPLER4:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.71 | P12:230:OTP:AUTO-SINGLE:PILSBRY4:MAPLER4:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.29 | P12:230:OTP:AUTO-SINGLE:PILSBRY4:MAPLER4:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 114.43 | P12:230:OTP:AUTO-SINGLE:RGBYWND4:RUGBY4:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 111.18 | P12:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26229 | 102.91 | P12:230:OTP-GRE::GRE-SILVRLK4B2.SLV-INM
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 115.83 | P12:230:OTP-MPC:B2.PB4-LUV
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24966 | 104.24 | P12:230:UMZ:# 5541 #: IN . PROPER N-1 (LINE) FOR 652426-659128-1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26234 | 102.89 | P12:230:UMZ:# 5541 #: IN . PROPER N-1 (LINE) FOR 652426-659128-1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24952 | 103.9 | P12:230:UMZ:# 5549 #: IN . PROPER N-1 (LINE) FOR 652437-657759-1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2622 | 102.52 | P12:230:UMZ:# 5549 #: IN . PROPER N-1 (LINE) FOR 652437-657759-1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24913 | 115.45 | P12:230:UMZ:# 5605 #: IN . PROPER N-1 (LINE) FOR 655765-655510-1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25275 | 102.63 | P12:230:UMZ:# 5605 #: IN . PROPER N-1 (LINE) FOR 655765-655510-1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26549 | 101.04 | P12:230:UMZ:# 5605 #: IN . PROPER N-1 (LINE) FOR 655765-655510-1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24993 | 118.57 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25492 | 104.75 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26774 | 103.19 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24913 | 115.41 | P12:230:UMZ:# 5867 #: IN . PROPER N-1 (LINE) FOR 655510-655487-Z
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25275 | 102.61 | P12:230:UMZ:# 5867 #: IN . PROPER N-1 (LINE) FOR 655510-655487-Z
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26549 | 101.01 | P12:230:UMZ:# 5867 #: IN . PROPER N-1 (LINE) FOR 655510-655487-Z
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24913 | 115.44 | P12:230:UMZB:# 109 #: SB IN SD. SULLY BUTTES-WHITLOCK-GLENHAM
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25275 | 102.63 | P12:230:UMZB:# 109 #: SB IN SD. SULLY BUTTES-WHITLOCK-GLENHAM
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26549 | 101.04 | P12:230:UMZB:# 109 #: SB IN SD. SULLY BUTTES-WHITLOCK-GLENHAM
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25663 | 122.16 | P12:230:UMZB:# 111 #: ST IN SD. WESSINGTION SPRINGS-STORLA-VT HANLON
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26104 | 110.22 | P12:230:UMZB:# 111 #: ST IN SD. WESSINGTION SPRINGS-STORLA-VT HANLON
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.27383 | 108.97 | P12:230:UMZB:# 111 #: ST IN SD. WESSINGTION SPRINGS-STORLA-VT HANLON
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.27388 | 105.62 | P12:230:UMZB:# 111 #: ST IN SD. WESSINGTION SPRINGS-STORLA-VT HANLON
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25946 | 101.28 | P12:230:UMZB:# 111 #: ST IN SD. WESSINGTION SPRINGS-STORLA-VT HANLON
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24809 | 117.39 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25269 | 104.65 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26545 | 103.22 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24966 | 104.24 | P12:230:UMZB:# 2937 #: HWB IN ND. LOSS OF HERBERT WEBER TAP
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26234 | 102.89 | P12:230:UMZB:# 2937 #: HWB IN ND. LOSS OF HERBERT WEBER TAP
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25023 | 104.65 | P12:230:UMZW:# 136 #: GF IN MN. GF-APD LINE FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26294 | 103.39 | P12:230:UMZW:# 136 #: GF IN MN. GF-APD LINE FAULT
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26293 | 100.21 | P12:230:UMZW:# 136 #: GF IN MN. GF-APD LINE FAULT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2459 | 117.42 | P12:230:UMZW:# 137 #: GF IN MN. GF-FB LINE FAULT
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24992 | 105.03 | P12:230:UMZW:# 137 #: GF IN MN. GF-FB LINE FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26261 | 103.75 | P12:230:UMZW:# 137 #: GF IN MN. GF-FB LINE FAULT
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26261 | 100.48 | P12:230:UMZW:# 137 #: GF IN MN. GF-FB LINE FAULT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25113 | 118.89 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25366 | 104.55 | P12:230:UMZW:# 169 #: WT IN SD. WT-CRP LINE FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26644 | 103.13 | P12:230:UMZW:# 169 #: WT IN SD. WT-CRP LINE FAULT
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25366 | 104.61 | P12:230:UMZW:# 170 #: WT IN SD. WT-HU LINE FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26644 | 103.18 | P12:230:UMZW:# 170 #: WT IN SD. WT-HU LINE FAULT
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25023 | 104.77 | P12:230:UMZW:# 172 #: WT IN SD. WT-APD LINE FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26294 | 103.51 | P12:230:UMZW:# 172 #: WT IN SD. WT-APD LINE FAULT
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26293 | 100.35 | P12:230:UMZW:# 172 #: WT IN SD. WT-APD LINE FAULT
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24982 | 104.43 | P12:230:UMZW:# 1720 #: GF IN MN. GF-MNVLTAP LINE FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26251 | 103.2 | P12:230:UMZW:# 1720 #: GF IN MN. GF-MNVLTAP LINE FAULT
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26251 | 100.01 | P12:230:UMZW:# 1720 #: GF IN MN. GF-MNVLTAP LINE FAULT
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25995 | 105.11 | P12:230:UMZW:# 691 #: FT IN SD. FT-WSG LINE FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.27276 | 103.72 | P12:230:UMZW:# 691 #: FT IN SD. FT-WSG LINE FAULT
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2728 | 100.39 | P12:230:UMZW:# 691 #: FT IN SD. FT-WSG LINE FAULT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25692 | 120.01 | P12:230:UMZW:# 692 #: FT IN SD. FT-LET LINE FAULT
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26133 | 108.71 | P12:230:UMZW:# 692 #: FT IN SD. FT-LET LINE FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.27412 | 107.44 | P12:230:UMZW:# 692 #: FT IN SD. FT-LET LINE FAULT
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.27417 | 104.1 | P12:230:UMZW:# 692 #: FT IN SD. FT-LET LINE FAULT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25839 | 120.95 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26293 | 109.35 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.27578 | 108.09 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.27579 | 104.71 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26104 | 101.37 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25807 | 120.89 | P12:230:UMZW:# 694 #: FT IN SD. FT-LP LINE FAULT
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26259 | 109.27 | P12:230:UMZW:# 694 #: FT IN SD. FT-LP LINE FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.27544 | 107.98 | P12:230:UMZW:# 694 #: FT IN SD. FT-LP LINE FAULT
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.27544 | 104.69 | P12:230:UMZW:# 694 #: FT IN SD. FT-LP LINE FAULT
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26071 | 101.25 | P12:230:UMZW:# 694 #: FT IN SD. FT-LP LINE FAULT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24911 | 118.76 | P12:230:WAPA:FTRANDALL-SIOUXCY:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25346 | 105.94 | P12:230:WAPA:FTRANDALL-SIOUXCY:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26605 | 104.53 | P12:230:WAPA:FTRANDALL-SIOUXCY:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26607 | 101.19 | P12:230:WAPA:FTRANDALL-SIOUXCY:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26261 | 102.87 | P12:230:WAPA:SIOUXCY-DENISON:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24605 | 117.66 | P12:230:WAPA:TWINCH-SIOUXCY:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25007 | 105.08 | P12:230:WAPA:TWINCH-SIOUXCY:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26278 | 103.62 | P12:230:WAPA:TWINCH-SIOUXCY:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26278 | 100.46 | P12:230:WAPA:TWINCH-SIOUXCY:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24516 | 115.6 | P12:230:WERE:SUMM-MWE_230::
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24976 | 104.35 | P12:230:XEL:AUTO-SINGLE:GRE-PANTHER4:HUC-MCLEOD4:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26245 | 103.07 | P12:230:XEL:AUTO-SINGLE:GRE-PANTHER4:HUC-MCLEOD4:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2498 | 104.47 | P12:230:XEL:AUTO-SINGLE:MNVLTAP4:GRE-PANTHER4:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24624 | 117.68 | P12:230:XEL:MNV-GRA-PTH
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25032 | 104.72 | P12:230:XEL:MNV-GRA-PTH
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26303 | 103.48 | P12:230:XEL:MNV-GRA-PTH
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25004 | 104.86 | P12:230:XEL-MH:AUTO-SINGLE:PEACEGARD5:GLENBOR4:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.93 | P12:345:AEPW:R.S.S.-7:COGENT7
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.61 | P12:345:AEPW:R.S.S.-7:COGENT7
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24579 | 117.79 | P12:345:ALTW:AUTO-SINGLE:ARNOLD3:MORGANV3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.246 | 118.12 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:ARNOLD3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25008 | 104.57 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:ARNOLD3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26274 | 103.03 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:ARNOLD3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24564 | 117.61 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:HCKRYCK3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24659 | 120.83 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:MITCHLCO3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25091 | 106.56 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:MITCHLCO3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26343 | 104.58 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:MITCHLCO3:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26342 | 101.69 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:MITCHLCO3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24658 | 118.48 | P12:345:ALTW:AUTO-SINGLE:HUNTLEY3:LEDYARD3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25032 | 104.83 | P12:345:ALTW:AUTO-SINGLE:HUNTLEY3:LEDYARD3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26342 | 103.67 | P12:345:ALTW:AUTO-SINGLE:HUNTLEY3:LEDYARD3:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26342 | 100.27 | P12:345:ALTW:AUTO-SINGLE:HUNTLEY3:LEDYARD3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25002 | 104.66 | P12:345:ALTW:AUTO-SINGLE:LAKEFLD3:HUNTLEY3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25003 | 104.45 | P12:345:ALTW-MEC:AUTO-SINGLE:ARNOLD3:TIFFIN3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24627 | 117.5 | P12:345:ALTW-MEC:AUTO-SINGLE:LAKEFLD3:OBRIEN3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2459 | 117.85 | P12:345:ALTW-MEC:AUTO-SINGLE:MORGANV3:TIFFIN3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24631 | 120.2 | P12:345:ATC:8E2:ASKING3:EAUCL3
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2505 | 107.71 | P12:345:ATC:8E2:ASKING3:EAUCL3
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26311 | 105.49 | P12:345:ATC:8E2:ASKING3:EAUCL3
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2631 | 102.12 | P12:345:ATC:8E2:ASKING3:EAUCL3
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24887 | 100.25 | P12:345:ATC:8E2:ASKING3:EAUCL3
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24638 | 120.69 | P12:345:ATC:8E2_GD:ASKING3:EAUCL3
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25059 | 107.87 | P12:345:ATC:8E2_GD:ASKING3:EAUCL3
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2632 | 105.93 | P12:345:ATC:8E2_GD:ASKING3:EAUCL3
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26318 | 102.48 | P12:345:ATC:8E2_GD:ASKING3:EAUCL3
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24895 | 100.59 | P12:345:ATC:8E2_GD:ASKING3:EAUCL3
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24611 | 119.01 | P12:345:ATC-XEL:8E5:ARPINB4:EAUCL3
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25025 | 106.27 | P12:345:ATC-XEL:8E5:ARPINB4:EAUCL3
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26288 | 104.36 | P12:345:ATC-XEL:8E5:ARPINB4:EAUCL3
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26287 | 101.15 | P12:345:ATC-XEL:8E5:ARPINB4:EAUCL3
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24619 | 119.37 | P12:345:ATC-XEL:8E5_GD:ARPINB4:EAUCL3
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25033 | 106.66 | P12:345:ATC-XEL:8E5_GD:ARPINB4:EAUCL3
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26297 | 104.68 | P12:345:ATC-XEL:8E5_GD:ARPINB4:EAUCL3
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26296 | 101.48 | P12:345:ATC-XEL:8E5_GD:ARPINB4:EAUCL3
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24608 | 118.76 | P12:345:ATC-XEL:W-13:NMAB3345:BRIGGSRD
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25019 | 105.79 | P12:345:ATC-XEL:W-13:NMAB3345:BRIGGSRD
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26284 | 104.01 | P12:345:ATC-XEL:W-13:NMAB3345:BRIGGSRD
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26279 | 100.68 | P12:345:ATC-XEL:W-13:NMAB3345:BRIGGSRD
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24876 | 102.9 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24876 | 102.9 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24506 | 115.85 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24876 | 102.76 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24494 | 114.89 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24881 | 102.18 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26154 | 101.27 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24975 | 102.4 | P12:345:MEC:AUTO-SINGLE:OBRIEN3:HIGHLND3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26244 | 101.12 | P12:345:MEC:AUTO-SINGLE:OBRIEN3:HIGHLND3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2464 | 118.6 | P12:345:MEC:AUTO-SINGLE:WEBSTER3:LEHIGH3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25045 | 104.57 | P12:345:MEC:AUTO-SINGLE:WEBSTER3:LEHIGH3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26322 | 103.28 | P12:345:MEC:AUTO-SINGLE:WEBSTER3:LEHIGH3:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26319 | 100.14 | P12:345:MEC:AUTO-SINGLE:WEBSTER3:LEHIGH3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24975 | 102.4 | P12:345:MEC:OBRIEN-HIGHLAND AND REACTOR
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24627 | 117.45 | P12:345:MEC:OBRIEN-LAKEFIELD + REACTOR
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24496 | 114.94 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24883 | 102.17 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2459 | 117.84 | P12:345:MEC:TIFFIN 9T1 SPS
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25003 | 104.42 | P12:345:MEC:TIFFIN 9T1 SPS
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2459 | 117.85 | P12:345:MEC:TIFFIN-ARNOLD
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25003 | 104.43 | P12:345:MEC:TIFFIN-ARNOLD
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2459 | 117.85 | P12:345:MEC-ITCM:TIFFIN 3 - MORGANV3:IA-EC
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25003 | 104.42 | P12:345:MEC-ITCM:TIFFIN 3 - MORGANV3:IA-EC
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24716 | 107.58 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2606 | 105.87 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26052 | 102.97 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24872 | 120.5 | P12:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2529 | 107.39 | P12:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26578 | 106.67 | P12:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26575 | 103.33 | P12:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25127 | 100.95 | P12:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24947 | 120.13 | P12:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25412 | 104.95 | P12:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26662 | 103.54 | P12:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2666 | 100.02 | P12:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24968 | 105.05 | P12:345:MPC:CENTER-PRAIRIE:CENTER 3:PRAIRIE3
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2624 | 104.08 | P12:345:MPC:CENTER-PRAIRIE:CENTER 3:PRAIRIE3
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24608 | 118.43 | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25029 | 107.79 | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26303 | 106.81 | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26303 | 103.62 | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.7 | P12:345:OKGE:BKBK1501NEW
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 117.01 | P12:345:OKGE:BKRBKR604
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.95 | P12:345:OKGE:BKRBKR604_2
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.73 | P12:345:OKGE:BKRBKR605
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.82 | P12:345:OKGE:BKRBKR608
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24872 | 120.5 | P12:345:OPPD-MEC:S3451-RAUN
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2529 | 107.39 | P12:345:OPPD-MEC:S3451-RAUN
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26578 | 106.67 | P12:345:OPPD-MEC:S3451-RAUN
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26575 | 103.33 | P12:345:OPPD-MEC:S3451-RAUN
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25127 | 100.95 | P12:345:OPPD-MEC:S3451-RAUN
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24608 | 118.41 | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25028 | 107.73 | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26302 | 106.81 | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24968 | 105.08 | P12:345:OTP:AUTO-SINGLE:CENTER3:CNTSHNT3:Z1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2624 | 103.95 | P12:345:OTP:AUTO-SINGLE:CENTER3:CNTSHNT3:Z1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24951 | 104.76 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26217 | 103.47 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24608 | 118.38 | P12:345:OTP:AUTO-SINGLE:JAMESTN3:CENTER3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25029 | 106.87 | P12:345:OTP:AUTO-SINGLE:JAMESTN3:CENTER3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26302 | 106.09 | P12:345:OTP:AUTO-SINGLE:JAMESTN3:CENTER3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24968 | 105.09 | P12:345:OTP:AUTO-SINGLE:PRAIRIE3:CNTSHNT3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2624 | 104.15 | P12:345:OTP:AUTO-SINGLE:PRAIRIE3:CNTSHNT3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24991 | 102.92 | P12:345:UMZ:# 5852 #: IN . PROPER N-1 (LINE) FOR 659101-659420-Z
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26259 | 101.37 | P12:345:UMZ:# 5852 #: IN . PROPER N-1 (LINE) FOR 659101-659420-Z
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25034 | 104.89 | P12:345:UMZ:# 5859 #: IN . PROPER N-1 (LINE) FOR 659160-659423-Z
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26305 | 103.49 | P12:345:UMZ:# 5859 #: IN . PROPER N-1 (LINE) FOR 659160-659423-Z
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26311 | 100.03 | P12:345:UMZ:# 5859 #: IN . PROPER N-1 (LINE) FOR 659160-659423-Z
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24726 | 118.4 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25103 | 107.47 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26366 | 106.64 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26367 | 103.39 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24907 | 100.09 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24955 | 104.92 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2622 | 103.61 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2622 | 100.4 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2487 | 122.93 | P12:345:UMZ:# 5865 #: IN . PROPER N-1 (LINE) FOR 652564-652864-Z
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25338 | 109.23 | P12:345:UMZ:# 5865 #: IN . PROPER N-1 (LINE) FOR 652564-652864-Z
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26585 | 107.59 | P12:345:UMZ:# 5865 #: IN . PROPER N-1 (LINE) FOR 652564-652864-Z
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26582 | 104.12 | P12:345:UMZ:# 5865 #: IN . PROPER N-1 (LINE) FOR 652564-652864-Z
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25168 | 101.59 | P12:345:UMZ:# 5865 #: IN . PROPER N-1 (LINE) FOR 652564-652864-Z
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2662 | 103.19 | P12:345:UMZ:# 5869 #: IN . PROPER N-1 (LINE) FOR 652529-652829-Z
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2141 | 100.62 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25034 | 104.89 | P12:345:UMZB:# 104 #: LOS GRT IN ND. LELAND OLDS-GROTON
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26305 | 103.49 | P12:345:UMZB:# 104 #: LOS GRT IN ND. LELAND OLDS-GROTON
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26311 | 100.03 | P12:345:UMZB:# 104 #: LOS GRT IN ND. LELAND OLDS-GROTON
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24991 | 102.92 | P12:345:UMZB:# 98 #: AVS BD IN ND. ANTELOPE VALLEY-BROADLAND
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26259 | 101.37 | P12:345:UMZB:# 98 #: AVS BD IN ND. ANTELOPE VALLEY-BROADLAND
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26259 | 101.35 | P12:345:UMZB:# 99 #: BD IN SD. BROADLAND-ANTELOPE VALLEY
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2662 | 103.19 | P12:345:UMZW:# 1682 #: WT2 IN SD. WT2-WHT LINE FAULT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2487 | 122.93 | P12:345:UMZW:# 851 #: SC2-SR IN IA. SC2-SR 345 KV LINE
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25338 | 109.23 | P12:345:UMZW:# 851 #: SC2-SR IN IA. SC2-SR 345 KV LINE
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26585 | 107.59 | P12:345:UMZW:# 851 #: SC2-SR IN IA. SC2-SR 345 KV LINE
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26582 | 104.12 | P12:345:UMZW:# 851 #: SC2-SR IN IA. SC2-SR 345 KV LINE
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25168 | 101.59 | P12:345:UMZW:# 851 #: SC2-SR IN IA. SC2-SR 345 KV LINE
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.69 | P12:345:WERE:FR2EAST-FR2WEST_345::
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24605 | 119.45 | P12:345:XEL:ASAK-ECL
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2502 | 106.89 | P12:345:XEL:ASAK-ECL
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26282 | 104.81 | P12:345:XEL:ASAK-ECL
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26281 | 101.68 | P12:345:XEL:ASAK-ECL
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24631 | 120.21 | P12:345:XEL:ASAK-ECL SPS
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2505 | 107.69 | P12:345:XEL:ASAK-ECL SPS
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26311 | 105.48 | P12:345:XEL:ASAK-ECL SPS
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2631 | 102.01 | P12:345:XEL:ASAK-ECL SPS
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24887 | 100.3 | P12:345:XEL:ASAK-ECL SPS
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24631 | 120.21 | P12:345:XEL:ASK-ECL SPS
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2505 | 107.69 | P12:345:XEL:ASK-ECL SPS
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26311 | 105.48 | P12:345:XEL:ASK-ECL SPS
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2631 | 102.02 | P12:345:XEL:ASK-ECL SPS
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24887 | 100.29 | P12:345:XEL:ASK-ECL SPS
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24625 | 118.52 | P12:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25054 | 105.28 | P12:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24602 | 119.35 | P12:345:XEL:AUTO-SINGLE:ASKING3:EAUCL3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25016 | 106.8 | P12:345:XEL:AUTO-SINGLE:ASKING3:EAUCL3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26277 | 104.76 | P12:345:XEL:AUTO-SINGLE:ASKING3:EAUCL3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24968 | 100.25 | P12:345:XEL:AUTO-SINGLE:FIELD_S3:CRANDAL3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24968 | 100.26 | P12:345:XEL:AUTO-SINGLE:FIELD_S3:FIELD_N3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24581 | 115.7 | P12:345:XEL:AUTO-SINGLE:HELENA3:SHEASLK3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24972 | 100.95 | P12:345:XEL:AUTO-SINGLE:HELENA3:SHEASLK3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24968 | 101.08 | P12:345:XEL:AUTO-SINGLE:LKFLDXL3:CRANDAL3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 117.14 | P12:345:XEL:AUTO-SINGLE:LKFLDXL3:TRIMONTWD3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.97 | P12:345:XEL:AUTO-SINGLE:LKFLDXL3:TRIMONTWD3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24588 | 118.63 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24996 | 105.96 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2626 | 104.28 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2458 | 117.7 | P12:345:XEL:AUTO-SINGLE:PRISLD3:NROC3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24993 | 104.43 | P12:345:XEL:AUTO-SINGLE:PRISLD3:NROC3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24968 | 100.27 | P12:345:XEL:AUTO-SINGLE:WILMART3:FIELD_N3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.82 | P12:345:XEL:AUTO-SINGLE:WILMART3:MEC-345:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2458 | 115.59 | P12:345:XEL:AUTO-SINGLE:WILMART3:SHEASLK3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24971 | 100.91 | P12:345:XEL:AUTO-SINGLE:WILMART3:SHEASLK3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 117.06 | P12:345:XEL:AUTO-SINGLE:WOADHILL3:CRANDAL3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.98 | P12:345:XEL:AUTO-SINGLE:WOADHILL3:CRANDAL3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24582 | 115.64 | P12:345:XEL:SPS HNA-SSL
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24973 | 101.49 | P12:345:XEL:SPS HNA-SSL
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24582 | 115.63 | P12:345:XEL:SPS WLM-SSL
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24973 | 101.49 | P12:345:XEL:SPS WLM-SSL
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24611 | 119.01 | P12:345:XEL-ALTE:AUTO-SINGLE:EAUCL3:ARPINB4:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25025 | 106.27 | P12:345:XEL-ALTE:AUTO-SINGLE:EAUCL3:ARPINB4:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26288 | 104.36 | P12:345:XEL-ALTE:AUTO-SINGLE:EAUCL3:ARPINB4:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24659 | 120.07 | P12:345:XEL-ALTW:AUTO-SINGLE:ADAMS3:MITCHLCO3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25091 | 106.35 | P12:345:XEL-ALTW:AUTO-SINGLE:ADAMS3:MITCHLCO3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26343 | 104.32 | P12:345:XEL-ALTW:AUTO-SINGLE:ADAMS3:MITCHLCO3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24748 | 121.05 | P12:345:XEL-ALTW:AUTO-SINGLE:NOBLES3:LAKEFLD3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2517 | 107.52 | P12:345:XEL-ALTW:AUTO-SINGLE:NOBLES3:LAKEFLD3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26433 | 106.03 | P12:345:XEL-ALTW:AUTO-SINGLE:NOBLES3:LAKEFLD3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24762 | 120.84 | P12:345:XEL-GRE-ITCM:LKFLDXL3 - CRANDAL 3:MN
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25138 | 100.92 | P12:345:XEL-GRE-ITCM:LKFLDXL3 - CRANDAL 3:MN
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2467 | 120.2 | P12:345:XEL-ITC:AMD-PVS & BKR 8S2
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25108 | 106.49 | P12:345:XEL-ITC:AMD-PVS & BKR 8S2
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26357 | 104.43 | P12:345:XEL-ITC:AMD-PVS & BKR 8S2
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26355 | 101.27 | P12:345:XEL-ITC:AMD-PVS & BKR 8S2
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24944 | 100.16 | P12:345:XEL-ITC:AMD-PVS & BKR 8S2
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2467 | 120.2 | P12:345:XEL-ITC:AMD-PVS-MTC AS
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25108 | 106.49 | P12:345:XEL-ITC:AMD-PVS-MTC AS
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26357 | 104.43 | P12:345:XEL-ITC:AMD-PVS-MTC AS
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26355 | 101.27 | P12:345:XEL-ITC:AMD-PVS-MTC AS
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24944 | 100.16 | P12:345:XEL-ITC:AMD-PVS-MTC AS
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24608 | 118.76 | P12:345:XEL-MGE:AUTO-SINGLE:BRIGGSRD3:NMAB5345:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25019 | 105.79 | P12:345:XEL-MGE:AUTO-SINGLE:BRIGGSRD3:NMAB5345:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26284 | 104.01 | P12:345:XEL-MGE:AUTO-SINGLE:BRIGGSRD3:NMAB5345:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24589 | 117.75 | P12:345:XEL-OTP:AUTO-SINGLE:BISON3:BUFFALO3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25004 | 106.05 | P12:345:XEL-OTP:AUTO-SINGLE:BISON3:BUFFALO3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26275 | 105.08 | P12:345:XEL-OTP:AUTO-SINGLE:BISON3:BUFFALO3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2504 | 104.46 | P12:345:XEL-OTP:AUTO-SINGLE:GRE-RIVRVRD3:ALEXMRES3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26312 | 103.16 | P12:345:XEL-OTP:AUTO-SINGLE:GRE-RIVRVRD3:ALEXMRES3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2487 | 123.07 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25338 | 109.26 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26585 | 107.62 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25168 | 101.63 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24672 | 122.12 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25119 | 111.03 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26367 | 109.48 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24952 | 102.24 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 117.14 | P12:345-34.5:XEL-IBERDROLA:TRIMONT-ELMCRK WIND
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.97 | P12:345-34.5:XEL-IBERDROLA:TRIMONT-ELMCRK WIND
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.42 | P12:345-34.5:XEL-IBERDROLA:TRIMONT-ELMCRK WIND
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26265 | 102.79 | P12:500:EES-EAI:ARK_NU:FTSMTH:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24567 | 117.57 | P12:500:MH:M602F
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26241 | 104.1 | P12:500:MH:M602F
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26241 | 101.02 | P12:500:MH:M602F
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25015 | 106.07 | P12:500:XEL:AUTO-SINGLE:CHISCO2:CHIS-N2:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26264 | 103.99 | P12:500:XEL:AUTO-SINGLE:CHISCO2:CHIS-N2:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25015 | 105.92 | P12:500:XEL:AUTO-SINGLE:FORBES2:CHIS-N2:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26264 | 103.93 | P12:500:XEL:AUTO-SINGLE:FORBES2:CHIS-N2:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24567 | 117.65 | P12:500:XEL:AUTO-SINGLE:FORBES2:ROSEAUS2:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26241 | 104.17 | P12:500:XEL:AUTO-SINGLE:FORBES2:ROSEAUS2:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24567 | 117.57 | P12:500:XEL:AUTO-SINGLE:ROSEAUN2:ROSEAUM2:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26241 | 104.1 | P12:500:XEL:AUTO-SINGLE:ROSEAUN2:ROSEAUM2:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24567 | 117.57 | P12:500:XEL:AUTO-SINGLE:ROSEAUS2:ROSEAUM2:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26241 | 104.1 | P12:500:XEL:AUTO-SINGLE:ROSEAUS2:ROSEAUM2:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24567 | 117.57 | P12:500:XEL-MH:AUTO-SINGLE:ROSEAUN2:RIEL2:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26241 | 104.1 | P12:500:XEL-MH:AUTO-SINGLE:ROSEAUN2:RIEL2:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.69 | P12:EHV:EES::8ANO%:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.68 | P12:EHV:EES::8ANO%:1(1)
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.6 | P12:HV:EES::TURK 4%:1(1)
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.44 | P12:LV-EHV:EES::MUSKOGE7!:MUSKOG5G:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.44 | P12:LV-EHV:EES::MUSKOGE7!:MUSKOG6G:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 104.17 | P13:014-115:GRIS:GSUPGS
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.76 | P13:014-115:GRIS:GSUPGS
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 102.48 | P13:115:MDU:HESKETT 2 GSU LOSS:HESKETT::1::::
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.59 | P13:115:MDU:HESKETT 3 GSU LOSS:HESKETT::1::::
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.5 | P13:115:MDU:LEWIS & CLARK GSU LOSS:LEWIS & CLARK::1::::
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 104.14 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.93 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.56 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.23 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.41 | P13:115-13:OTP:AUTO-SINGLE:HOOTLK7:HOOTLK3G:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26249 | 102.98 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.74 | P13:115-34:XEL:AUTO-SINGLE:NOBLES7:NOBLESCO18:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.73 | P13:115-34:XEL:AUTO-SINGLE:NOBLES7:NOBLESCO18:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.13 | P13:115-34:XEL:AUTO-SINGLE:NOBLES7:NOBLESCO18:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.73 | P13:115-34:XEL:AUTO-SINGLE:NOBLES7:NOBLESCO28:2
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.13 | P13:115-34:XEL:AUTO-SINGLE:NOBLES7:NOBLESCO28:2
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.22 | P13:115-34:XEL:AUTO-SINGLE:OAKLAKEW7:BUFRDG2B1:5
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.14 | P13:115-34:XEL:AUTO-SINGLE:OAKLAKEW7:BUFRDG2B1:5
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.22 | P13:115-34:XEL:AUTO-SINGLE:OAKLAKEW7:BUFRDG2B2:4
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.14 | P13:115-34:XEL:AUTO-SINGLE:OAKLAKEW7:BUFRDG2B2:4
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.41 | P13:115-34:XEL:AUTO-SINGLE:PROSEWIND7:PROSEB19:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.4 | P13:115-34:XEL:AUTO-SINGLE:PROSEWIND7:PROSEB19:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 101.81 | P13:115-34:XEL:AUTO-SINGLE:PROSEWIND7:PROSEB19:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.41 | P13:115-34:XEL:AUTO-SINGLE:PROSEWIND7:PROSEB29:2
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.4 | P13:115-34:XEL:AUTO-SINGLE:PROSEWIND7:PROSEB29:2
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 101.81 | P13:115-34:XEL:AUTO-SINGLE:PROSEWIND7:PROSEB29:2
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.21 | P13:115-34:XEL:AUTO-SINGLE:YANKEE7:YANKEEB2:2
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.15 | P13:115-34:XEL:AUTO-SINGLE:YANKEE7:YANKEEB2:2
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24546 | 117.37 | P13:115-345:NPPD:ANTELOPE:T1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24935 | 101.72 | P13:115-345:NPPD:ANTELOPE:T1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26236 | 100.52 | P13:115-345:NPPD:ANTELOPE:T1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24945 | 103.18 | P13:115-345:NPPD:NUCOR-2
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26212 | 101.85 | P13:115-345:NPPD:NUCOR-2
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26226 | 101.14 | P13:115-345:NPPD:THEDFRD3:T2
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 102.81 | P13:13-115:GRE-OTP:AUTO-SINGLE:GRE-SPRITWDG:SPIRITWD7:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.17 | P13:13-115:XEL:AUTO-SINGLE:BLKD72G:BLKDOG7:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.7 | P13:13-115:XEL:AUTO-SINGLE:HBRS73G:HIBRDGE7:9
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.21 | P13:13-115:XEL:AUTO-SINGLE:HBRS73G:HIBRDGE7:9
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.67 | P13:13-115:XEL:AUTO-SINGLE:LSPCTG:LSPOWER7:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.26 | P13:13-115:XEL:AUTO-SINGLE:LSPCTG:LSPOWER7:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.53 | P13:13-13-115:XEL:AUTO-SINGLE:ANS72G:ANS73G:ANSON7:2
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 101.86 | P13:13-13-115:XEL:AUTO-SINGLE:ANS72G:ANS73G:ANSON7:2
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.38 | P13:138-22:AEPW:R.S.S.-4
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.38 | P13:138-24:AEPW:R.S.S.-4
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.72 | P13:138-24:AEPW:TURK 4
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.6 | P13:138-24:AEPW:TURK 4
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.19 | P13:138-24:AEPW:TURK 4
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.87 | P13:15-115:XEL:AUTO-SINGLE:MEC-CT1:MEC-115:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.4 | P13:15-115:XEL:AUTO-SINGLE:MEC-CT1:MEC-115:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.57 | P13:16-115:XEL:AUTO-SINGLE:RIVRS77G:RIVRSID7:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.15 | P13:16-115:XEL:AUTO-SINGLE:RIVRS77G:RIVRSID7:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.33 | P13:161-22:AEPW:FLINTCR5
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 104.02 | P13:16-161:GRE:AUTO-SINGLE:GRE-PVS51G:GRE-PLVLLY5:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.58 | P13:16-161:GRE:AUTO-SINGLE:GRE-PVS51G:GRE-PLVLLY5:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 104.03 | P13:16-161:GRE:AUTO-SINGLE:GRE-PVS52G:GRE-PLVLLY5:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.58 | P13:16-161:GRE:AUTO-SINGLE:GRE-PVS52G:GRE-PLVLLY5:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.52 | P13:16-230:GRE:AUTO-SINGLE:GRE-ER14G:GRE-ELKRIV4:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.1 | P13:16-230:GRE:AUTO-SINGLE:GRE-ER14G:GRE-ELKRIV4:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 117.86 | P13:18-115:HAST::EGYCNTR7 XFMR G2:WEC 2 GSU
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 104.86 | P13:18-115:HAST::EGYCNTR7 XFMR G2:WEC 2 GSU
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 103.52 | P13:18-115:HAST::EGYCNTR7 XFMR G2:WEC 2 GSU
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 100.46 | P13:18-115:HAST::EGYCNTR7 XFMR G2:WEC 2 GSU
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.62 | P13:18-115:XEL:AUTO-SINGLE:BLKD75G:BLKDOG7:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.21 | P13:18-115:XEL:AUTO-SINGLE:BLKD75G:BLKDOG7:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.68 | P13:18-115:XEL:AUTO-SINGLE:COLVILL1G:CANONFLSG7:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.27 | P13:18-115:XEL:AUTO-SINGLE:COLVILL1G:CANONFLSG7:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.68 | P13:18-115:XEL:AUTO-SINGLE:COLVILLG:CANONFLSG7:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.27 | P13:18-115:XEL:AUTO-SINGLE:COLVILLG:CANONFLSG7:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.71 | P13:18-115:XEL:AUTO-SINGLE:FEPCTG:FARIBALTGEN:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.31 | P13:18-115:XEL:AUTO-SINGLE:FEPCTG:FARIBALTGEN:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.63 | P13:18-115:XEL:AUTO-SINGLE:HBRC71G:HIBRDGE7:7
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.22 | P13:18-115:XEL:AUTO-SINGLE:HBRC71G:HIBRDGE7:7
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.63 | P13:18-115:XEL:AUTO-SINGLE:HBRC72G:HIBRDGE7:8
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.22 | P13:18-115:XEL:AUTO-SINGLE:HBRC72G:HIBRDGE7:8
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.59 | P13:18-115:XEL:AUTO-SINGLE:RIVRSIDEG97:RIVRSID7:9
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.16 | P13:18-115:XEL:AUTO-SINGLE:RIVRSIDEG97:RIVRSID7:9
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.59 | P13:18-115:XEL:AUTO-SINGLE:RIVRSIDG107:RIVRSID7:10
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.16 | P13:18-115:XEL:AUTO-SINGLE:RIVRSIDG107:RIVRSID7:10
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.91 | P13:18-345:OPPD:NEBCTY1G
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.53 | P13:18-345:OPPD:NEBCTY1G
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.82 | P13:19-345:XEL:AUTO-SINGLE:MEC-ST:MEC-345:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.44 | P13:19-345:XEL:AUTO-SINGLE:MEC-ST:MEC-345:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 111.18 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.97 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.8 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 102.8 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 101.38 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 114.64 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 114.1 | P13:22-230:OTP:AUTO-SINGLE:CENTER1G:CENTER4:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 102.79 | P13:22-230:OTP:AUTO-SINGLE:CENTER1G:CENTER4:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.53 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.37 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 115.18 | P13:230:MDU:HETTINGER GSU & COLLECTOR LOSS:HETTINGER::1::::
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 115.64 | P13:230:MDU:TATANKA GSU & COLLECTOR LOSS:TATANKA::1::::
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.7 | P13:230:MDU:TATANKA GSU & COLLECTOR LOSS:TATANKA::1::::
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 115.18 | P13:230:MDU:THUNDER SPIRIT & G752-2 GSUS & COLLECTOR LOSS:HETTINGER::1::::
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 115.18 | P13:230:MDU:THUNDER SPIRIT GSU & COLLECTOR LOSS:HETTINGER::1::::
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24542 | 117.5 | P13:230:UMZW:# 2144 #: FP IN MT. LOSS OF TRANSFORMER (AT2).
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 104.42 | P13:230:UMZW:# 2144 #: FP IN MT. LOSS OF TRANSFORMER (AT2).
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.91 | P13:230:UMZW:# 2144 #: FP IN MT. LOSS OF TRANSFORMER (AT2).
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25057 | 104.8 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26341 | 103.35 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2634 | 100.27 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 115.46 | P13:230-34:OTP:AUTO-SINGLE:BARNES4:ASH19:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.77 | P13:230-34:OTP:AUTO-SINGLE:BARNES4:ASH19:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 115.83 | P13:230-34:OTP:AUTO-SINGLE:LUVERNE4:ASH29:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.23 | P13:230-34:OTP:AUTO-SINGLE:SIBLEY4:ASH39:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.01 | P13:230-34:XEL:AUTO-SINGLE:PEACEGARD5:PEACEGARD9:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24958 | 103.37 | P13:230-345:NPPD:NUCOR-1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26227 | 101.99 | P13:230-345:NPPD:NUCOR-1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24809 | 117.39 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25269 | 104.65 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26545 | 103.22 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 117.67 | P13:23-345:OPPD:NEBCTY2G
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.9 | P13:23-345:OPPD:NEBCTY2G
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.56 | P13:23-345:OPPD:NEBCTY2G
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 104.12 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.4 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 114.48 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 101.4 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 112.18 | P13:24-345:OTP:AUTO-SINGLE:COYOTE1G:COYOTE3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.58 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 108.48 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.71 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 115.6 | P13:34-115:OTP:AUTO-SINGLE:LNG19:LANGWIN7:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 101.18 | P13:34-161:ALTW:AUTO-SINGLE:G735_WF5:CRYSTLKII5:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 114.43 | P13:34-230:OTP:AUTO-SINGLE:RGBYCOL9:RGBYWND4:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24991 | 102.92 | P13:345:UMZB:# 233 #: BD IN SD. BROADLAND TX
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26259 | 101.38 | P13:345:UMZB:# 233 #: BD IN SD. BROADLAND TX
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 117.07 | P13:345-115:XEL:AUTO-SINGLE:WOADHILL3:WOADHILL7:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.98 | P13:345-115:XEL:AUTO-SINGLE:WOADHILL3:WOADHILL7:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.46 | P13:345-115:XEL:AUTO-SINGLE:WOADHILL3:WOADHILL7:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.99 | P13:345-13-13:GRE:AUTO-SINGLE:GRE-LKFDGEN3:GRE-LGS31G:GRE-LGS32G:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.48 | P13:345-13-13:GRE:AUTO-SINGLE:GRE-LKFDGEN3:GRE-LGS31G:GRE-LGS32G:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.99 | P13:345-13-13:GRE:AUTO-SINGLE:GRE-LKFDGEN3:GRE-LGS33G:GRE-LGS34G:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.47 | P13:345-13-13:GRE:AUTO-SINGLE:GRE-LKFDGEN3:GRE-LGS33G:GRE-LGS34G:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.99 | P13:345-13-13:GRE:AUTO-SINGLE:GRE-LKFDGEN3:GRE-LGS35G:GRE-LGS36G:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.48 | P13:345-13-13:GRE:AUTO-SINGLE:GRE-LKFDGEN3:GRE-LGS35G:GRE-LGS36G:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.38 | P13:345-22:AEPW:N.E.S.-7_#1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 117.36 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 105.52 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 104.51 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 101.28 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.3 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.14 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 101 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 117.59 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 105.72 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 104.7 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 101.53 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 117 | P13:345-34:XEL:AUTO-SINGLE:TRIMONTWD3:ELMCREEK2W8:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.88 | P13:345-34:XEL:AUTO-SINGLE:TRIMONTWD3:ELMCREEK2W8:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.37 | P13:345-34:XEL:AUTO-SINGLE:TRIMONTWD3:ELMCREEK2W8:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.83 | P13:500:EES-EAI:ARK_NU:T1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.69 | P13:500:EES-EAI:ARK_NU:T1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.28 | P13:500:EES-EAI:ARK_NU:T1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.86 | P13:500:EES-EAI:ARK_NU:T2
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.68 | P13:500:EES-EAI:ARK_NU:T2
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.3 | P13:500:EES-EAI:ARK_NU:T2
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24872 | 120.5 | P14:345:OPPD-MEC:S3451 REAC-1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2529 | 107.39 | P14:345:OPPD-MEC:S3451 REAC-1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26578 | 106.67 | P14:345:OPPD-MEC:S3451 REAC-1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26575 | 103.33 | P14:345:OPPD-MEC:S3451 REAC-1
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25127 | 100.95 | P14:345:OPPD-MEC:S3451 REAC-1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24579 | 117.79 | P21:345:ALTW:AUTO-SINGLE:ARNOLD3:MORGANV3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.246 | 118.12 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:ARNOLD3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25008 | 104.57 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:ARNOLD3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26274 | 103.03 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:ARNOLD3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24564 | 117.61 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:HCKRYCK3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24659 | 120.83 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:MITCHLCO3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25091 | 106.56 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:MITCHLCO3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26343 | 104.58 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:MITCHLCO3:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26342 | 101.69 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:MITCHLCO3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24658 | 118.48 | P21:345:ALTW:AUTO-SINGLE:HUNTLEY3:LEDYARD3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25032 | 104.83 | P21:345:ALTW:AUTO-SINGLE:HUNTLEY3:LEDYARD3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26342 | 103.67 | P21:345:ALTW:AUTO-SINGLE:HUNTLEY3:LEDYARD3:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26342 | 100.27 | P21:345:ALTW:AUTO-SINGLE:HUNTLEY3:LEDYARD3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25002 | 104.66 | P21:345:ALTW:AUTO-SINGLE:LAKEFLD3:HUNTLEY3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25003 | 104.45 | P21:345:ALTW-MEC:AUTO-SINGLE:ARNOLD3:TIFFIN3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24627 | 117.5 | P21:345:ALTW-MEC:AUTO-SINGLE:LAKEFLD3:OBRIEN3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2459 | 117.85 | P21:345:ALTW-MEC:AUTO-SINGLE:MORGANV3:TIFFIN3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24494 | 114.89 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24881 | 102.18 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26154 | 101.27 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24975 | 102.4 | P21:345:MEC:AUTO-SINGLE:OBRIEN3:HIGHLND3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26244 | 101.12 | P21:345:MEC:AUTO-SINGLE:OBRIEN3:HIGHLND3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2464 | 118.6 | P21:345:MEC:AUTO-SINGLE:WEBSTER3:LEHIGH3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25045 | 104.57 | P21:345:MEC:AUTO-SINGLE:WEBSTER3:LEHIGH3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26322 | 103.28 | P21:345:MEC:AUTO-SINGLE:WEBSTER3:LEHIGH3:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26319 | 100.14 | P21:345:MEC:AUTO-SINGLE:WEBSTER3:LEHIGH3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24716 | 107.58 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2606 | 105.87 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26052 | 102.97 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24872 | 120.5 | P21:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2529 | 107.39 | P21:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26578 | 106.67 | P21:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26575 | 103.33 | P21:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25127 | 100.95 | P21:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24947 | 120.13 | P21:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25412 | 104.95 | P21:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26662 | 103.54 | P21:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2666 | 100.02 | P21:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24608 | 118.41 | P21:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25028 | 107.73 | P21:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26302 | 106.81 | P21:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26303 | 103.62 | P21:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24968 | 105.08 | P21:345:OTP:AUTO-SINGLE:CENTER3:CNTSHNT3:Z1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2624 | 103.95 | P21:345:OTP:AUTO-SINGLE:CENTER3:CNTSHNT3:Z1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2624 | 100.88 | P21:345:OTP:AUTO-SINGLE:CENTER3:CNTSHNT3:Z1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24951 | 104.76 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26217 | 103.47 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26217 | 100.19 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24608 | 118.38 | P21:345:OTP:AUTO-SINGLE:JAMESTN3:CENTER3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25029 | 106.87 | P21:345:OTP:AUTO-SINGLE:JAMESTN3:CENTER3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26302 | 106.09 | P21:345:OTP:AUTO-SINGLE:JAMESTN3:CENTER3:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26303 | 102.96 | P21:345:OTP:AUTO-SINGLE:JAMESTN3:CENTER3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24968 | 105.09 | P21:345:OTP:AUTO-SINGLE:PRAIRIE3:CNTSHNT3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2624 | 104.15 | P21:345:OTP:AUTO-SINGLE:PRAIRIE3:CNTSHNT3:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2624 | 101.06 | P21:345:OTP:AUTO-SINGLE:PRAIRIE3:CNTSHNT3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24339 | 102.72 | P21:345:UMZW:# 323 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25578 | 101.25 | P21:345:UMZW:# 323 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24084 | 112.85 | P21:345:UMZW:# 325 #: GI IN NE. GI-MCCOOL LINE FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2662 | 103.15 | P21:345:UMZW:# 326 #: WT2 IN SD. OPENING OF A LINE SECTION WO A FAULT (WT2-WT2LNX3 LINE REACTOR)
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24379 | 105.04 | P21:345:UMZW:# 725 #: GI IN NE. GI-SWEET LINE FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26016 | 102.94 | P21:345:UMZW:# 725 #: GI IN NE. GI-SWEET LINE FAULT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24625 | 118.52 | P21:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25054 | 105.28 | P21:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26305 | 103.49 | P21:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26305 | 100.27 | P21:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24602 | 119.35 | P21:345:XEL:AUTO-SINGLE:ASKING3:EAUCL3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25016 | 106.8 | P21:345:XEL:AUTO-SINGLE:ASKING3:EAUCL3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26277 | 104.76 | P21:345:XEL:AUTO-SINGLE:ASKING3:EAUCL3:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26277 | 101.57 | P21:345:XEL:AUTO-SINGLE:ASKING3:EAUCL3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.262 | 101.11 | P21:345:XEL:AUTO-SINGLE:FIELD_S3:CRANDAL3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24968 | 100.25 | P21:345:XEL:AUTO-SINGLE:FIELD_S3:CRANDAL3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.262 | 101.17 | P21:345:XEL:AUTO-SINGLE:FIELD_S3:FIELD_N3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24968 | 100.26 | P21:345:XEL:AUTO-SINGLE:FIELD_S3:FIELD_N3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24581 | 115.7 | P21:345:XEL:AUTO-SINGLE:HELENA3:SHEASLK3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24972 | 100.95 | P21:345:XEL:AUTO-SINGLE:HELENA3:SHEASLK3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.262 | 101.39 | P21:345:XEL:AUTO-SINGLE:LKFLDXL3:CRANDAL3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24968 | 101.08 | P21:345:XEL:AUTO-SINGLE:LKFLDXL3:CRANDAL3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 117.14 | P21:345:XEL:AUTO-SINGLE:LKFLDXL3:TRIMONTWD3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.97 | P21:345:XEL:AUTO-SINGLE:LKFLDXL3:TRIMONTWD3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.42 | P21:345:XEL:AUTO-SINGLE:LKFLDXL3:TRIMONTWD3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26241 | 103.2 | P21:345:XEL:AUTO-SINGLE:LYONCO3:GRE-CEDARMT3:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26241 | 100.05 | P21:345:XEL:AUTO-SINGLE:LYONCO3:GRE-CEDARMT3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24588 | 118.63 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24996 | 105.96 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2626 | 104.28 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26259 | 100.82 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2458 | 117.7 | P21:345:XEL:AUTO-SINGLE:PRISLD3:NROC3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24993 | 104.43 | P21:345:XEL:AUTO-SINGLE:PRISLD3:NROC3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.262 | 101.15 | P21:345:XEL:AUTO-SINGLE:WILMART3:FIELD_N3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24968 | 100.27 | P21:345:XEL:AUTO-SINGLE:WILMART3:FIELD_N3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.82 | P21:345:XEL:AUTO-SINGLE:WILMART3:MEC-345:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.44 | P21:345:XEL:AUTO-SINGLE:WILMART3:MEC-345:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2458 | 115.59 | P21:345:XEL:AUTO-SINGLE:WILMART3:SHEASLK3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24971 | 100.91 | P21:345:XEL:AUTO-SINGLE:WILMART3:SHEASLK3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 117.06 | P21:345:XEL:AUTO-SINGLE:WOADHILL3:CRANDAL3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.98 | P21:345:XEL:AUTO-SINGLE:WOADHILL3:CRANDAL3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.46 | P21:345:XEL:AUTO-SINGLE:WOADHILL3:CRANDAL3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24611 | 119.01 | P21:345:XEL-ALTE:AUTO-SINGLE:EAUCL3:ARPINB4:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25025 | 106.27 | P21:345:XEL-ALTE:AUTO-SINGLE:EAUCL3:ARPINB4:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26288 | 104.36 | P21:345:XEL-ALTE:AUTO-SINGLE:EAUCL3:ARPINB4:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26287 | 101.15 | P21:345:XEL-ALTE:AUTO-SINGLE:EAUCL3:ARPINB4:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24659 | 120.07 | P21:345:XEL-ALTW:AUTO-SINGLE:ADAMS3:MITCHLCO3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25091 | 106.35 | P21:345:XEL-ALTW:AUTO-SINGLE:ADAMS3:MITCHLCO3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26343 | 104.32 | P21:345:XEL-ALTW:AUTO-SINGLE:ADAMS3:MITCHLCO3:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26342 | 101.19 | P21:345:XEL-ALTW:AUTO-SINGLE:ADAMS3:MITCHLCO3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24748 | 121.05 | P21:345:XEL-ALTW:AUTO-SINGLE:NOBLES3:LAKEFLD3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2517 | 107.52 | P21:345:XEL-ALTW:AUTO-SINGLE:NOBLES3:LAKEFLD3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26433 | 106.03 | P21:345:XEL-ALTW:AUTO-SINGLE:NOBLES3:LAKEFLD3:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26433 | 102.53 | P21:345:XEL-ALTW:AUTO-SINGLE:NOBLES3:LAKEFLD3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24608 | 118.76 | P21:345:XEL-MGE:AUTO-SINGLE:BRIGGSRD3:NMAB5345:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25019 | 105.79 | P21:345:XEL-MGE:AUTO-SINGLE:BRIGGSRD3:NMAB5345:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26284 | 104.01 | P21:345:XEL-MGE:AUTO-SINGLE:BRIGGSRD3:NMAB5345:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26279 | 100.68 | P21:345:XEL-MGE:AUTO-SINGLE:BRIGGSRD3:NMAB5345:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24589 | 117.75 | P21:345:XEL-OTP:AUTO-SINGLE:BISON3:BUFFALO3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25004 | 106.05 | P21:345:XEL-OTP:AUTO-SINGLE:BISON3:BUFFALO3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26275 | 105.08 | P21:345:XEL-OTP:AUTO-SINGLE:BISON3:BUFFALO3:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26276 | 101.92 | P21:345:XEL-OTP:AUTO-SINGLE:BISON3:BUFFALO3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2504 | 104.46 | P21:345:XEL-OTP:AUTO-SINGLE:GRE-RIVRVRD3:ALEXMRES3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26312 | 103.16 | P21:345:XEL-OTP:AUTO-SINGLE:GRE-RIVRVRD3:ALEXMRES3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2487 | 123.07 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25338 | 109.26 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26585 | 107.62 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26582 | 104.16 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25168 | 101.63 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24672 | 122.12 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25119 | 111.03 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26367 | 109.48 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26364 | 106.19 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24952 | 102.24 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24889 | 123.17 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25356 | 109.26 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26606 | 107.69 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26602 | 104.83 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25187 | 101.7 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25015 | 106.07 | P21:500:XEL:AUTO-SINGLE:CHISCO2:CHIS-N2:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26264 | 103.99 | P21:500:XEL:AUTO-SINGLE:CHISCO2:CHIS-N2:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26264 | 100.7 | P21:500:XEL:AUTO-SINGLE:CHISCO2:CHIS-N2:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25015 | 105.92 | P21:500:XEL:AUTO-SINGLE:FORBES2:CHIS-N2:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26264 | 103.93 | P21:500:XEL:AUTO-SINGLE:FORBES2:CHIS-N2:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26264 | 100.56 | P21:500:XEL:AUTO-SINGLE:FORBES2:CHIS-N2:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24567 | 117.65 | P21:500:XEL:AUTO-SINGLE:FORBES2:ROSEAUS2:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26241 | 104.17 | P21:500:XEL:AUTO-SINGLE:FORBES2:ROSEAUS2:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26241 | 101.01 | P21:500:XEL:AUTO-SINGLE:FORBES2:ROSEAUS2:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24567 | 117.57 | P21:500:XEL:AUTO-SINGLE:ROSEAUN2:ROSEAUM2:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26241 | 104.1 | P21:500:XEL:AUTO-SINGLE:ROSEAUN2:ROSEAUM2:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26241 | 101.02 | P21:500:XEL:AUTO-SINGLE:ROSEAUN2:ROSEAUM2:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24567 | 117.57 | P21:500:XEL:AUTO-SINGLE:ROSEAUS2:ROSEAUM2:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26241 | 104.1 | P21:500:XEL:AUTO-SINGLE:ROSEAUS2:ROSEAUM2:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26241 | 101.02 | P21:500:XEL:AUTO-SINGLE:ROSEAUS2:ROSEAUM2:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24567 | 117.57 | P21:500:XEL-MH:AUTO-SINGLE:ROSEAUN2:RIEL2:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26241 | 104.1 | P21:500:XEL-MH:AUTO-SINGLE:ROSEAUN2:RIEL2:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26241 | 101.02 | P21:500:XEL-MH:AUTO-SINGLE:ROSEAUN2:RIEL2:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24545 | 115.45 | P22:345:AMMO::OVERTON:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2459 | 117.85 | P22:345:MEC-ITCM:TIFFIN 3:IA-EC
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25003 | 104.42 | P22:345:MEC-ITCM:TIFFIN 3:IA-EC
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24872 | 120.5 | P22:345:OPPD:S3451-RAUN
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2529 | 107.39 | P22:345:OPPD:S3451-RAUN
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26578 | 106.67 | P22:345:OPPD:S3451-RAUN
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26575 | 103.33 | P22:345:OPPD:S3451-RAUN
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25127 | 100.95 | P22:345:OPPD:S3451-RAUN
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.91 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.53 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.91 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.45 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 117.67 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.9 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.56 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 117.88 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.96 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.49 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24631 | 120.21 | P22:345:XEL:345KV SEC 2 ECL SPS
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2505 | 107.69 | P22:345:XEL:345KV SEC 2 ECL SPS
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26311 | 105.48 | P22:345:XEL:345KV SEC 2 ECL SPS
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2631 | 102.01 | P22:345:XEL:345KV SEC 2 ECL SPS
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24887 | 100.3 | P22:345:XEL:345KV SEC 2 ECL SPS
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24689 | 121.06 | P22:345:XEL:ADAMS 3 N1:MN
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25136 | 106.81 | P22:345:XEL:ADAMS 3 N1:MN
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26379 | 104.83 | P22:345:XEL:ADAMS 3 N1:MN
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26378 | 101.57 | P22:345:XEL:ADAMS 3 N1:MN
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24971 | 100.8 | P22:345:XEL:ADAMS 3 N1:MN
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.62 | P23:161-345:KCPL:IATAN_R1-11::IATANU1-IATANT11
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.18 | P23:161-345:KCPL:IATAN_R1-11::IATANU1-IATANT11
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.79 | P23:345:AEPW:NES CB 3413B NBTB
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.41 | P23:345:AEPW:NES CB 3413B NBTB
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24938 | 103.81 | P23:345:AEPW:NES CB 3417B NBTB
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26204 | 102.42 | P23:345:AEPW:NES CB 3417B NBTB
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24941 | 103.93 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26207 | 102.6 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.93 | P23:345:AEPW:RIVERSIDE CB 3433A NBTB
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.61 | P23:345:AEPW:RIVERSIDE CB 3433A NBTB
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24659 | 120.01 | P23:345:ALTW:MITCHLCO:1130
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25091 | 106.3 | P23:345:ALTW:MITCHLCO:1130
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26343 | 104.3 | P23:345:ALTW:MITCHLCO:1130
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26342 | 101.17 | P23:345:ALTW:MITCHLCO:1130
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24659 | 119.93 | P23:345:ALTW:MITCHLCO:1140
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25091 | 106.28 | P23:345:ALTW:MITCHLCO:1140
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26343 | 104.28 | P23:345:ALTW:MITCHLCO:1140
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26342 | 101.05 | P23:345:ALTW:MITCHLCO:1140
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24659 | 120.28 | P23:345:ALTW:MITCHLCO:1150
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25091 | 106.31 | P23:345:ALTW:MITCHLCO:1150
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26343 | 104.39 | P23:345:ALTW:MITCHLCO:1150
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26342 | 101.16 | P23:345:ALTW:MITCHLCO:1150
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24659 | 120.54 | P23:345:ALTW:MITCHLCO:1160
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25091 | 106.44 | P23:345:ALTW:MITCHLCO:1160
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26343 | 104.48 | P23:345:ALTW:MITCHLCO:1160
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26342 | 101.53 | P23:345:ALTW:MITCHLCO:1160
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24618 | 119.33 | P23:345:ATC:ARPIN:424-S_GD
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25033 | 106.59 | P23:345:ATC:ARPIN:424-S_GD
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26296 | 104.61 | P23:345:ATC:ARPIN:424-S_GD
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26295 | 101.57 | P23:345:ATC:ARPIN:424-S_GD
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24608 | 118.77 | P23:345:ATC:NORTHMADISON:6033-S
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25019 | 105.8 | P23:345:ATC:NORTHMADISON:6033-S
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26284 | 104.01 | P23:345:ATC:NORTHMADISON:6033-S
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26279 | 100.68 | P23:345:ATC:NORTHMADISON:6033-S
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24609 | 118.8 | P23:345:ATC:NORTHMADISON:6037-S
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25019 | 105.81 | P23:345:ATC:NORTHMADISON:6037-S
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26284 | 104.02 | P23:345:ATC:NORTHMADISON:6037-S
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26279 | 100.62 | P23:345:ATC:NORTHMADISON:6037-S
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24522 | 114.93 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24909 | 102.42 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26194 | 101.4 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24542 | 115.41 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24951 | 102.94 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24864 | 102.99 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2467 | 120.2 | P23:345:GRE:PVS 19JB2
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2511 | 106.44 | P23:345:GRE:PVS 19JB2
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26358 | 104.37 | P23:345:GRE:PVS 19JB2
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26356 | 101.2 | P23:345:GRE:PVS 19JB2
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24945 | 100.06 | P23:345:GRE:PVS 19JB2
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2467 | 120.2 | P23:345:GRE:PVS 19JB3
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2511 | 106.44 | P23:345:GRE:PVS 19JB3
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26358 | 104.37 | P23:345:GRE:PVS 19JB3
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26356 | 101.2 | P23:345:GRE:PVS 19JB3
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24945 | 100.07 | P23:345:GRE:PVS 19JB3
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24666 | 121.05 | P23:345:ITCM:HAZLTON3 9985:IA-NE
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25096 | 106.83 | P23:345:ITCM:HAZLTON3 9985:IA-NE
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26352 | 104.9 | P23:345:ITCM:HAZLTON3 9985:IA-NE
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26345 | 101.92 | P23:345:ITCM:HAZLTON3 9985:IA-NE
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24932 | 100.04 | P23:345:ITCM:HAZLTON3 9985:IA-NE
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24567 | 117.67 | P23:345:ITCM:HCKRYCK:5267-PRESENT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24567 | 117.67 | P23:345:ITCM:HCKRYCK:5268-PRESENT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24567 | 117.65 | P23:345:ITCM:HCKRYCK:5269-PRESENT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24564 | 117.61 | P23:345:ITCM:HCKRYCK:FUT1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24567 | 117.67 | P23:345:ITCM:HCKRYCK3 5267-5268-5269:IA-MVP
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24509 | 114.67 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.249 | 101.98 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26172 | 101.07 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24939 | 103.51 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2621 | 102.12 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24924 | 103.3 | P23:345:KCPL-WERE:LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26193 | 101.98 | P23:345:KCPL-WERE:LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24544 | 112.33 | P23:345:MDU::COYOTE::5707-5712-5715::::
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24566 | 118.33 | P23:345:MEC:BLACK HAWK 901
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26235 | 103.49 | P23:345:MEC:BLACK HAWK 901
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26235 | 100.37 | P23:345:MEC:BLACK HAWK 901
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24496 | 114.94 | P23:345:MEC:BONDURANT 906
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24883 | 102.17 | P23:345:MEC:BONDURANT 906
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26156 | 101.27 | P23:345:MEC:BONDURANT 906
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24544 | 117.51 | P23:345:MEC:CBEC 905
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24944 | 105.58 | P23:345:MEC:CBEC 905
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2621 | 104.56 | P23:345:MEC:CBEC 905
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26209 | 101.41 | P23:345:MEC:CBEC 905
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 117.35 | P23:345:MEC:CBEC 908
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 105.51 | P23:345:MEC:CBEC 908
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 104.47 | P23:345:MEC:CBEC 908
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26205 | 101.27 | P23:345:MEC:CBEC 908
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24496 | 114.94 | P23:345:MEC:GDMEC 901
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24883 | 102.38 | P23:345:MEC:GDMEC 901
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26156 | 101.51 | P23:345:MEC:GDMEC 901
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24496 | 114.94 | P23:345:MEC:GDMEC 902
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24883 | 102.39 | P23:345:MEC:GDMEC 902
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26156 | 101.51 | P23:345:MEC:GDMEC 902
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24975 | 102.4 | P23:345:MEC:HIGHLAND 902
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26244 | 101.1 | P23:345:MEC:HIGHLAND 902
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24975 | 102.4 | P23:345:MEC:HIGHLAND 903
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26244 | 101.1 | P23:345:MEC:HIGHLAND 903
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 115.23 | P23:345:MEC:HIGHLAND 906
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 102.7 | P23:345:MEC:HIGHLAND 906
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 101.32 | P23:345:MEC:HIGHLAND 906
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24584 | 117.54 | P23:345:MEC:HILLS 984
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2464 | 118.61 | P23:345:MEC:LEHIGH 0350
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25045 | 104.57 | P23:345:MEC:LEHIGH 0350
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26322 | 103.28 | P23:345:MEC:LEHIGH 0350
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26319 | 100.14 | P23:345:MEC:LEHIGH 0350
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24937 | 103.19 | P23:345:MEC:LOUISA 954
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26204 | 102.07 | P23:345:MEC:LOUISA 954
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24978 | 103.21 | P23:345:MEC:LOUISA 964
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26249 | 102.15 | P23:345:MEC:LOUISA 964
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24494 | 114.89 | P23:345:MEC:MONTEZUMA 901
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24881 | 102.18 | P23:345:MEC:MONTEZUMA 901
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26154 | 101.27 | P23:345:MEC:MONTEZUMA 901
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24509 | 114.72 | P23:345:MEC:MONTEZUMA 903
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.249 | 102.05 | P23:345:MEC:MONTEZUMA 903
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26172 | 101.15 | P23:345:MEC:MONTEZUMA 903
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24595 | 118.04 | P23:345:MEC:MORGANV FUT1:IA-EC
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24595 | 118.04 | P23:345:MEC:MORGANV FUT2:IA-EC
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26208 | 100.88 | P23:345:MEC:RAUN 0210
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24939 | 124.12 | P23:345:MEC:RAUN 0270
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25353 | 116.27 | P23:345:MEC:RAUN 0270
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26698 | 115.05 | P23:345:MEC:RAUN 0270
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26683 | 112.12 | P23:345:MEC:RAUN 0270
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2517 | 108.94 | P23:345:MEC:RAUN 0270
Thermal | 15ALL | 2 | 24WP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2631 | 101.08 | P23:345:MEC:RAUN 0270
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24495 | 114.91 | P23:345:MEC:SYCAMORE 901
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24882 | 102.14 | P23:345:MEC:SYCAMORE 901
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26155 | 101.24 | P23:345:MEC:SYCAMORE 901
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24495 | 114.92 | P23:345:MEC:SYCAMORE 902
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24882 | 102.14 | P23:345:MEC:SYCAMORE 902
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26155 | 101.24 | P23:345:MEC:SYCAMORE 902
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2459 | 117.85 | P23:345:MEC:TIFFIN 944
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25003 | 104.43 | P23:345:MEC:TIFFIN 944
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24592 | 117.88 | P23:345:MEC:TIFFIN 954
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25008 | 104.39 | P23:345:MEC:TIFFIN 954
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24669 | 119.71 | P23:345:MEC:WEBSTER 901
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25071 | 105.88 | P23:345:MEC:WEBSTER 901
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26355 | 104.87 | P23:345:MEC:WEBSTER 901
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26353 | 101.37 | P23:345:MEC:WEBSTER 901
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2464 | 118.59 | P23:345:MEC:WEBSTER 905
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25045 | 104.57 | P23:345:MEC:WEBSTER 905
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26322 | 103.24 | P23:345:MEC:WEBSTER 905
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26319 | 100.13 | P23:345:MEC:WEBSTER 905
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2464 | 118.2 | P23:345:MPC:BISON 3:6720
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25069 | 106.85 | P23:345:MPC:BISON 3:6720
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26344 | 105.79 | P23:345:MPC:BISON 3:6720
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26345 | 102.69 | P23:345:MPC:BISON 3:6720
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24971 | 105.06 | P23:345:MPC:CENTER 3:8810
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26244 | 104.09 | P23:345:MPC:CENTER 3:8810
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26244 | 101.06 | P23:345:MPC:CENTER 3:8810
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24971 | 105.05 | P23:345:MPC:CENTER 3:8820
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26244 | 104.11 | P23:345:MPC:CENTER 3:8820
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26244 | 101.06 | P23:345:MPC:CENTER 3:8820
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24968 | 105.05 | P23:345:MPC:PRAIRIE3:4440
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2624 | 104.08 | P23:345:MPC:PRAIRIE3:4440
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2624 | 100.95 | P23:345:MPC:PRAIRIE3:4440
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24968 | 105.04 | P23:345:MPC:PRAIRIE3:4450
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2624 | 104.07 | P23:345:MPC:PRAIRIE3:4450
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2624 | 100.95 | P23:345:MPC:PRAIRIE3:4450
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24968 | 105.09 | P23:345:MPC:PRAIRIE3:4470
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2624 | 104.15 | P23:345:MPC:PRAIRIE3:4470
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2624 | 101.06 | P23:345:MPC:PRAIRIE3:4470
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24638 | 117.56 | P23:345:MRES:ALEXMRES3:3385:FUTURE
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25063 | 105.19 | P23:345:MRES:ALEXMRES3:3385:FUTURE
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26336 | 103.97 | P23:345:MRES:ALEXMRES3:3385:FUTURE
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26337 | 100.58 | P23:345:MRES:ALEXMRES3:3385:FUTURE
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24872 | 120.5 | P23:345:OPPD:S3451-RAUN
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2529 | 107.39 | P23:345:OPPD:S3451-RAUN
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26578 | 106.67 | P23:345:OPPD:S3451-RAUN
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26575 | 103.33 | P23:345:OPPD:S3451-RAUN
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25127 | 100.95 | P23:345:OPPD:S3451-RAUN
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24873 | 120.45 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25291 | 107.39 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2658 | 106.66 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26576 | 103.32 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25128 | 100.96 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.91 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.53 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.91 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.45 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 117.67 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.9 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.56 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 117.88 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.96 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.49 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24592 | 117.84 | P23:345:OTP:BUFFALO3:3615:V2016
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25007 | 106.3 | P23:345:OTP:BUFFALO3:3615:V2016
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26279 | 105.5 | P23:345:OTP:BUFFALO3:3615:V2016
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26279 | 102.29 | P23:345:OTP:BUFFALO3:3615:V2016
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24608 | 118.41 | P23:345:OTP:BUFFALO3:3655:V2016
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25029 | 107.73 | P23:345:OTP:BUFFALO3:3655:V2016
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26302 | 106.81 | P23:345:OTP:BUFFALO3:3655:V2016
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26303 | 103.64 | P23:345:OTP:BUFFALO3:3655:V2016
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2455 | 112.48 | P23:345:OTP:CENTER 3:3215
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2455 | 112.48 | P23:345:OTP:CENTER 3:3215(1)
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2455 | 112.48 | P23:345:OTP:CENTER 3:3225
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2455 | 112.48 | P23:345:OTP:CENTER 3:3225(1)
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24609 | 118.39 | P23:345:OTP:CENTER 3:3235
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2503 | 106.91 | P23:345:OTP:CENTER 3:3235
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26304 | 106.23 | P23:345:OTP:CENTER 3:3235
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26305 | 102.85 | P23:345:OTP:CENTER 3:3235
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24609 | 118.42 | P23:345:OTP:CENTER 3:3245
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2503 | 106.92 | P23:345:OTP:CENTER 3:3245
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26304 | 106.23 | P23:345:OTP:CENTER 3:3245
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26305 | 102.85 | P23:345:OTP:CENTER 3:3245
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24608 | 118.38 | P23:345:OTP:JAMESTN3:3115:V2020
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25029 | 106.88 | P23:345:OTP:JAMESTN3:3115:V2020
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26302 | 106.1 | P23:345:OTP:JAMESTN3:3115:V2020
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26303 | 102.97 | P23:345:OTP:JAMESTN3:3115:V2020
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24608 | 118.38 | P23:345:OTP:JAMESTN3:3125:V2020
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25029 | 106.88 | P23:345:OTP:JAMESTN3:3125:V2020
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26302 | 106.1 | P23:345:OTP:JAMESTN3:3125:V2020
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26303 | 102.97 | P23:345:OTP:JAMESTN3:3125:V2020
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24608 | 118.49 | P23:345:OTP:JAMESTN3:3135:V2020
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25028 | 107.73 | P23:345:OTP:JAMESTN3:3135:V2020
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26302 | 106.81 | P23:345:OTP:JAMESTN3:3135:V2020
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26303 | 103.59 | P23:345:OTP:JAMESTN3:3135:V2020
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24608 | 118.49 | P23:345:OTP:JAMESTN3:3145:V2020
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25028 | 107.72 | P23:345:OTP:JAMESTN3:3145:V2020
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26302 | 106.8 | P23:345:OTP:JAMESTN3:3145:V2020
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26303 | 103.6 | P23:345:OTP:JAMESTN3:3145:V2020
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25928 | 101.19 | P23:345:SUNC:MO_BRK188
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25928 | 101.19 | P23:345:SUNC:MO_BRK388
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25085 | 104.82 | P23:345:UMZB:# 102 #: GRT IN SD. BREAKER FAULT (8392)
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26353 | 103.54 | P23:345:UMZB:# 102 #: GRT IN SD. BREAKER FAULT (8392)
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26352 | 100.52 | P23:345:UMZB:# 102 #: GRT IN SD. BREAKER FAULT (8392)
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2662 | 103.2 | P23:345:UMZW:# 824 #: WH IN SD.
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25377 | 105.62 | P23:345:UMZW:# 844 #: WT2 IN SD. BREAKER FAULT (7296)
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26645 | 104.63 | P23:345:UMZW:# 844 #: WT2 IN SD. BREAKER FAULT (7296)
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26642 | 101.46 | P23:345:UMZW:# 844 #: WT2 IN SD. BREAKER FAULT (7296)
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25377 | 105.58 | P23:345:UMZW:# 845 #: WT2 IN SD. BREAKER FAULT (7192)
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26645 | 104.59 | P23:345:UMZW:# 845 #: WT2 IN SD. BREAKER FAULT (7192)
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26642 | 101.39 | P23:345:UMZW:# 845 #: WT2 IN SD. BREAKER FAULT (7192)
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25062 | 123.77 | P23:345:UMZW:# 853 #: SC2 IN IA. SC2 345 KV BREAKER FAILURE
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25557 | 109.07 | P23:345:UMZW:# 853 #: SC2 IN IA. SC2 345 KV BREAKER FAILURE
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26798 | 107.3 | P23:345:UMZW:# 853 #: SC2 IN IA. SC2 345 KV BREAKER FAILURE
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26795 | 103.7 | P23:345:UMZW:# 853 #: SC2 IN IA. SC2 345 KV BREAKER FAILURE
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25388 | 101.47 | P23:345:UMZW:# 853 #: SC2 IN IA. SC2 345 KV BREAKER FAILURE
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25062 | 123.77 | P23:345:WAPA:SIOUXCY:8592-8696
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25557 | 109.07 | P23:345:WAPA:SIOUXCY:8592-8696
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26798 | 107.3 | P23:345:WAPA:SIOUXCY:8592-8696
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26795 | 103.7 | P23:345:WAPA:SIOUXCY:8592-8696
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25388 | 101.47 | P23:345:WAPA:SIOUXCY:8592-8696
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25062 | 123.77 | P23:345:WAPA:SIOUXCY:8692
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25557 | 109 | P23:345:WAPA:SIOUXCY:8692
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26798 | 107.25 | P23:345:WAPA:SIOUXCY:8692
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26795 | 103.71 | P23:345:WAPA:SIOUXCY:8692
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25388 | 101.42 | P23:345:WAPA:SIOUXCY:8692
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.58 | P23:345:WERE:JEC_345-15::
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.2 | P23:345:WERE:JEC_345-15::
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24949 | 103.47 | P23:345:WERE:JEC_345-16::
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26225 | 101.99 | P23:345:WERE:JEC_345-16::
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.58 | P23:345:WERE:JEC_345-19::
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.2 | P23:345:WERE:JEC_345-19::
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.57 | P23:345:WERE:JEC_345-20::
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.2 | P23:345:WERE:JEC_345-20::
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24746 | 122.38 | P23:345:XEL:192 BKR SPK AS
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.252 | 111.23 | P23:345:XEL:192 BKR SPK AS
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26448 | 109.55 | P23:345:XEL:192 BKR SPK AS
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26444 | 106.23 | P23:345:XEL:192 BKR SPK AS
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25032 | 102.54 | P23:345:XEL:192 BKR SPK AS
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24749 | 122.37 | P23:345:XEL:196 BKR SPK AS
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25203 | 111.24 | P23:345:XEL:196 BKR SPK AS
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26451 | 109.55 | P23:345:XEL:196 BKR SPK AS
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26448 | 106.23 | P23:345:XEL:196 BKR SPK AS
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25036 | 102.56 | P23:345:XEL:196 BKR SPK AS
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2523 | 125.43 | P23:345:XEL:396 BKR SPK
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25742 | 111.86 | P23:345:XEL:396 BKR SPK
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26982 | 109.97 | P23:345:XEL:396 BKR SPK
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26979 | 106.1 | P23:345:XEL:396 BKR SPK
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25571 | 104.37 | P23:345:XEL:396 BKR SPK
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24886 | 122.87 | P23:345:XEL:492 BKR SPK AS
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25353 | 109.07 | P23:345:XEL:492 BKR SPK AS
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26601 | 107.41 | P23:345:XEL:492 BKR SPK AS
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25183 | 101.47 | P23:345:XEL:492 BKR SPK AS
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24614 | 119.16 | P23:345:XEL:8E5 ECL BS
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25028 | 106.48 | P23:345:XEL:8E5 ECL BS
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26291 | 104.4 | P23:345:XEL:8E5 ECL BS
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2629 | 101.31 | P23:345:XEL:8E5 ECL BS
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24542 | 116.82 | P23:345:XEL:8N17 SHC
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24942 | 103.63 | P23:345:XEL:8N17 SHC
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24543 | 108.46 | P23:345:XEL:8N22 SHC
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24544 | 116.49 | P23:345:XEL:8N28 SHC
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24543 | 116.17 | P23:345:XEL:8N8 MNN
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24944 | 103.15 | P23:345:XEL:8N8 MNN
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24541 | 117 | P23:345:XEL:8P1 KING
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 104.05 | P23:345:XEL:8P1 KING
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.97 | P23:345:XEL:8P2 KING
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24943 | 103.65 | P23:345:XEL:8P2 KING
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24634 | 120.29 | P23:345:XEL:8P5 KING
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25054 | 107.72 | P23:345:XEL:8P5 KING
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26315 | 105.48 | P23:345:XEL:8P5 KING
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26314 | 102.03 | P23:345:XEL:8P5 KING
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2489 | 100.39 | P23:345:XEL:8P5 KING
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24633 | 120.22 | P23:345:XEL:8P6 KING
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25055 | 107.79 | P23:345:XEL:8P6 KING
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26315 | 105.52 | P23:345:XEL:8P6 KING
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26314 | 102.04 | P23:345:XEL:8P6 KING
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24891 | 100.26 | P23:345:XEL:8P6 KING
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.262 | 101.14 | P23:345:XEL:8S22 WLM
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24969 | 100.27 | P23:345:XEL:8S22 WLM
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.262 | 101.46 | P23:345:XEL:8S23 WLM
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24968 | 100.34 | P23:345:XEL:8S23 WLM
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.82 | P23:345:XEL:8S24 WLM AS
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.43 | P23:345:XEL:8S24 WLM AS
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24583 | 115.55 | P23:345:XEL:8S25 WLM AS
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24973 | 101.38 | P23:345:XEL:8S25 WLM AS
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24583 | 115.54 | P23:345:XEL:8S27 WLM AS
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24973 | 101.38 | P23:345:XEL:8S27 WLM AS
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 117.13 | P23:345:XEL:8S31 LFD
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25007 | 101.62 | P23:345:XEL:8S72 HNA
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26299 | 100.17 | P23:345:XEL:8S72 HNA
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24582 | 115.64 | P23:345:XEL:8S81 SSL
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24973 | 100.86 | P23:345:XEL:8S81 SSL
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24582 | 115.64 | P23:345:XEL:8S82 & 8S79 SSL
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24973 | 100.87 | P23:345:XEL:8S82 & 8S79 SSL
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24582 | 115.64 | P23:345:XEL:8S82 SSL
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24973 | 100.87 | P23:345:XEL:8S82 SSL
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24642 | 118 | P23:345:XEL:8S97 NRH
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24625 | 118.02 | P23:345:XEL:8S98 NRH
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24748 | 121.12 | P23:345:XEL:8X24 NOB
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2517 | 107.58 | P23:345:XEL:8X24 NOB
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26433 | 106.07 | P23:345:XEL:8X24 NOB
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26433 | 102.5 | P23:345:XEL:8X24 NOB
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24748 | 121.13 | P23:345:XEL:8X25 NOB
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2517 | 107.58 | P23:345:XEL:8X25 NOB
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26433 | 106.07 | P23:345:XEL:8X25 NOB
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26433 | 102.5 | P23:345:XEL:8X25 NOB
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24612 | 118.98 | P23:345:XEL:ARPIN:ARP_424-S
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25025 | 106.3 | P23:345:XEL:ARPIN:ARP_424-S
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26288 | 104.2 | P23:345:XEL:ARPIN:ARP_424-S
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26287 | 101.11 | P23:345:XEL:ARPIN:ARP_424-S
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25008 | 102.23 | P23:345:XEL:SPS 8S72 HNA
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24582 | 115.64 | P23:345:XEL:SPS 8S81 SSL
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24973 | 101.49 | P23:345:XEL:SPS 8S81 SSL
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24626 | 118 | P23:345:XEL-SMMPA:8H8 PRI AS
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24626 | 118.1 | P23:345:XEL-SMMPA:8H9 PRI AS
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26265 | 102.79 | P23:500:EES-EAI:ARK_NU:B5106
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24966 | 102.92 | P23:500:EES-EAI:KEO:B4921
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26236 | 101.43 | P23:500:EES-EAI:KEO:B4921
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2497 | 102.83 | P23:500:EES-EAI:KEO:B4941
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26241 | 101.33 | P23:500:EES-EAI:KEO:B4941
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24749 | 121.05 | P24:161-345:ITCM:LAKEFLD 8160 T1:MN
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2517 | 107.5 | P24:161-345:ITCM:LAKEFLD 8160 T1:MN
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26434 | 106 | P24:161-345:ITCM:LAKEFLD 8160 T1:MN
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26434 | 102.45 | P24:161-345:ITCM:LAKEFLD 8160 T1:MN
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24777 | 121.09 | P24:345:ITCM:LAKEFLD 885 FUT:MN
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25313 | 109.59 | P24:345:ITCM:LAKEFLD 885 FUT:MN
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26473 | 106.22 | P24:345:ITCM:LAKEFLD 885 FUT:MN
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26473 | 102.54 | P24:345:ITCM:LAKEFLD 885 FUT:MN
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25144 | 101.19 | P24:345:ITCM:LAKEFLD 885 FUT:MN
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24631 | 120.2 | P24:345:XEL:8E7 ECL BS
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2505 | 107.69 | P24:345:XEL:8E7 ECL BS
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26311 | 105.46 | P24:345:XEL:8E7 ECL BS
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2631 | 102.01 | P24:345:XEL:8E7 ECL BS
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24887 | 100.26 | P24:345:XEL:8E7 ECL BS
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24631 | 120.2 | P24:345:XEL:8E7 ECL BS SPS
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2505 | 107.69 | P24:345:XEL:8E7 ECL BS SPS
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26311 | 105.46 | P24:345:XEL:8E7 ECL BS SPS
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2631 | 102.01 | P24:345:XEL:8E7 ECL BS SPS
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24887 | 100.26 | P24:345:XEL:8E7 ECL BS SPS
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25019 | 106.23 | P24:500:MP:FBS:601LX
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26265 | 104.03 | P24:500:MP:FBS:601LX
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.79 | P41:345:AEPW:NES CB 3413B NBTB+FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.41 | P41:345:AEPW:NES CB 3413B NBTB+FAULT
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24938 | 103.81 | P41:345:AEPW:NES CB 3417B NBTB+FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26204 | 102.42 | P41:345:AEPW:NES CB 3417B NBTB+FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 101.99 | P41:345:OKGE:SB_MUGE7384
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26237 | 101.83 | P41:345:OKGE:SB_MUGE7385
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.15 | P41:345:OKGE:SB_REUD7381
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.15 | P41:345:OKGE:SB_REUD7383
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.51 | P41:345:OKGE:SB_SEOL7382
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.12 | P41:345:OKGE:SB_SEOL7382
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.52 | P41:345:OKGE:SB_SEOL7383
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26205 | 102.12 | P41:345:OKGE:SB_SEOL7383
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.75 | P41:345:OKGE:SB_SOER7382
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.58 | P41:345:OKGE:SB_SOER7382
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.19 | P41:345:OKGE:SB_SOER7382
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24941 | 103.93 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26207 | 102.6 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 103.93 | P42:345:AEPW:RIVERSIDE CB 3433A NBTB+FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.61 | P42:345:AEPW:RIVERSIDE CB 3433A NBTB+FAULT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24664 | 118.54 | P42:345:ITCM:HUNTLEY3-LAKEFLD3 3651-3654:IA-MVP
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25034 | 104.89 | P42:345:ITCM:HUNTLEY3-LAKEFLD3 3651-3654:IA-MVP
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2635 | 103.75 | P42:345:ITCM:HUNTLEY3-LAKEFLD3 3651-3654:IA-MVP
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2635 | 100.31 | P42:345:ITCM:HUNTLEY3-LAKEFLD3 3651-3654:IA-MVP
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2457 | 117.89 | P42:345:ITCM:KILLDEER3-COLBY3 3821-3822:IA-MVP
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2624 | 103.43 | P42:345:ITCM:KILLDEER3-COLBY3 3821-3822:IA-MVP
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26239 | 100.31 | P42:345:ITCM:KILLDEER3-COLBY3 3821-3822:IA-MVP
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24645 | 118.17 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25017 | 104.44 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26329 | 103.45 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26328 | 100.06 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24323 | 115.85 | P42:345:NPPD:BKR-AXT-3302
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24803 | 102.64 | P42:345:NPPD:BKR-AXT-3302
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25995 | 100.74 | P42:345:NPPD:BKR-AXT-3302
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24409 | 115.87 | P42:345:NPPD:BKR-AXT-3308
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24842 | 102.45 | P42:345:NPPD:BKR-AXT-3308
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26085 | 100.53 | P42:345:NPPD:BKR-AXT-3308
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24596 | 115.9 | P42:345:NPPD:BKR-CPR-3304
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2495 | 102.74 | P42:345:NPPD:BKR-CPR-3304
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.23697 | 113.99 | P42:345:NPPD:BKR-GGS-3310
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24877 | 104.47 | P42:345:NPPD:BKR-GGS-3310
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25224 | 103.76 | P42:345:NPPD:BKR-GGS-3310
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25231 | 100.43 | P42:345:NPPD:BKR-GGS-3310
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26172 | 102.81 | P42:345:NPPD:BKR-GGS-3316
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26071 | 101.26 | P42:345:NPPD:BKR-GGS-3322
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2363 | 111.24 | P42:345:NPPD:BKR-HOS-3308
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.23531 | 100.83 | P42:345:NPPD:BKR-HOS-3308
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25299 | 100.07 | P42:345:NPPD:BKR-HOS-3308
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24724 | 107.21 | P42:345:NPPD:BKR-HOS-3310
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26081 | 105.48 | P42:345:NPPD:BKR-HOS-3310
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26071 | 102.62 | P42:345:NPPD:BKR-HOS-3310
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24717 | 106.92 | P42:345:NPPD:BKR-HOS-3312
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26066 | 105.23 | P42:345:NPPD:BKR-HOS-3312
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26058 | 102.33 | P42:345:NPPD:BKR-HOS-3312
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24778 | 101.54 | P42:345:NPPD:BKR-HOS-3322
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26126 | 100.76 | P42:345:NPPD:BKR-HOS-3322
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24703 | 118.49 | P42:345:NPPD:BKR-KEY-3310
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2511 | 107.63 | P42:345:NPPD:BKR-KEY-3310
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26338 | 106.7 | P42:345:NPPD:BKR-KEY-3310
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2634 | 103.44 | P42:345:NPPD:BKR-KEY-3310
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24911 | 100.59 | P42:345:NPPD:BKR-KEY-3310
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24141 | 113.74 | P42:345:NPPD:BKR-MOR-3306
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24532 | 101.56 | P42:345:NPPD:BKR-MOR-3306
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24152 | 113.8 | P42:345:NPPD:BKR-MOR-3310
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24523 | 101.61 | P42:345:NPPD:BKR-MOR-3310
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24535 | 115.72 | P42:345:NPPD:BKR-PLN-3310
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25843 | 100.93 | P42:345:NPPD:BKR-RW-3302
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24802 | 102.41 | P42:345:NPPD:BKR-SC-3306
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26048 | 100.8 | P42:345:NPPD:BKR-SW-3304
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24373 | 105.32 | P42:345:NPPD:BKR-SW-3306
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26011 | 102.76 | P42:345:NPPD:BKR-SW-3306
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24371 | 105.41 | P42:345:NPPD:BKR-SW-3308
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26009 | 102.67 | P42:345:NPPD:BKR-SW-3308
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26043 | 100.84 | P42:345:NPPD:BKR-SW-3310
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24541 | 116.93 | P42:345:OKGE:SB_BVTY7305
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24541 | 117.01 | P42:345:OKGE:SB_BVTY7387
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.69 | P42:345:OKGE:SB_CION7384
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24536 | 116.69 | P42:345:OKGE:SB_TAGA7386
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24873 | 120.45 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25291 | 107.39 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2658 | 106.66 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26576 | 103.32 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25128 | 100.96 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2454 | 116.55 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 102.09 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.27742 | 112.61 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25034 | 104.89 | P42:345:UMZB:# 2495 #: LO IN ND. STUCK BREAKER (2396)
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26305 | 103.49 | P42:345:UMZB:# 2495 #: LO IN ND. STUCK BREAKER (2396)
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26311 | 100.03 | P42:345:UMZB:# 2495 #: LO IN ND. STUCK BREAKER (2396)
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2497 | 105.51 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26235 | 104.28 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26235 | 101 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24991 | 102.92 | P42:345:UMZB:# 2514 #: BD IN SD. BREAKER FAULT (192)
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26259 | 101.38 | P42:345:UMZB:# 2514 #: BD IN SD. BREAKER FAULT (192)
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26265 | 102.76 | P42:500:OKGE:SB_FTTH8581
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26265 | 102.78 | P42:500:OKGE:SB_FTTH8583
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26265 | 102.76 | P42:500:OKGE:SB_FTTH8585
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 104.36 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 103 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24605 | 118.31 | P43:161-345:ITCM:ARNOLD 3 2820 T1:IA
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25022 | 104.76 | P43:161-345:ITCM:ARNOLD 3 2820 T1:IA
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2628 | 103.15 | P43:161-345:ITCM:ARNOLD 3 2820 T1:IA
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24584 | 117.54 | P43:161-345:ITCM-MEC:HILLS 3 984 T1:IA
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24584 | 117.54 | P43:161-345:ITCM-MEC:HILLS 3 984 T1:IA(1)
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24873 | 120.45 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25291 | 107.39 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2658 | 106.66 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26576 | 103.32 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25128 | 100.96 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24627 | 117.45 | P44:345:ITCM-MEC:LAKEFLD 873 50MVAR:MN-SS
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24873 | 120.45 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25291 | 107.39 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2658 | 106.66 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26576 | 103.32 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25128 | 100.96 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24873 | 120.45 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25291 | 107.39 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2658 | 106.66 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26576 | 103.32 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25128 | 100.96 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24566 | 122.6 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26257 | 118.31 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24988 | 117.81 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26256 | 115.01 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24838 | 108.23 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 15ALL | 2 | 24WP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2591 | 103.29 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24496 | 115.67 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24867 | 102.71 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 104.37 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 103.01 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2494 | 104.37 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26206 | 103.01 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24612 | 119 | P55:345:ATC:ARPIN
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25025 | 106.3 | P55:345:ATC:ARPIN
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26288 | 104.2 | P55:345:ATC:ARPIN
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26287 | 101.11 | P55:345:ATC:ARPIN
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24659 | 119.97 | P55:345:ITCM:MITCHLCO3 N9-N10:IA
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.25091 | 106.21 | P55:345:ITCM:MITCHLCO3 N9-N10:IA
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26343 | 104.29 | P55:345:ITCM:MITCHLCO3 N9-N10:IA
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.26342 | 101.06 | P55:345:ITCM:MITCHLCO3 N9-N10:IA
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 |  | 0.2454 | 116.72 | System Intact
Thermal | 15ALL | 2 | 24L | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 |  | 0.16701 | 116.72 | System Intact
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 |  | 0.2494 | 103.55 | System Intact
Thermal | 15ALL | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 |  | 0.17382 | 103.55 | System Intact
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 |  | 0.26206 | 102.09 | System Intact
Thermal | 15ALL | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 |  | 0.18367 | 102.09 | System Intact
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 115.51 | P11:0:OTP:AUTO-SINGLE:ASH1GEN9:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.25 | P11:0:OTP:AUTO-SINGLE:ASH1GEN9:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.02 | P11:0:XEL:AUTO-SINGLE:G349BUFRG1:W
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 102.71 | P11:0:XEL:AUTO-SINGLE:G349BUFRG1:W
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.02 | P11:0:XEL:AUTO-SINGLE:G349BUFRG2:W
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 102.71 | P11:0:XEL:AUTO-SINGLE:G349BUFRG2:W
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.74 | P11:0:XEL:AUTO-SINGLE:G514ECRK2W:W
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.44 | P11:0:XEL:AUTO-SINGLE:G514ECRK2W:W
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.2 | P11:0:XEL:AUTO-SINGLE:J183PROSEW1:W
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 102.96 | P11:0:XEL:AUTO-SINGLE:J183PROSEW1:W
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.2 | P11:0:XEL:AUTO-SINGLE:J183PROSEW2:W
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 102.96 | P11:0:XEL:AUTO-SINGLE:J183PROSEW2:W
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 115.8 | P11:0:XEL:AUTO-SINGLE:J290BORDRW:W
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.43 | P11:001:599:IRONWOODWIND1:152:539106(1)
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.43 | P11:001:599:SPEARVILLEWIND2:154:539120(1)
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.5 | P11:001:UMZB:# 26 #: WILT2 IN ND. WILTON 2
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.99 | P11:014:NPPD:CANADY1G:1:128
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.18 | P11:014:UMZB:# 17 #: LSS1 IN ND. LONESOME UNIT1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.67 | P11:014:UMZB:# 17 #: LSS1 IN ND. LONESOME UNIT1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.18 | P11:014:UMZB:# 18 #: LSS2 IN ND. LONESOME UNIT2
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.67 | P11:014:UMZB:# 18 #: LSS2 IN ND. LONESOME UNIT2
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.18 | P11:014:UMZB:# 19 #: LSS3 IN ND. LONESOME UNIT3
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.67 | P11:014:UMZB:# 19 #: LSS3 IN ND. LONESOME UNIT3
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.19 | P11:014:UMZB:# 20 #: PNS1 IN ND. PNS1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.69 | P11:014:UMZB:# 20 #: PNS1 IN ND. PNS1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.19 | P11:014:UMZB:# 21 #: PNS2 IN ND. PNS2
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.69 | P11:014:UMZB:# 21 #: PNS2 IN ND. PNS2
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.19 | P11:014:UMZB:# 22 #: PNS3 IN ND. PNS3
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.69 | P11:014:UMZB:# 22 #: PNS3 IN ND. PNS3
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.17 | P11:014:UMZB:# 2988 #: LSS 4 IN ND. LONESOME CREEK 4
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.66 | P11:014:UMZB:# 2988 #: LSS 4 IN ND. LONESOME CREEK 4
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.17 | P11:014:UMZB:# 2989 #: LSS 5 IN ND. LONESOME CREEK 5
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.66 | P11:014:UMZB:# 2989 #: LSS 5 IN ND. LONESOME CREEK 5
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.5 | P11:014:UMZB:# 39 #: WILT1 IN ND. WILTON 1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.59 | P11:014:UMZB:# 41 #: WILT3 IN ND. WILTON 3
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.86 | P11:014:UMZW:# 58 #: FP IN MT. LOSS OF UNIT (4).
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.53 | P11:014:UMZW:# 58 #: FP IN MT. LOSS OF UNIT (4).
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 102.05 | P11:014:UMZW:# 58 #: FP IN MT. LOSS OF UNIT (4).
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 117.33 | P11:014:UMZW:# 68 #: GA IN ND. LOSS OF UNIT (1).
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 104.06 | P11:014:UMZW:# 68 #: GA IN ND. LOSS OF UNIT (1).
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 102.5 | P11:014:UMZW:# 68 #: GA IN ND. LOSS OF UNIT (1).
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 117.34 | P11:014:UMZW:# 69 #: GA IN ND. LOSS OF UNIT (2).
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 104.06 | P11:014:UMZW:# 69 #: GA IN ND. LOSS OF UNIT (2).
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 102.5 | P11:014:UMZW:# 69 #: GA IN ND. LOSS OF UNIT (2).
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.95 | P11:014:UMZW:# 70 #: GA IN ND. LOSS OF UNIT (3).
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 104.06 | P11:014:UMZW:# 70 #: GA IN ND. LOSS OF UNIT (3).
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 102.5 | P11:014:UMZW:# 70 #: GA IN ND. LOSS OF UNIT (3).
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 117.35 | P11:014:UMZW:# 71 #: GA IN ND. LOSS OF UNIT (4).
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 104.09 | P11:014:UMZW:# 71 #: GA IN ND. LOSS OF UNIT (4).
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 102.52 | P11:014:UMZW:# 71 #: GA IN ND. LOSS OF UNIT (4).
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 117.35 | P11:014:UMZW:# 72 #: GA IN ND. LOSS OF UNIT (5).
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 104.09 | P11:014:UMZW:# 72 #: GA IN ND. LOSS OF UNIT (5).
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 102.52 | P11:014:UMZW:# 72 #: GA IN ND. LOSS OF UNIT (5).
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.37 | P11:014:UMZW:# 77 #: OA IN SD. LOSS OF UNIT (2).
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.04 | P11:014:UMZW:# 77 #: OA IN SD. LOSS OF UNIT (2).
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.37 | P11:014:UMZW:# 78 #: OA IN SD. LOSS OF UNIT (3).
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.04 | P11:014:UMZW:# 78 #: OA IN SD. LOSS OF UNIT (3).
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.04 | P11:014:UMZW:# 79 #: OA IN SD. LOSS OF UNIT (4).
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.04 | P11:014:UMZW:# 80 #: OA IN SD. LOSS OF UNIT (5).
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.07 | P11:014:UMZW:# 81 #: OA IN SD. LOSS OF UNIT (6).
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 114.03 | P11:014:UMZW:# 83 #: OA IN SD. LOSS OF UNIT (1).
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 100.32 | P11:014:UMZW:# 83 #: OA IN SD. LOSS OF UNIT (1).
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 114.07 | P11:024:DPC:ALMA2:6
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 100.82 | P11:024:DPC:ALMA2:6
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.57 | P11:035:UMZB:# 2983 #: BRADY WIND IN ND. BRADY WIND 2
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.2 | P11:035:UMZB:# 2983 #: BRADY WIND IN ND. BRADY WIND 2
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.7 | P11:035:UMZB:# 2983 #: BRADY WIND IN ND. BRADY WIND 2
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.57 | P11:035:UMZB:# 2984 #: BRADY WIND IN ND. BRADY WIND 1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.2 | P11:035:UMZB:# 2984 #: BRADY WIND IN ND. BRADY WIND 1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.7 | P11:035:UMZB:# 2984 #: BRADY WIND IN ND. BRADY WIND 1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.61 | P11:035:UMZB:# 2985 #: LINDAHL WIND IN ND. LINDAHL WIND
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.2 | P11:035:UMZB:# 2985 #: LINDAHL WIND IN ND. LINDAHL WIND
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.71 | P11:035:UMZB:# 2985 #: LINDAHL WIND IN ND. LINDAHL WIND
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.77 | P11:035:UMZB:# 3562 #: DCW IN SD. DAY COUNTY WIND 1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.47 | P11:035:UMZB:# 3562 #: DCW IN SD. DAY COUNTY WIND 1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 102.06 | P11:035:UMZB:# 3562 #: DCW IN SD. DAY COUNTY WIND 1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.63 | P11:035:UMZB:# 3563 #: IN ND. ND SUNFLOWER WIND
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.22 | P11:035:UMZB:# 3563 #: IN ND. ND SUNFLOWER WIND
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.72 | P11:035:UMZB:# 3563 #: IN ND. ND SUNFLOWER WIND
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.03 | P11:035:UMZB:# 3564 #: CBW IN SD. CAMBELL COUNTY WIND 1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 102.8 | P11:035:UMZB:# 3564 #: CBW IN SD. CAMBELL COUNTY WIND 1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.33 | P11:035:UMZB:# 3564 #: CBW IN SD. CAMBELL COUNTY WIND 1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.57 | P11:035:UMZW:# 28 #: WWC IN SD. LOSS OF UNIT (WIND).
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 115.88 | P11:069:UMZB:# 12 #: HY IN SD. HYDE
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 102.67 | P11:069:UMZB:# 12 #: HY IN SD. HYDE
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.16 | P11:069:UMZB:# 12 #: HY IN SD. HYDE
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.75 | P11:115:GRIS:PGS
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 102.3 | P11:115:GRIS:PGS
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 101.91 | P11:115:MDU::HESKETT::2::::
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.15 | P11:115:MDU::HESKETT::3::::
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 102.96 | P11:115:MDU::LEWIS & CLARK::1::::
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.7 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 102.45 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.13 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.76 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.69 | P11:115:UMZB:# 2 #: CQ IN ND. CULBERTSON GEN
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.65 | P11:115:UMZB:# 34 #: PWN IN ND. NDPRARIE WINDS
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 102.01 | P11:115:UMZB:# 36 #: GGS2 IN SD. GROTON 2
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 117.82 | P11:115:UMZZ:# 2991 #: BH IN SD. LOSS OF BEETHOVEN WIND FARM
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.26 | P11:115:XEL:HBR #6
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.77 | P11:115:XEL:HBR #6
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.52 | P11:115:XEL:HBR #6 7 8
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.26 | P11:115:XEL:HBR #7
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.77 | P11:115:XEL:HBR #7
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.38 | P11:115:XEL:RIV COMBINE CYCLE
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.15 | P11:13:XEL:AUTO-SINGLE:BLKD72G:2
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.27 | P11:13:XEL:AUTO-SINGLE:HBRS73G:9
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.23 | P11:13:XEL:AUTO-SINGLE:LSPCTG:C
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.54 | P11:138:OKGE:BKRBKR_GSU03
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.14 | P11:138:OKGE:BKRBKR_GSU03
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.72 | P11:138:OKGE:BKRBKR_GSU03
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 117.32 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 102.45 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.38 | P11:15:XEL:AUTO-SINGLE:MEC-CT1:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 101.51 | P11:16:GRE:AUTO-SINGLE:GRE-CGS82G:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.09 | P11:16:GRE:AUTO-SINGLE:GRE-ER14G:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.59 | P11:16:GRE:AUTO-SINGLE:GRE-PVS51G:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.58 | P11:16:GRE:AUTO-SINGLE:GRE-PVS52G:2
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.14 | P11:16:XEL:AUTO-SINGLE:RIVRS77G:7
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.62 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 117.65 | P11:18:HAST:255 MW:EGYCTR2G WEC2:LOSS OF WEC 2 GEN
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 104.44 | P11:18:HAST:255 MW:EGYCTR2G WEC2:LOSS OF WEC 2 GEN
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 103.05 | P11:18:HAST:255 MW:EGYCTR2G WEC2:LOSS OF WEC 2 GEN
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 100.02 | P11:18:HAST:255 MW:EGYCTR2G WEC2:LOSS OF WEC 2 GEN
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 100.82 | P11:18:ITCM:EMERYGT1:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 100.83 | P11:18:ITCM:EMERYGT2:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.18 | P11:18:XEL:AUTO-SINGLE:BLKD75G:5
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.25 | P11:18:XEL:AUTO-SINGLE:COLVILL1G:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.25 | P11:18:XEL:AUTO-SINGLE:COLVILLG:2
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.29 | P11:18:XEL:AUTO-SINGLE:FEPCTG:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.17 | P11:18:XEL:AUTO-SINGLE:HBRC71G:7
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.17 | P11:18:XEL:AUTO-SINGLE:HBRC72G:8
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.15 | P11:18:XEL:AUTO-SINGLE:RIVRSIDEG97:9
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.15 | P11:18:XEL:AUTO-SINGLE:RIVRSIDG107:10
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.38 | P11:19:XEL:AUTO-SINGLE:MEC-ST:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 110.29 | P11:20:OTP:AUTO-SINGLE:CENTER2G:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.77 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.58 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 117 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.65 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 117.26 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.65 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.31 | P11:22:AEPW:FLINTCR1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.88 | P11:22:AEPW:FLINTCR1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.35 | P11:22:AEPW:NES3-1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.94 | P11:22:AEPW:NES3-1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.92 | P11:22:AEPW:RSS2-1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 100.89 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.67 | P11:22:EES-EAI:ARK_NU:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.26 | P11:22:EES-EAI:ARK_NU:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.84 | P11:22:EES-EAI:ARK_NU:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.63 | P11:22:EES-EAI:ARK_NU:1:D395
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.26 | P11:22:EES-EAI:ARK_NU:1:D395
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.82 | P11:22:EES-EAI:ARK_NU:1:D395
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 113.93 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 113.43 | P11:22:OTP:AUTO-SINGLE:CENTER1G:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 102.26 | P11:22:OTP:AUTO-SINGLE:CENTER1G:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.35 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 102.94 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 115.43 | P11:230:MDU::TATANKA::W::::
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 115.37 | P11:230:MDU::THUNDER SPIRIT::W::::
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 115.46 | P11:230:UMZB:# 40 #: CRW IN SD. SD PRAIRIE WIND
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 102.33 | P11:230:UMZB:# 40 #: CRW IN SD. SD PRAIRIE WIND
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.15 | P11:230:WERE:JECU1_GEN::
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.75 | P11:230:WERE:JECU1_GEN::
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.61 | P11:24:AEPW:PIRKEY 1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.92 | P11:24:AEPW:RSS1-1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.52 | P11:24:AEPW:TURKCOAL
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.17 | P11:24:AEPW:TURKCOAL
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.73 | P11:24:AEPW:TURKCOAL
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.72 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 114.07 | P11:24:DPC:AUTO-SINGLE:JPM:6
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 100.82 | P11:24:DPC:AUTO-SINGLE:JPM:6
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 117.25 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 105.27 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 104.04 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.02 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 102.93 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.76 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 100.53 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 111.53 | P11:24:OTP:AUTO-SINGLE:COYOTE1G:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.36 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 107.87 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 117.39 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 105.71 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 104.63 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.35 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.42 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 115.67 | P11:34:ALTW:AUTO-SINGLE:G735_WF5:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 100.95 | P11:34:ALTW:AUTO-SINGLE:G735_WF5:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.49 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24537 | 117.63 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24935 | 103.44 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.55 | P11:345:OKGE:BKRBKR_GSU04
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.14 | P11:345:OKGE:BKRBKR_GSU04
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.72 | P11:345:OKGE:BKRBKR_GSU04
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.52 | P11:345:OKGE:BKRBKR_GSU05
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.01 | P11:345:OKGE:BKRBKR_GSU06
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.52 | P11:345:OKGE:BKRBKR_GSU06
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.07 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.64 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.07 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.64 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.01 | P11:345:OKGE:BKRBKR_GSU22
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.52 | P11:345:OKGE:BKRBKR_GSU22
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.68 | P11:345:OKGE:BKRBKR_GSU24
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.68 | P11:345:OKGE:BKRBKR_GSU25
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.68 | P11:345:OKGE:BKRBKR_GSU26
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.68 | P11:345:OKGE:BKRBKR_GSU27
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.48 | P11:345:OPPD:NEBCTY1G
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 102.07 | P11:345:OPPD:NEBCTY1G
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.49 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.99 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 117.69 | P11:345:OPPD:NEBCTY2G
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.54 | P11:345:OPPD:NEBCTY2G
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 102.03 | P11:345:OPPD:NEBCTY2G
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.27 | P11:345:UMZB:# 15 #: LO IN ND. LELAND OLDS 1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 111.14 | P11:345:UMZB:# 16 #: LO IN ND. LELAND OLDS 2
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.46 | P11:345:UMZB:# 31 #: AVS IN ND. ANTELOPE VALLEY 1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 122.16 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 117.44 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 117.2 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 114.15 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2478 | 107.6 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 15ALL | 2 | 24WP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25852 | 102.55 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 105.93 | P11:345:UMZB:# 5 #: DCS IN SD. DEERCREEK
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.14 | P11:345:WERE:JECU2_GEN::
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.74 | P11:345:WERE:JECU2_GEN::
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.14 | P11:345:WERE:JECU3_GEN::
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.74 | P11:345:WERE:JECU3_GEN::
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24964 | 103.93 | P12:115:MDU:ND:BISCENTRYCE7:CENTURY7:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26232 | 102.23 | P12:115:MDU:ND:BISCENTRYCE7:CENTURY7:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24682 | 117.5 | P12:115:NPPD:1090:AINSWND7:THEDFRD7:BTB
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25011 | 103.54 | P12:115:NPPD:1091:VALENTN7:MISSION7:BTB
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26308 | 102.09 | P12:115:NPPD:1091:VALENTN7:MISSION7:BTB
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2476 | 117.77 | P12:115:NPPD:WAPA6:FTRANDL7:ONEILL 7:BTB
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25165 | 106.19 | P12:115:NPPD:WAPA6:FTRANDL7:ONEILL 7:BTB
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26456 | 104.82 | P12:115:NPPD:WAPA6:FTRANDL7:ONEILL 7:BTB
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26456 | 101.69 | P12:115:NPPD:WAPA6:FTRANDL7:ONEILL 7:BTB
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 118.74 | P12:115:OTP::DONALDS7:TRFALLS7
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 102.47 | P12:115:OTP::DONALDS7:TRFALLS7
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 100.85 | P12:115:OTP::DONALDS7:TRFALLS7
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 115.17 | P12:115:OTP:AUTO-SINGLE:LANGWIN7:LANGDON7:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24541 | 118.4 | P12:115:OTP-MPC::TRFALLS7:WINGER 7
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24941 | 102.55 | P12:115:OTP-MPC::TRFALLS7:WINGER 7
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 100.91 | P12:115:OTP-MPC::TRFALLS7:WINGER 7
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2497 | 104.13 | P12:115:OTP-MRES::HOOT LK7:FERGSFL7
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26237 | 102.75 | P12:115:OTP-MRES::HOOT LK7:FERGSFL7
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24538 | 116.68 | P12:115:UMZ:# 5503 #: IN . PROPER N-1 (LINE) FOR 603023-652440-1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.69 | P12:115:UMZ:# 5537 #: IN . PROPER N-1 (LINE) FOR 652421-659262-1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24538 | 116.67 | P12:115:UMZ:# 5551 #: IN . PROPER N-1 (LINE) FOR 652440-655690-1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26262 | 101.69 | P12:115:UMZ:# 5567 #: IN . PROPER N-1 (LINE) FOR 655490-652525-1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24965 | 103.83 | P12:115:UMZ:# 5576 #: IN . PROPER N-1 (LINE) FOR 652479-659153-1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26242 | 102.48 | P12:115:UMZ:# 5576 #: IN . PROPER N-1 (LINE) FOR 652479-659153-1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25024 | 103.59 | P12:115:UMZ:# 5595 #: IN . PROPER N-1 (LINE) FOR 652501-652510-1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26293 | 102.11 | P12:115:UMZ:# 5595 #: IN . PROPER N-1 (LINE) FOR 652501-652510-1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24618 | 117.2 | P12:115:UMZ:# 5614 #: IN . PROPER N-1 (LINE) FOR 652626-660007-1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.55 | P12:115:UMZ:# 5700 #: IN . PROPER N-1 (LINE) FOR 655946-655947-1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26205 | 101.69 | P12:115:UMZ:# 5798 #: IN . PROPER N-1 (LINE) FOR 659112-659262-1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26205 | 101.69 | P12:115:UMZB:# 2944 #: CQ IN MT. POPLAR - WILLISTON
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25024 | 103.59 | P12:115:UMZW:# 123 #: AR IN SD. MV-AR-FR 115
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26293 | 102.11 | P12:115:UMZW:# 123 #: AR IN SD. MV-AR-FR 115
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24965 | 103.83 | P12:115:UMZW:# 153 #: MS-VE-MR IN SD. VETAL TAP IS A TAP WITH NON-FAULT INTERUPTERS
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26242 | 102.48 | P12:115:UMZW:# 153 #: MS-VE-MR IN SD. VETAL TAP IS A TAP WITH NON-FAULT INTERUPTERS
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24538 | 116.67 | P12:115:UMZW:# 156 #: NEL IN ND. FAULT ON ML-NEL-MX-GA 115 KV
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25169 | 104.02 | P12:115:UMZW:# 1843 #: YJ IN SD. YJ-GP LINE FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26432 | 102.46 | P12:115:UMZW:# 1843 #: YJ IN SD. YJ-GP LINE FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26262 | 101.69 | P12:115:UMZW:# 509 #: TY IN SD. TY-YJ LINE FAULT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24618 | 117.2 | P12:115:UMZZ:# 228 #: MEN IN SD. MENNO JUNCTION IS A TAP (UJ-MEN-TP).
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 115.58 | P12:115:XEL:AUTO-SINGLE:BRKNGCO7:OAKLAKEW7:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 102.28 | P12:115:XEL:AUTO-SINGLE:BRKNGCO7:OAKLAKEW7:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.32 | P12:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.44 | P12:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.43 | P12:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.24 | P12:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 102.99 | P12:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.27 | P12:115:XEL:AUTO-SINGLE:NSSTAP7:NSSTL7:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.86 | P12:115:XEL:AUTO-SINGLE:ODELLWIND7:WOADHILL7:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.54 | P12:115:XEL:AUTO-SINGLE:ODELLWIND7:WOADHILL7:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 115.95 | P12:115:XEL:AUTO-SINGLE:PROSEWIND7:PROSECAP7:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 102.82 | P12:115:XEL:AUTO-SINGLE:PROSEWIND7:PROSECAP7:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.23 | P12:115:XEL:AUTO-SINGLE:REDROCK7:NSSJCT7:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 102.96 | P12:115:XEL:AUTO-SINGLE:REDROCK7:NSSJCT7:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.09 | P12:115:XEL:AUTO-SINGLE:SPLTRK7:ANSON7:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 115.95 | P12:115:XEL:AUTO-SINGLE:SPLTRK7:PROSECAP7:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 102.82 | P12:115:XEL:AUTO-SINGLE:SPLTRK7:PROSECAP7:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.43 | P12:115:XEL:AUTO-SINGLE:WILMART7:MEC-115:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.23 | P12:115:XEL:BDS #2 5
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.76 | P12:115:XEL:BDS #2 5
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.22 | P12:115:XEL:BLL GEN 1-4
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.71 | P12:115:XEL:BLL GEN 1-4
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.05 | P12:115:XEL:DLK-HYL
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.58 | P12:115:XEL:DLK-HYL
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.05 | P12:115:XEL:SCO-DLK-HYL-BLL
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.58 | P12:115:XEL:SCO-DLK-HYL-BLL
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.55 | P12:116:UMZB:# 2911 #: LND IN ND. LINDAHL - NESET
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 100.72 | P12:161:ALTW:AUTO-SINGLE:CRYSTLK5:CRYSTLKII5:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 115.47 | P12:161:ALTW:AUTO-SINGLE:FREEBORN5:G870_TAP5:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 102.33 | P12:161:ALTW:AUTO-SINGLE:FREEBORN5:G870_TAP5:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 100.76 | P12:161:ALTW:AUTO-SINGLE:FREEBORN5:G870_TAP5:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.52 | P12:161:XEL:ECL-WHT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 102.06 | P12:161:XEL:ECL-WHT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.95 | P12:161:XEL-GRE:AUTO-SINGLE:GRNDMDOW5:GRE-PLVLLY5:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.62 | P12:161:XEL-GRE:AUTO-SINGLE:GRNDMDOW5:GRE-PLVLLY5:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.94 | P12:161:XEL-GRE:AUTO-SINGLE:PLSVLLYW5:GRE-PLVLLY5:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.62 | P12:161:XEL-GRE:AUTO-SINGLE:PLSVLLYW5:GRE-PLVLLY5:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25017 | 104.13 | P12:230:GRE-WAPA:AUTO-SINGLE:GRE-STANTON4:LELANDO4:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2628 | 102.55 | P12:230:GRE-WAPA:AUTO-SINGLE:GRE-STANTON4:LELANDO4:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 115.44 | P12:230:MDU::TATANKA NORTH:TATANKA SOUTH:1::::
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.27 | P12:230:MDU::TATANKA NORTH:TATANKA SOUTH:1::::
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24516 | 115.4 | P12:230:MIDW-WERE:SMOKYHL6-SUMMIT6
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24956 | 104.59 | P12:230:OTP:AUTO-SINGLE:HANKSON4:WAHPETN4:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26224 | 103.25 | P12:230:OTP:AUTO-SINGLE:HANKSON4:WAHPETN4:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 114.88 | P12:230:OTP:AUTO-SINGLE:PILSBRY4:BARNES4:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.26 | P12:230:OTP:AUTO-SINGLE:PILSBRY4:BARNES4:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 115.63 | P12:230:OTP:AUTO-SINGLE:PILSBRY4:LUVERNE4:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 114.13 | P12:230:OTP:AUTO-SINGLE:PILSBRY4:MAPLER4:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.28 | P12:230:OTP:AUTO-SINGLE:PILSBRY4:MAPLER4:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 114.24 | P12:230:OTP:AUTO-SINGLE:RGBYWND4:RUGBY4:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 110.99 | P12:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26229 | 102.44 | P12:230:OTP-GRE::GRE-SILVRLK4B2.SLV-INM
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 115.63 | P12:230:OTP-MPC:B2.PB4-LUV
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24966 | 103.8 | P12:230:UMZ:# 5541 #: IN . PROPER N-1 (LINE) FOR 652426-659128-1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26234 | 102.42 | P12:230:UMZ:# 5541 #: IN . PROPER N-1 (LINE) FOR 652426-659128-1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24952 | 103.46 | P12:230:UMZ:# 5549 #: IN . PROPER N-1 (LINE) FOR 652437-657759-1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2622 | 102.05 | P12:230:UMZ:# 5549 #: IN . PROPER N-1 (LINE) FOR 652437-657759-1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24913 | 115.25 | P12:230:UMZ:# 5605 #: IN . PROPER N-1 (LINE) FOR 655765-655510-1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25275 | 102.19 | P12:230:UMZ:# 5605 #: IN . PROPER N-1 (LINE) FOR 655765-655510-1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26549 | 100.58 | P12:230:UMZ:# 5605 #: IN . PROPER N-1 (LINE) FOR 655765-655510-1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24993 | 118.36 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25492 | 104.3 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26774 | 102.72 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24913 | 115.21 | P12:230:UMZ:# 5867 #: IN . PROPER N-1 (LINE) FOR 655510-655487-Z
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25275 | 102.18 | P12:230:UMZ:# 5867 #: IN . PROPER N-1 (LINE) FOR 655510-655487-Z
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26549 | 100.55 | P12:230:UMZ:# 5867 #: IN . PROPER N-1 (LINE) FOR 655510-655487-Z
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24913 | 115.24 | P12:230:UMZB:# 109 #: SB IN SD. SULLY BUTTES-WHITLOCK-GLENHAM
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25275 | 102.19 | P12:230:UMZB:# 109 #: SB IN SD. SULLY BUTTES-WHITLOCK-GLENHAM
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26549 | 100.58 | P12:230:UMZB:# 109 #: SB IN SD. SULLY BUTTES-WHITLOCK-GLENHAM
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25663 | 121.92 | P12:230:UMZB:# 111 #: ST IN SD. WESSINGTION SPRINGS-STORLA-VT HANLON
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26104 | 109.75 | P12:230:UMZB:# 111 #: ST IN SD. WESSINGTION SPRINGS-STORLA-VT HANLON
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.27383 | 108.46 | P12:230:UMZB:# 111 #: ST IN SD. WESSINGTION SPRINGS-STORLA-VT HANLON
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.27388 | 105.13 | P12:230:UMZB:# 111 #: ST IN SD. WESSINGTION SPRINGS-STORLA-VT HANLON
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25946 | 100.93 | P12:230:UMZB:# 111 #: ST IN SD. WESSINGTION SPRINGS-STORLA-VT HANLON
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24809 | 117.18 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25269 | 104.2 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26545 | 102.74 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24966 | 103.8 | P12:230:UMZB:# 2937 #: HWB IN ND. LOSS OF HERBERT WEBER TAP
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26234 | 102.42 | P12:230:UMZB:# 2937 #: HWB IN ND. LOSS OF HERBERT WEBER TAP
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25023 | 104.21 | P12:230:UMZW:# 136 #: GF IN MN. GF-APD LINE FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26294 | 102.92 | P12:230:UMZW:# 136 #: GF IN MN. GF-APD LINE FAULT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2459 | 117.21 | P12:230:UMZW:# 137 #: GF IN MN. GF-FB LINE FAULT
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24992 | 104.58 | P12:230:UMZW:# 137 #: GF IN MN. GF-FB LINE FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26261 | 103.27 | P12:230:UMZW:# 137 #: GF IN MN. GF-FB LINE FAULT
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26261 | 100.03 | P12:230:UMZW:# 137 #: GF IN MN. GF-FB LINE FAULT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25113 | 118.68 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25366 | 104.11 | P12:230:UMZW:# 169 #: WT IN SD. WT-CRP LINE FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26644 | 102.66 | P12:230:UMZW:# 169 #: WT IN SD. WT-CRP LINE FAULT
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25366 | 104.17 | P12:230:UMZW:# 170 #: WT IN SD. WT-HU LINE FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26644 | 102.71 | P12:230:UMZW:# 170 #: WT IN SD. WT-HU LINE FAULT
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25023 | 104.33 | P12:230:UMZW:# 172 #: WT IN SD. WT-APD LINE FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26294 | 103.03 | P12:230:UMZW:# 172 #: WT IN SD. WT-APD LINE FAULT
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24982 | 103.99 | P12:230:UMZW:# 1720 #: GF IN MN. GF-MNVLTAP LINE FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26251 | 102.73 | P12:230:UMZW:# 1720 #: GF IN MN. GF-MNVLTAP LINE FAULT
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25995 | 104.67 | P12:230:UMZW:# 691 #: FT IN SD. FT-WSG LINE FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.27276 | 103.24 | P12:230:UMZW:# 691 #: FT IN SD. FT-WSG LINE FAULT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25692 | 119.79 | P12:230:UMZW:# 692 #: FT IN SD. FT-LET LINE FAULT
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26133 | 108.27 | P12:230:UMZW:# 692 #: FT IN SD. FT-LET LINE FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.27412 | 106.95 | P12:230:UMZW:# 692 #: FT IN SD. FT-LET LINE FAULT
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.27417 | 103.64 | P12:230:UMZW:# 692 #: FT IN SD. FT-LET LINE FAULT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25839 | 120.72 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26293 | 108.89 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.27578 | 107.58 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.27579 | 104.22 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26104 | 101.01 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25807 | 120.66 | P12:230:UMZW:# 694 #: FT IN SD. FT-LP LINE FAULT
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26259 | 108.8 | P12:230:UMZW:# 694 #: FT IN SD. FT-LP LINE FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.27544 | 107.47 | P12:230:UMZW:# 694 #: FT IN SD. FT-LP LINE FAULT
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.27544 | 104.2 | P12:230:UMZW:# 694 #: FT IN SD. FT-LP LINE FAULT
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26071 | 100.89 | P12:230:UMZW:# 694 #: FT IN SD. FT-LP LINE FAULT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24911 | 118.57 | P12:230:WAPA:FTRANDALL-SIOUXCY:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25346 | 105.5 | P12:230:WAPA:FTRANDALL-SIOUXCY:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26605 | 104.06 | P12:230:WAPA:FTRANDALL-SIOUXCY:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26607 | 100.74 | P12:230:WAPA:FTRANDALL-SIOUXCY:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26261 | 102.41 | P12:230:WAPA:SIOUXCY-DENISON:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24605 | 117.46 | P12:230:WAPA:TWINCH-SIOUXCY:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25007 | 104.64 | P12:230:WAPA:TWINCH-SIOUXCY:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26278 | 103.16 | P12:230:WAPA:TWINCH-SIOUXCY:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26278 | 100.01 | P12:230:WAPA:TWINCH-SIOUXCY:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24516 | 115.4 | P12:230:WERE:SUMM-MWE_230::
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24976 | 103.91 | P12:230:XEL:AUTO-SINGLE:GRE-PANTHER4:HUC-MCLEOD4:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26245 | 102.6 | P12:230:XEL:AUTO-SINGLE:GRE-PANTHER4:HUC-MCLEOD4:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2498 | 104.03 | P12:230:XEL:AUTO-SINGLE:MNVLTAP4:GRE-PANTHER4:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24624 | 117.48 | P12:230:XEL:MNV-GRA-PTH
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25032 | 104.29 | P12:230:XEL:MNV-GRA-PTH
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26303 | 103.01 | P12:230:XEL:MNV-GRA-PTH
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25004 | 104.42 | P12:230:XEL-MH:AUTO-SINGLE:PEACEGARD5:GLENBOR4:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.5 | P12:345:AEPW:R.S.S.-7:COGENT7
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 102.14 | P12:345:AEPW:R.S.S.-7:COGENT7
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24579 | 117.53 | P12:345:ALTW:AUTO-SINGLE:ARNOLD3:MORGANV3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.246 | 117.92 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:ARNOLD3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25008 | 104.13 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:ARNOLD3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26274 | 102.56 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:ARNOLD3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24564 | 117.4 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:HCKRYCK3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24659 | 120.64 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:MITCHLCO3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25091 | 106.12 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:MITCHLCO3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26343 | 104.1 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:MITCHLCO3:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26342 | 101.23 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:MITCHLCO3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24658 | 118.28 | P12:345:ALTW:AUTO-SINGLE:HUNTLEY3:LEDYARD3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25032 | 104.39 | P12:345:ALTW:AUTO-SINGLE:HUNTLEY3:LEDYARD3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26342 | 103.2 | P12:345:ALTW:AUTO-SINGLE:HUNTLEY3:LEDYARD3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25002 | 104.22 | P12:345:ALTW:AUTO-SINGLE:LAKEFLD3:HUNTLEY3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25003 | 104.01 | P12:345:ALTW-MEC:AUTO-SINGLE:ARNOLD3:TIFFIN3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24627 | 117.3 | P12:345:ALTW-MEC:AUTO-SINGLE:LAKEFLD3:OBRIEN3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2459 | 117.65 | P12:345:ALTW-MEC:AUTO-SINGLE:MORGANV3:TIFFIN3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24631 | 120 | P12:345:ATC:8E2:ASKING3:EAUCL3
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2505 | 107.26 | P12:345:ATC:8E2:ASKING3:EAUCL3
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26311 | 105.01 | P12:345:ATC:8E2:ASKING3:EAUCL3
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2631 | 101.65 | P12:345:ATC:8E2:ASKING3:EAUCL3
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24638 | 120.49 | P12:345:ATC:8E2_GD:ASKING3:EAUCL3
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25059 | 107.43 | P12:345:ATC:8E2_GD:ASKING3:EAUCL3
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2632 | 105.45 | P12:345:ATC:8E2_GD:ASKING3:EAUCL3
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26318 | 102.02 | P12:345:ATC:8E2_GD:ASKING3:EAUCL3
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24895 | 100.25 | P12:345:ATC:8E2_GD:ASKING3:EAUCL3
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24611 | 118.8 | P12:345:ATC-XEL:8E5:ARPINB4:EAUCL3
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25025 | 105.84 | P12:345:ATC-XEL:8E5:ARPINB4:EAUCL3
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26288 | 103.89 | P12:345:ATC-XEL:8E5:ARPINB4:EAUCL3
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26287 | 100.69 | P12:345:ATC-XEL:8E5:ARPINB4:EAUCL3
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24619 | 119.17 | P12:345:ATC-XEL:8E5_GD:ARPINB4:EAUCL3
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25033 | 106.22 | P12:345:ATC-XEL:8E5_GD:ARPINB4:EAUCL3
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26297 | 104.2 | P12:345:ATC-XEL:8E5_GD:ARPINB4:EAUCL3
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26296 | 101.02 | P12:345:ATC-XEL:8E5_GD:ARPINB4:EAUCL3
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24608 | 118.57 | P12:345:ATC-XEL:W-13:NMAB3345:BRIGGSRD
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25019 | 105.35 | P12:345:ATC-XEL:W-13:NMAB3345:BRIGGSRD
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26284 | 103.53 | P12:345:ATC-XEL:W-13:NMAB3345:BRIGGSRD
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24876 | 102.47 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24876 | 102.47 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24506 | 115.65 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24876 | 102.33 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24494 | 114.69 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24881 | 101.75 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26154 | 100.81 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24975 | 101.97 | P12:345:MEC:AUTO-SINGLE:OBRIEN3:HIGHLND3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26244 | 100.66 | P12:345:MEC:AUTO-SINGLE:OBRIEN3:HIGHLND3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2464 | 118.41 | P12:345:MEC:AUTO-SINGLE:WEBSTER3:LEHIGH3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25045 | 104.13 | P12:345:MEC:AUTO-SINGLE:WEBSTER3:LEHIGH3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26322 | 102.81 | P12:345:MEC:AUTO-SINGLE:WEBSTER3:LEHIGH3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24975 | 101.97 | P12:345:MEC:OBRIEN-HIGHLAND AND REACTOR
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24627 | 117.24 | P12:345:MEC:OBRIEN-LAKEFIELD + REACTOR
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24496 | 114.74 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24883 | 101.74 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2459 | 117.64 | P12:345:MEC:TIFFIN 9T1 SPS
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25003 | 103.99 | P12:345:MEC:TIFFIN 9T1 SPS
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2459 | 117.65 | P12:345:MEC:TIFFIN-ARNOLD
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25003 | 103.99 | P12:345:MEC:TIFFIN-ARNOLD
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2459 | 117.65 | P12:345:MEC-ITCM:TIFFIN 3 - MORGANV3:IA-EC
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25003 | 103.99 | P12:345:MEC-ITCM:TIFFIN 3 - MORGANV3:IA-EC
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24716 | 107.14 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2606 | 105.4 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26052 | 102.52 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24872 | 120.32 | P12:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2529 | 107 | P12:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26578 | 106.23 | P12:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26575 | 102.9 | P12:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25127 | 100.66 | P12:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24947 | 119.93 | P12:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25412 | 104.52 | P12:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26662 | 103.07 | P12:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24968 | 104.6 | P12:345:MPC:CENTER-PRAIRIE:CENTER 3:PRAIRIE3
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2624 | 103.6 | P12:345:MPC:CENTER-PRAIRIE:CENTER 3:PRAIRIE3
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24608 | 118.22 | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25029 | 107.33 | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26303 | 106.3 | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26303 | 103.13 | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.49 | P12:345:OKGE:BKBK1501NEW
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.8 | P12:345:OKGE:BKRBKR604
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.74 | P12:345:OKGE:BKRBKR604_2
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.52 | P12:345:OKGE:BKRBKR605
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.61 | P12:345:OKGE:BKRBKR608
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24872 | 120.32 | P12:345:OPPD-MEC:S3451-RAUN
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2529 | 107 | P12:345:OPPD-MEC:S3451-RAUN
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26578 | 106.23 | P12:345:OPPD-MEC:S3451-RAUN
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26575 | 102.9 | P12:345:OPPD-MEC:S3451-RAUN
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25127 | 100.66 | P12:345:OPPD-MEC:S3451-RAUN
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24608 | 118.2 | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25028 | 107.27 | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26302 | 106.3 | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24968 | 104.64 | P12:345:OTP:AUTO-SINGLE:CENTER3:CNTSHNT3:Z1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2624 | 103.47 | P12:345:OTP:AUTO-SINGLE:CENTER3:CNTSHNT3:Z1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24951 | 104.31 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26217 | 103 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24608 | 118.17 | P12:345:OTP:AUTO-SINGLE:JAMESTN3:CENTER3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25029 | 106.41 | P12:345:OTP:AUTO-SINGLE:JAMESTN3:CENTER3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26302 | 105.59 | P12:345:OTP:AUTO-SINGLE:JAMESTN3:CENTER3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24968 | 104.64 | P12:345:OTP:AUTO-SINGLE:PRAIRIE3:CNTSHNT3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2624 | 103.67 | P12:345:OTP:AUTO-SINGLE:PRAIRIE3:CNTSHNT3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24991 | 102.48 | P12:345:UMZ:# 5852 #: IN . PROPER N-1 (LINE) FOR 659101-659420-Z
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26259 | 100.89 | P12:345:UMZ:# 5852 #: IN . PROPER N-1 (LINE) FOR 659101-659420-Z
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25034 | 104.44 | P12:345:UMZ:# 5859 #: IN . PROPER N-1 (LINE) FOR 659160-659423-Z
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26305 | 103 | P12:345:UMZ:# 5859 #: IN . PROPER N-1 (LINE) FOR 659160-659423-Z
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24726 | 118.21 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25103 | 107.02 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26366 | 106.14 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26367 | 102.91 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24955 | 104.48 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2622 | 103.13 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2487 | 122.71 | P12:345:UMZ:# 5865 #: IN . PROPER N-1 (LINE) FOR 652564-652864-Z
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25338 | 108.77 | P12:345:UMZ:# 5865 #: IN . PROPER N-1 (LINE) FOR 652564-652864-Z
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26585 | 107.09 | P12:345:UMZ:# 5865 #: IN . PROPER N-1 (LINE) FOR 652564-652864-Z
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26582 | 103.64 | P12:345:UMZ:# 5865 #: IN . PROPER N-1 (LINE) FOR 652564-652864-Z
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25168 | 101.24 | P12:345:UMZ:# 5865 #: IN . PROPER N-1 (LINE) FOR 652564-652864-Z
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2662 | 102.72 | P12:345:UMZ:# 5869 #: IN . PROPER N-1 (LINE) FOR 652529-652829-Z
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2141 | 100.63 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25034 | 104.44 | P12:345:UMZB:# 104 #: LOS GRT IN ND. LELAND OLDS-GROTON
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26305 | 103 | P12:345:UMZB:# 104 #: LOS GRT IN ND. LELAND OLDS-GROTON
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24991 | 102.48 | P12:345:UMZB:# 98 #: AVS BD IN ND. ANTELOPE VALLEY-BROADLAND
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26259 | 100.89 | P12:345:UMZB:# 98 #: AVS BD IN ND. ANTELOPE VALLEY-BROADLAND
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26259 | 100.87 | P12:345:UMZB:# 99 #: BD IN SD. BROADLAND-ANTELOPE VALLEY
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2662 | 102.72 | P12:345:UMZW:# 1682 #: WT2 IN SD. WT2-WHT LINE FAULT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2487 | 122.71 | P12:345:UMZW:# 851 #: SC2-SR IN IA. SC2-SR 345 KV LINE
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25338 | 108.77 | P12:345:UMZW:# 851 #: SC2-SR IN IA. SC2-SR 345 KV LINE
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26585 | 107.09 | P12:345:UMZW:# 851 #: SC2-SR IN IA. SC2-SR 345 KV LINE
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26582 | 103.64 | P12:345:UMZW:# 851 #: SC2-SR IN IA. SC2-SR 345 KV LINE
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25168 | 101.24 | P12:345:UMZW:# 851 #: SC2-SR IN IA. SC2-SR 345 KV LINE
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.48 | P12:345:WERE:FR2EAST-FR2WEST_345::
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24605 | 119.24 | P12:345:XEL:ASAK-ECL
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2502 | 106.45 | P12:345:XEL:ASAK-ECL
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26282 | 104.33 | P12:345:XEL:ASAK-ECL
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26281 | 101.22 | P12:345:XEL:ASAK-ECL
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24631 | 120 | P12:345:XEL:ASAK-ECL SPS
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2505 | 107.25 | P12:345:XEL:ASAK-ECL SPS
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26311 | 104.99 | P12:345:XEL:ASAK-ECL SPS
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2631 | 101.55 | P12:345:XEL:ASAK-ECL SPS
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24631 | 120 | P12:345:XEL:ASK-ECL SPS
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2505 | 107.25 | P12:345:XEL:ASK-ECL SPS
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26311 | 105 | P12:345:XEL:ASK-ECL SPS
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2631 | 101.56 | P12:345:XEL:ASK-ECL SPS
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24625 | 118.32 | P12:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25054 | 104.84 | P12:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24602 | 119.15 | P12:345:XEL:AUTO-SINGLE:ASKING3:EAUCL3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25016 | 106.36 | P12:345:XEL:AUTO-SINGLE:ASKING3:EAUCL3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26277 | 104.28 | P12:345:XEL:AUTO-SINGLE:ASKING3:EAUCL3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24581 | 115.5 | P12:345:XEL:AUTO-SINGLE:HELENA3:SHEASLK3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24972 | 100.54 | P12:345:XEL:AUTO-SINGLE:HELENA3:SHEASLK3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24968 | 100.66 | P12:345:XEL:AUTO-SINGLE:LKFLDXL3:CRANDAL3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.93 | P12:345:XEL:AUTO-SINGLE:LKFLDXL3:TRIMONTWD3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.53 | P12:345:XEL:AUTO-SINGLE:LKFLDXL3:TRIMONTWD3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24588 | 118.42 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24996 | 105.51 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2626 | 103.8 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2458 | 117.5 | P12:345:XEL:AUTO-SINGLE:PRISLD3:NROC3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24993 | 103.99 | P12:345:XEL:AUTO-SINGLE:PRISLD3:NROC3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.38 | P12:345:XEL:AUTO-SINGLE:WILMART3:MEC-345:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2458 | 115.39 | P12:345:XEL:AUTO-SINGLE:WILMART3:SHEASLK3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24971 | 100.5 | P12:345:XEL:AUTO-SINGLE:WILMART3:SHEASLK3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.85 | P12:345:XEL:AUTO-SINGLE:WOADHILL3:CRANDAL3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.54 | P12:345:XEL:AUTO-SINGLE:WOADHILL3:CRANDAL3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24582 | 115.44 | P12:345:XEL:SPS HNA-SSL
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24973 | 101.07 | P12:345:XEL:SPS HNA-SSL
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24582 | 115.43 | P12:345:XEL:SPS WLM-SSL
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24973 | 101.07 | P12:345:XEL:SPS WLM-SSL
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24611 | 118.8 | P12:345:XEL-ALTE:AUTO-SINGLE:EAUCL3:ARPINB4:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25025 | 105.84 | P12:345:XEL-ALTE:AUTO-SINGLE:EAUCL3:ARPINB4:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26288 | 103.89 | P12:345:XEL-ALTE:AUTO-SINGLE:EAUCL3:ARPINB4:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24659 | 119.87 | P12:345:XEL-ALTW:AUTO-SINGLE:ADAMS3:MITCHLCO3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25091 | 105.89 | P12:345:XEL-ALTW:AUTO-SINGLE:ADAMS3:MITCHLCO3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26343 | 103.84 | P12:345:XEL-ALTW:AUTO-SINGLE:ADAMS3:MITCHLCO3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24748 | 120.86 | P12:345:XEL-ALTW:AUTO-SINGLE:NOBLES3:LAKEFLD3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2517 | 107.08 | P12:345:XEL-ALTW:AUTO-SINGLE:NOBLES3:LAKEFLD3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26433 | 105.55 | P12:345:XEL-ALTW:AUTO-SINGLE:NOBLES3:LAKEFLD3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24762 | 120.65 | P12:345:XEL-GRE-ITCM:LKFLDXL3 - CRANDAL 3:MN
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25138 | 100.58 | P12:345:XEL-GRE-ITCM:LKFLDXL3 - CRANDAL 3:MN
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2467 | 120 | P12:345:XEL-ITC:AMD-PVS & BKR 8S2
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25108 | 106.05 | P12:345:XEL-ITC:AMD-PVS & BKR 8S2
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26357 | 103.96 | P12:345:XEL-ITC:AMD-PVS & BKR 8S2
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2467 | 120 | P12:345:XEL-ITC:AMD-PVS-MTC AS
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25108 | 106.05 | P12:345:XEL-ITC:AMD-PVS-MTC AS
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26357 | 103.96 | P12:345:XEL-ITC:AMD-PVS-MTC AS
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26355 | 100.81 | P12:345:XEL-ITC:AMD-PVS-MTC AS
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24608 | 118.57 | P12:345:XEL-MGE:AUTO-SINGLE:BRIGGSRD3:NMAB5345:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25019 | 105.35 | P12:345:XEL-MGE:AUTO-SINGLE:BRIGGSRD3:NMAB5345:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26284 | 103.53 | P12:345:XEL-MGE:AUTO-SINGLE:BRIGGSRD3:NMAB5345:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24589 | 117.54 | P12:345:XEL-OTP:AUTO-SINGLE:BISON3:BUFFALO3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25004 | 105.59 | P12:345:XEL-OTP:AUTO-SINGLE:BISON3:BUFFALO3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26275 | 104.59 | P12:345:XEL-OTP:AUTO-SINGLE:BISON3:BUFFALO3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2504 | 104.02 | P12:345:XEL-OTP:AUTO-SINGLE:GRE-RIVRVRD3:ALEXMRES3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26312 | 102.69 | P12:345:XEL-OTP:AUTO-SINGLE:GRE-RIVRVRD3:ALEXMRES3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2487 | 122.86 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25338 | 108.8 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26585 | 107.13 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25168 | 101.28 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24672 | 121.88 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25119 | 110.53 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26367 | 108.93 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24952 | 101.87 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.93 | P12:345-34.5:XEL-IBERDROLA:TRIMONT-ELMCRK WIND
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.53 | P12:345-34.5:XEL-IBERDROLA:TRIMONT-ELMCRK WIND
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.95 | P12:345-34.5:XEL-IBERDROLA:TRIMONT-ELMCRK WIND
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26265 | 102.32 | P12:500:EES-EAI:ARK_NU:FTSMTH:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24567 | 117.37 | P12:500:MH:M602F
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26241 | 103.61 | P12:500:MH:M602F
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26241 | 100.56 | P12:500:MH:M602F
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25015 | 105.62 | P12:500:XEL:AUTO-SINGLE:CHISCO2:CHIS-N2:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25015 | 105.47 | P12:500:XEL:AUTO-SINGLE:FORBES2:CHIS-N2:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24567 | 117.44 | P12:500:XEL:AUTO-SINGLE:FORBES2:ROSEAUS2:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24567 | 117.37 | P12:500:XEL:AUTO-SINGLE:ROSEAUN2:ROSEAUM2:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26241 | 103.62 | P12:500:XEL:AUTO-SINGLE:ROSEAUN2:ROSEAUM2:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24567 | 117.37 | P12:500:XEL:AUTO-SINGLE:ROSEAUS2:ROSEAUM2:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26241 | 103.62 | P12:500:XEL:AUTO-SINGLE:ROSEAUS2:ROSEAUM2:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24567 | 117.37 | P12:500:XEL-MH:AUTO-SINGLE:ROSEAUN2:RIEL2:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26241 | 103.61 | P12:500:XEL-MH:AUTO-SINGLE:ROSEAUN2:RIEL2:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.25 | P12:EHV:EES::8ANO%:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.24 | P12:EHV:EES::8ANO%:1(1)
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.17 | P12:HV:EES::TURK 4%:1(1)
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.01 | P12:LV-EHV:EES::MUSKOGE7!:MUSKOG5G:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.01 | P12:LV-EHV:EES::MUSKOGE7!:MUSKOG6G:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.75 | P13:014-115:GRIS:GSUPGS
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 102.3 | P13:014-115:GRIS:GSUPGS
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 102.05 | P13:115:MDU:HESKETT 2 GSU LOSS:HESKETT::1::::
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.15 | P13:115:MDU:HESKETT 3 GSU LOSS:HESKETT::1::::
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.07 | P13:115:MDU:LEWIS & CLARK GSU LOSS:LEWIS & CLARK::1::::
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.7 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 102.45 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.13 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.76 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.94 | P13:115-13:OTP:AUTO-SINGLE:HOOTLK7:HOOTLK3G:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26249 | 102.51 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.53 | P13:115-34:XEL:AUTO-SINGLE:NOBLES7:NOBLESCO18:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.29 | P13:115-34:XEL:AUTO-SINGLE:NOBLES7:NOBLESCO18:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.53 | P13:115-34:XEL:AUTO-SINGLE:NOBLES7:NOBLESCO28:2
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.02 | P13:115-34:XEL:AUTO-SINGLE:OAKLAKEW7:BUFRDG2B1:5
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 102.71 | P13:115-34:XEL:AUTO-SINGLE:OAKLAKEW7:BUFRDG2B1:5
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.02 | P13:115-34:XEL:AUTO-SINGLE:OAKLAKEW7:BUFRDG2B2:4
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 102.71 | P13:115-34:XEL:AUTO-SINGLE:OAKLAKEW7:BUFRDG2B2:4
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.2 | P13:115-34:XEL:AUTO-SINGLE:PROSEWIND7:PROSEB19:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 102.96 | P13:115-34:XEL:AUTO-SINGLE:PROSEWIND7:PROSEB19:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.21 | P13:115-34:XEL:AUTO-SINGLE:PROSEWIND7:PROSEB29:2
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 102.97 | P13:115-34:XEL:AUTO-SINGLE:PROSEWIND7:PROSEB29:2
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.01 | P13:115-34:XEL:AUTO-SINGLE:YANKEE7:YANKEEB2:2
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 102.71 | P13:115-34:XEL:AUTO-SINGLE:YANKEE7:YANKEEB2:2
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24546 | 117.15 | P13:115-345:NPPD:ANTELOPE:T1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24935 | 101.3 | P13:115-345:NPPD:ANTELOPE:T1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26236 | 100.06 | P13:115-345:NPPD:ANTELOPE:T1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24945 | 102.75 | P13:115-345:NPPD:NUCOR-2
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26212 | 101.39 | P13:115-345:NPPD:NUCOR-2
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26226 | 100.7 | P13:115-345:NPPD:THEDFRD3:T2
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 102.38 | P13:13-115:GRE-OTP:AUTO-SINGLE:GRE-SPRITWDG:SPIRITWD7:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.27 | P13:13-115:XEL:AUTO-SINGLE:HBRS73G:HIBRDGE7:9
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.23 | P13:13-115:XEL:AUTO-SINGLE:LSPCTG:LSPOWER7:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.09 | P13:13-13-115:XEL:AUTO-SINGLE:ANS72G:ANS73G:ANSON7:2
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.91 | P13:138-22:AEPW:R.S.S.-4
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.91 | P13:138-24:AEPW:R.S.S.-4
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.52 | P13:138-24:AEPW:TURK 4
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.17 | P13:138-24:AEPW:TURK 4
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.72 | P13:138-24:AEPW:TURK 4
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.43 | P13:15-115:XEL:AUTO-SINGLE:MEC-CT1:MEC-115:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.93 | P13:15-115:XEL:AUTO-SINGLE:MEC-CT1:MEC-115:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.14 | P13:16-115:XEL:AUTO-SINGLE:RIVRS77G:RIVRSID7:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.86 | P13:161-22:AEPW:FLINTCR5
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.58 | P13:16-161:GRE:AUTO-SINGLE:GRE-PVS51G:GRE-PLVLLY5:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 102.11 | P13:16-161:GRE:AUTO-SINGLE:GRE-PVS51G:GRE-PLVLLY5:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.59 | P13:16-161:GRE:AUTO-SINGLE:GRE-PVS52G:GRE-PLVLLY5:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 102.11 | P13:16-161:GRE:AUTO-SINGLE:GRE-PVS52G:GRE-PLVLLY5:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.09 | P13:16-230:GRE:AUTO-SINGLE:GRE-ER14G:GRE-ELKRIV4:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 117.65 | P13:18-115:HAST::EGYCNTR7 XFMR G2:WEC 2 GSU
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 104.44 | P13:18-115:HAST::EGYCNTR7 XFMR G2:WEC 2 GSU
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 103.05 | P13:18-115:HAST::EGYCNTR7 XFMR G2:WEC 2 GSU
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 100.02 | P13:18-115:HAST::EGYCNTR7 XFMR G2:WEC 2 GSU
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.18 | P13:18-115:XEL:AUTO-SINGLE:BLKD75G:BLKDOG7:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.25 | P13:18-115:XEL:AUTO-SINGLE:COLVILL1G:CANONFLSG7:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.25 | P13:18-115:XEL:AUTO-SINGLE:COLVILLG:CANONFLSG7:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.27 | P13:18-115:XEL:AUTO-SINGLE:FEPCTG:FARIBALTGEN:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.19 | P13:18-115:XEL:AUTO-SINGLE:HBRC71G:HIBRDGE7:7
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.19 | P13:18-115:XEL:AUTO-SINGLE:HBRC72G:HIBRDGE7:8
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.15 | P13:18-115:XEL:AUTO-SINGLE:RIVRSIDEG97:RIVRSID7:9
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.15 | P13:18-115:XEL:AUTO-SINGLE:RIVRSIDG107:RIVRSID7:10
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.48 | P13:18-345:OPPD:NEBCTY1G
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 102.07 | P13:18-345:OPPD:NEBCTY1G
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.38 | P13:19-345:XEL:AUTO-SINGLE:MEC-ST:MEC-345:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.97 | P13:19-345:XEL:AUTO-SINGLE:MEC-ST:MEC-345:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 110.99 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.77 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.37 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 102.37 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 100.92 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 114.44 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 113.9 | P13:22-230:OTP:AUTO-SINGLE:CENTER1G:CENTER4:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 102.36 | P13:22-230:OTP:AUTO-SINGLE:CENTER1G:CENTER4:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.34 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 102.93 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 114.98 | P13:230:MDU:HETTINGER GSU & COLLECTOR LOSS:HETTINGER::1::::
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 115.44 | P13:230:MDU:TATANKA GSU & COLLECTOR LOSS:TATANKA::1::::
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.27 | P13:230:MDU:TATANKA GSU & COLLECTOR LOSS:TATANKA::1::::
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 114.98 | P13:230:MDU:THUNDER SPIRIT & G752-2 GSUS & COLLECTOR LOSS:HETTINGER::1::::
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 114.98 | P13:230:MDU:THUNDER SPIRIT GSU & COLLECTOR LOSS:HETTINGER::1::::
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24542 | 117.29 | P13:230:UMZW:# 2144 #: FP IN MT. LOSS OF TRANSFORMER (AT2).
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.94 | P13:230:UMZW:# 2144 #: FP IN MT. LOSS OF TRANSFORMER (AT2).
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 102.44 | P13:230:UMZW:# 2144 #: FP IN MT. LOSS OF TRANSFORMER (AT2).
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25057 | 104.36 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26341 | 102.88 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 115.25 | P13:230-34:OTP:AUTO-SINGLE:BARNES4:ASH19:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.33 | P13:230-34:OTP:AUTO-SINGLE:BARNES4:ASH19:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 115.63 | P13:230-34:OTP:AUTO-SINGLE:LUVERNE4:ASH29:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.76 | P13:230-34:OTP:AUTO-SINGLE:SIBLEY4:ASH39:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 115.8 | P13:230-34:XEL:AUTO-SINGLE:PEACEGARD5:PEACEGARD9:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24958 | 102.94 | P13:230-345:NPPD:NUCOR-1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26227 | 101.53 | P13:230-345:NPPD:NUCOR-1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24809 | 117.19 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25269 | 104.2 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26545 | 102.74 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 117.47 | P13:23-345:OPPD:NEBCTY2G
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.48 | P13:23-345:OPPD:NEBCTY2G
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 102.1 | P13:23-345:OPPD:NEBCTY2G
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.68 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.93 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 114.27 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 100.97 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 111.99 | P13:24-345:OTP:AUTO-SINGLE:COYOTE1G:COYOTE3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.38 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 108.28 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.5 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 115.4 | P13:34-115:OTP:AUTO-SINGLE:LNG19:LANGWIN7:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 100.72 | P13:34-161:ALTW:AUTO-SINGLE:G735_WF5:CRYSTLKII5:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 114.23 | P13:34-230:OTP:AUTO-SINGLE:RGBYCOL9:RGBYWND4:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24991 | 102.48 | P13:345:UMZB:# 233 #: BD IN SD. BROADLAND TX
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26259 | 100.9 | P13:345:UMZB:# 233 #: BD IN SD. BROADLAND TX
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.86 | P13:345-115:XEL:AUTO-SINGLE:WOADHILL3:WOADHILL7:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.54 | P13:345-115:XEL:AUTO-SINGLE:WOADHILL3:WOADHILL7:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.99 | P13:345-115:XEL:AUTO-SINGLE:WOADHILL3:WOADHILL7:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.55 | P13:345-13-13:GRE:AUTO-SINGLE:GRE-LKFDGEN3:GRE-LGS31G:GRE-LGS32G:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 102.01 | P13:345-13-13:GRE:AUTO-SINGLE:GRE-LKFDGEN3:GRE-LGS31G:GRE-LGS32G:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.55 | P13:345-13-13:GRE:AUTO-SINGLE:GRE-LKFDGEN3:GRE-LGS33G:GRE-LGS34G:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 102 | P13:345-13-13:GRE:AUTO-SINGLE:GRE-LKFDGEN3:GRE-LGS33G:GRE-LGS34G:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.55 | P13:345-13-13:GRE:AUTO-SINGLE:GRE-LKFDGEN3:GRE-LGS35G:GRE-LGS36G:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 102.01 | P13:345-13-13:GRE:AUTO-SINGLE:GRE-LKFDGEN3:GRE-LGS35G:GRE-LGS36G:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.92 | P13:345-22:AEPW:N.E.S.-7_#1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 117.16 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 105.12 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 104.06 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 100.86 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 102.91 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.7 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 100.54 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 117.39 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 105.34 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 104.26 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.11 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.79 | P13:345-34:XEL:AUTO-SINGLE:TRIMONTWD3:ELMCREEK2W8:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.44 | P13:345-34:XEL:AUTO-SINGLE:TRIMONTWD3:ELMCREEK2W8:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.9 | P13:345-34:XEL:AUTO-SINGLE:TRIMONTWD3:ELMCREEK2W8:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.62 | P13:500:EES-EAI:ARK_NU:T1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.25 | P13:500:EES-EAI:ARK_NU:T1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.81 | P13:500:EES-EAI:ARK_NU:T1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.65 | P13:500:EES-EAI:ARK_NU:T2
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.24 | P13:500:EES-EAI:ARK_NU:T2
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.84 | P13:500:EES-EAI:ARK_NU:T2
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24872 | 120.32 | P14:345:OPPD-MEC:S3451 REAC-1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2529 | 107 | P14:345:OPPD-MEC:S3451 REAC-1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26578 | 106.23 | P14:345:OPPD-MEC:S3451 REAC-1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26575 | 102.9 | P14:345:OPPD-MEC:S3451 REAC-1
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25127 | 100.66 | P14:345:OPPD-MEC:S3451 REAC-1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24579 | 117.53 | P21:345:ALTW:AUTO-SINGLE:ARNOLD3:MORGANV3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.246 | 117.92 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:ARNOLD3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25008 | 104.13 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:ARNOLD3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26274 | 102.56 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:ARNOLD3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24564 | 117.4 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:HCKRYCK3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24659 | 120.64 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:MITCHLCO3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25091 | 106.12 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:MITCHLCO3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26343 | 104.1 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:MITCHLCO3:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26342 | 101.23 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:MITCHLCO3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24658 | 118.28 | P21:345:ALTW:AUTO-SINGLE:HUNTLEY3:LEDYARD3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25032 | 104.39 | P21:345:ALTW:AUTO-SINGLE:HUNTLEY3:LEDYARD3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26342 | 103.2 | P21:345:ALTW:AUTO-SINGLE:HUNTLEY3:LEDYARD3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25002 | 104.22 | P21:345:ALTW:AUTO-SINGLE:LAKEFLD3:HUNTLEY3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25003 | 104.01 | P21:345:ALTW-MEC:AUTO-SINGLE:ARNOLD3:TIFFIN3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24627 | 117.3 | P21:345:ALTW-MEC:AUTO-SINGLE:LAKEFLD3:OBRIEN3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2459 | 117.65 | P21:345:ALTW-MEC:AUTO-SINGLE:MORGANV3:TIFFIN3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24494 | 114.69 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24881 | 101.75 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26154 | 100.81 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24975 | 101.97 | P21:345:MEC:AUTO-SINGLE:OBRIEN3:HIGHLND3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26244 | 100.66 | P21:345:MEC:AUTO-SINGLE:OBRIEN3:HIGHLND3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2464 | 118.41 | P21:345:MEC:AUTO-SINGLE:WEBSTER3:LEHIGH3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25045 | 104.13 | P21:345:MEC:AUTO-SINGLE:WEBSTER3:LEHIGH3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26322 | 102.81 | P21:345:MEC:AUTO-SINGLE:WEBSTER3:LEHIGH3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24716 | 107.14 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2606 | 105.4 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26052 | 102.52 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24872 | 120.32 | P21:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2529 | 107 | P21:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26578 | 106.23 | P21:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26575 | 102.9 | P21:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25127 | 100.66 | P21:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24947 | 119.93 | P21:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25412 | 104.52 | P21:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26662 | 103.07 | P21:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24608 | 118.2 | P21:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25028 | 107.27 | P21:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26302 | 106.3 | P21:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26303 | 103.13 | P21:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24968 | 104.64 | P21:345:OTP:AUTO-SINGLE:CENTER3:CNTSHNT3:Z1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2624 | 103.47 | P21:345:OTP:AUTO-SINGLE:CENTER3:CNTSHNT3:Z1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2624 | 100.41 | P21:345:OTP:AUTO-SINGLE:CENTER3:CNTSHNT3:Z1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24951 | 104.31 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26217 | 103 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24608 | 118.17 | P21:345:OTP:AUTO-SINGLE:JAMESTN3:CENTER3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25029 | 106.41 | P21:345:OTP:AUTO-SINGLE:JAMESTN3:CENTER3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26302 | 105.59 | P21:345:OTP:AUTO-SINGLE:JAMESTN3:CENTER3:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26303 | 102.48 | P21:345:OTP:AUTO-SINGLE:JAMESTN3:CENTER3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24968 | 104.64 | P21:345:OTP:AUTO-SINGLE:PRAIRIE3:CNTSHNT3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2624 | 103.67 | P21:345:OTP:AUTO-SINGLE:PRAIRIE3:CNTSHNT3:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2624 | 100.6 | P21:345:OTP:AUTO-SINGLE:PRAIRIE3:CNTSHNT3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24339 | 102.27 | P21:345:UMZW:# 323 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25578 | 100.77 | P21:345:UMZW:# 323 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24084 | 112.67 | P21:345:UMZW:# 325 #: GI IN NE. GI-MCCOOL LINE FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2662 | 102.68 | P21:345:UMZW:# 326 #: WT2 IN SD. OPENING OF A LINE SECTION WO A FAULT (WT2-WT2LNX3 LINE REACTOR)
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24379 | 104.72 | P21:345:UMZW:# 725 #: GI IN NE. GI-SWEET LINE FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26016 | 102.57 | P21:345:UMZW:# 725 #: GI IN NE. GI-SWEET LINE FAULT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24625 | 118.32 | P21:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25054 | 104.84 | P21:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26305 | 103.02 | P21:345:XEL:AUTO-SINGLE:ADAMS3:GRE-PLVLLY3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24602 | 119.15 | P21:345:XEL:AUTO-SINGLE:ASKING3:EAUCL3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25016 | 106.36 | P21:345:XEL:AUTO-SINGLE:ASKING3:EAUCL3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26277 | 104.28 | P21:345:XEL:AUTO-SINGLE:ASKING3:EAUCL3:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26277 | 101.11 | P21:345:XEL:AUTO-SINGLE:ASKING3:EAUCL3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.262 | 100.66 | P21:345:XEL:AUTO-SINGLE:FIELD_S3:CRANDAL3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.262 | 100.72 | P21:345:XEL:AUTO-SINGLE:FIELD_S3:FIELD_N3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24581 | 115.5 | P21:345:XEL:AUTO-SINGLE:HELENA3:SHEASLK3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24972 | 100.54 | P21:345:XEL:AUTO-SINGLE:HELENA3:SHEASLK3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.262 | 100.93 | P21:345:XEL:AUTO-SINGLE:LKFLDXL3:CRANDAL3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24968 | 100.66 | P21:345:XEL:AUTO-SINGLE:LKFLDXL3:CRANDAL3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.93 | P21:345:XEL:AUTO-SINGLE:LKFLDXL3:TRIMONTWD3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.53 | P21:345:XEL:AUTO-SINGLE:LKFLDXL3:TRIMONTWD3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.95 | P21:345:XEL:AUTO-SINGLE:LKFLDXL3:TRIMONTWD3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26241 | 102.73 | P21:345:XEL:AUTO-SINGLE:LYONCO3:GRE-CEDARMT3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24588 | 118.42 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24996 | 105.51 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2626 | 103.8 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26259 | 100.36 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2458 | 117.5 | P21:345:XEL:AUTO-SINGLE:PRISLD3:NROC3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24993 | 103.99 | P21:345:XEL:AUTO-SINGLE:PRISLD3:NROC3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.262 | 100.7 | P21:345:XEL:AUTO-SINGLE:WILMART3:FIELD_N3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.38 | P21:345:XEL:AUTO-SINGLE:WILMART3:MEC-345:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.97 | P21:345:XEL:AUTO-SINGLE:WILMART3:MEC-345:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2458 | 115.39 | P21:345:XEL:AUTO-SINGLE:WILMART3:SHEASLK3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24971 | 100.5 | P21:345:XEL:AUTO-SINGLE:WILMART3:SHEASLK3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.85 | P21:345:XEL:AUTO-SINGLE:WOADHILL3:CRANDAL3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.54 | P21:345:XEL:AUTO-SINGLE:WOADHILL3:CRANDAL3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.99 | P21:345:XEL:AUTO-SINGLE:WOADHILL3:CRANDAL3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24611 | 118.8 | P21:345:XEL-ALTE:AUTO-SINGLE:EAUCL3:ARPINB4:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25025 | 105.84 | P21:345:XEL-ALTE:AUTO-SINGLE:EAUCL3:ARPINB4:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26288 | 103.89 | P21:345:XEL-ALTE:AUTO-SINGLE:EAUCL3:ARPINB4:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26287 | 100.69 | P21:345:XEL-ALTE:AUTO-SINGLE:EAUCL3:ARPINB4:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24659 | 119.87 | P21:345:XEL-ALTW:AUTO-SINGLE:ADAMS3:MITCHLCO3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25091 | 105.89 | P21:345:XEL-ALTW:AUTO-SINGLE:ADAMS3:MITCHLCO3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26343 | 103.84 | P21:345:XEL-ALTW:AUTO-SINGLE:ADAMS3:MITCHLCO3:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26342 | 100.73 | P21:345:XEL-ALTW:AUTO-SINGLE:ADAMS3:MITCHLCO3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24748 | 120.86 | P21:345:XEL-ALTW:AUTO-SINGLE:NOBLES3:LAKEFLD3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2517 | 107.08 | P21:345:XEL-ALTW:AUTO-SINGLE:NOBLES3:LAKEFLD3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26433 | 105.55 | P21:345:XEL-ALTW:AUTO-SINGLE:NOBLES3:LAKEFLD3:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26433 | 102.07 | P21:345:XEL-ALTW:AUTO-SINGLE:NOBLES3:LAKEFLD3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24608 | 118.57 | P21:345:XEL-MGE:AUTO-SINGLE:BRIGGSRD3:NMAB5345:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25019 | 105.35 | P21:345:XEL-MGE:AUTO-SINGLE:BRIGGSRD3:NMAB5345:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26284 | 103.53 | P21:345:XEL-MGE:AUTO-SINGLE:BRIGGSRD3:NMAB5345:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26279 | 100.22 | P21:345:XEL-MGE:AUTO-SINGLE:BRIGGSRD3:NMAB5345:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24589 | 117.54 | P21:345:XEL-OTP:AUTO-SINGLE:BISON3:BUFFALO3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25004 | 105.59 | P21:345:XEL-OTP:AUTO-SINGLE:BISON3:BUFFALO3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26275 | 104.59 | P21:345:XEL-OTP:AUTO-SINGLE:BISON3:BUFFALO3:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26276 | 101.45 | P21:345:XEL-OTP:AUTO-SINGLE:BISON3:BUFFALO3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2504 | 104.02 | P21:345:XEL-OTP:AUTO-SINGLE:GRE-RIVRVRD3:ALEXMRES3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26312 | 102.69 | P21:345:XEL-OTP:AUTO-SINGLE:GRE-RIVRVRD3:ALEXMRES3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2487 | 122.86 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25338 | 108.8 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26585 | 107.13 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26582 | 103.68 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25168 | 101.28 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24672 | 121.88 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25119 | 110.53 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26367 | 108.93 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26364 | 105.67 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24952 | 101.87 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24889 | 122.95 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25356 | 108.81 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26606 | 107.19 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26602 | 104.35 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25187 | 101.35 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25015 | 105.62 | P21:500:XEL:AUTO-SINGLE:CHISCO2:CHIS-N2:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26264 | 103.51 | P21:500:XEL:AUTO-SINGLE:CHISCO2:CHIS-N2:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26264 | 100.24 | P21:500:XEL:AUTO-SINGLE:CHISCO2:CHIS-N2:1
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25015 | 105.47 | P21:500:XEL:AUTO-SINGLE:FORBES2:CHIS-N2:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26264 | 103.45 | P21:500:XEL:AUTO-SINGLE:FORBES2:CHIS-N2:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26264 | 100.1 | P21:500:XEL:AUTO-SINGLE:FORBES2:CHIS-N2:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24567 | 117.44 | P21:500:XEL:AUTO-SINGLE:FORBES2:ROSEAUS2:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26241 | 103.68 | P21:500:XEL:AUTO-SINGLE:FORBES2:ROSEAUS2:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26241 | 100.55 | P21:500:XEL:AUTO-SINGLE:FORBES2:ROSEAUS2:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24567 | 117.37 | P21:500:XEL:AUTO-SINGLE:ROSEAUN2:ROSEAUM2:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26241 | 103.62 | P21:500:XEL:AUTO-SINGLE:ROSEAUN2:ROSEAUM2:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26241 | 100.56 | P21:500:XEL:AUTO-SINGLE:ROSEAUN2:ROSEAUM2:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24567 | 117.37 | P21:500:XEL:AUTO-SINGLE:ROSEAUS2:ROSEAUM2:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26241 | 103.62 | P21:500:XEL:AUTO-SINGLE:ROSEAUS2:ROSEAUM2:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26241 | 100.56 | P21:500:XEL:AUTO-SINGLE:ROSEAUS2:ROSEAUM2:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24567 | 117.37 | P21:500:XEL-MH:AUTO-SINGLE:ROSEAUN2:RIEL2:1
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26241 | 103.61 | P21:500:XEL-MH:AUTO-SINGLE:ROSEAUN2:RIEL2:1
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26241 | 100.56 | P21:500:XEL-MH:AUTO-SINGLE:ROSEAUN2:RIEL2:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24545 | 115.25 | P22:345:AMMO::OVERTON:1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2459 | 117.65 | P22:345:MEC-ITCM:TIFFIN 3:IA-EC
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25003 | 103.99 | P22:345:MEC-ITCM:TIFFIN 3:IA-EC
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24872 | 120.32 | P22:345:OPPD:S3451-RAUN
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2529 | 107 | P22:345:OPPD:S3451-RAUN
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26578 | 106.23 | P22:345:OPPD:S3451-RAUN
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26575 | 102.9 | P22:345:OPPD:S3451-RAUN
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25127 | 100.66 | P22:345:OPPD:S3451-RAUN
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.48 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 102.07 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.49 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.99 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 117.47 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.48 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 102.1 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 117.69 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.54 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 102.03 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24631 | 120 | P22:345:XEL:345KV SEC 2 ECL SPS
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2505 | 107.25 | P22:345:XEL:345KV SEC 2 ECL SPS
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26311 | 104.99 | P22:345:XEL:345KV SEC 2 ECL SPS
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2631 | 101.55 | P22:345:XEL:345KV SEC 2 ECL SPS
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24689 | 120.87 | P22:345:XEL:ADAMS 3 N1:MN
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25136 | 106.37 | P22:345:XEL:ADAMS 3 N1:MN
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26379 | 104.35 | P22:345:XEL:ADAMS 3 N1:MN
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26378 | 101.12 | P22:345:XEL:ADAMS 3 N1:MN
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24971 | 100.46 | P22:345:XEL:ADAMS 3 N1:MN
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.19 | P23:161-345:KCPL:IATAN_R1-11::IATANU1-IATANT11
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.72 | P23:161-345:KCPL:IATAN_R1-11::IATANU1-IATANT11
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.35 | P23:345:AEPW:NES CB 3413B NBTB
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.94 | P23:345:AEPW:NES CB 3413B NBTB
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24938 | 103.37 | P23:345:AEPW:NES CB 3417B NBTB
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26204 | 101.95 | P23:345:AEPW:NES CB 3417B NBTB
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24941 | 103.49 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26207 | 102.14 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.5 | P23:345:AEPW:RIVERSIDE CB 3433A NBTB
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 102.14 | P23:345:AEPW:RIVERSIDE CB 3433A NBTB
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24659 | 119.8 | P23:345:ALTW:MITCHLCO:1130
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25091 | 105.86 | P23:345:ALTW:MITCHLCO:1130
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26343 | 103.82 | P23:345:ALTW:MITCHLCO:1130
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26342 | 100.71 | P23:345:ALTW:MITCHLCO:1130
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24659 | 119.73 | P23:345:ALTW:MITCHLCO:1140
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25091 | 105.84 | P23:345:ALTW:MITCHLCO:1140
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26343 | 103.8 | P23:345:ALTW:MITCHLCO:1140
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26342 | 100.6 | P23:345:ALTW:MITCHLCO:1140
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24659 | 120.08 | P23:345:ALTW:MITCHLCO:1150
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25091 | 105.87 | P23:345:ALTW:MITCHLCO:1150
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26343 | 103.91 | P23:345:ALTW:MITCHLCO:1150
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26342 | 100.7 | P23:345:ALTW:MITCHLCO:1150
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24659 | 120.34 | P23:345:ALTW:MITCHLCO:1160
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25091 | 106.01 | P23:345:ALTW:MITCHLCO:1160
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26343 | 104 | P23:345:ALTW:MITCHLCO:1160
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26342 | 101.07 | P23:345:ALTW:MITCHLCO:1160
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24618 | 119.12 | P23:345:ATC:ARPIN:424-S_GD
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25033 | 106.16 | P23:345:ATC:ARPIN:424-S_GD
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26296 | 104.13 | P23:345:ATC:ARPIN:424-S_GD
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26295 | 101.11 | P23:345:ATC:ARPIN:424-S_GD
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24608 | 118.57 | P23:345:ATC:NORTHMADISON:6033-S
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25019 | 105.36 | P23:345:ATC:NORTHMADISON:6033-S
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26284 | 103.54 | P23:345:ATC:NORTHMADISON:6033-S
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26279 | 100.23 | P23:345:ATC:NORTHMADISON:6033-S
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24609 | 118.6 | P23:345:ATC:NORTHMADISON:6037-S
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25019 | 105.37 | P23:345:ATC:NORTHMADISON:6037-S
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26284 | 103.55 | P23:345:ATC:NORTHMADISON:6037-S
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26279 | 100.16 | P23:345:ATC:NORTHMADISON:6037-S
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24522 | 114.73 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24909 | 101.99 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26194 | 100.93 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24542 | 115.21 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24951 | 102.51 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24864 | 102.56 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2467 | 120 | P23:345:GRE:PVS 19JB2
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2511 | 106 | P23:345:GRE:PVS 19JB2
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26358 | 103.89 | P23:345:GRE:PVS 19JB2
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26356 | 100.74 | P23:345:GRE:PVS 19JB2
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2467 | 120.01 | P23:345:GRE:PVS 19JB3
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2511 | 106 | P23:345:GRE:PVS 19JB3
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26358 | 103.9 | P23:345:GRE:PVS 19JB3
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26356 | 100.74 | P23:345:GRE:PVS 19JB3
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24666 | 120.85 | P23:345:ITCM:HAZLTON3 9985:IA-NE
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25096 | 106.39 | P23:345:ITCM:HAZLTON3 9985:IA-NE
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26352 | 104.42 | P23:345:ITCM:HAZLTON3 9985:IA-NE
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26345 | 101.46 | P23:345:ITCM:HAZLTON3 9985:IA-NE
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24567 | 117.47 | P23:345:ITCM:HCKRYCK:5267-PRESENT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24567 | 117.47 | P23:345:ITCM:HCKRYCK:5268-PRESENT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24567 | 117.44 | P23:345:ITCM:HCKRYCK:5269-PRESENT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24564 | 117.4 | P23:345:ITCM:HCKRYCK:FUT1
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24567 | 117.47 | P23:345:ITCM:HCKRYCK3 5267-5268-5269:IA-MVP
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24509 | 114.47 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.249 | 101.55 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26172 | 100.61 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24939 | 103.08 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2621 | 101.65 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24924 | 102.87 | P23:345:KCPL-WERE:LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26193 | 101.52 | P23:345:KCPL-WERE:LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24544 | 112.14 | P23:345:MDU::COYOTE::5707-5712-5715::::
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24566 | 118.13 | P23:345:MEC:BLACK HAWK 901
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26235 | 103.02 | P23:345:MEC:BLACK HAWK 901
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24496 | 114.74 | P23:345:MEC:BONDURANT 906
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24883 | 101.74 | P23:345:MEC:BONDURANT 906
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26156 | 100.8 | P23:345:MEC:BONDURANT 906
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24544 | 117.31 | P23:345:MEC:CBEC 905
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24944 | 105.19 | P23:345:MEC:CBEC 905
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2621 | 104.11 | P23:345:MEC:CBEC 905
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26209 | 101 | P23:345:MEC:CBEC 905
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 117.15 | P23:345:MEC:CBEC 908
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 105.12 | P23:345:MEC:CBEC 908
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 104.02 | P23:345:MEC:CBEC 908
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26205 | 100.84 | P23:345:MEC:CBEC 908
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24496 | 114.74 | P23:345:MEC:GDMEC 901
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24883 | 101.96 | P23:345:MEC:GDMEC 901
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26156 | 101.05 | P23:345:MEC:GDMEC 901
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24496 | 114.74 | P23:345:MEC:GDMEC 902
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24883 | 101.96 | P23:345:MEC:GDMEC 902
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26156 | 101.05 | P23:345:MEC:GDMEC 902
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24975 | 101.97 | P23:345:MEC:HIGHLAND 902
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26244 | 100.64 | P23:345:MEC:HIGHLAND 902
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24975 | 101.97 | P23:345:MEC:HIGHLAND 903
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26244 | 100.64 | P23:345:MEC:HIGHLAND 903
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 115.02 | P23:345:MEC:HIGHLAND 906
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 102.27 | P23:345:MEC:HIGHLAND 906
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 100.86 | P23:345:MEC:HIGHLAND 906
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24584 | 117.34 | P23:345:MEC:HILLS 984
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2464 | 118.4 | P23:345:MEC:LEHIGH 0350
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25045 | 104.13 | P23:345:MEC:LEHIGH 0350
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26322 | 102.81 | P23:345:MEC:LEHIGH 0350
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24937 | 102.8 | P23:345:MEC:LOUISA 954
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26204 | 101.63 | P23:345:MEC:LOUISA 954
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24978 | 102.82 | P23:345:MEC:LOUISA 964
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26249 | 101.71 | P23:345:MEC:LOUISA 964
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24494 | 114.69 | P23:345:MEC:MONTEZUMA 901
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24881 | 101.75 | P23:345:MEC:MONTEZUMA 901
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26154 | 100.81 | P23:345:MEC:MONTEZUMA 901
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24509 | 114.52 | P23:345:MEC:MONTEZUMA 903
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.249 | 101.62 | P23:345:MEC:MONTEZUMA 903
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26172 | 100.69 | P23:345:MEC:MONTEZUMA 903
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24595 | 117.84 | P23:345:MEC:MORGANV FUT1:IA-EC
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24595 | 117.84 | P23:345:MEC:MORGANV FUT2:IA-EC
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26208 | 100.42 | P23:345:MEC:RAUN 0210
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24939 | 123.97 | P23:345:MEC:RAUN 0270
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25353 | 115.86 | P23:345:MEC:RAUN 0270
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26698 | 114.56 | P23:345:MEC:RAUN 0270
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26683 | 111.66 | P23:345:MEC:RAUN 0270
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2517 | 108.62 | P23:345:MEC:RAUN 0270
Thermal | 15ALL | 2 | 24WP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2631 | 100.69 | P23:345:MEC:RAUN 0270
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24495 | 114.71 | P23:345:MEC:SYCAMORE 901
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24882 | 101.71 | P23:345:MEC:SYCAMORE 901
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26155 | 100.77 | P23:345:MEC:SYCAMORE 901
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24495 | 114.72 | P23:345:MEC:SYCAMORE 902
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24882 | 101.71 | P23:345:MEC:SYCAMORE 902
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26155 | 100.78 | P23:345:MEC:SYCAMORE 902
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2459 | 117.65 | P23:345:MEC:TIFFIN 944
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25003 | 103.99 | P23:345:MEC:TIFFIN 944
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24592 | 117.68 | P23:345:MEC:TIFFIN 954
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25008 | 103.95 | P23:345:MEC:TIFFIN 954
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24669 | 119.51 | P23:345:MEC:WEBSTER 901
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25071 | 105.44 | P23:345:MEC:WEBSTER 901
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26355 | 104.39 | P23:345:MEC:WEBSTER 901
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26353 | 100.91 | P23:345:MEC:WEBSTER 901
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2464 | 118.39 | P23:345:MEC:WEBSTER 905
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25045 | 104.13 | P23:345:MEC:WEBSTER 905
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26322 | 102.77 | P23:345:MEC:WEBSTER 905
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2464 | 117.99 | P23:345:MPC:BISON 3:6720
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25069 | 106.39 | P23:345:MPC:BISON 3:6720
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26344 | 105.29 | P23:345:MPC:BISON 3:6720
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26345 | 102.21 | P23:345:MPC:BISON 3:6720
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24971 | 104.61 | P23:345:MPC:CENTER 3:8810
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26244 | 103.61 | P23:345:MPC:CENTER 3:8810
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26244 | 100.6 | P23:345:MPC:CENTER 3:8810
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24971 | 104.61 | P23:345:MPC:CENTER 3:8820
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26244 | 103.63 | P23:345:MPC:CENTER 3:8820
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26244 | 100.59 | P23:345:MPC:CENTER 3:8820
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24968 | 104.6 | P23:345:MPC:PRAIRIE3:4440
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2624 | 103.6 | P23:345:MPC:PRAIRIE3:4440
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2624 | 100.49 | P23:345:MPC:PRAIRIE3:4440
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24968 | 104.6 | P23:345:MPC:PRAIRIE3:4450
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2624 | 103.59 | P23:345:MPC:PRAIRIE3:4450
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2624 | 100.49 | P23:345:MPC:PRAIRIE3:4450
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24968 | 104.64 | P23:345:MPC:PRAIRIE3:4470
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2624 | 103.67 | P23:345:MPC:PRAIRIE3:4470
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2624 | 100.6 | P23:345:MPC:PRAIRIE3:4470
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24638 | 117.35 | P23:345:MRES:ALEXMRES3:3385:FUTURE
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25063 | 104.75 | P23:345:MRES:ALEXMRES3:3385:FUTURE
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26336 | 103.48 | P23:345:MRES:ALEXMRES3:3385:FUTURE
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26337 | 100.12 | P23:345:MRES:ALEXMRES3:3385:FUTURE
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24872 | 120.32 | P23:345:OPPD:S3451-RAUN
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2529 | 107 | P23:345:OPPD:S3451-RAUN
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26578 | 106.23 | P23:345:OPPD:S3451-RAUN
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26575 | 102.9 | P23:345:OPPD:S3451-RAUN
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25127 | 100.66 | P23:345:OPPD:S3451-RAUN
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24873 | 120.27 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25291 | 107.01 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2658 | 106.21 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26576 | 102.89 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25128 | 100.68 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.48 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 102.07 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.49 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.99 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 117.47 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.48 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 102.1 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 117.69 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.54 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 102.03 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24592 | 117.63 | P23:345:OTP:BUFFALO3:3615:V2016
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25007 | 105.85 | P23:345:OTP:BUFFALO3:3615:V2016
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26279 | 105 | P23:345:OTP:BUFFALO3:3615:V2016
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26279 | 101.81 | P23:345:OTP:BUFFALO3:3615:V2016
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24608 | 118.19 | P23:345:OTP:BUFFALO3:3655:V2016
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25029 | 107.27 | P23:345:OTP:BUFFALO3:3655:V2016
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26302 | 106.3 | P23:345:OTP:BUFFALO3:3655:V2016
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26303 | 103.15 | P23:345:OTP:BUFFALO3:3655:V2016
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2455 | 112.29 | P23:345:OTP:CENTER 3:3215
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2455 | 112.29 | P23:345:OTP:CENTER 3:3215(1)
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2455 | 112.28 | P23:345:OTP:CENTER 3:3225
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2455 | 112.28 | P23:345:OTP:CENTER 3:3225(1)
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24609 | 118.18 | P23:345:OTP:CENTER 3:3235
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2503 | 106.47 | P23:345:OTP:CENTER 3:3235
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26304 | 105.72 | P23:345:OTP:CENTER 3:3235
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26305 | 102.37 | P23:345:OTP:CENTER 3:3235
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24609 | 118.2 | P23:345:OTP:CENTER 3:3245
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2503 | 106.47 | P23:345:OTP:CENTER 3:3245
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26304 | 105.72 | P23:345:OTP:CENTER 3:3245
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26305 | 102.37 | P23:345:OTP:CENTER 3:3245
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24608 | 118.17 | P23:345:OTP:JAMESTN3:3115:V2020
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25029 | 106.42 | P23:345:OTP:JAMESTN3:3115:V2020
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26302 | 105.6 | P23:345:OTP:JAMESTN3:3115:V2020
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26303 | 102.49 | P23:345:OTP:JAMESTN3:3115:V2020
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24608 | 118.17 | P23:345:OTP:JAMESTN3:3125:V2020
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25029 | 106.42 | P23:345:OTP:JAMESTN3:3125:V2020
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26302 | 105.6 | P23:345:OTP:JAMESTN3:3125:V2020
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26303 | 102.49 | P23:345:OTP:JAMESTN3:3125:V2020
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24608 | 118.24 | P23:345:OTP:JAMESTN3:3135:V2020
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25028 | 107.27 | P23:345:OTP:JAMESTN3:3135:V2020
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26302 | 106.3 | P23:345:OTP:JAMESTN3:3135:V2020
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26303 | 103.11 | P23:345:OTP:JAMESTN3:3135:V2020
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24608 | 118.24 | P23:345:OTP:JAMESTN3:3145:V2020
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25028 | 107.26 | P23:345:OTP:JAMESTN3:3145:V2020
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26302 | 106.29 | P23:345:OTP:JAMESTN3:3145:V2020
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26303 | 103.11 | P23:345:OTP:JAMESTN3:3145:V2020
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25928 | 100.75 | P23:345:SUNC:MO_BRK188
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25928 | 100.75 | P23:345:SUNC:MO_BRK388
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25085 | 104.37 | P23:345:UMZB:# 102 #: GRT IN SD. BREAKER FAULT (8392)
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26353 | 103.06 | P23:345:UMZB:# 102 #: GRT IN SD. BREAKER FAULT (8392)
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26352 | 100.05 | P23:345:UMZB:# 102 #: GRT IN SD. BREAKER FAULT (8392)
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2662 | 102.72 | P23:345:UMZW:# 824 #: WH IN SD.
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25377 | 105.17 | P23:345:UMZW:# 844 #: WT2 IN SD. BREAKER FAULT (7296)
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26645 | 104.14 | P23:345:UMZW:# 844 #: WT2 IN SD. BREAKER FAULT (7296)
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26642 | 100.98 | P23:345:UMZW:# 844 #: WT2 IN SD. BREAKER FAULT (7296)
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25377 | 105.12 | P23:345:UMZW:# 845 #: WT2 IN SD. BREAKER FAULT (7192)
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26645 | 104.1 | P23:345:UMZW:# 845 #: WT2 IN SD. BREAKER FAULT (7192)
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26642 | 100.91 | P23:345:UMZW:# 845 #: WT2 IN SD. BREAKER FAULT (7192)
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25062 | 123.55 | P23:345:UMZW:# 853 #: SC2 IN IA. SC2 345 KV BREAKER FAILURE
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25557 | 108.61 | P23:345:UMZW:# 853 #: SC2 IN IA. SC2 345 KV BREAKER FAILURE
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26798 | 106.8 | P23:345:UMZW:# 853 #: SC2 IN IA. SC2 345 KV BREAKER FAILURE
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26795 | 103.22 | P23:345:UMZW:# 853 #: SC2 IN IA. SC2 345 KV BREAKER FAILURE
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25388 | 101.12 | P23:345:UMZW:# 853 #: SC2 IN IA. SC2 345 KV BREAKER FAILURE
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25062 | 123.55 | P23:345:WAPA:SIOUXCY:8592-8696
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25557 | 108.61 | P23:345:WAPA:SIOUXCY:8592-8696
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26798 | 106.8 | P23:345:WAPA:SIOUXCY:8592-8696
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26795 | 103.22 | P23:345:WAPA:SIOUXCY:8592-8696
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25388 | 101.12 | P23:345:WAPA:SIOUXCY:8592-8696
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25062 | 123.55 | P23:345:WAPA:SIOUXCY:8692
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25557 | 108.55 | P23:345:WAPA:SIOUXCY:8692
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26798 | 106.76 | P23:345:WAPA:SIOUXCY:8692
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26795 | 103.23 | P23:345:WAPA:SIOUXCY:8692
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25388 | 101.06 | P23:345:WAPA:SIOUXCY:8692
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.14 | P23:345:WERE:JEC_345-15::
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.74 | P23:345:WERE:JEC_345-15::
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24949 | 103.04 | P23:345:WERE:JEC_345-16::
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26225 | 101.53 | P23:345:WERE:JEC_345-16::
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.14 | P23:345:WERE:JEC_345-19::
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.74 | P23:345:WERE:JEC_345-19::
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.14 | P23:345:WERE:JEC_345-20::
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.74 | P23:345:WERE:JEC_345-20::
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24746 | 122.14 | P23:345:XEL:192 BKR SPK AS
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.252 | 110.74 | P23:345:XEL:192 BKR SPK AS
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26448 | 109 | P23:345:XEL:192 BKR SPK AS
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26444 | 105.7 | P23:345:XEL:192 BKR SPK AS
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25032 | 102.16 | P23:345:XEL:192 BKR SPK AS
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24749 | 122.14 | P23:345:XEL:196 BKR SPK AS
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25203 | 110.73 | P23:345:XEL:196 BKR SPK AS
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26451 | 109 | P23:345:XEL:196 BKR SPK AS
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26448 | 105.7 | P23:345:XEL:196 BKR SPK AS
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25036 | 102.18 | P23:345:XEL:196 BKR SPK AS
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2523 | 125.22 | P23:345:XEL:396 BKR SPK
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25742 | 111.4 | P23:345:XEL:396 BKR SPK
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26982 | 109.46 | P23:345:XEL:396 BKR SPK
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26979 | 105.62 | P23:345:XEL:396 BKR SPK
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25571 | 104 | P23:345:XEL:396 BKR SPK
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24886 | 122.65 | P23:345:XEL:492 BKR SPK AS
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25353 | 108.61 | P23:345:XEL:492 BKR SPK AS
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26601 | 106.91 | P23:345:XEL:492 BKR SPK AS
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25183 | 101.11 | P23:345:XEL:492 BKR SPK AS
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24614 | 118.96 | P23:345:XEL:8E5 ECL BS
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25028 | 106.04 | P23:345:XEL:8E5 ECL BS
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26291 | 103.92 | P23:345:XEL:8E5 ECL BS
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2629 | 100.85 | P23:345:XEL:8E5 ECL BS
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24542 | 116.61 | P23:345:XEL:8N17 SHC
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24942 | 103.19 | P23:345:XEL:8N17 SHC
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24543 | 108.27 | P23:345:XEL:8N22 SHC
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24544 | 116.28 | P23:345:XEL:8N28 SHC
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24543 | 115.96 | P23:345:XEL:8N8 MNN
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24944 | 102.72 | P23:345:XEL:8N8 MNN
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.79 | P23:345:XEL:8P1 KING
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.62 | P23:345:XEL:8P1 KING
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.77 | P23:345:XEL:8P2 KING
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24943 | 103.22 | P23:345:XEL:8P2 KING
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24634 | 120.09 | P23:345:XEL:8P5 KING
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25054 | 107.28 | P23:345:XEL:8P5 KING
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26315 | 105 | P23:345:XEL:8P5 KING
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26314 | 101.57 | P23:345:XEL:8P5 KING
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2489 | 100.05 | P23:345:XEL:8P5 KING
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24633 | 120.01 | P23:345:XEL:8P6 KING
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25055 | 107.35 | P23:345:XEL:8P6 KING
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26315 | 105.04 | P23:345:XEL:8P6 KING
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26314 | 101.58 | P23:345:XEL:8P6 KING
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.262 | 100.69 | P23:345:XEL:8S22 WLM
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.262 | 101.01 | P23:345:XEL:8S23 WLM
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.38 | P23:345:XEL:8S24 WLM AS
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.96 | P23:345:XEL:8S24 WLM AS
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24583 | 115.35 | P23:345:XEL:8S25 WLM AS
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24973 | 100.96 | P23:345:XEL:8S25 WLM AS
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24583 | 115.34 | P23:345:XEL:8S27 WLM AS
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24973 | 100.96 | P23:345:XEL:8S27 WLM AS
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.92 | P23:345:XEL:8S31 LFD
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25007 | 101.2 | P23:345:XEL:8S72 HNA
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24582 | 115.44 | P23:345:XEL:8S81 SSL
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24973 | 100.45 | P23:345:XEL:8S81 SSL
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24582 | 115.44 | P23:345:XEL:8S82 & 8S79 SSL
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24973 | 100.45 | P23:345:XEL:8S82 & 8S79 SSL
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24582 | 115.44 | P23:345:XEL:8S82 SSL
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24973 | 100.45 | P23:345:XEL:8S82 SSL
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24642 | 117.8 | P23:345:XEL:8S97 NRH
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24625 | 117.82 | P23:345:XEL:8S98 NRH
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24748 | 120.93 | P23:345:XEL:8X24 NOB
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2517 | 107.14 | P23:345:XEL:8X24 NOB
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26433 | 105.6 | P23:345:XEL:8X24 NOB
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26433 | 102.04 | P23:345:XEL:8X24 NOB
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24748 | 120.93 | P23:345:XEL:8X25 NOB
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2517 | 107.14 | P23:345:XEL:8X25 NOB
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26433 | 105.6 | P23:345:XEL:8X25 NOB
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26433 | 102.04 | P23:345:XEL:8X25 NOB
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24612 | 118.77 | P23:345:XEL:ARPIN:ARP_424-S
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25025 | 105.86 | P23:345:XEL:ARPIN:ARP_424-S
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26288 | 103.72 | P23:345:XEL:ARPIN:ARP_424-S
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26287 | 100.65 | P23:345:XEL:ARPIN:ARP_424-S
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25008 | 101.81 | P23:345:XEL:SPS 8S72 HNA
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24582 | 115.44 | P23:345:XEL:SPS 8S81 SSL
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24973 | 101.07 | P23:345:XEL:SPS 8S81 SSL
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24626 | 117.79 | P23:345:XEL-SMMPA:8H8 PRI AS
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24626 | 117.9 | P23:345:XEL-SMMPA:8H9 PRI AS
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26265 | 102.32 | P23:500:EES-EAI:ARK_NU:B5106
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24966 | 102.49 | P23:500:EES-EAI:KEO:B4921
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26236 | 100.97 | P23:500:EES-EAI:KEO:B4921
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2497 | 102.4 | P23:500:EES-EAI:KEO:B4941
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26241 | 100.87 | P23:500:EES-EAI:KEO:B4941
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24749 | 120.86 | P24:161-345:ITCM:LAKEFLD 8160 T1:MN
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2517 | 107.06 | P24:161-345:ITCM:LAKEFLD 8160 T1:MN
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26434 | 105.52 | P24:161-345:ITCM:LAKEFLD 8160 T1:MN
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26434 | 102 | P24:161-345:ITCM:LAKEFLD 8160 T1:MN
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24777 | 120.89 | P24:345:ITCM:LAKEFLD 885 FUT:MN
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25313 | 109.15 | P24:345:ITCM:LAKEFLD 885 FUT:MN
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26473 | 105.74 | P24:345:ITCM:LAKEFLD 885 FUT:MN
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26473 | 102.08 | P24:345:ITCM:LAKEFLD 885 FUT:MN
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25144 | 100.85 | P24:345:ITCM:LAKEFLD 885 FUT:MN
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24631 | 120 | P24:345:XEL:8E7 ECL BS
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2505 | 107.24 | P24:345:XEL:8E7 ECL BS
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26311 | 104.98 | P24:345:XEL:8E7 ECL BS
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2631 | 101.55 | P24:345:XEL:8E7 ECL BS
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24631 | 120 | P24:345:XEL:8E7 ECL BS SPS
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2505 | 107.24 | P24:345:XEL:8E7 ECL BS SPS
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26311 | 104.98 | P24:345:XEL:8E7 ECL BS SPS
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2631 | 101.55 | P24:345:XEL:8E7 ECL BS SPS
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25019 | 105.78 | P24:500:MP:FBS:601LX
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26265 | 103.54 | P24:500:MP:FBS:601LX
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.35 | P41:345:AEPW:NES CB 3413B NBTB+FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.94 | P41:345:AEPW:NES CB 3413B NBTB+FAULT
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24938 | 103.37 | P41:345:AEPW:NES CB 3417B NBTB+FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26204 | 101.95 | P41:345:AEPW:NES CB 3417B NBTB+FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.52 | P41:345:OKGE:SB_MUGE7384
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26237 | 101.37 | P41:345:OKGE:SB_MUGE7385
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.68 | P41:345:OKGE:SB_REUD7381
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.68 | P41:345:OKGE:SB_REUD7383
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.08 | P41:345:OKGE:SB_SEOL7382
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.65 | P41:345:OKGE:SB_SEOL7382
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.08 | P41:345:OKGE:SB_SEOL7383
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26205 | 101.66 | P41:345:OKGE:SB_SEOL7383
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.55 | P41:345:OKGE:SB_SOER7382
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.14 | P41:345:OKGE:SB_SOER7382
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.72 | P41:345:OKGE:SB_SOER7382
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24941 | 103.49 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26207 | 102.14 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.5 | P42:345:AEPW:RIVERSIDE CB 3433A NBTB+FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 102.14 | P42:345:AEPW:RIVERSIDE CB 3433A NBTB+FAULT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24664 | 118.34 | P42:345:ITCM:HUNTLEY3-LAKEFLD3 3651-3654:IA-MVP
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25034 | 104.45 | P42:345:ITCM:HUNTLEY3-LAKEFLD3 3651-3654:IA-MVP
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2635 | 103.27 | P42:345:ITCM:HUNTLEY3-LAKEFLD3 3651-3654:IA-MVP
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2457 | 117.69 | P42:345:ITCM:KILLDEER3-COLBY3 3821-3822:IA-MVP
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2624 | 102.96 | P42:345:ITCM:KILLDEER3-COLBY3 3821-3822:IA-MVP
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24645 | 117.96 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25017 | 104.01 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26329 | 102.98 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24323 | 115.65 | P42:345:NPPD:BKR-AXT-3302
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24803 | 102.26 | P42:345:NPPD:BKR-AXT-3302
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25995 | 100.33 | P42:345:NPPD:BKR-AXT-3302
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24409 | 115.68 | P42:345:NPPD:BKR-AXT-3308
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24842 | 102.04 | P42:345:NPPD:BKR-AXT-3308
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26085 | 100.1 | P42:345:NPPD:BKR-AXT-3308
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24596 | 115.69 | P42:345:NPPD:BKR-CPR-3304
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2495 | 102.3 | P42:345:NPPD:BKR-CPR-3304
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.23697 | 113.87 | P42:345:NPPD:BKR-GGS-3310
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24877 | 104.04 | P42:345:NPPD:BKR-GGS-3310
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25224 | 103.32 | P42:345:NPPD:BKR-GGS-3310
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25231 | 100.01 | P42:345:NPPD:BKR-GGS-3310
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26172 | 102.34 | P42:345:NPPD:BKR-GGS-3316
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26071 | 100.84 | P42:345:NPPD:BKR-GGS-3322
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2363 | 111.15 | P42:345:NPPD:BKR-HOS-3308
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.23531 | 100.6 | P42:345:NPPD:BKR-HOS-3308
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24724 | 106.77 | P42:345:NPPD:BKR-HOS-3310
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26081 | 105.01 | P42:345:NPPD:BKR-HOS-3310
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26071 | 102.16 | P42:345:NPPD:BKR-HOS-3310
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24717 | 106.49 | P42:345:NPPD:BKR-HOS-3312
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26066 | 104.77 | P42:345:NPPD:BKR-HOS-3312
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26058 | 101.88 | P42:345:NPPD:BKR-HOS-3312
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24778 | 101.14 | P42:345:NPPD:BKR-HOS-3322
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26126 | 100.33 | P42:345:NPPD:BKR-HOS-3322
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24703 | 118.28 | P42:345:NPPD:BKR-KEY-3310
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2511 | 107.18 | P42:345:NPPD:BKR-KEY-3310
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26338 | 106.19 | P42:345:NPPD:BKR-KEY-3310
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2634 | 102.96 | P42:345:NPPD:BKR-KEY-3310
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24911 | 100.24 | P42:345:NPPD:BKR-KEY-3310
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24141 | 113.57 | P42:345:NPPD:BKR-MOR-3306
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24532 | 101.2 | P42:345:NPPD:BKR-MOR-3306
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24152 | 113.63 | P42:345:NPPD:BKR-MOR-3310
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24523 | 101.25 | P42:345:NPPD:BKR-MOR-3310
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24535 | 115.52 | P42:345:NPPD:BKR-PLN-3310
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25843 | 100.5 | P42:345:NPPD:BKR-RW-3302
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24802 | 102.02 | P42:345:NPPD:BKR-SC-3306
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26048 | 100.38 | P42:345:NPPD:BKR-SW-3304
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24373 | 105 | P42:345:NPPD:BKR-SW-3306
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26011 | 102.4 | P42:345:NPPD:BKR-SW-3306
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24371 | 105.09 | P42:345:NPPD:BKR-SW-3308
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26009 | 102.31 | P42:345:NPPD:BKR-SW-3308
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26043 | 100.43 | P42:345:NPPD:BKR-SW-3310
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24541 | 116.72 | P42:345:OKGE:SB_BVTY7305
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24541 | 116.8 | P42:345:OKGE:SB_BVTY7387
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.48 | P42:345:OKGE:SB_CION7384
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24536 | 116.48 | P42:345:OKGE:SB_TAGA7386
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24873 | 120.27 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25291 | 107.01 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2658 | 106.21 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26576 | 102.89 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25128 | 100.68 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2454 | 116.35 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 101.63 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.27742 | 112.39 | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25034 | 104.44 | P42:345:UMZB:# 2495 #: LO IN ND. STUCK BREAKER (2396)
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26305 | 103 | P42:345:UMZB:# 2495 #: LO IN ND. STUCK BREAKER (2396)
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2497 | 105.07 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26235 | 103.8 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26235 | 100.54 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24991 | 102.48 | P42:345:UMZB:# 2514 #: BD IN SD. BREAKER FAULT (192)
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26259 | 100.9 | P42:345:UMZB:# 2514 #: BD IN SD. BREAKER FAULT (192)
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26265 | 102.28 | P42:500:OKGE:SB_FTTH8581
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26265 | 102.31 | P42:500:OKGE:SB_FTTH8583
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26265 | 102.28 | P42:500:OKGE:SB_FTTH8585
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.93 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 102.53 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24605 | 118.11 | P43:161-345:ITCM:ARNOLD 3 2820 T1:IA
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25022 | 104.32 | P43:161-345:ITCM:ARNOLD 3 2820 T1:IA
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2628 | 102.68 | P43:161-345:ITCM:ARNOLD 3 2820 T1:IA
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24584 | 117.34 | P43:161-345:ITCM-MEC:HILLS 3 984 T1:IA
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24584 | 117.34 | P43:161-345:ITCM-MEC:HILLS 3 984 T1:IA(1)
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24873 | 120.27 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25291 | 107.01 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2658 | 106.21 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26576 | 102.89 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25128 | 100.68 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24627 | 117.24 | P44:345:ITCM-MEC:LAKEFLD 873 50MVAR:MN-SS
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24873 | 120.27 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25291 | 107.01 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2658 | 106.21 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26576 | 102.89 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25128 | 100.68 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24873 | 120.27 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25291 | 107.01 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2658 | 106.21 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26576 | 102.89 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25128 | 100.68 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24566 | 122.38 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26257 | 117.68 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24988 | 117.28 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26256 | 114.4 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24838 | 107.83 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 15ALL | 2 | 24WP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2591 | 102.78 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24496 | 115.47 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24867 | 102.28 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.94 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 102.54 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.2494 | 103.94 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26206 | 102.54 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24612 | 118.8 | P55:345:ATC:ARPIN
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25025 | 105.86 | P55:345:ATC:ARPIN
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26288 | 103.72 | P55:345:ATC:ARPIN
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26287 | 100.66 | P55:345:ATC:ARPIN
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.24659 | 119.76 | P55:345:ITCM:MITCHLCO3 N9-N10:IA
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.25091 | 105.77 | P55:345:ITCM:MITCHLCO3 N9-N10:IA
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26343 | 103.82 | P55:345:ITCM:MITCHLCO3 N9-N10:IA
Thermal | 15ALL | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.26342 | 100.6 | P55:345:ITCM:MITCHLCO3 N9-N10:IA
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 |  | 0.2454 | 116.52 | System Intact
Thermal | 15ALL | 2 | 24L | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 |  | 0.16701 | 116.52 | System Intact
Thermal | 15ALL | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 |  | 0.2494 | 103.12 | System Intact
Thermal | 15ALL | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 |  | 0.17382 | 103.12 | System Intact
Thermal | 15ALL | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 |  | 0.26206 | 101.62 | System Intact
Thermal | 15ALL | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 |  | 0.18367 | 101.62 | System Intact
Non-Converge | 16ALL | 0 |  |  | '' | None |  |  |  |  | None
Thermal | 16ALL | 2 | 29SP | GEN-2017-010 | 'FROM -> TO' | 659120 BROADLND-BE3 345 997093 BD KU2A 230 1 | 400 |  | 0.09675 | 108.83 | System Intact
Thermal | 16ALL | 2 | 29SP | GEN-2017-048 | 'FROM -> TO' | 659120 BROADLND-BE3 345 997093 BD KU2A 230 1 | 400 |  | 0.12528 | 108.83 | System Intact
Thermal | 16ALL | 2 | 24SP | GEN-2017-010 | 'FROM -> TO' | 659120 BROADLND-BE3 345 997094 BD KU2A 230 1 | 400 |  | 0.09626 | 112.41 | System Intact
Thermal | 16ALL | 2 | 24SP | GEN-2017-048 | 'FROM -> TO' | 659120 BROADLND-BE3 345 997094 BD KU2A 230 1 | 400 |  | 0.1248 | 112.41 | System Intact
Thermal | 16ALL | 2 | 20SP | GEN-2017-010 | 'FROM -> TO' | 659120 BROADLND-BE3 345 997103 BD KU2A 230 1 | 400 |  | 0.09423 | 109.59 | System Intact
Thermal | 16ALL | 2 | 20SP | GEN-2017-048 | 'FROM -> TO' | 659120 BROADLND-BE3 345 997103 BD KU2A 230 1 | 400 |  | 0.12169 | 109.59 | System Intact
Thermal | 16ALL | 2 | 24SP | GEN-2017-048 | 'FROM -> TO' | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z |  | 506 | 0.8888 | 140.65 | P12:345:UMZ:# 5868 #: IN . PROPER N-1 (LINE) FOR 659336-659427-Z
Thermal | 16ALL | 2 | 29SP | GEN-2017-048 | 'FROM -> TO' | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z |  | 506 | 0.88883 | 139.83 | P12:345:UMZ:# 5868 #: IN . PROPER N-1 (LINE) FOR 659336-659427-Z
Thermal | 16ALL | 2 | 20SP | GEN-2017-048 | 'FROM -> TO' | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z |  | 506 | 0.88892 | 139.69 | P12:345:UMZ:# 5868 #: IN . PROPER N-1 (LINE) FOR 659336-659427-Z
Thermal | 16ALL | 2 | 24L | GEN-2017-048 | 'FROM -> TO' | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z |  | 506 | 0.88903 | 139.31 | P12:345:UMZ:# 5868 #: IN . PROPER N-1 (LINE) FOR 659336-659427-Z
Thermal | 16ALL | 2 | 20G | GEN-2017-048 | 'FROM -> TO' | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z |  | 506 | 0.889 | 138.14 | P12:345:UMZ:# 5868 #: IN . PROPER N-1 (LINE) FOR 659336-659427-Z
Thermal | 16ALL | 2 | 24WP | GEN-2017-048 | 'FROM -> TO' | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z |  | 526 | 0.88879 | 131.97 | P12:345:UMZ:# 5868 #: IN . PROPER N-1 (LINE) FOR 659336-659427-Z
Thermal | 16ALL | 2 | 19WP | GEN-2017-048 | 'FROM -> TO' | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z |  | 526 | 0.88881 | 130.62 | P12:345:UMZ:# 5868 #: IN . PROPER N-1 (LINE) FOR 659336-659427-Z
Thermal | 16ALL | 2 | 24SP | GEN-2017-048 | 'FROM -> TO' | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z |  | 506 | 0.8888 | 140.65 | P23:345:UMZB:# 3708 #: JDM IN ND. BREAKER FAULT JUDSON (696)
Thermal | 16ALL | 2 | 29SP | GEN-2017-048 | 'FROM -> TO' | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z |  | 506 | 0.88883 | 139.83 | P23:345:UMZB:# 3708 #: JDM IN ND. BREAKER FAULT JUDSON (696)
Thermal | 16ALL | 2 | 20SP | GEN-2017-048 | 'FROM -> TO' | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z |  | 506 | 0.88892 | 139.69 | P23:345:UMZB:# 3708 #: JDM IN ND. BREAKER FAULT JUDSON (696)
Thermal | 16ALL | 2 | 24L | GEN-2017-048 | 'FROM -> TO' | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z |  | 506 | 0.88903 | 139.31 | P23:345:UMZB:# 3708 #: JDM IN ND. BREAKER FAULT JUDSON (696)
Thermal | 16ALL | 2 | 20G | GEN-2017-048 | 'FROM -> TO' | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z |  | 506 | 0.889 | 138.14 | P23:345:UMZB:# 3708 #: JDM IN ND. BREAKER FAULT JUDSON (696)
Thermal | 16ALL | 2 | 24WP | GEN-2017-048 | 'FROM -> TO' | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z |  | 526 | 0.88879 | 131.97 | P23:345:UMZB:# 3708 #: JDM IN ND. BREAKER FAULT JUDSON (696)
Thermal | 16ALL | 2 | 19WP | GEN-2017-048 | 'FROM -> TO' | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z |  | 526 | 0.88881 | 130.62 | P23:345:UMZB:# 3708 #: JDM IN ND. BREAKER FAULT JUDSON (696)
Thermal | 16ALL | 2 | 29SP | GEN-2017-010 | 'FROM -> TO' | 659205 BROADLND-BE4 230 997093 BD KU2A 230 1 | 400 |  | 0.09675 | 113.27 | System Intact
Thermal | 16ALL | 2 | 29SP | GEN-2017-048 | 'FROM -> TO' | 659205 BROADLND-BE4 230 997093 BD KU2A 230 1 | 400 |  | 0.12528 | 113.27 | System Intact
Thermal | 16ALL | 2 | 24SP | GEN-2017-010 | 'FROM -> TO' | 659205 BROADLND-BE4 230 997094 BD KU2A 230 1 | 400 |  | 0.09626 | 117.6 | System Intact
Thermal | 16ALL | 2 | 24SP | GEN-2017-048 | 'FROM -> TO' | 659205 BROADLND-BE4 230 997094 BD KU2A 230 1 | 400 |  | 0.1248 | 117.6 | System Intact
Thermal | 16ALL | 2 | 20SP | GEN-2017-010 | 'FROM -> TO' | 659205 BROADLND-BE4 230 997103 BD KU2A 230 1 | 400 |  | 0.09423 | 114.17 | System Intact
Thermal | 16ALL | 2 | 20SP | GEN-2017-048 | 'FROM -> TO' | 659205 BROADLND-BE4 230 997103 BD KU2A 230 1 | 400 |  | 0.12169 | 114.17 | System Intact
Thermal | 16ALL | 2 | 20G | GEN-2017-010 | 'FROM -> TO' | 659205 BROADLND-BE4 230 997109 BD KU2A 230 1 | 400 |  | 0.08907 | 100.16 | System Intact
Thermal | 16ALL | 2 | 20G | GEN-2017-048 | 'FROM -> TO' | 659205 BROADLND-BE4 230 997109 BD KU2A 230 1 | 400 |  | 0.11653 | 100.16 | System Intact
Thermal | 16ALL | 2 | 24SP | GEN-2017-010 | 'FROM -> TO' | 661091 NAPOLEON SW4 230 661094 WISHEK 4 230 1 | 343 |  | 0.08504 | 118.58 | System Intact
Thermal | 16ALL | 2 | 24SP | GEN-2017-048 | 'FROM -> TO' | 661091 NAPOLEON SW4 230 661094 WISHEK 4 230 1 | 343 |  | 0.0871 | 118.58 | System Intact
Thermal | 16ALL | 2 | 20SP | GEN-2017-010 | 'FROM -> TO' | 661091 NAPOLEON SW4 230 661094 WISHEK 4 230 1 | 343 |  | 0.08225 | 110.03 | System Intact
Thermal | 16ALL | 2 | 20SP | GEN-2017-048 | 'FROM -> TO' | 661091 NAPOLEON SW4 230 661094 WISHEK 4 230 1 | 343 |  | 0.08299 | 110.03 | System Intact
Thermal | 16ALL | 2 | 29SP | GEN-2017-010 | 'FROM -> TO' | 661091 NAPOLEON SW4 230 661094 WISHEK 4 230 1 | 343 |  | 0.08567 | 108.35 | System Intact
Thermal | 16ALL | 2 | 29SP | GEN-2017-048 | 'FROM -> TO' | 661091 NAPOLEON SW4 230 661094 WISHEK 4 230 1 | 343 |  | 0.08772 | 108.35 | System Intact
Thermal | 16ALL | 2 | 24SP | GEN-2017-010 | 'FROM -> TO' | 661093 MERRCRT4 230 661094 WISHEK 4 230 1 | 343 |  | 0.08504 | 116.79 | System Intact
Thermal | 16ALL | 2 | 24SP | GEN-2017-048 | 'FROM -> TO' | 661093 MERRCRT4 230 661094 WISHEK 4 230 1 | 343 |  | 0.0871 | 116.79 | System Intact
Thermal | 16ALL | 2 | 20SP | GEN-2017-010 | 'FROM -> TO' | 661093 MERRCRT4 230 661094 WISHEK 4 230 1 | 343 |  | 0.08225 | 108.41 | System Intact
Thermal | 16ALL | 2 | 20SP | GEN-2017-048 | 'FROM -> TO' | 661093 MERRCRT4 230 661094 WISHEK 4 230 1 | 343 |  | 0.08299 | 108.41 | System Intact
Thermal | 16ALL | 2 | 29SP | GEN-2017-010 | 'FROM -> TO' | 661093 MERRCRT4 230 661094 WISHEK 4 230 1 | 343 |  | 0.08567 | 106.43 | System Intact
Thermal | 16ALL | 2 | 29SP | GEN-2017-048 | 'FROM -> TO' | 661093 MERRCRT4 230 661094 WISHEK 4 230 1 | 343 |  | 0.08772 | 106.43 | System Intact
Non-Converge | 17ALL | 0 | 19WP | GEN-2017-014 | '' | Non-Converge |  |  | 0.6801 |  | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Non-Converge | 17ALL | 0 | 19WP | GEN-2017-014 | '' | Non-Converge |  |  | 0.51375 |  | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Non-Converge | 17ALL | 0 | 19WP | GEN-2017-014 | '' | Non-Converge |  |  | 0.16636 |  | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Non-Converge | 17ALL | 0 | 20G | GEN-2017-014 | '' | Non-Converge |  |  | 0.67999 |  | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Non-Converge | 17ALL | 0 | 20G | GEN-2017-014 | '' | Non-Converge |  |  | 0.51359 |  | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Non-Converge | 17ALL | 0 | 20G | GEN-2017-014 | '' | Non-Converge |  |  | 0.16641 |  | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Non-Converge | 17ALL | 0 | 20SP | GEN-2017-014 | '' | Non-Converge |  |  | 0.68023 |  | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Non-Converge | 17ALL | 0 | 20SP | GEN-2017-014 | '' | Non-Converge |  |  | 0.51384 |  | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Non-Converge | 17ALL | 0 | 20SP | GEN-2017-014 | '' | Non-Converge |  |  | 0.16639 |  | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Non-Converge | 17ALL | 0 | 19WP | GEN-2017-064 | '' | Non-Converge |  |  | 0.28073 |  | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Non-Converge | 17ALL | 0 | 19WP | GEN-2017-064 | '' | Non-Converge |  |  | 0.281 |  | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Non-Converge | 17ALL | 0 | 20G | GEN-2017-064 | '' | Non-Converge |  |  | 0.28062 |  | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Non-Converge | 17ALL | 0 | 20G | GEN-2017-064 | '' | Non-Converge |  |  | 0.28084 |  | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Non-Converge | 17ALL | 0 | 20SP | GEN-2017-064 | '' | Non-Converge |  |  | 0.28086 |  | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Non-Converge | 17ALL | 0 | 20SP | GEN-2017-064 | '' | Non-Converge |  |  | 0.28109 |  | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Non-Converge | 17ALL | 0 | 19WP | GEN-2017-097 | '' | Non-Converge |  |  | 0.33384 |  | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Non-Converge | 17ALL | 0 | 19WP | GEN-2017-097 | '' | Non-Converge |  |  | 0.34376 |  | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Non-Converge | 17ALL | 0 | 20G | GEN-2017-097 | '' | Non-Converge |  |  | 0.33373 |  | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Non-Converge | 17ALL | 0 | 20G | GEN-2017-097 | '' | Non-Converge |  |  | 0.3436 |  | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Non-Converge | 17ALL | 0 | 20SP | GEN-2017-097 | '' | Non-Converge |  |  | 0.33396 |  | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Non-Converge | 17ALL | 0 | 20SP | GEN-2017-097 | '' | Non-Converge |  |  | 0.34386 |  | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 17ALL | 2 | 20G | GEN-2017-064 | 'FROM -> TO' | 640184 GENTLMN4 230 640302 OGALALA4 230 1 |  | 320 | 0.23469 | 102.46 | P42:345:NPPD:BKR-KEY-3310
Thermal | 17ALL | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.23768 | 121.79 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 17ALL | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.23459 | 121.36 | P42:345:NPPD:BKR-KEY-3310
Thermal | 17ALL | 2 | 20G | GEN-2017-064 | 'FROM -> TO' | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.22822 | 120.11 | P42:345:NPPD:BKR-KEY-3310
Thermal | 17ALL | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.23484 | 120.07 | P42:345:NPPD:BKR-KEY-3310

## All Voltage
SOLUTIONTYPE | GROUP | SCENARIO | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME
Voltage | 01ALL | 3 |  |  | None | [7 empty] | None
Voltage | 02ALL | 3 |  |  | None | [7 empty] | None
Voltage | 03ALL | 3 |  |  | None | [7 empty] | None
Voltage | 04ALL | 3 |  |  | None | [7 empty] | None
Voltage | 06ALL | 3 |  |  | None | [7 empty] | None
Voltage | 07ALL | 3 |  |  | None | [7 empty] | None
Voltage | 08ALL | 3 |  |  | None | [7 empty] | None
Voltage | 09ALL | 3 |  |  | None | [7 empty] | None
Voltage | 10ALL | 3 |  |  | None | [7 empty] | None
Voltage | 12ALL | 3 |  |  | None | [7 empty] | None
Voltage | 13ALL | 3 |  |  | None | [7 empty] | None
Voltage | 14ALL | 3 |  |  | None | [7 empty] | None
Voltage | 15ALL | 3 |  |  | None | [7 empty] | None
Voltage | 16ALL | 3 |  |  | None | [7 empty] | None
Voltage | 17ALL | 3 |  |  | None | [7 empty] | None

## Short Circuit Ratio
Study Request | Current Cluster | Cluster Group | Transmission Owner | Capacity | Service Type | Generation Type | Point of Interconnection | GEN Bus # | Gen ID | POI Bus # | DIS1701TC01ALL-24WP0.SAV |  | DIS1701TC01ALL-29SP0.SAV |  | DIS1701TC02ALL-24WP0.SAV |  | DIS1701TC02ALL-29SP0.SAV |  | DIS1701TC03ALL-24WP0.SAV |  | DIS1701TC03ALL-29SP0.SAV |  | DIS1701TC04ALL-24WP0.SAV |  | DIS1701TC04ALL-29SP0.SAV |  | DIS1701TC06ALL-24WP0.SAV |  | DIS1701TC06ALL-29SP0.SAV |  | DIS1701TC07ALL-24WP0.SAV |  | DIS1701TC07ALL-29SP0.SAV |  | DIS1701TC08ALL-24WP0.SAV |  | DIS1701TC08ALL-29SP0.SAV |  | DIS1701TC09ALL-24WP0.SAV |  | DIS1701TC09ALL-29SP0.SAV |  | DIS1701TC10ALL-24WP0.SAV |  | DIS1701TC10ALL-29SP0.SAV |  | DIS1701TC12ALL-24WP0.SAV |  | DIS1701TC12ALL-29SP0.SAV |  | DIS1701TC13ALL-24WP0.SAV |  | DIS1701TC13ALL-29SP0.SAV |  | DIS1701TC14ALL-24WP0.SAV |  | DIS1701TC14ALL-29SP0.SAV |  | DIS1701TC15ALL-24WP0.SAV |  | DIS1701TC15ALL-29SP0.SAV |  | DIS1701TC16ALL-24WP0.SAV |  | DIS1701TC16ALL-29SP0.SAV |  | DIS1701TC17ALL-24WP0.SAV |  | DIS1701TC17ALL-29SP0.SAV
[11 empty] | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio
Short Circuit Ratio calculation not applicable in DISIS Phase 2.